## OGE Safety Data Incidents Creat
Incident Management Data
OGE Safety Data Incidents Created in Last Month
Incident No. | Location | Date of Occurrence | Incident Description | Incident Level | Possible Serious Injury / Fatality | Near Miss? | Incident Type | Approving VP/Director | Assign for Investigation Assigned By | Assign for Investigation Comment | Assign for Investigation Date Assigned | Business Unit | Created By | Date Closed | Date Created | Date First Report Sent | Date Investigated | Date Investigation Due | Date Reported | Date Reviewed | Date Safety Mgr Reviewed | Date Safety Professional Reviewed | Describe Location | EMS Called | EMS Arrived | Final Approval Approved By | Final Approval Comment | Functional Area | Immediate Corrective Action Taken | Incident Level | Incident Type | Incident Type Clearance LOTO | Incident Type Contractor | Incident Type Member Injury | Incident Type Property Damage | Incident Type Switching | Incident Type System Operation | Incident Type Vehicle | Investigated By | Investigation Completion | Investigation Results | Investigation Team | Investigation Team Lead | Is the injury related to a previously reported First Aid Incident? | Location | Mark Confidential? | Nature of Injury (Aggregate) | Near Miss? | OGE Department | Provide the Incident No. of the previously reported First Aid Incident. | Reported By | Reported To | Responsible Safety Professional | Reviewed By | Reviewer Comment | Reviewing Manager | Reviewing Safety Manager | Risk Ranking | RC - 01. Inadequate Physical/Physiological Capability | RC - 02. Inadequate Mental/Psychological Capability | RC - 03. Physical or Physiological Stress | RC - 04. Mental or Psychological Stress | RC - 05. Lack of Knowledge | RC - 06. Lack of Skill | RC - 07. Improper Motivation | RC - 08. Abuse or Misuse | RC - 09. Inadequate Leadership and/or Supervision | RC - 10. Inadequate Engineering | RC - 11. Inadequate Purchasing | RC - 12. Inadequate Maintenance | RC - 13. Inadequate Tools and Equipment | RC - 14. Inadequate Work Standards | RC - 15. Excessive Wear and Tear | RC - 16. Inadequate Communications | RC - Cause Description | RC - Immediate/Direct Cause | RC - Type of Event | Safety Manager Review Comments | Safety Professional Review Comments | Second Investigator | Shift | Contractor - Capital Projects | Contractor - Contractor Incident Type | Contractor - Contractor Injury | Contractor - Created By | Contractor - Description of Damage | Contractor - Description of Injury | Contractor - EMR Activated? | Contractor - EMS Arrived | Contractor - EMS Called | Contractor - Event Type | Contractor - Individual Reporting | Contractor - Name of Contractor Company | Contractor - Name of Contractor Employee | Contractor - Nature of Injury | Contractor - Nature of Property Damage | Contractor - Primary Body Part Injured | Contractor - Responsible Person/OGE Contact | Contractor - Side of Body | Contractor - Taken To Hospital | Contractor - Transportation Method | Contractor - Vehicle/Equipment No. | Contractor - Was OGE Vehicle or Equipment Involved? | Injury - Body Fluid Exposure? | Injury - Body Parts | Injury - Case Classification | Injury - Date Hired (Hidden) | Injury - Date of Birth (Hidden) | Injury - Date of Death | Injury - Date/Time member began work | Injury - Days Away From Work | Injury - Days on Job Transfer or Restriction | Injury - Details of First Aid | Injury - EMR Activated? | Injury - Gender | Injury - How did the injury occur? | Injury - If treatment was given away from the worksite, where was it given? | Injury - Initial treatment given? | Injury - Injured Party | Injury - Injury Classification | Injury - Injury Status | Injury - Member Name (Hidden) | Injury - Member taken to hospital | Injury - Name and Address of Hospital/Doctor | Injury - Name of Facility | Injury - Name of Health Care Professional | Injury - Nature of Injury/Illness | Injury - Notes | Injury - OSHA Recordable? | Injury - Person(s) Exposed | Injury - Position (Hidden) | Injury - Primary Body Part Injured | Injury - Select 'Injury' or choose Illness Type (M) | Injury - Side of Body | Injury - Southeast Electric Exchange (SEE) | Injury - Supervisor | Injury - Team$hare | Injury - Team$hare Year | Injury - Time Began Work (Text) | Injury - Time on job | Injury - Treatment given away from worksite? | Injury - Was member hospitalized overnight as an in patient? | Injury - Was member treated in an emergency room? | Injury - What object or substance directly harmed the member? | Injury - What was the member doing just before the incident occurred? | Prop Dmg - Description of Damage | Prop Dmg - Estimated Cost | Prop Dmg - Member Name (Hidden) | Prop Dmg - Nature of Property Damage | Prop Dmg - Person(s) Involved | Vehicle - Vehicle/Equipment Number | Vehicle - Chargeable | Vehicle - Citation Issued | Vehicle - City | Vehicle - Collision Type | Vehicle - Collision Type (Secondary) | Vehicle - Date Hired (Hidden) | Vehicle - Description Of Damage | Vehicle - DOT Incident | Vehicle - Driver Condition | Vehicle - Driver's Name | Vehicle - Light Conditions | Vehicle - Number of Fatalities | Vehicle - Number of Injuries | Vehicle - Surface Type | Vehicle - Vehicle No. | Vehicle - Weather Condition | Vehicle - Were any vehicles towed as a result of this incident? | Vehicle - Were hazardous materials released, other than fuel spilled from the fuel tanks of motor vehicles involved in the accident? | Work Order #
8645 | Ada Service Center | 2019-01-03 01:00 | This is a First Aid incident. While doing a 360 before leaving home to go on a trouble call, member walked around the truck. While doing this member stepped on a landscaping timer. The timber had a fine layer of ice on them. Member slipped, fell to the ground, and landed on his left side. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Lyle Just | 2019-01-11 10:59 | 2019-01-03 07:40 | 2019-01-03 07:40 | 2019-01-03 07:56 | 2019-01-17 01:00 | 2019-01-03 07:29 | 2019-01-10 12:16 |  | 2019-01-07 12:45 | 11055 CR 3579 Ada |  |  | Lindle Coleman | this action item will be implemented in all of T&D and proposed for all the utility | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Lyle Just |  | This is a First Aid incident. While doing a 360 before leaving home to go on a trouble call, member walked around the truck. While doing this member stepped on a landscaping timer. The timber had a fine layer of ice on them. Member slipped, fell to the ground, and landed on his left side. Member stated he is okay and does not appear to be injured. Left wrist and ribs were impacted. |  |  | FALSE | Ada Service Center | FALSE |  | FALSE | Construction Services |  | Todd Janda | Lyle Just |  | Kenneth McKinzie | Approved | Kenneth McKinzie |  | Medium |  |  |  | 4.04 Routine, monotony, demand for uneventful vigilance | [12 empty] | This is a First Aid incident. While doing a 360 before leaving home to go on a trouble call, member walked around the truck. While doing this member stepped on a landscaping timer. The timber had a fine layer of ice on them. Member slipped, fell to the ground, and landed on his left side. | 17. Failure to Identify Hazard, Risk | 4. Fall on Same Level (Slip and Fall, Trip Over) |  | Reviewed/approved. Followed up with member on 01/07/19 at 12:30 PM and confirmed that he was doing fine. | [24 empty] | FALSE |  |  | 2016-01-04 | 1991-06-25 |  | 2019-01-03 01:00 | 0 | 0 |  | FALSE | Male | slipped on icy timber |  | FALSE | Todd Hudson |  | First Aid | Todd Hudson |  |  |  |  | Contusion |  | FALSE |  | Asset Mgmt Engineer | Abdomen |  | Left | FALSE | Lyle Just | FALSE |  | 1/3/2019 1:00:00 AM |  | FALSE |  |  | land scape timber | [25 empty] | N/A
8646 | South District Service Center | 2019-01-03 15:00 | Member was running extendo stick and felt a pop in his right shoulder resulting in discomfort. | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Joshua Fisk | 2019-01-03 18:44 | 2019-01-03 18:32 | 2019-01-03 18:32 | 2019-01-03 18:38 | 2019-01-17 15:00 | 2019-01-03 18:10 |  |  |  | SE 29th and Anderson Rd |  |  | Brent Perdue | This incident was reported promptly. I approve | T&D Ops |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | [5 empty] | FALSE | South District Service Center | FALSE |  | FALSE | Construction Services |  | Gary Duncan | Joshua Fisk |  |  |  | Jeffrey Gleim |  | Low | [45 empty] | FALSE |  |  | 2014-05-28 | 1979-11-12 |  | 2019-01-03 07:00 | 0 | 0 |  | FALSE | Male | Running extendo stick |  | FALSE | Gary Duncan |  | First Aid | Gary Duncan |  |  |  |  | Sprain/Strain |  | FALSE |  | Service Technician | Shoulder |  | Right | FALSE | Joshua Fisk | FALSE |  | 1/3/2019 7:00:00 AM |  | FALSE |  |  | Shoulder popped while running extendo stick
8647 | Sooner Power Plant | 2019-01-03 17:00 | Contract members were working on sump in reclaim area. Contract members filled out Confined Space Permit without filling out Pre-Entry Form. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Michael Dowell | 2019-01-30 09:31 | 2019-01-04 10:38 | 2019-01-04 10:38 | 2019-01-19 19:12 | 2019-01-17 17:00 | 2019-01-04 09:57 | 2019-01-21 14:17 |  |  | Sooner PP Fuel Supply Reclaim Sump |  |  | Brady Sowell | approved | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Michael Dowell |  | The crew was task to do work in a pump sump. The sump is classified as a permit required confined space. The employees obtained the proper permit confined space permit and took proper precautions and began the task. However the crew failed to obtain and complete a Confined Space pre-entry assessment form. Once the work was complete when the crew turned in the LOTO the customer rep. noticed a C/S pre-entry assessment form had not been completed and no tracking number assigned. Later that day this was brought to the attention of the G/F . The G/F did not see it as an incident or near miss only a mis-communication. Employees also stated they thought since they were treating it as a permit required confined space they did not think the pre-assessment form was required. The employees were in no danger and had taken all the necessary precautions. The process should flow as follows: Obtain and complete confined space pre-entry assessment form Have control room assign tracking number, log the confined space and sign onto LOTO, obtain clearance number. Go to confined space to complete Confined space entry form If all is in order as per all permit requirements. Then the work may proceed. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Lance Lantz | Michael Dowell |  | Kent Wilson | I added an additional Corrective Action based upon my review of SSOP 604.146. | Frank Brixey |  | Low |  |  |  |  | 5.03 Inadequate initial training | [11 empty] | Employees stated they thought since they were treating it as a permit required confined space they did not think the pre-assessment form was required. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Michael Dowell | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Lance Lantz | Zachary | Monty Brewer |  |  |  | Lance Lantz | [71 empty] | 9576008
8648 | Metro Service Center | 2019-01-04 12:30 | Contract Tree Worker tripped and/or slipped while pulling brush in snow and injured hip in fall. Transported by company vehicle for medical attention. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services |  | 2019-02-07 16:38 | 2019-01-04 13:32 | 2019-01-04 13:32 | 2019-01-31 18:29 | 2019-01-18 12:30 | 2019-01-04 13:23 | 2019-02-06 10:12 |  | 2019-02-04 16:46 | Residence 4100 S. Shatwell Rd, OKC |  |  | William Young | Reviewed contractor CA Alert and PowerPoint. Approved WCY 2/7/2019. | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | See Attachments |  |  |  | Metro Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | David Jones |  |  | Nicole Rhodes | Reviewed. | Nicole Rhodes |  | Medium |  |  |  | 4.08 Conflicting demands/directions | 5.01 Lack of experience | 6.02 Inadequate practice | 7.10 Inappropriate peer pressure |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Crew felt "rushed" due to outage situation. They took shortcuts. | 04. Operating at Improper Speed | 4. Fall on Same Level (Slip and Fall, Trip Over) |  | Approved. J. Looney |  |  |  | Injury / Illness |  |  |  | Dislocated hip | FALSE |  |  | 4. Fall on Same Level (Slip and Fall, Trip Over) | David Jones | Asplundh | Steven Martinez | Dislocation |  | Hip |  |  | TRUE | Company Vehicle | [68 empty] | none
8648 | Metro Service Center | 2019-01-04 12:30 | Contract Tree Worker tripped and/or slipped while pulling brush in snow and injured hip in fall. Transported by company vehicle for medical attention. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services |  | 2019-02-07 16:38 | 2019-01-04 13:32 | 2019-01-04 13:32 | 2019-01-31 18:29 | 2019-01-18 12:30 | 2019-01-04 13:23 | 2019-02-06 10:12 |  | 2019-02-04 16:46 | Residence 4100 S. Shatwell Rd, OKC |  |  | William Young | Reviewed contractor CA Alert and PowerPoint. Approved WCY 2/7/2019. | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | See Attachments |  |  |  | Metro Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | David Jones |  |  | Nicole Rhodes | Reviewed. | Nicole Rhodes |  | Medium |  |  |  | 4.08 Conflicting demands/directions | 5.01 Lack of experience | 6.02 Inadequate practice | 7.06 Improper attempt to save time or effort |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Crew felt "rushed" due to outage situation. They took shortcuts. | 04. Operating at Improper Speed | 4. Fall on Same Level (Slip and Fall, Trip Over) |  | Approved. J. Looney |  |  |  | Injury / Illness |  |  |  | Dislocated hip | FALSE |  |  | 4. Fall on Same Level (Slip and Fall, Trip Over) | David Jones | Asplundh | Steven Martinez | Dislocation |  | Hip |  |  | TRUE | Company Vehicle | [68 empty] | none
8648 | Metro Service Center | 2019-01-04 12:30 | Contract Tree Worker tripped and/or slipped while pulling brush in snow and injured hip in fall. Transported by company vehicle for medical attention. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services |  | 2019-02-07 16:38 | 2019-01-04 13:32 | 2019-01-04 13:32 | 2019-01-31 18:29 | 2019-01-18 12:30 | 2019-01-04 13:23 | 2019-02-06 10:12 |  | 2019-02-04 16:46 | Residence 4100 S. Shatwell Rd, OKC |  |  | William Young | Reviewed contractor CA Alert and PowerPoint. Approved WCY 2/7/2019. | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | See Attachments |  |  |  | Metro Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | David Jones |  |  | Nicole Rhodes | Reviewed. | Nicole Rhodes |  | Medium |  |  |  | 4.08 Conflicting demands/directions | 5.06 Lack of situational awareness | 6.02 Inadequate practice | 7.10 Inappropriate peer pressure |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Crew felt "rushed" due to outage situation. They took shortcuts. | 04. Operating at Improper Speed | 4. Fall on Same Level (Slip and Fall, Trip Over) |  | Approved. J. Looney |  |  |  | Injury / Illness |  |  |  | Dislocated hip | FALSE |  |  | 4. Fall on Same Level (Slip and Fall, Trip Over) | David Jones | Asplundh | Steven Martinez | Dislocation |  | Hip |  |  | TRUE | Company Vehicle | [68 empty] | none
8648 | Metro Service Center | 2019-01-04 12:30 | Contract Tree Worker tripped and/or slipped while pulling brush in snow and injured hip in fall. Transported by company vehicle for medical attention. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services |  | 2019-02-07 16:38 | 2019-01-04 13:32 | 2019-01-04 13:32 | 2019-01-31 18:29 | 2019-01-18 12:30 | 2019-01-04 13:23 | 2019-02-06 10:12 |  | 2019-02-04 16:46 | Residence 4100 S. Shatwell Rd, OKC |  |  | William Young | Reviewed contractor CA Alert and PowerPoint. Approved WCY 2/7/2019. | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | See Attachments |  |  |  | Metro Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | David Jones |  |  | Nicole Rhodes | Reviewed. | Nicole Rhodes |  | Medium |  |  |  | 4.08 Conflicting demands/directions | 5.06 Lack of situational awareness | 6.02 Inadequate practice | 7.06 Improper attempt to save time or effort |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Crew felt "rushed" due to outage situation. They took shortcuts. | 04. Operating at Improper Speed | 4. Fall on Same Level (Slip and Fall, Trip Over) |  | Approved. J. Looney |  |  |  | Injury / Illness |  |  |  | Dislocated hip | FALSE |  |  | 4. Fall on Same Level (Slip and Fall, Trip Over) | David Jones | Asplundh | Steven Martinez | Dislocation |  | Hip |  |  | TRUE | Company Vehicle | [68 empty] | none
8649 | Sooner Power Plant | 2019-01-03 15:30 | While inventorying grating material delivered for a capital project, member tripped over a piece of grating extending out from the pallet that was being inventoried and fell to the ground. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | David Willis | 2019-01-24 08:29 | 2019-01-04 14:18 | 2019-01-04 14:18 | 2019-01-04 15:45 | 2019-01-17 15:30 | 2019-01-04 14:08 | 2019-01-14 09:01 |  | 2019-01-14 08:38 | Sooner Coal Yard |  |  | Jesse Murray | Approved Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | David Willis |  | While member was moving pieces of grating material for an inventory of the material that had been delivered for a capital project the member tripped over material that had already been moved and inventory. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Engineering & Planning |  | David Willis | David Willis |  | Donald Wyckoff | I approve of incident corrective actions. Member has taken personal initiative to identify the root cause and develop an action plan for preventing future events. Donald Wyckoff 1/14/19. | Donald Wyckoff |  | Medium |  |  |  | 4.04 Routine, monotony, demand for uneventful vigilance |  |  |  |  | 9.06 Inadequate work planning or programming | [7 empty] | Lack of attention to detail, in particular not paying close attention to material and pallets surrounding the area where inventory was being conducted. | 17. Failure to Identify Hazard, Risk | 4. Fall on Same Level (Slip and Fall, Trip Over) |  | Approved by Brady Sowell on 1/14/2018 | [90 empty] | None
8652 | Horseshoe Lake Power Plant | 2019-01-07 10:30 | Transporting 220 gallon caustic tote to Unit 8 cooling Tower. Forklift front wheel hit pot hole causing tote to fall from forks. | Level 3 |  | TRUE | Property Damage | Jean Leger | William Young | Reclassify incident as Close call as there was no property damage, acid loss or member injuries. Maintain risk assessment as "High" W. C. Young 1-8-2019. Assigned team to investigate incident, determine causal factors and establish CA's | 2019-01-08 14:42 | OG&E Corp Services | Robert Butler | 2019-03-04 07:31 | 2019-01-07 12:55 | 2019-01-07 12:55 | 2019-02-07 17:18 | 2019-01-21 10:30 | 2019-01-07 12:45 | 2019-02-08 09:54 | 2019-02-22 15:24 | 2019-02-07 17:19 | Horseshoe Lake, North of Unit 8 |  |  | Jean Leger | No additional comments. | UTS |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | William Young |  | Close Call Statement: Member transporting 220 gallon caustic tote to Unit 8 cooling Tower. Forklift front wheel hit pot hole causing tote to fall from forks. Event timeline and description: 1. Unit 8 cooling tower shut down 12.18.18. Sulfuric Acid valve to cooling tower not closed so isolation of acid did not occur. 2. On 1.7.19 cooling tower circulation restarted and pH found low at 2.7 (normal 8.4) 3. Env. Ops added 2,000 lbs Soda Ash on hand to raise pH but operating parameters not reached (6.5) 4. Decision made to utilize Sodium Hydroxide to raise pH 5. Env. Ops proceeded to transport caustic tote from chemical storage area in #6 basement to Unit 8 CT Pump Bay 6. Operator chose forktruck F30-942 (5600 lb truck) for caustic tote transport. 7. In route, operator drove into 4” deep pothole in roadway, resulting in tote falling, landing on its side. 8. Supervisor responded and 2 maintenance operators came with Broderson crane to upright tote. 9. Tote weight 3,116 lbs - too heavy for crane. Skytrak used to upright tote. 10. Operator returned tote to #6 basement via forktruck - pH had normalized by new Soda Ash arrival. Tote Details: 46” x 46” x 52” Sodium Hydroxide, 50% caustic Weight of chemical and tote, 3,116 lbs. 4” notch in tote base without fork pocket Per Corp Environmental, loss potential was estimated to be: $21,105 (remediation and chemical value) Additional Findings: 1. Prior incident on 2.14.18 with Corrective Action to adjust OI (manual close of valve) 2. OI not followed on 12.18.18 - shutdown of Unit 8 3. Forktruck F30-942 not pre-op’d prior to use 4. Forktruck has shop-manufactured hitch – replace with approved device | Jerrie Looney | William Young |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | UTS - Envir. & Process Chem |  | Thomas Gent | Robert Butler |  | Les Waller | I have reviewed the incident with the investigation team and the Intelex report. LW. | Les Waller | William Young | High |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance | 7.06 Improper attempt to save time or effort |  | 9.06 Inadequate work planning or programming | 10.03 Inadequate standards, specifications and/or design criteria | [6 empty] | Transporting 220 gallon caustic tote to Unit 8 cooling Tower. Forklift front wheel hit pot hole causing tote to fall from forks | 15. Using Equipment Improperly | 13. Environmental Release | Investigation complete. Findings presented to PS Ops leadership and Enviro Ops leadership. WCY 2/22/19 | Approved. J. Looney, 2/7/19 | [90 empty] | N/A
8652 | Horseshoe Lake Power Plant | 2019-01-07 10:30 | Transporting 220 gallon caustic tote to Unit 8 cooling Tower. Forklift front wheel hit pot hole causing tote to fall from forks. | Level 3 |  | TRUE | Property Damage | Jean Leger | William Young | Reclassify incident as Close call as there was no property damage, acid loss or member injuries. Maintain risk assessment as "High" W. C. Young 1-8-2019. Assigned team to investigate incident, determine causal factors and establish CA's | 2019-01-08 14:42 | OG&E Corp Services | Robert Butler | 2019-03-04 07:31 | 2019-01-07 12:55 | 2019-01-07 12:55 | 2019-02-07 17:18 | 2019-01-21 10:30 | 2019-01-07 12:45 | 2019-02-08 09:54 | 2019-02-22 15:24 | 2019-02-07 17:19 | Horseshoe Lake, North of Unit 8 |  |  | Jean Leger | No additional comments. | UTS |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | William Young |  | Close Call Statement: Member transporting 220 gallon caustic tote to Unit 8 cooling Tower. Forklift front wheel hit pot hole causing tote to fall from forks. Event timeline and description: 1. Unit 8 cooling tower shut down 12.18.18. Sulfuric Acid valve to cooling tower not closed so isolation of acid did not occur. 2. On 1.7.19 cooling tower circulation restarted and pH found low at 2.7 (normal 8.4) 3. Env. Ops added 2,000 lbs Soda Ash on hand to raise pH but operating parameters not reached (6.5) 4. Decision made to utilize Sodium Hydroxide to raise pH 5. Env. Ops proceeded to transport caustic tote from chemical storage area in #6 basement to Unit 8 CT Pump Bay 6. Operator chose forktruck F30-942 (5600 lb truck) for caustic tote transport. 7. In route, operator drove into 4” deep pothole in roadway, resulting in tote falling, landing on its side. 8. Supervisor responded and 2 maintenance operators came with Broderson crane to upright tote. 9. Tote weight 3,116 lbs - too heavy for crane. Skytrak used to upright tote. 10. Operator returned tote to #6 basement via forktruck - pH had normalized by new Soda Ash arrival. Tote Details: 46” x 46” x 52” Sodium Hydroxide, 50% caustic Weight of chemical and tote, 3,116 lbs. 4” notch in tote base without fork pocket Per Corp Environmental, loss potential was estimated to be: $21,105 (remediation and chemical value) Additional Findings: 1. Prior incident on 2.14.18 with Corrective Action to adjust OI (manual close of valve) 2. OI not followed on 12.18.18 - shutdown of Unit 8 3. Forktruck F30-942 not pre-op’d prior to use 4. Forktruck has shop-manufactured hitch – replace with approved device | Jerrie Looney | William Young |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | UTS - Envir. & Process Chem |  | Thomas Gent | Robert Butler |  | Les Waller | I have reviewed the incident with the investigation team and the Intelex report. LW. | Les Waller | William Young | High |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance | 7.06 Improper attempt to save time or effort |  | 9.06 Inadequate work planning or programming | 10.01 Inadequate assessment of loss exposures | [6 empty] | Transporting 220 gallon caustic tote to Unit 8 cooling Tower. Forklift front wheel hit pot hole causing tote to fall from forks | 15. Using Equipment Improperly | 13. Environmental Release | Investigation complete. Findings presented to PS Ops leadership and Enviro Ops leadership. WCY 2/22/19 | Approved. J. Looney, 2/7/19 | [90 empty] | N/A
8652 | Horseshoe Lake Power Plant | 2019-01-07 10:30 | Transporting 220 gallon caustic tote to Unit 8 cooling Tower. Forklift front wheel hit pot hole causing tote to fall from forks. | Level 3 |  | TRUE | Property Damage | Jean Leger | William Young | Reclassify incident as Close call as there was no property damage, acid loss or member injuries. Maintain risk assessment as "High" W. C. Young 1-8-2019. Assigned team to investigate incident, determine causal factors and establish CA's | 2019-01-08 14:42 | OG&E Corp Services | Robert Butler | 2019-03-04 07:31 | 2019-01-07 12:55 | 2019-01-07 12:55 | 2019-02-07 17:18 | 2019-01-21 10:30 | 2019-01-07 12:45 | 2019-02-08 09:54 | 2019-02-22 15:24 | 2019-02-07 17:19 | Horseshoe Lake, North of Unit 8 |  |  | Jean Leger | No additional comments. | UTS |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | William Young |  | Close Call Statement: Member transporting 220 gallon caustic tote to Unit 8 cooling Tower. Forklift front wheel hit pot hole causing tote to fall from forks. Event timeline and description: 1. Unit 8 cooling tower shut down 12.18.18. Sulfuric Acid valve to cooling tower not closed so isolation of acid did not occur. 2. On 1.7.19 cooling tower circulation restarted and pH found low at 2.7 (normal 8.4) 3. Env. Ops added 2,000 lbs Soda Ash on hand to raise pH but operating parameters not reached (6.5) 4. Decision made to utilize Sodium Hydroxide to raise pH 5. Env. Ops proceeded to transport caustic tote from chemical storage area in #6 basement to Unit 8 CT Pump Bay 6. Operator chose forktruck F30-942 (5600 lb truck) for caustic tote transport. 7. In route, operator drove into 4” deep pothole in roadway, resulting in tote falling, landing on its side. 8. Supervisor responded and 2 maintenance operators came with Broderson crane to upright tote. 9. Tote weight 3,116 lbs - too heavy for crane. Skytrak used to upright tote. 10. Operator returned tote to #6 basement via forktruck - pH had normalized by new Soda Ash arrival. Tote Details: 46” x 46” x 52” Sodium Hydroxide, 50% caustic Weight of chemical and tote, 3,116 lbs. 4” notch in tote base without fork pocket Per Corp Environmental, loss potential was estimated to be: $21,105 (remediation and chemical value) Additional Findings: 1. Prior incident on 2.14.18 with Corrective Action to adjust OI (manual close of valve) 2. OI not followed on 12.18.18 - shutdown of Unit 8 3. Forktruck F30-942 not pre-op’d prior to use 4. Forktruck has shop-manufactured hitch – replace with approved device | Jerrie Looney | William Young |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | UTS - Envir. & Process Chem |  | Thomas Gent | Robert Butler |  | Les Waller | I have reviewed the incident with the investigation team and the Intelex report. LW. | Les Waller | William Young | High |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance | 7.06 Improper attempt to save time or effort |  | 9.06 Inadequate work planning or programming | 10.08 Inadequate evaluation of changes | [6 empty] | Transporting 220 gallon caustic tote to Unit 8 cooling Tower. Forklift front wheel hit pot hole causing tote to fall from forks | 15. Using Equipment Improperly | 13. Environmental Release | Investigation complete. Findings presented to PS Ops leadership and Enviro Ops leadership. WCY 2/22/19 | Approved. J. Looney, 2/7/19 | [90 empty] | N/A
8652 | Horseshoe Lake Power Plant | 2019-01-07 10:30 | Transporting 220 gallon caustic tote to Unit 8 cooling Tower. Forklift front wheel hit pot hole causing tote to fall from forks. | Level 3 |  | TRUE | Property Damage | Jean Leger | William Young | Reclassify incident as Close call as there was no property damage, acid loss or member injuries. Maintain risk assessment as "High" W. C. Young 1-8-2019. Assigned team to investigate incident, determine causal factors and establish CA's | 2019-01-08 14:42 | OG&E Corp Services | Robert Butler | 2019-03-04 07:31 | 2019-01-07 12:55 | 2019-01-07 12:55 | 2019-02-07 17:18 | 2019-01-21 10:30 | 2019-01-07 12:45 | 2019-02-08 09:54 | 2019-02-22 15:24 | 2019-02-07 17:19 | Horseshoe Lake, North of Unit 8 |  |  | Jean Leger | No additional comments. | UTS |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | William Young |  | Close Call Statement: Member transporting 220 gallon caustic tote to Unit 8 cooling Tower. Forklift front wheel hit pot hole causing tote to fall from forks. Event timeline and description: 1. Unit 8 cooling tower shut down 12.18.18. Sulfuric Acid valve to cooling tower not closed so isolation of acid did not occur. 2. On 1.7.19 cooling tower circulation restarted and pH found low at 2.7 (normal 8.4) 3. Env. Ops added 2,000 lbs Soda Ash on hand to raise pH but operating parameters not reached (6.5) 4. Decision made to utilize Sodium Hydroxide to raise pH 5. Env. Ops proceeded to transport caustic tote from chemical storage area in #6 basement to Unit 8 CT Pump Bay 6. Operator chose forktruck F30-942 (5600 lb truck) for caustic tote transport. 7. In route, operator drove into 4” deep pothole in roadway, resulting in tote falling, landing on its side. 8. Supervisor responded and 2 maintenance operators came with Broderson crane to upright tote. 9. Tote weight 3,116 lbs - too heavy for crane. Skytrak used to upright tote. 10. Operator returned tote to #6 basement via forktruck - pH had normalized by new Soda Ash arrival. Tote Details: 46” x 46” x 52” Sodium Hydroxide, 50% caustic Weight of chemical and tote, 3,116 lbs. 4” notch in tote base without fork pocket Per Corp Environmental, loss potential was estimated to be: $21,105 (remediation and chemical value) Additional Findings: 1. Prior incident on 2.14.18 with Corrective Action to adjust OI (manual close of valve) 2. OI not followed on 12.18.18 - shutdown of Unit 8 3. Forktruck F30-942 not pre-op’d prior to use 4. Forktruck has shop-manufactured hitch – replace with approved device | Cody Vinyard | William Young |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | UTS - Envir. & Process Chem |  | Thomas Gent | Robert Butler |  | Les Waller | I have reviewed the incident with the investigation team and the Intelex report. LW. | Les Waller | William Young | High |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance | 7.06 Improper attempt to save time or effort |  | 9.06 Inadequate work planning or programming | 10.03 Inadequate standards, specifications and/or design criteria | [6 empty] | Transporting 220 gallon caustic tote to Unit 8 cooling Tower. Forklift front wheel hit pot hole causing tote to fall from forks | 15. Using Equipment Improperly | 13. Environmental Release | Investigation complete. Findings presented to PS Ops leadership and Enviro Ops leadership. WCY 2/22/19 | Approved. J. Looney, 2/7/19 | [90 empty] | N/A
8652 | Horseshoe Lake Power Plant | 2019-01-07 10:30 | Transporting 220 gallon caustic tote to Unit 8 cooling Tower. Forklift front wheel hit pot hole causing tote to fall from forks. | Level 3 |  | TRUE | Property Damage | Jean Leger | William Young | Reclassify incident as Close call as there was no property damage, acid loss or member injuries. Maintain risk assessment as "High" W. C. Young 1-8-2019. Assigned team to investigate incident, determine causal factors and establish CA's | 2019-01-08 14:42 | OG&E Corp Services | Robert Butler | 2019-03-04 07:31 | 2019-01-07 12:55 | 2019-01-07 12:55 | 2019-02-07 17:18 | 2019-01-21 10:30 | 2019-01-07 12:45 | 2019-02-08 09:54 | 2019-02-22 15:24 | 2019-02-07 17:19 | Horseshoe Lake, North of Unit 8 |  |  | Jean Leger | No additional comments. | UTS |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | William Young |  | Close Call Statement: Member transporting 220 gallon caustic tote to Unit 8 cooling Tower. Forklift front wheel hit pot hole causing tote to fall from forks. Event timeline and description: 1. Unit 8 cooling tower shut down 12.18.18. Sulfuric Acid valve to cooling tower not closed so isolation of acid did not occur. 2. On 1.7.19 cooling tower circulation restarted and pH found low at 2.7 (normal 8.4) 3. Env. Ops added 2,000 lbs Soda Ash on hand to raise pH but operating parameters not reached (6.5) 4. Decision made to utilize Sodium Hydroxide to raise pH 5. Env. Ops proceeded to transport caustic tote from chemical storage area in #6 basement to Unit 8 CT Pump Bay 6. Operator chose forktruck F30-942 (5600 lb truck) for caustic tote transport. 7. In route, operator drove into 4” deep pothole in roadway, resulting in tote falling, landing on its side. 8. Supervisor responded and 2 maintenance operators came with Broderson crane to upright tote. 9. Tote weight 3,116 lbs - too heavy for crane. Skytrak used to upright tote. 10. Operator returned tote to #6 basement via forktruck - pH had normalized by new Soda Ash arrival. Tote Details: 46” x 46” x 52” Sodium Hydroxide, 50% caustic Weight of chemical and tote, 3,116 lbs. 4” notch in tote base without fork pocket Per Corp Environmental, loss potential was estimated to be: $21,105 (remediation and chemical value) Additional Findings: 1. Prior incident on 2.14.18 with Corrective Action to adjust OI (manual close of valve) 2. OI not followed on 12.18.18 - shutdown of Unit 8 3. Forktruck F30-942 not pre-op’d prior to use 4. Forktruck has shop-manufactured hitch – replace with approved device | Cody Vinyard | William Young |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | UTS - Envir. & Process Chem |  | Thomas Gent | Robert Butler |  | Les Waller | I have reviewed the incident with the investigation team and the Intelex report. LW. | Les Waller | William Young | High |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance | 7.06 Improper attempt to save time or effort |  | 9.06 Inadequate work planning or programming | 10.01 Inadequate assessment of loss exposures | [6 empty] | Transporting 220 gallon caustic tote to Unit 8 cooling Tower. Forklift front wheel hit pot hole causing tote to fall from forks | 15. Using Equipment Improperly | 13. Environmental Release | Investigation complete. Findings presented to PS Ops leadership and Enviro Ops leadership. WCY 2/22/19 | Approved. J. Looney, 2/7/19 | [90 empty] | N/A
8652 | Horseshoe Lake Power Plant | 2019-01-07 10:30 | Transporting 220 gallon caustic tote to Unit 8 cooling Tower. Forklift front wheel hit pot hole causing tote to fall from forks. | Level 3 |  | TRUE | Property Damage | Jean Leger | William Young | Reclassify incident as Close call as there was no property damage, acid loss or member injuries. Maintain risk assessment as "High" W. C. Young 1-8-2019. Assigned team to investigate incident, determine causal factors and establish CA's | 2019-01-08 14:42 | OG&E Corp Services | Robert Butler | 2019-03-04 07:31 | 2019-01-07 12:55 | 2019-01-07 12:55 | 2019-02-07 17:18 | 2019-01-21 10:30 | 2019-01-07 12:45 | 2019-02-08 09:54 | 2019-02-22 15:24 | 2019-02-07 17:19 | Horseshoe Lake, North of Unit 8 |  |  | Jean Leger | No additional comments. | UTS |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | William Young |  | Close Call Statement: Member transporting 220 gallon caustic tote to Unit 8 cooling Tower. Forklift front wheel hit pot hole causing tote to fall from forks. Event timeline and description: 1. Unit 8 cooling tower shut down 12.18.18. Sulfuric Acid valve to cooling tower not closed so isolation of acid did not occur. 2. On 1.7.19 cooling tower circulation restarted and pH found low at 2.7 (normal 8.4) 3. Env. Ops added 2,000 lbs Soda Ash on hand to raise pH but operating parameters not reached (6.5) 4. Decision made to utilize Sodium Hydroxide to raise pH 5. Env. Ops proceeded to transport caustic tote from chemical storage area in #6 basement to Unit 8 CT Pump Bay 6. Operator chose forktruck F30-942 (5600 lb truck) for caustic tote transport. 7. In route, operator drove into 4” deep pothole in roadway, resulting in tote falling, landing on its side. 8. Supervisor responded and 2 maintenance operators came with Broderson crane to upright tote. 9. Tote weight 3,116 lbs - too heavy for crane. Skytrak used to upright tote. 10. Operator returned tote to #6 basement via forktruck - pH had normalized by new Soda Ash arrival. Tote Details: 46” x 46” x 52” Sodium Hydroxide, 50% caustic Weight of chemical and tote, 3,116 lbs. 4” notch in tote base without fork pocket Per Corp Environmental, loss potential was estimated to be: $21,105 (remediation and chemical value) Additional Findings: 1. Prior incident on 2.14.18 with Corrective Action to adjust OI (manual close of valve) 2. OI not followed on 12.18.18 - shutdown of Unit 8 3. Forktruck F30-942 not pre-op’d prior to use 4. Forktruck has shop-manufactured hitch – replace with approved device | Cody Vinyard | William Young |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | UTS - Envir. & Process Chem |  | Thomas Gent | Robert Butler |  | Les Waller | I have reviewed the incident with the investigation team and the Intelex report. LW. | Les Waller | William Young | High |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance | 7.06 Improper attempt to save time or effort |  | 9.06 Inadequate work planning or programming | 10.08 Inadequate evaluation of changes | [6 empty] | Transporting 220 gallon caustic tote to Unit 8 cooling Tower. Forklift front wheel hit pot hole causing tote to fall from forks | 15. Using Equipment Improperly | 13. Environmental Release | Investigation complete. Findings presented to PS Ops leadership and Enviro Ops leadership. WCY 2/22/19 | Approved. J. Looney, 2/7/19 | [90 empty] | N/A
8652 | Horseshoe Lake Power Plant | 2019-01-07 10:30 | Transporting 220 gallon caustic tote to Unit 8 cooling Tower. Forklift front wheel hit pot hole causing tote to fall from forks. | Level 3 |  | TRUE | Property Damage | Jean Leger | William Young | Reclassify incident as Close call as there was no property damage, acid loss or member injuries. Maintain risk assessment as "High" W. C. Young 1-8-2019. Assigned team to investigate incident, determine causal factors and establish CA's | 2019-01-08 14:42 | OG&E Corp Services | Robert Butler | 2019-03-04 07:31 | 2019-01-07 12:55 | 2019-01-07 12:55 | 2019-02-07 17:18 | 2019-01-21 10:30 | 2019-01-07 12:45 | 2019-02-08 09:54 | 2019-02-22 15:24 | 2019-02-07 17:19 | Horseshoe Lake, North of Unit 8 |  |  | Jean Leger | No additional comments. | UTS |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | William Young |  | Close Call Statement: Member transporting 220 gallon caustic tote to Unit 8 cooling Tower. Forklift front wheel hit pot hole causing tote to fall from forks. Event timeline and description: 1. Unit 8 cooling tower shut down 12.18.18. Sulfuric Acid valve to cooling tower not closed so isolation of acid did not occur. 2. On 1.7.19 cooling tower circulation restarted and pH found low at 2.7 (normal 8.4) 3. Env. Ops added 2,000 lbs Soda Ash on hand to raise pH but operating parameters not reached (6.5) 4. Decision made to utilize Sodium Hydroxide to raise pH 5. Env. Ops proceeded to transport caustic tote from chemical storage area in #6 basement to Unit 8 CT Pump Bay 6. Operator chose forktruck F30-942 (5600 lb truck) for caustic tote transport. 7. In route, operator drove into 4” deep pothole in roadway, resulting in tote falling, landing on its side. 8. Supervisor responded and 2 maintenance operators came with Broderson crane to upright tote. 9. Tote weight 3,116 lbs - too heavy for crane. Skytrak used to upright tote. 10. Operator returned tote to #6 basement via forktruck - pH had normalized by new Soda Ash arrival. Tote Details: 46” x 46” x 52” Sodium Hydroxide, 50% caustic Weight of chemical and tote, 3,116 lbs. 4” notch in tote base without fork pocket Per Corp Environmental, loss potential was estimated to be: $21,105 (remediation and chemical value) Additional Findings: 1. Prior incident on 2.14.18 with Corrective Action to adjust OI (manual close of valve) 2. OI not followed on 12.18.18 - shutdown of Unit 8 3. Forktruck F30-942 not pre-op’d prior to use 4. Forktruck has shop-manufactured hitch – replace with approved device | Edward Bugby | William Young |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | UTS - Envir. & Process Chem |  | Thomas Gent | Robert Butler |  | Les Waller | I have reviewed the incident with the investigation team and the Intelex report. LW. | Les Waller | William Young | High |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance | 7.06 Improper attempt to save time or effort |  | 9.06 Inadequate work planning or programming | 10.03 Inadequate standards, specifications and/or design criteria | [6 empty] | Transporting 220 gallon caustic tote to Unit 8 cooling Tower. Forklift front wheel hit pot hole causing tote to fall from forks | 15. Using Equipment Improperly | 13. Environmental Release | Investigation complete. Findings presented to PS Ops leadership and Enviro Ops leadership. WCY 2/22/19 | Approved. J. Looney, 2/7/19 | [90 empty] | N/A
8652 | Horseshoe Lake Power Plant | 2019-01-07 10:30 | Transporting 220 gallon caustic tote to Unit 8 cooling Tower. Forklift front wheel hit pot hole causing tote to fall from forks. | Level 3 |  | TRUE | Property Damage | Jean Leger | William Young | Reclassify incident as Close call as there was no property damage, acid loss or member injuries. Maintain risk assessment as "High" W. C. Young 1-8-2019. Assigned team to investigate incident, determine causal factors and establish CA's | 2019-01-08 14:42 | OG&E Corp Services | Robert Butler | 2019-03-04 07:31 | 2019-01-07 12:55 | 2019-01-07 12:55 | 2019-02-07 17:18 | 2019-01-21 10:30 | 2019-01-07 12:45 | 2019-02-08 09:54 | 2019-02-22 15:24 | 2019-02-07 17:19 | Horseshoe Lake, North of Unit 8 |  |  | Jean Leger | No additional comments. | UTS |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | William Young |  | Close Call Statement: Member transporting 220 gallon caustic tote to Unit 8 cooling Tower. Forklift front wheel hit pot hole causing tote to fall from forks. Event timeline and description: 1. Unit 8 cooling tower shut down 12.18.18. Sulfuric Acid valve to cooling tower not closed so isolation of acid did not occur. 2. On 1.7.19 cooling tower circulation restarted and pH found low at 2.7 (normal 8.4) 3. Env. Ops added 2,000 lbs Soda Ash on hand to raise pH but operating parameters not reached (6.5) 4. Decision made to utilize Sodium Hydroxide to raise pH 5. Env. Ops proceeded to transport caustic tote from chemical storage area in #6 basement to Unit 8 CT Pump Bay 6. Operator chose forktruck F30-942 (5600 lb truck) for caustic tote transport. 7. In route, operator drove into 4” deep pothole in roadway, resulting in tote falling, landing on its side. 8. Supervisor responded and 2 maintenance operators came with Broderson crane to upright tote. 9. Tote weight 3,116 lbs - too heavy for crane. Skytrak used to upright tote. 10. Operator returned tote to #6 basement via forktruck - pH had normalized by new Soda Ash arrival. Tote Details: 46” x 46” x 52” Sodium Hydroxide, 50% caustic Weight of chemical and tote, 3,116 lbs. 4” notch in tote base without fork pocket Per Corp Environmental, loss potential was estimated to be: $21,105 (remediation and chemical value) Additional Findings: 1. Prior incident on 2.14.18 with Corrective Action to adjust OI (manual close of valve) 2. OI not followed on 12.18.18 - shutdown of Unit 8 3. Forktruck F30-942 not pre-op’d prior to use 4. Forktruck has shop-manufactured hitch – replace with approved device | Edward Bugby | William Young |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | UTS - Envir. & Process Chem |  | Thomas Gent | Robert Butler |  | Les Waller | I have reviewed the incident with the investigation team and the Intelex report. LW. | Les Waller | William Young | High |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance | 7.06 Improper attempt to save time or effort |  | 9.06 Inadequate work planning or programming | 10.01 Inadequate assessment of loss exposures | [6 empty] | Transporting 220 gallon caustic tote to Unit 8 cooling Tower. Forklift front wheel hit pot hole causing tote to fall from forks | 15. Using Equipment Improperly | 13. Environmental Release | Investigation complete. Findings presented to PS Ops leadership and Enviro Ops leadership. WCY 2/22/19 | Approved. J. Looney, 2/7/19 | [90 empty] | N/A
8652 | Horseshoe Lake Power Plant | 2019-01-07 10:30 | Transporting 220 gallon caustic tote to Unit 8 cooling Tower. Forklift front wheel hit pot hole causing tote to fall from forks. | Level 3 |  | TRUE | Property Damage | Jean Leger | William Young | Reclassify incident as Close call as there was no property damage, acid loss or member injuries. Maintain risk assessment as "High" W. C. Young 1-8-2019. Assigned team to investigate incident, determine causal factors and establish CA's | 2019-01-08 14:42 | OG&E Corp Services | Robert Butler | 2019-03-04 07:31 | 2019-01-07 12:55 | 2019-01-07 12:55 | 2019-02-07 17:18 | 2019-01-21 10:30 | 2019-01-07 12:45 | 2019-02-08 09:54 | 2019-02-22 15:24 | 2019-02-07 17:19 | Horseshoe Lake, North of Unit 8 |  |  | Jean Leger | No additional comments. | UTS |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | William Young |  | Close Call Statement: Member transporting 220 gallon caustic tote to Unit 8 cooling Tower. Forklift front wheel hit pot hole causing tote to fall from forks. Event timeline and description: 1. Unit 8 cooling tower shut down 12.18.18. Sulfuric Acid valve to cooling tower not closed so isolation of acid did not occur. 2. On 1.7.19 cooling tower circulation restarted and pH found low at 2.7 (normal 8.4) 3. Env. Ops added 2,000 lbs Soda Ash on hand to raise pH but operating parameters not reached (6.5) 4. Decision made to utilize Sodium Hydroxide to raise pH 5. Env. Ops proceeded to transport caustic tote from chemical storage area in #6 basement to Unit 8 CT Pump Bay 6. Operator chose forktruck F30-942 (5600 lb truck) for caustic tote transport. 7. In route, operator drove into 4” deep pothole in roadway, resulting in tote falling, landing on its side. 8. Supervisor responded and 2 maintenance operators came with Broderson crane to upright tote. 9. Tote weight 3,116 lbs - too heavy for crane. Skytrak used to upright tote. 10. Operator returned tote to #6 basement via forktruck - pH had normalized by new Soda Ash arrival. Tote Details: 46” x 46” x 52” Sodium Hydroxide, 50% caustic Weight of chemical and tote, 3,116 lbs. 4” notch in tote base without fork pocket Per Corp Environmental, loss potential was estimated to be: $21,105 (remediation and chemical value) Additional Findings: 1. Prior incident on 2.14.18 with Corrective Action to adjust OI (manual close of valve) 2. OI not followed on 12.18.18 - shutdown of Unit 8 3. Forktruck F30-942 not pre-op’d prior to use 4. Forktruck has shop-manufactured hitch – replace with approved device | Edward Bugby | William Young |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | UTS - Envir. & Process Chem |  | Thomas Gent | Robert Butler |  | Les Waller | I have reviewed the incident with the investigation team and the Intelex report. LW. | Les Waller | William Young | High |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance | 7.06 Improper attempt to save time or effort |  | 9.06 Inadequate work planning or programming | 10.08 Inadequate evaluation of changes | [6 empty] | Transporting 220 gallon caustic tote to Unit 8 cooling Tower. Forklift front wheel hit pot hole causing tote to fall from forks | 15. Using Equipment Improperly | 13. Environmental Release | Investigation complete. Findings presented to PS Ops leadership and Enviro Ops leadership. WCY 2/22/19 | Approved. J. Looney, 2/7/19 | [90 empty] | N/A
8654 | Horseshoe Lake Power Plant | 2019-01-07 08:40 | Place tower in service to start blowing down to pass our copper testing. After starting 8A Circulating water pump the Control Operator noticed the Cooling tower PH went low. He immediately called the Chemist and awaited further instruction. | Level 2 |  | FALSE | System Operational Incident | Donnie Jones |  |  |  | Power Supply | Mark Haynes | 2019-04-19 08:04 | 2019-01-07 13:31 | 2019-01-07 13:31 | 2019-02-20 14:35 | 2019-02-18 08:40 | 2019-01-07 13:10 | 2019-04-05 13:31 |  | 2019-02-28 13:58 | Horseshoe Lake Unit 8 Cooling Tower. |  |  | Jesse Murray | Approve. Jesse Murray | Power Supply |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Jon Harriet |  | The circulating water system was started and the low ph alarm came in. It was discovered that the sulfuric acid system was not isolated from the previous operation. This had allowed acid to seep into the tower during the shutdown period. Isolating the sulfuric acid system is a step on the OI for shutting down the circulating water system. The members who had shut the system down had forgotten about the new OI and did not utilize it. The shutdown of the circulating water system was added to the OI May 2, 2018 due to a similar incident which occurred February 14, 2018. Prior to this incident this had never been an issue. The acid system operates through an eductor off of the circulating water system and a control valve operates off of a ph. meter. It was believed that a contributing factor for the earlier incident was the level of the acid tanks. They were filled to a higher level than ever before because we had moved the acid from Mustang to here. The thought was that the weight of the acid had caused it to flow into the tower when the system was off. However, this incident the tank was at a normal level. An erratic ph. meter reading had the control valve opening while the system was off along with the system not being isolated allowed acid to flow to the tower. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Operations |  | Mark Haynes | Michael Kennedy |  | Michael Kennedy | The conversation was with Jon Harriet. Proceeding so other can complete their tasks. | Michael Kennedy |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.05 Inadequate review instruction |  |  | 9.09 Inadequate identification and evaluation of loss exposures |  |  |  |  | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  |  | The OI was not followed when the system was shutdown. | 16. Failure to Follow Procedure, Policy, Practice | 13. Environmental Release |  | 2/5/2019-had some questions about the incident. Sent email with list of questions. Returned to investigation stage. 2/20/19 - chatted with Jonny Jonas and got clarification on my questions. 2/28/19 - Inserted two additional corrective actions per the conversation with Jonny Jonas. | [66 empty] | Concern of damage to circ. water system piping. At this time no visible damage. | 500 | Zachary Miller | Structural | [20 empty] | 483434
8654 | Horseshoe Lake Power Plant | 2019-01-07 08:40 | Place tower in service to start blowing down to pass our copper testing. After starting 8A Circulating water pump the Control Operator noticed the Cooling tower PH went low. He immediately called the Chemist and awaited further instruction. | Level 2 |  | FALSE | System Operational Incident | Donnie Jones |  |  |  | Power Supply | Mark Haynes | 2019-04-19 08:04 | 2019-01-07 13:31 | 2019-01-07 13:31 | 2019-02-20 14:35 | 2019-02-18 08:40 | 2019-01-07 13:10 | 2019-04-05 13:31 |  | 2019-02-28 13:58 | Horseshoe Lake Unit 8 Cooling Tower. |  |  | Jesse Murray | Approve. Jesse Murray | Power Supply |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Jon Harriet |  | The circulating water system was started and the low ph alarm came in. It was discovered that the sulfuric acid system was not isolated from the previous operation. This had allowed acid to seep into the tower during the shutdown period. Isolating the sulfuric acid system is a step on the OI for shutting down the circulating water system. The members who had shut the system down had forgotten about the new OI and did not utilize it. The shutdown of the circulating water system was added to the OI May 2, 2018 due to a similar incident which occurred February 14, 2018. Prior to this incident this had never been an issue. The acid system operates through an eductor off of the circulating water system and a control valve operates off of a ph. meter. It was believed that a contributing factor for the earlier incident was the level of the acid tanks. They were filled to a higher level than ever before because we had moved the acid from Mustang to here. The thought was that the weight of the acid had caused it to flow into the tower when the system was off. However, this incident the tank was at a normal level. An erratic ph. meter reading had the control valve opening while the system was off along with the system not being isolated allowed acid to flow to the tower. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Operations |  | Mark Haynes | Michael Kennedy |  | Michael Kennedy | The conversation was with Jon Harriet. Proceeding so other can complete their tasks. | Michael Kennedy |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.05 Inadequate review instruction |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  |  | The OI was not followed when the system was shutdown. | 16. Failure to Follow Procedure, Policy, Practice | 13. Environmental Release |  | 2/5/2019-had some questions about the incident. Sent email with list of questions. Returned to investigation stage. 2/20/19 - chatted with Jonny Jonas and got clarification on my questions. 2/28/19 - Inserted two additional corrective actions per the conversation with Jonny Jonas. | [66 empty] | Concern of damage to circ. water system piping. At this time no visible damage. | 500 | Zachary Miller | Structural | [20 empty] | 483434
8654 | Horseshoe Lake Power Plant | 2019-01-07 08:40 | Place tower in service to start blowing down to pass our copper testing. After starting 8A Circulating water pump the Control Operator noticed the Cooling tower PH went low. He immediately called the Chemist and awaited further instruction. | Level 2 |  | FALSE | System Operational Incident | Donnie Jones |  |  |  | Power Supply | Mark Haynes | 2019-04-19 08:04 | 2019-01-07 13:31 | 2019-01-07 13:31 | 2019-02-20 14:35 | 2019-02-18 08:40 | 2019-01-07 13:10 | 2019-04-05 13:31 |  | 2019-02-28 13:58 | Horseshoe Lake Unit 8 Cooling Tower. |  |  | Jesse Murray | Approve. Jesse Murray | Power Supply |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Jon Harriet |  | The circulating water system was started and the low ph alarm came in. It was discovered that the sulfuric acid system was not isolated from the previous operation. This had allowed acid to seep into the tower during the shutdown period. Isolating the sulfuric acid system is a step on the OI for shutting down the circulating water system. The members who had shut the system down had forgotten about the new OI and did not utilize it. The shutdown of the circulating water system was added to the OI May 2, 2018 due to a similar incident which occurred February 14, 2018. Prior to this incident this had never been an issue. The acid system operates through an eductor off of the circulating water system and a control valve operates off of a ph. meter. It was believed that a contributing factor for the earlier incident was the level of the acid tanks. They were filled to a higher level than ever before because we had moved the acid from Mustang to here. The thought was that the weight of the acid had caused it to flow into the tower when the system was off. However, this incident the tank was at a normal level. An erratic ph. meter reading had the control valve opening while the system was off along with the system not being isolated allowed acid to flow to the tower. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Operations |  | Mark Haynes | Michael Kennedy |  | Michael Kennedy | The conversation was with Jon Harriet. Proceeding so other can complete their tasks. | Michael Kennedy |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.05 Inadequate review instruction |  |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  |  | The OI was not followed when the system was shutdown. | 16. Failure to Follow Procedure, Policy, Practice | 13. Environmental Release |  | 2/5/2019-had some questions about the incident. Sent email with list of questions. Returned to investigation stage. 2/20/19 - chatted with Jonny Jonas and got clarification on my questions. 2/28/19 - Inserted two additional corrective actions per the conversation with Jonny Jonas. | [66 empty] | Concern of damage to circ. water system piping. At this time no visible damage. | 500 | Zachary Miller | Structural | [20 empty] | 483434
8654 | Horseshoe Lake Power Plant | 2019-01-07 08:40 | Place tower in service to start blowing down to pass our copper testing. After starting 8A Circulating water pump the Control Operator noticed the Cooling tower PH went low. He immediately called the Chemist and awaited further instruction. | Level 2 |  | FALSE | System Operational Incident | Donnie Jones |  |  |  | Power Supply | Mark Haynes | 2019-04-19 08:04 | 2019-01-07 13:31 | 2019-01-07 13:31 | 2019-02-20 14:35 | 2019-02-18 08:40 | 2019-01-07 13:10 | 2019-04-05 13:31 |  | 2019-02-28 13:58 | Horseshoe Lake Unit 8 Cooling Tower. |  |  | Jesse Murray | Approve. Jesse Murray | Power Supply |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Jon Harriet |  | The circulating water system was started and the low ph alarm came in. It was discovered that the sulfuric acid system was not isolated from the previous operation. This had allowed acid to seep into the tower during the shutdown period. Isolating the sulfuric acid system is a step on the OI for shutting down the circulating water system. The members who had shut the system down had forgotten about the new OI and did not utilize it. The shutdown of the circulating water system was added to the OI May 2, 2018 due to a similar incident which occurred February 14, 2018. Prior to this incident this had never been an issue. The acid system operates through an eductor off of the circulating water system and a control valve operates off of a ph. meter. It was believed that a contributing factor for the earlier incident was the level of the acid tanks. They were filled to a higher level than ever before because we had moved the acid from Mustang to here. The thought was that the weight of the acid had caused it to flow into the tower when the system was off. However, this incident the tank was at a normal level. An erratic ph. meter reading had the control valve opening while the system was off along with the system not being isolated allowed acid to flow to the tower. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Operations |  | Mark Haynes | Michael Kennedy |  | Michael Kennedy | The conversation was with Jon Harriet. Proceeding so other can complete their tasks. | Michael Kennedy |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.03 Infrequent performance |  |  | 9.09 Inadequate identification and evaluation of loss exposures |  |  |  |  | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  |  | The OI was not followed when the system was shutdown. | 16. Failure to Follow Procedure, Policy, Practice | 13. Environmental Release |  | 2/5/2019-had some questions about the incident. Sent email with list of questions. Returned to investigation stage. 2/20/19 - chatted with Jonny Jonas and got clarification on my questions. 2/28/19 - Inserted two additional corrective actions per the conversation with Jonny Jonas. | [66 empty] | Concern of damage to circ. water system piping. At this time no visible damage. | 500 | Zachary Miller | Structural | [20 empty] | 483434
8654 | Horseshoe Lake Power Plant | 2019-01-07 08:40 | Place tower in service to start blowing down to pass our copper testing. After starting 8A Circulating water pump the Control Operator noticed the Cooling tower PH went low. He immediately called the Chemist and awaited further instruction. | Level 2 |  | FALSE | System Operational Incident | Donnie Jones |  |  |  | Power Supply | Mark Haynes | 2019-04-19 08:04 | 2019-01-07 13:31 | 2019-01-07 13:31 | 2019-02-20 14:35 | 2019-02-18 08:40 | 2019-01-07 13:10 | 2019-04-05 13:31 |  | 2019-02-28 13:58 | Horseshoe Lake Unit 8 Cooling Tower. |  |  | Jesse Murray | Approve. Jesse Murray | Power Supply |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Jon Harriet |  | The circulating water system was started and the low ph alarm came in. It was discovered that the sulfuric acid system was not isolated from the previous operation. This had allowed acid to seep into the tower during the shutdown period. Isolating the sulfuric acid system is a step on the OI for shutting down the circulating water system. The members who had shut the system down had forgotten about the new OI and did not utilize it. The shutdown of the circulating water system was added to the OI May 2, 2018 due to a similar incident which occurred February 14, 2018. Prior to this incident this had never been an issue. The acid system operates through an eductor off of the circulating water system and a control valve operates off of a ph. meter. It was believed that a contributing factor for the earlier incident was the level of the acid tanks. They were filled to a higher level than ever before because we had moved the acid from Mustang to here. The thought was that the weight of the acid had caused it to flow into the tower when the system was off. However, this incident the tank was at a normal level. An erratic ph. meter reading had the control valve opening while the system was off along with the system not being isolated allowed acid to flow to the tower. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Operations |  | Mark Haynes | Michael Kennedy |  | Michael Kennedy | The conversation was with Jon Harriet. Proceeding so other can complete their tasks. | Michael Kennedy |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.03 Infrequent performance |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  |  | The OI was not followed when the system was shutdown. | 16. Failure to Follow Procedure, Policy, Practice | 13. Environmental Release |  | 2/5/2019-had some questions about the incident. Sent email with list of questions. Returned to investigation stage. 2/20/19 - chatted with Jonny Jonas and got clarification on my questions. 2/28/19 - Inserted two additional corrective actions per the conversation with Jonny Jonas. | [66 empty] | Concern of damage to circ. water system piping. At this time no visible damage. | 500 | Zachary Miller | Structural | [20 empty] | 483434
8654 | Horseshoe Lake Power Plant | 2019-01-07 08:40 | Place tower in service to start blowing down to pass our copper testing. After starting 8A Circulating water pump the Control Operator noticed the Cooling tower PH went low. He immediately called the Chemist and awaited further instruction. | Level 2 |  | FALSE | System Operational Incident | Donnie Jones |  |  |  | Power Supply | Mark Haynes | 2019-04-19 08:04 | 2019-01-07 13:31 | 2019-01-07 13:31 | 2019-02-20 14:35 | 2019-02-18 08:40 | 2019-01-07 13:10 | 2019-04-05 13:31 |  | 2019-02-28 13:58 | Horseshoe Lake Unit 8 Cooling Tower. |  |  | Jesse Murray | Approve. Jesse Murray | Power Supply |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Jon Harriet |  | The circulating water system was started and the low ph alarm came in. It was discovered that the sulfuric acid system was not isolated from the previous operation. This had allowed acid to seep into the tower during the shutdown period. Isolating the sulfuric acid system is a step on the OI for shutting down the circulating water system. The members who had shut the system down had forgotten about the new OI and did not utilize it. The shutdown of the circulating water system was added to the OI May 2, 2018 due to a similar incident which occurred February 14, 2018. Prior to this incident this had never been an issue. The acid system operates through an eductor off of the circulating water system and a control valve operates off of a ph. meter. It was believed that a contributing factor for the earlier incident was the level of the acid tanks. They were filled to a higher level than ever before because we had moved the acid from Mustang to here. The thought was that the weight of the acid had caused it to flow into the tower when the system was off. However, this incident the tank was at a normal level. An erratic ph. meter reading had the control valve opening while the system was off along with the system not being isolated allowed acid to flow to the tower. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Operations |  | Mark Haynes | Michael Kennedy |  | Michael Kennedy | The conversation was with Jon Harriet. Proceeding so other can complete their tasks. | Michael Kennedy |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.03 Infrequent performance |  |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  |  | The OI was not followed when the system was shutdown. | 16. Failure to Follow Procedure, Policy, Practice | 13. Environmental Release |  | 2/5/2019-had some questions about the incident. Sent email with list of questions. Returned to investigation stage. 2/20/19 - chatted with Jonny Jonas and got clarification on my questions. 2/28/19 - Inserted two additional corrective actions per the conversation with Jonny Jonas. | [66 empty] | Concern of damage to circ. water system piping. At this time no visible damage. | 500 | Zachary Miller | Structural | [20 empty] | 483434
8654 | Horseshoe Lake Power Plant | 2019-01-07 08:40 | Place tower in service to start blowing down to pass our copper testing. After starting 8A Circulating water pump the Control Operator noticed the Cooling tower PH went low. He immediately called the Chemist and awaited further instruction. | Level 2 |  | FALSE | System Operational Incident | Donnie Jones |  |  |  | Power Supply | Mark Haynes | 2019-04-19 08:04 | 2019-01-07 13:31 | 2019-01-07 13:31 | 2019-02-20 14:35 | 2019-02-18 08:40 | 2019-01-07 13:10 | 2019-04-05 13:31 |  | 2019-02-28 13:58 | Horseshoe Lake Unit 8 Cooling Tower. |  |  | Jesse Murray | Approve. Jesse Murray | Power Supply |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Jon Harriet |  | The circulating water system was started and the low ph alarm came in. It was discovered that the sulfuric acid system was not isolated from the previous operation. This had allowed acid to seep into the tower during the shutdown period. Isolating the sulfuric acid system is a step on the OI for shutting down the circulating water system. The members who had shut the system down had forgotten about the new OI and did not utilize it. The shutdown of the circulating water system was added to the OI May 2, 2018 due to a similar incident which occurred February 14, 2018. Prior to this incident this had never been an issue. The acid system operates through an eductor off of the circulating water system and a control valve operates off of a ph. meter. It was believed that a contributing factor for the earlier incident was the level of the acid tanks. They were filled to a higher level than ever before because we had moved the acid from Mustang to here. The thought was that the weight of the acid had caused it to flow into the tower when the system was off. However, this incident the tank was at a normal level. An erratic ph. meter reading had the control valve opening while the system was off along with the system not being isolated allowed acid to flow to the tower. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Operations |  | Mark Haynes | Michael Kennedy |  | Michael Kennedy | The conversation was with Jon Harriet. Proceeding so other can complete their tasks. | Michael Kennedy |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.02 Inadequate practice |  |  | 9.09 Inadequate identification and evaluation of loss exposures |  |  |  |  | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  |  | The OI was not followed when the system was shutdown. | 16. Failure to Follow Procedure, Policy, Practice | 13. Environmental Release |  | 2/5/2019-had some questions about the incident. Sent email with list of questions. Returned to investigation stage. 2/20/19 - chatted with Jonny Jonas and got clarification on my questions. 2/28/19 - Inserted two additional corrective actions per the conversation with Jonny Jonas. | [66 empty] | Concern of damage to circ. water system piping. At this time no visible damage. | 500 | Zachary Miller | Structural | [20 empty] | 483434
8654 | Horseshoe Lake Power Plant | 2019-01-07 08:40 | Place tower in service to start blowing down to pass our copper testing. After starting 8A Circulating water pump the Control Operator noticed the Cooling tower PH went low. He immediately called the Chemist and awaited further instruction. | Level 2 |  | FALSE | System Operational Incident | Donnie Jones |  |  |  | Power Supply | Mark Haynes | 2019-04-19 08:04 | 2019-01-07 13:31 | 2019-01-07 13:31 | 2019-02-20 14:35 | 2019-02-18 08:40 | 2019-01-07 13:10 | 2019-04-05 13:31 |  | 2019-02-28 13:58 | Horseshoe Lake Unit 8 Cooling Tower. |  |  | Jesse Murray | Approve. Jesse Murray | Power Supply |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Jon Harriet |  | The circulating water system was started and the low ph alarm came in. It was discovered that the sulfuric acid system was not isolated from the previous operation. This had allowed acid to seep into the tower during the shutdown period. Isolating the sulfuric acid system is a step on the OI for shutting down the circulating water system. The members who had shut the system down had forgotten about the new OI and did not utilize it. The shutdown of the circulating water system was added to the OI May 2, 2018 due to a similar incident which occurred February 14, 2018. Prior to this incident this had never been an issue. The acid system operates through an eductor off of the circulating water system and a control valve operates off of a ph. meter. It was believed that a contributing factor for the earlier incident was the level of the acid tanks. They were filled to a higher level than ever before because we had moved the acid from Mustang to here. The thought was that the weight of the acid had caused it to flow into the tower when the system was off. However, this incident the tank was at a normal level. An erratic ph. meter reading had the control valve opening while the system was off along with the system not being isolated allowed acid to flow to the tower. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Operations |  | Mark Haynes | Michael Kennedy |  | Michael Kennedy | The conversation was with Jon Harriet. Proceeding so other can complete their tasks. | Michael Kennedy |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.02 Inadequate practice |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  |  | The OI was not followed when the system was shutdown. | 16. Failure to Follow Procedure, Policy, Practice | 13. Environmental Release |  | 2/5/2019-had some questions about the incident. Sent email with list of questions. Returned to investigation stage. 2/20/19 - chatted with Jonny Jonas and got clarification on my questions. 2/28/19 - Inserted two additional corrective actions per the conversation with Jonny Jonas. | [66 empty] | Concern of damage to circ. water system piping. At this time no visible damage. | 500 | Zachary Miller | Structural | [20 empty] | 483434
8654 | Horseshoe Lake Power Plant | 2019-01-07 08:40 | Place tower in service to start blowing down to pass our copper testing. After starting 8A Circulating water pump the Control Operator noticed the Cooling tower PH went low. He immediately called the Chemist and awaited further instruction. | Level 2 |  | FALSE | System Operational Incident | Donnie Jones |  |  |  | Power Supply | Mark Haynes | 2019-04-19 08:04 | 2019-01-07 13:31 | 2019-01-07 13:31 | 2019-02-20 14:35 | 2019-02-18 08:40 | 2019-01-07 13:10 | 2019-04-05 13:31 |  | 2019-02-28 13:58 | Horseshoe Lake Unit 8 Cooling Tower. |  |  | Jesse Murray | Approve. Jesse Murray | Power Supply |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Jon Harriet |  | The circulating water system was started and the low ph alarm came in. It was discovered that the sulfuric acid system was not isolated from the previous operation. This had allowed acid to seep into the tower during the shutdown period. Isolating the sulfuric acid system is a step on the OI for shutting down the circulating water system. The members who had shut the system down had forgotten about the new OI and did not utilize it. The shutdown of the circulating water system was added to the OI May 2, 2018 due to a similar incident which occurred February 14, 2018. Prior to this incident this had never been an issue. The acid system operates through an eductor off of the circulating water system and a control valve operates off of a ph. meter. It was believed that a contributing factor for the earlier incident was the level of the acid tanks. They were filled to a higher level than ever before because we had moved the acid from Mustang to here. The thought was that the weight of the acid had caused it to flow into the tower when the system was off. However, this incident the tank was at a normal level. An erratic ph. meter reading had the control valve opening while the system was off along with the system not being isolated allowed acid to flow to the tower. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Operations |  | Mark Haynes | Michael Kennedy |  | Michael Kennedy | The conversation was with Jon Harriet. Proceeding so other can complete their tasks. | Michael Kennedy |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.02 Inadequate practice |  |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  |  | The OI was not followed when the system was shutdown. | 16. Failure to Follow Procedure, Policy, Practice | 13. Environmental Release |  | 2/5/2019-had some questions about the incident. Sent email with list of questions. Returned to investigation stage. 2/20/19 - chatted with Jonny Jonas and got clarification on my questions. 2/28/19 - Inserted two additional corrective actions per the conversation with Jonny Jonas. | [66 empty] | Concern of damage to circ. water system piping. At this time no visible damage. | 500 | Zachary Miller | Structural | [20 empty] | 483434
8654 | Horseshoe Lake Power Plant | 2019-01-07 08:40 | Place tower in service to start blowing down to pass our copper testing. After starting 8A Circulating water pump the Control Operator noticed the Cooling tower PH went low. He immediately called the Chemist and awaited further instruction. | Level 2 |  | FALSE | System Operational Incident | Donnie Jones |  |  |  | Power Supply | Mark Haynes | 2019-04-19 08:04 | 2019-01-07 13:31 | 2019-01-07 13:31 | 2019-02-20 14:35 | 2019-02-18 08:40 | 2019-01-07 13:10 | 2019-04-05 13:31 |  | 2019-02-28 13:58 | Horseshoe Lake Unit 8 Cooling Tower. |  |  | Jesse Murray | Approve. Jesse Murray | Power Supply |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Jon Harriet |  | The circulating water system was started and the low ph alarm came in. It was discovered that the sulfuric acid system was not isolated from the previous operation. This had allowed acid to seep into the tower during the shutdown period. Isolating the sulfuric acid system is a step on the OI for shutting down the circulating water system. The members who had shut the system down had forgotten about the new OI and did not utilize it. The shutdown of the circulating water system was added to the OI May 2, 2018 due to a similar incident which occurred February 14, 2018. Prior to this incident this had never been an issue. The acid system operates through an eductor off of the circulating water system and a control valve operates off of a ph. meter. It was believed that a contributing factor for the earlier incident was the level of the acid tanks. They were filled to a higher level than ever before because we had moved the acid from Mustang to here. The thought was that the weight of the acid had caused it to flow into the tower when the system was off. However, this incident the tank was at a normal level. An erratic ph. meter reading had the control valve opening while the system was off along with the system not being isolated allowed acid to flow to the tower. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Operations |  | Mark Haynes | Michael Kennedy |  | Michael Kennedy | The conversation was with Jon Harriet. Proceeding so other can complete their tasks. | Michael Kennedy |  | Medium |  |  |  |  | 5.04 Inadequate update training | 6.05 Inadequate review instruction |  |  | 9.09 Inadequate identification and evaluation of loss exposures |  |  |  |  | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  |  | The OI was not followed when the system was shutdown. | 16. Failure to Follow Procedure, Policy, Practice | 13. Environmental Release |  | 2/5/2019-had some questions about the incident. Sent email with list of questions. Returned to investigation stage. 2/20/19 - chatted with Jonny Jonas and got clarification on my questions. 2/28/19 - Inserted two additional corrective actions per the conversation with Jonny Jonas. | [66 empty] | Concern of damage to circ. water system piping. At this time no visible damage. | 500 | Zachary Miller | Structural | [20 empty] | 483434
8654 | Horseshoe Lake Power Plant | 2019-01-07 08:40 | Place tower in service to start blowing down to pass our copper testing. After starting 8A Circulating water pump the Control Operator noticed the Cooling tower PH went low. He immediately called the Chemist and awaited further instruction. | Level 2 |  | FALSE | System Operational Incident | Donnie Jones |  |  |  | Power Supply | Mark Haynes | 2019-04-19 08:04 | 2019-01-07 13:31 | 2019-01-07 13:31 | 2019-02-20 14:35 | 2019-02-18 08:40 | 2019-01-07 13:10 | 2019-04-05 13:31 |  | 2019-02-28 13:58 | Horseshoe Lake Unit 8 Cooling Tower. |  |  | Jesse Murray | Approve. Jesse Murray | Power Supply |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Jon Harriet |  | The circulating water system was started and the low ph alarm came in. It was discovered that the sulfuric acid system was not isolated from the previous operation. This had allowed acid to seep into the tower during the shutdown period. Isolating the sulfuric acid system is a step on the OI for shutting down the circulating water system. The members who had shut the system down had forgotten about the new OI and did not utilize it. The shutdown of the circulating water system was added to the OI May 2, 2018 due to a similar incident which occurred February 14, 2018. Prior to this incident this had never been an issue. The acid system operates through an eductor off of the circulating water system and a control valve operates off of a ph. meter. It was believed that a contributing factor for the earlier incident was the level of the acid tanks. They were filled to a higher level than ever before because we had moved the acid from Mustang to here. The thought was that the weight of the acid had caused it to flow into the tower when the system was off. However, this incident the tank was at a normal level. An erratic ph. meter reading had the control valve opening while the system was off along with the system not being isolated allowed acid to flow to the tower. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Operations |  | Mark Haynes | Michael Kennedy |  | Michael Kennedy | The conversation was with Jon Harriet. Proceeding so other can complete their tasks. | Michael Kennedy |  | Medium |  |  |  |  | 5.04 Inadequate update training | 6.05 Inadequate review instruction |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  |  | The OI was not followed when the system was shutdown. | 16. Failure to Follow Procedure, Policy, Practice | 13. Environmental Release |  | 2/5/2019-had some questions about the incident. Sent email with list of questions. Returned to investigation stage. 2/20/19 - chatted with Jonny Jonas and got clarification on my questions. 2/28/19 - Inserted two additional corrective actions per the conversation with Jonny Jonas. | [66 empty] | Concern of damage to circ. water system piping. At this time no visible damage. | 500 | Zachary Miller | Structural | [20 empty] | 483434
8654 | Horseshoe Lake Power Plant | 2019-01-07 08:40 | Place tower in service to start blowing down to pass our copper testing. After starting 8A Circulating water pump the Control Operator noticed the Cooling tower PH went low. He immediately called the Chemist and awaited further instruction. | Level 2 |  | FALSE | System Operational Incident | Donnie Jones |  |  |  | Power Supply | Mark Haynes | 2019-04-19 08:04 | 2019-01-07 13:31 | 2019-01-07 13:31 | 2019-02-20 14:35 | 2019-02-18 08:40 | 2019-01-07 13:10 | 2019-04-05 13:31 |  | 2019-02-28 13:58 | Horseshoe Lake Unit 8 Cooling Tower. |  |  | Jesse Murray | Approve. Jesse Murray | Power Supply |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Jon Harriet |  | The circulating water system was started and the low ph alarm came in. It was discovered that the sulfuric acid system was not isolated from the previous operation. This had allowed acid to seep into the tower during the shutdown period. Isolating the sulfuric acid system is a step on the OI for shutting down the circulating water system. The members who had shut the system down had forgotten about the new OI and did not utilize it. The shutdown of the circulating water system was added to the OI May 2, 2018 due to a similar incident which occurred February 14, 2018. Prior to this incident this had never been an issue. The acid system operates through an eductor off of the circulating water system and a control valve operates off of a ph. meter. It was believed that a contributing factor for the earlier incident was the level of the acid tanks. They were filled to a higher level than ever before because we had moved the acid from Mustang to here. The thought was that the weight of the acid had caused it to flow into the tower when the system was off. However, this incident the tank was at a normal level. An erratic ph. meter reading had the control valve opening while the system was off along with the system not being isolated allowed acid to flow to the tower. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Operations |  | Mark Haynes | Michael Kennedy |  | Michael Kennedy | The conversation was with Jon Harriet. Proceeding so other can complete their tasks. | Michael Kennedy |  | Medium |  |  |  |  | 5.04 Inadequate update training | 6.05 Inadequate review instruction |  |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  |  | The OI was not followed when the system was shutdown. | 16. Failure to Follow Procedure, Policy, Practice | 13. Environmental Release |  | 2/5/2019-had some questions about the incident. Sent email with list of questions. Returned to investigation stage. 2/20/19 - chatted with Jonny Jonas and got clarification on my questions. 2/28/19 - Inserted two additional corrective actions per the conversation with Jonny Jonas. | [66 empty] | Concern of damage to circ. water system piping. At this time no visible damage. | 500 | Zachary Miller | Structural | [20 empty] | 483434
8654 | Horseshoe Lake Power Plant | 2019-01-07 08:40 | Place tower in service to start blowing down to pass our copper testing. After starting 8A Circulating water pump the Control Operator noticed the Cooling tower PH went low. He immediately called the Chemist and awaited further instruction. | Level 2 |  | FALSE | System Operational Incident | Donnie Jones |  |  |  | Power Supply | Mark Haynes | 2019-04-19 08:04 | 2019-01-07 13:31 | 2019-01-07 13:31 | 2019-02-20 14:35 | 2019-02-18 08:40 | 2019-01-07 13:10 | 2019-04-05 13:31 |  | 2019-02-28 13:58 | Horseshoe Lake Unit 8 Cooling Tower. |  |  | Jesse Murray | Approve. Jesse Murray | Power Supply |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Jon Harriet |  | The circulating water system was started and the low ph alarm came in. It was discovered that the sulfuric acid system was not isolated from the previous operation. This had allowed acid to seep into the tower during the shutdown period. Isolating the sulfuric acid system is a step on the OI for shutting down the circulating water system. The members who had shut the system down had forgotten about the new OI and did not utilize it. The shutdown of the circulating water system was added to the OI May 2, 2018 due to a similar incident which occurred February 14, 2018. Prior to this incident this had never been an issue. The acid system operates through an eductor off of the circulating water system and a control valve operates off of a ph. meter. It was believed that a contributing factor for the earlier incident was the level of the acid tanks. They were filled to a higher level than ever before because we had moved the acid from Mustang to here. The thought was that the weight of the acid had caused it to flow into the tower when the system was off. However, this incident the tank was at a normal level. An erratic ph. meter reading had the control valve opening while the system was off along with the system not being isolated allowed acid to flow to the tower. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Operations |  | Mark Haynes | Michael Kennedy |  | Michael Kennedy | The conversation was with Jon Harriet. Proceeding so other can complete their tasks. | Michael Kennedy |  | Medium |  |  |  |  | 5.04 Inadequate update training | 6.03 Infrequent performance |  |  | 9.09 Inadequate identification and evaluation of loss exposures |  |  |  |  | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  |  | The OI was not followed when the system was shutdown. | 16. Failure to Follow Procedure, Policy, Practice | 13. Environmental Release |  | 2/5/2019-had some questions about the incident. Sent email with list of questions. Returned to investigation stage. 2/20/19 - chatted with Jonny Jonas and got clarification on my questions. 2/28/19 - Inserted two additional corrective actions per the conversation with Jonny Jonas. | [66 empty] | Concern of damage to circ. water system piping. At this time no visible damage. | 500 | Zachary Miller | Structural | [20 empty] | 483434
8654 | Horseshoe Lake Power Plant | 2019-01-07 08:40 | Place tower in service to start blowing down to pass our copper testing. After starting 8A Circulating water pump the Control Operator noticed the Cooling tower PH went low. He immediately called the Chemist and awaited further instruction. | Level 2 |  | FALSE | System Operational Incident | Donnie Jones |  |  |  | Power Supply | Mark Haynes | 2019-04-19 08:04 | 2019-01-07 13:31 | 2019-01-07 13:31 | 2019-02-20 14:35 | 2019-02-18 08:40 | 2019-01-07 13:10 | 2019-04-05 13:31 |  | 2019-02-28 13:58 | Horseshoe Lake Unit 8 Cooling Tower. |  |  | Jesse Murray | Approve. Jesse Murray | Power Supply |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Jon Harriet |  | The circulating water system was started and the low ph alarm came in. It was discovered that the sulfuric acid system was not isolated from the previous operation. This had allowed acid to seep into the tower during the shutdown period. Isolating the sulfuric acid system is a step on the OI for shutting down the circulating water system. The members who had shut the system down had forgotten about the new OI and did not utilize it. The shutdown of the circulating water system was added to the OI May 2, 2018 due to a similar incident which occurred February 14, 2018. Prior to this incident this had never been an issue. The acid system operates through an eductor off of the circulating water system and a control valve operates off of a ph. meter. It was believed that a contributing factor for the earlier incident was the level of the acid tanks. They were filled to a higher level than ever before because we had moved the acid from Mustang to here. The thought was that the weight of the acid had caused it to flow into the tower when the system was off. However, this incident the tank was at a normal level. An erratic ph. meter reading had the control valve opening while the system was off along with the system not being isolated allowed acid to flow to the tower. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Operations |  | Mark Haynes | Michael Kennedy |  | Michael Kennedy | The conversation was with Jon Harriet. Proceeding so other can complete their tasks. | Michael Kennedy |  | Medium |  |  |  |  | 5.04 Inadequate update training | 6.03 Infrequent performance |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  |  | The OI was not followed when the system was shutdown. | 16. Failure to Follow Procedure, Policy, Practice | 13. Environmental Release |  | 2/5/2019-had some questions about the incident. Sent email with list of questions. Returned to investigation stage. 2/20/19 - chatted with Jonny Jonas and got clarification on my questions. 2/28/19 - Inserted two additional corrective actions per the conversation with Jonny Jonas. | [66 empty] | Concern of damage to circ. water system piping. At this time no visible damage. | 500 | Zachary Miller | Structural | [20 empty] | 483434
8654 | Horseshoe Lake Power Plant | 2019-01-07 08:40 | Place tower in service to start blowing down to pass our copper testing. After starting 8A Circulating water pump the Control Operator noticed the Cooling tower PH went low. He immediately called the Chemist and awaited further instruction. | Level 2 |  | FALSE | System Operational Incident | Donnie Jones |  |  |  | Power Supply | Mark Haynes | 2019-04-19 08:04 | 2019-01-07 13:31 | 2019-01-07 13:31 | 2019-02-20 14:35 | 2019-02-18 08:40 | 2019-01-07 13:10 | 2019-04-05 13:31 |  | 2019-02-28 13:58 | Horseshoe Lake Unit 8 Cooling Tower. |  |  | Jesse Murray | Approve. Jesse Murray | Power Supply |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Jon Harriet |  | The circulating water system was started and the low ph alarm came in. It was discovered that the sulfuric acid system was not isolated from the previous operation. This had allowed acid to seep into the tower during the shutdown period. Isolating the sulfuric acid system is a step on the OI for shutting down the circulating water system. The members who had shut the system down had forgotten about the new OI and did not utilize it. The shutdown of the circulating water system was added to the OI May 2, 2018 due to a similar incident which occurred February 14, 2018. Prior to this incident this had never been an issue. The acid system operates through an eductor off of the circulating water system and a control valve operates off of a ph. meter. It was believed that a contributing factor for the earlier incident was the level of the acid tanks. They were filled to a higher level than ever before because we had moved the acid from Mustang to here. The thought was that the weight of the acid had caused it to flow into the tower when the system was off. However, this incident the tank was at a normal level. An erratic ph. meter reading had the control valve opening while the system was off along with the system not being isolated allowed acid to flow to the tower. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Operations |  | Mark Haynes | Michael Kennedy |  | Michael Kennedy | The conversation was with Jon Harriet. Proceeding so other can complete their tasks. | Michael Kennedy |  | Medium |  |  |  |  | 5.04 Inadequate update training | 6.03 Infrequent performance |  |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  |  | The OI was not followed when the system was shutdown. | 16. Failure to Follow Procedure, Policy, Practice | 13. Environmental Release |  | 2/5/2019-had some questions about the incident. Sent email with list of questions. Returned to investigation stage. 2/20/19 - chatted with Jonny Jonas and got clarification on my questions. 2/28/19 - Inserted two additional corrective actions per the conversation with Jonny Jonas. | [66 empty] | Concern of damage to circ. water system piping. At this time no visible damage. | 500 | Zachary Miller | Structural | [20 empty] | 483434
8654 | Horseshoe Lake Power Plant | 2019-01-07 08:40 | Place tower in service to start blowing down to pass our copper testing. After starting 8A Circulating water pump the Control Operator noticed the Cooling tower PH went low. He immediately called the Chemist and awaited further instruction. | Level 2 |  | FALSE | System Operational Incident | Donnie Jones |  |  |  | Power Supply | Mark Haynes | 2019-04-19 08:04 | 2019-01-07 13:31 | 2019-01-07 13:31 | 2019-02-20 14:35 | 2019-02-18 08:40 | 2019-01-07 13:10 | 2019-04-05 13:31 |  | 2019-02-28 13:58 | Horseshoe Lake Unit 8 Cooling Tower. |  |  | Jesse Murray | Approve. Jesse Murray | Power Supply |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Jon Harriet |  | The circulating water system was started and the low ph alarm came in. It was discovered that the sulfuric acid system was not isolated from the previous operation. This had allowed acid to seep into the tower during the shutdown period. Isolating the sulfuric acid system is a step on the OI for shutting down the circulating water system. The members who had shut the system down had forgotten about the new OI and did not utilize it. The shutdown of the circulating water system was added to the OI May 2, 2018 due to a similar incident which occurred February 14, 2018. Prior to this incident this had never been an issue. The acid system operates through an eductor off of the circulating water system and a control valve operates off of a ph. meter. It was believed that a contributing factor for the earlier incident was the level of the acid tanks. They were filled to a higher level than ever before because we had moved the acid from Mustang to here. The thought was that the weight of the acid had caused it to flow into the tower when the system was off. However, this incident the tank was at a normal level. An erratic ph. meter reading had the control valve opening while the system was off along with the system not being isolated allowed acid to flow to the tower. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Operations |  | Mark Haynes | Michael Kennedy |  | Michael Kennedy | The conversation was with Jon Harriet. Proceeding so other can complete their tasks. | Michael Kennedy |  | Medium |  |  |  |  | 5.04 Inadequate update training | 6.02 Inadequate practice |  |  | 9.09 Inadequate identification and evaluation of loss exposures |  |  |  |  | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  |  | The OI was not followed when the system was shutdown. | 16. Failure to Follow Procedure, Policy, Practice | 13. Environmental Release |  | 2/5/2019-had some questions about the incident. Sent email with list of questions. Returned to investigation stage. 2/20/19 - chatted with Jonny Jonas and got clarification on my questions. 2/28/19 - Inserted two additional corrective actions per the conversation with Jonny Jonas. | [66 empty] | Concern of damage to circ. water system piping. At this time no visible damage. | 500 | Zachary Miller | Structural | [20 empty] | 483434
8654 | Horseshoe Lake Power Plant | 2019-01-07 08:40 | Place tower in service to start blowing down to pass our copper testing. After starting 8A Circulating water pump the Control Operator noticed the Cooling tower PH went low. He immediately called the Chemist and awaited further instruction. | Level 2 |  | FALSE | System Operational Incident | Donnie Jones |  |  |  | Power Supply | Mark Haynes | 2019-04-19 08:04 | 2019-01-07 13:31 | 2019-01-07 13:31 | 2019-02-20 14:35 | 2019-02-18 08:40 | 2019-01-07 13:10 | 2019-04-05 13:31 |  | 2019-02-28 13:58 | Horseshoe Lake Unit 8 Cooling Tower. |  |  | Jesse Murray | Approve. Jesse Murray | Power Supply |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Jon Harriet |  | The circulating water system was started and the low ph alarm came in. It was discovered that the sulfuric acid system was not isolated from the previous operation. This had allowed acid to seep into the tower during the shutdown period. Isolating the sulfuric acid system is a step on the OI for shutting down the circulating water system. The members who had shut the system down had forgotten about the new OI and did not utilize it. The shutdown of the circulating water system was added to the OI May 2, 2018 due to a similar incident which occurred February 14, 2018. Prior to this incident this had never been an issue. The acid system operates through an eductor off of the circulating water system and a control valve operates off of a ph. meter. It was believed that a contributing factor for the earlier incident was the level of the acid tanks. They were filled to a higher level than ever before because we had moved the acid from Mustang to here. The thought was that the weight of the acid had caused it to flow into the tower when the system was off. However, this incident the tank was at a normal level. An erratic ph. meter reading had the control valve opening while the system was off along with the system not being isolated allowed acid to flow to the tower. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Operations |  | Mark Haynes | Michael Kennedy |  | Michael Kennedy | The conversation was with Jon Harriet. Proceeding so other can complete their tasks. | Michael Kennedy |  | Medium |  |  |  |  | 5.04 Inadequate update training | 6.02 Inadequate practice |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  |  | The OI was not followed when the system was shutdown. | 16. Failure to Follow Procedure, Policy, Practice | 13. Environmental Release |  | 2/5/2019-had some questions about the incident. Sent email with list of questions. Returned to investigation stage. 2/20/19 - chatted with Jonny Jonas and got clarification on my questions. 2/28/19 - Inserted two additional corrective actions per the conversation with Jonny Jonas. | [66 empty] | Concern of damage to circ. water system piping. At this time no visible damage. | 500 | Zachary Miller | Structural | [20 empty] | 483434
8654 | Horseshoe Lake Power Plant | 2019-01-07 08:40 | Place tower in service to start blowing down to pass our copper testing. After starting 8A Circulating water pump the Control Operator noticed the Cooling tower PH went low. He immediately called the Chemist and awaited further instruction. | Level 2 |  | FALSE | System Operational Incident | Donnie Jones |  |  |  | Power Supply | Mark Haynes | 2019-04-19 08:04 | 2019-01-07 13:31 | 2019-01-07 13:31 | 2019-02-20 14:35 | 2019-02-18 08:40 | 2019-01-07 13:10 | 2019-04-05 13:31 |  | 2019-02-28 13:58 | Horseshoe Lake Unit 8 Cooling Tower. |  |  | Jesse Murray | Approve. Jesse Murray | Power Supply |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Jon Harriet |  | The circulating water system was started and the low ph alarm came in. It was discovered that the sulfuric acid system was not isolated from the previous operation. This had allowed acid to seep into the tower during the shutdown period. Isolating the sulfuric acid system is a step on the OI for shutting down the circulating water system. The members who had shut the system down had forgotten about the new OI and did not utilize it. The shutdown of the circulating water system was added to the OI May 2, 2018 due to a similar incident which occurred February 14, 2018. Prior to this incident this had never been an issue. The acid system operates through an eductor off of the circulating water system and a control valve operates off of a ph. meter. It was believed that a contributing factor for the earlier incident was the level of the acid tanks. They were filled to a higher level than ever before because we had moved the acid from Mustang to here. The thought was that the weight of the acid had caused it to flow into the tower when the system was off. However, this incident the tank was at a normal level. An erratic ph. meter reading had the control valve opening while the system was off along with the system not being isolated allowed acid to flow to the tower. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Operations |  | Mark Haynes | Michael Kennedy |  | Michael Kennedy | The conversation was with Jon Harriet. Proceeding so other can complete their tasks. | Michael Kennedy |  | Medium |  |  |  |  | 5.04 Inadequate update training | 6.02 Inadequate practice |  |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  |  | The OI was not followed when the system was shutdown. | 16. Failure to Follow Procedure, Policy, Practice | 13. Environmental Release |  | 2/5/2019-had some questions about the incident. Sent email with list of questions. Returned to investigation stage. 2/20/19 - chatted with Jonny Jonas and got clarification on my questions. 2/28/19 - Inserted two additional corrective actions per the conversation with Jonny Jonas. | [66 empty] | Concern of damage to circ. water system piping. At this time no visible damage. | 500 | Zachary Miller | Structural | [20 empty] | 483434
8657 | Metro Service Center | 2019-01-03 06:30 | Employee was turning onto on ramp southbound Interstate 540 when a transformer fell off the trailer and spilled. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Delivery | John Legg | 2019-04-04 13:46 | 2019-01-07 14:10 | 2019-01-07 14:10 | 2019-03-18 16:17 | 2019-01-17 06:30 | 2019-01-03 10:00 | 2019-03-23 18:10 |  | 2019-03-18 16:23 | South bound on ramp to Interstate 540 near 5910 Rogers Avenue Fort Smith AR 72903 |  |  | William Young | Reviewed with John Legg 4/4/19 to clarify specific corrective actions to be taken by Fusion. Fusion was to inspect all of their tie-down straps to ensure that they had the correct type of strap (cargo) and replace as necessary. Will update corrective action statement and approve. WCY 4/4/19. | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | John Legg |  | contained in Fusions accident report |  |  |  | Metro Service Center | FALSE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  | Nicole Rhodes | Reviewed. | Nicole Rhodes |  | Medium |  |  |  |  | 5.01 Lack of experience | [11 empty] | Transformer not properly secured. Inadequate strap size and transformer placement. | 06. Using Defective Equipment | 12. Equipment Failure |  | Cause analysis needs to be completed. Let me know if you have any questions. MLH 2/12/19 No additional comments. MLH 3/18/19 |  |  |  | Property Damage |  | John Legg | Oil spill/damage to transformer |  |  |  |  | 3. Fall from Elevation to Lower Level | John Legg | Fusion Industries | Julius Alvarez |  | Vehicle (not related to vehicle's operation) |  | John Legg |  |  |  |  | FALSE | [66 empty] | none
8658 | Ada Service Center | 2019-01-07 12:30 | This is a First Aid Report. Member lost footing and twisted left knee, while stringing 3/0 sac cable through tree. | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Terry Looney | 2019-01-09 16:15 | 2019-01-07 15:26 | 2019-01-07 15:26 | 2019-01-07 15:31 | 2019-01-21 12:30 | 2019-01-07 15:07 |  |  |  | 600 W Main , Francis, OK |  |  | Terry Hackett | Reviewed/Approved | T&D Ops |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE |  |  | Member was working ticket for b/o 3/0 SAC secondary conductor. The 3/0 SAC conductor was down and laying through a tree. In order to string the wire through the tree, member stepped up in a fork of the tree approximately 2.5' high. While stringing the conductor through the tree the member's foot slipped and resulted in him landing on the ground on his left foot. Member stated he twisted his knee and was experiencing some discomfort. Member was advised to take first aid precautions (i.e. ice on and off for 15 minutes for the first 72 hours followed by heat if needed as well as OTC anti inflammatory medication). Followed up with member via phone on 1/09/2019 @ 3:40 PM and he stated that he had recovered and was no longer experiencing discomfort. |  |  | FALSE | Ada Service Center | FALSE |  | FALSE | Construction Services |  | Garrid Brown | Terry Looney |  |  |  | Kenneth McKinzie |  | Low | 1.01 Inappropriate height, weight, size, strength, reach, etc. | [7 empty] | 9.09 Inadequate identification and evaluation of loss exposures |  |  |  | 13.01 Inadequate assessment of needs and risks |  |  |  | Member's foot slipped from fork in tree | 11. Improper Position for Task | 3. Fall from Elevation to Lower Level | [26 empty] | FALSE |  |  | 2009-04-27 | 1988-05-06 |  | 2019-01-07 07:00 | 0 | 0 | Member has been advised to use ice in increments of 15 minutes on/15 minutes off in combination with OTC anti-inflammatory medication | FALSE | Male | Member lost footing and stepped backwards out of tree (approximately 3' high) |  | TRUE | Garrid Brown |  | First Aid | Garrid Brown |  |  |  |  | Sprain/Strain |  | FALSE |  | Area Service Technician | Knee |  | Left |  | Terry Looney | FALSE |  | 1/7/2019 7:00:00 AM |  | FALSE |  |  | The ground | [25 empty] | NA
8659 | Metro Service Center | 2019-01-03 17:30 | While on a storm related outage, Asplundh trimmer B was dropping an 8" diameter tree. The tree was loaded with ice and leaning slightly. The Arborist proceeded to cut the tree but did not follow procedures. Felling a tree of this size requires a rope in the tree to guide and control the tree. Also, the Arborist should have made a face cut on one side of the tree then finished with a back cut opposite the face cut, this prevents barber chair effect and allows the tree to fall useing hinge wood that prevents twisting. Failing to do this allowed the tree to barber chair which could have resulted in serious injury. | Level 1 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services | Wesley Lanier | 2019-02-15 11:34 | 2019-01-07 16:26 | 2019-01-07 16:26 | 2019-02-05 11:46 | 2019-01-17 17:30 | 2019-01-07 15:35 | 2019-02-13 10:42 |  |  | 949 Hickory Dr. Choctaw Ok |  |  | Jerrie Looney | Wrong attachment on this incident. This relates to hip incident - please remove and replace. J. Looney Approved. J. Looney 2.15.19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Wesley Lanier |  | While on a storm related outage, Asplundh trimmer B was dropping an 8" diameter tree. The tree was loaded with ice and leaning slightly. The Arborist proceeded to cut the tree but did not follow procedures. Felling a tree of this size requires a rope in the tree to guide and control the tree. Also, the Arborist should have made a face cut on one side of the tree then finished with a back cut opposite the face cut, this prevents barber chair effect and allows the tree to fall useing hinge wood that prevents twisting. Failing to do this allowed the tree to barber chair which could have resulted in serious injury. |  |  |  | Metro Service Center | FALSE |  | TRUE | PD - Resource Planning & Coord |  | Wesley Lanier | Wesley Lanier |  |  | Proper procedures discussed with crew. Issue should be resolved. Logged for future reference against JSO evaluations. No further action at this time. Cassada |  |  | Low |  |  | 3.02 Fatigue due to task load or duration |  | 5.01 Lack of experience | [11 empty] | possible fatigue due to weather conditions. A feeling of urgency due to the duration this particular outage. not trained to complete specific task | 16. Failure to Follow Procedure, Policy, Practice | 2. Struck By (Hit By Moving Object) | [5 empty] | Injury / Illness |  | Wesley Lanier | [5 empty] | 2. Struck By (Hit By Moving Object) | Wesley Lanier | Asplundh Tree Expert Co. | Asplundh Tree Expert Co. |  |  |  | Wesley Lanier | [71 empty] | N/A
8659 | Metro Service Center | 2019-01-03 17:30 | While on a storm related outage, Asplundh trimmer B was dropping an 8" diameter tree. The tree was loaded with ice and leaning slightly. The Arborist proceeded to cut the tree but did not follow procedures. Felling a tree of this size requires a rope in the tree to guide and control the tree. Also, the Arborist should have made a face cut on one side of the tree then finished with a back cut opposite the face cut, this prevents barber chair effect and allows the tree to fall useing hinge wood that prevents twisting. Failing to do this allowed the tree to barber chair which could have resulted in serious injury. | Level 1 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services | Wesley Lanier | 2019-02-15 11:34 | 2019-01-07 16:26 | 2019-01-07 16:26 | 2019-02-05 11:46 | 2019-01-17 17:30 | 2019-01-07 15:35 | 2019-02-13 10:42 |  |  | 949 Hickory Dr. Choctaw Ok |  |  | Jerrie Looney | Wrong attachment on this incident. This relates to hip incident - please remove and replace. J. Looney Approved. J. Looney 2.15.19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Wesley Lanier |  | While on a storm related outage, Asplundh trimmer B was dropping an 8" diameter tree. The tree was loaded with ice and leaning slightly. The Arborist proceeded to cut the tree but did not follow procedures. Felling a tree of this size requires a rope in the tree to guide and control the tree. Also, the Arborist should have made a face cut on one side of the tree then finished with a back cut opposite the face cut, this prevents barber chair effect and allows the tree to fall useing hinge wood that prevents twisting. Failing to do this allowed the tree to barber chair which could have resulted in serious injury. |  |  |  | Metro Service Center | FALSE |  | TRUE | PD - Resource Planning & Coord |  | Wesley Lanier | Wesley Lanier |  |  | Proper procedures discussed with crew. Issue should be resolved. Logged for future reference against JSO evaluations. No further action at this time. Cassada |  |  | Low |  |  | 3.02 Fatigue due to task load or duration |  | 5.03 Inadequate initial training | [11 empty] | possible fatigue due to weather conditions. A feeling of urgency due to the duration this particular outage. not trained to complete specific task | 16. Failure to Follow Procedure, Policy, Practice | 2. Struck By (Hit By Moving Object) | [5 empty] | Injury / Illness |  | Wesley Lanier | [5 empty] | 2. Struck By (Hit By Moving Object) | Wesley Lanier | Asplundh Tree Expert Co. | Asplundh Tree Expert Co. |  |  |  | Wesley Lanier | [71 empty] | N/A
8659 | Metro Service Center | 2019-01-03 17:30 | While on a storm related outage, Asplundh trimmer B was dropping an 8" diameter tree. The tree was loaded with ice and leaning slightly. The Arborist proceeded to cut the tree but did not follow procedures. Felling a tree of this size requires a rope in the tree to guide and control the tree. Also, the Arborist should have made a face cut on one side of the tree then finished with a back cut opposite the face cut, this prevents barber chair effect and allows the tree to fall useing hinge wood that prevents twisting. Failing to do this allowed the tree to barber chair which could have resulted in serious injury. | Level 1 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services | Wesley Lanier | 2019-02-15 11:34 | 2019-01-07 16:26 | 2019-01-07 16:26 | 2019-02-05 11:46 | 2019-01-17 17:30 | 2019-01-07 15:35 | 2019-02-13 10:42 |  |  | 949 Hickory Dr. Choctaw Ok |  |  | Jerrie Looney | Wrong attachment on this incident. This relates to hip incident - please remove and replace. J. Looney Approved. J. Looney 2.15.19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Wesley Lanier |  | While on a storm related outage, Asplundh trimmer B was dropping an 8" diameter tree. The tree was loaded with ice and leaning slightly. The Arborist proceeded to cut the tree but did not follow procedures. Felling a tree of this size requires a rope in the tree to guide and control the tree. Also, the Arborist should have made a face cut on one side of the tree then finished with a back cut opposite the face cut, this prevents barber chair effect and allows the tree to fall useing hinge wood that prevents twisting. Failing to do this allowed the tree to barber chair which could have resulted in serious injury. |  |  |  | Metro Service Center | FALSE |  | TRUE | PD - Resource Planning & Coord |  | Wesley Lanier | Wesley Lanier |  |  | Proper procedures discussed with crew. Issue should be resolved. Logged for future reference against JSO evaluations. No further action at this time. Cassada |  |  | Low |  |  | 3.03 Fatigue due to lack of rest |  | 5.01 Lack of experience | [11 empty] | possible fatigue due to weather conditions. A feeling of urgency due to the duration this particular outage. not trained to complete specific task | 16. Failure to Follow Procedure, Policy, Practice | 2. Struck By (Hit By Moving Object) | [5 empty] | Injury / Illness |  | Wesley Lanier | [5 empty] | 2. Struck By (Hit By Moving Object) | Wesley Lanier | Asplundh Tree Expert Co. | Asplundh Tree Expert Co. |  |  |  | Wesley Lanier | [71 empty] | N/A
8659 | Metro Service Center | 2019-01-03 17:30 | While on a storm related outage, Asplundh trimmer B was dropping an 8" diameter tree. The tree was loaded with ice and leaning slightly. The Arborist proceeded to cut the tree but did not follow procedures. Felling a tree of this size requires a rope in the tree to guide and control the tree. Also, the Arborist should have made a face cut on one side of the tree then finished with a back cut opposite the face cut, this prevents barber chair effect and allows the tree to fall useing hinge wood that prevents twisting. Failing to do this allowed the tree to barber chair which could have resulted in serious injury. | Level 1 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services | Wesley Lanier | 2019-02-15 11:34 | 2019-01-07 16:26 | 2019-01-07 16:26 | 2019-02-05 11:46 | 2019-01-17 17:30 | 2019-01-07 15:35 | 2019-02-13 10:42 |  |  | 949 Hickory Dr. Choctaw Ok |  |  | Jerrie Looney | Wrong attachment on this incident. This relates to hip incident - please remove and replace. J. Looney Approved. J. Looney 2.15.19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Wesley Lanier |  | While on a storm related outage, Asplundh trimmer B was dropping an 8" diameter tree. The tree was loaded with ice and leaning slightly. The Arborist proceeded to cut the tree but did not follow procedures. Felling a tree of this size requires a rope in the tree to guide and control the tree. Also, the Arborist should have made a face cut on one side of the tree then finished with a back cut opposite the face cut, this prevents barber chair effect and allows the tree to fall useing hinge wood that prevents twisting. Failing to do this allowed the tree to barber chair which could have resulted in serious injury. |  |  |  | Metro Service Center | FALSE |  | TRUE | PD - Resource Planning & Coord |  | Wesley Lanier | Wesley Lanier |  |  | Proper procedures discussed with crew. Issue should be resolved. Logged for future reference against JSO evaluations. No further action at this time. Cassada |  |  | Low |  |  | 3.03 Fatigue due to lack of rest |  | 5.03 Inadequate initial training | [11 empty] | possible fatigue due to weather conditions. A feeling of urgency due to the duration this particular outage. not trained to complete specific task | 16. Failure to Follow Procedure, Policy, Practice | 2. Struck By (Hit By Moving Object) | [5 empty] | Injury / Illness |  | Wesley Lanier | [5 empty] | 2. Struck By (Hit By Moving Object) | Wesley Lanier | Asplundh Tree Expert Co. | Asplundh Tree Expert Co. |  |  |  | Wesley Lanier | [71 empty] | N/A
8660 | Seminole PP; EGX Gath/Trans | 2019-01-08 15:00 | Member was taking backhoe to the river pump station and trailer fender made contact with rock on OGE road to pump station | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Supply | Matthew Cox | 2019-01-30 14:09 | 2019-01-08 17:16 | 2019-01-08 17:16 | 2019-01-28 06:08 | 2019-01-22 15:00 | 2019-01-08 15:30 | 2019-01-28 08:15 |  |  | Seminole power plant river pump station. |  |  | Chrysty Dorsey | See workflow comment for reason being returned to supervisor. - Reviewed and approved. | Power Supply |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Matthew Cox |  | On Tuesday January 8, 2019 member was moving metal to the Seminole river pump station house using truck F08-239 and trailer F20-808 when trailer fender came into contact with a large rock on the edge of the road bending fender into tire. The member was on a small gravel road going down the hill side to the pump station. This road was put in years ago so you can take trucks and trailer down it to avoid backing the trailer all the way to the pump station. The side road is on the side of a hill, it is a narrow road just wide enough for one vehicle and has a lot of large rocks placed on the side of it in spots to help control erosion. That morning the member took a backhoe to the pump station and took normal road in and tried to turn around to leave, but was not able to because of no room to turn around, so he took the side access road out. When coming back that afternoon with a load of metal the member decide to take the side road down, so he would not have to pull the backhoe out up the side road and could take the good road out. When taking a corner going down the hill the right side trailer fender clipped one of the large rocks on the edge of the road. The finder bent back into the tire causing damage to tire, but not deflating it. The tire was replaced and the finder straightened. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | Special Services |  | Danny Gist | Matthew Cox |  | Kelly Casey | Incident was investigated and action items were agreed upon. | Kelly Casey |  | Low | [12 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | Large rocks have been placed on the edge of the road to help control erosion of the road. | 39. Road Conditions | 1. Struck Against (Running or Bumping Into) | [74 empty] | TRUE |  | Konawa | Struck Fixed Object | Drove Forward Into Object | 2010-07-18 19:00 |  | FALSE |  |  | Day Light |  |  | Gravel |  | Clear |  |  | 615560
8661 | Northeast District Service Cen | 2019-01-04 21:00 | Member received trouble call and identified open wire secondary laying on fence still energized. No injury occurred. | Level 3 |  | TRUE | Member Injury |  | Lindle Coleman | Team Please work with appropriate resource from engineering | 2019-01-11 10:56 | Power Delivery | Randell Gilbert | 2019-02-08 10:45 | 2019-01-09 08:14 | 2019-01-09 08:13 | 2019-01-17 09:15 | 2019-01-18 21:00 | 2019-01-07 07:00 | 2019-01-21 14:24 | 2019-01-22 14:43 | 2019-01-17 09:34 | 211 E. 4th Shamrock, Ok |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Michael Gaunder |  | Completed: January 15, 2019 Incident: Member found downed open wire secondary still energized at 211 E. 4th Shamrock, Ok. On this date, there was a winter storm in effect. There was icing buildup on the cutout. The fuse did blow when the secondary wire contacted the fence as the tail of the fuse was hanging out of the fuse barrel, however the fuse barrel did not fall out of the cutout due to heavy ice. With the ice on the cutout, this allowed the electricity to track over the fuse barrel energizing transformer 42859 which energized the down secondary wire. There was not enough fault current to blow the lateral fuse feeding the transformer so the secondary remained energized until the ice was knocked off the fuse barrel which allowed the barrel to fall de-energizing the secondary. As part of this investigation, the following actions were taken: 1. Interviewed the member that responded to the call 2. Reviewed the trouble ticket 3. Reviewed video that the reporting member made of the fence glowing Sequence of Events 1. On January 4, 2019 at 21:04, troubleman responded to a partial lights/line down call. 2. On this evening of January 4th, winter conditions had set in including ice buildup on the wires and devices on the poles in this area. 3. Upon arriving at 211 E. 4th Shamrock, Ok, troubleman found open wire secondary laying on a fence and still energized. 4. After investigating, he found the fuse to transformer 42859 had blown as he saw the fuse tail hanging out of the fuse barrel. 5. He then noticed the fuse barrel did not fall open when the fuse blew due to heavy ice buildup on the cutout. With the ice buildup, the let the electricity track over the fuse barrel which energize transformer 42859 energizing the downed secondary wire. 6. He then knocked the ice off the cutout which allowed the fuse barrel to drop de-energizing the transformer. 7. There was not enough fault current to blow the lateral fuse that served transformer 42859. 8. The troubleman then spliced the secondary and re-energized transformer 42859 at 23:12. Synopsis On January 4, 2019, troubleman responded to a partial power/line down call at 211 E. 4th Shamrock, Ok. Upon arrival, troubleman found an open wire secondary phase had fallen on a metal fence and still energized. One of the fence posts was glowing red. The troubleman noticed the fuse barrel was still closed and the fuse tail hanging out of the fuse barrel. The ice buildup was enough to prevent the fuse barrel from opening when the fuse blew. The ice buildup allowed the electricity to track over the ice which kept the transformer energized although laying on the fence. The troubleman knocked the ice off the cutout which let the fuse barrel fall open de-energizing the transformer. The troubleman then made the necessary repairs and restored power. Conclusion: The investigation has determined that the Basic Root Cause(s) to this incident are as follows: 1. Weather – Ice buildup on the open secondary wire and the cutout | Michael Fox | Michael Gaunder |  | Northeast District Service Cen | FALSE |  | TRUE | Construction Services |  | Nicholas Manion | Randell Gilbert |  | Michael Fox | I approve. | Michael Fox | Lindle Coleman | High | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | Incident: Member found downed open wire secondary still energized at 211 E. 4th Shamrock, Ok. On this date, there was a winter storm in effect. There was icing buildup on the cutout. The fuse did blow when the secondary wire contacted the fence as the tail of the fuse was hanging out of the fuse barrel, however the fuse barrel did not fall out of the cutout due to heavy ice. With the ice on the cutout, this allowed the electricity to track over the fuse barrel energizing transformer 42859 which energized the down secondary wire. There was not enough fault current to blow the lateral fuse feeding the transformer so the secondary remained energized until the ice was knocked off the fuse barrel which allowed the barrel to fall de-energizing the secondary. As part of this investigation, the following actions were taken: 1. Interviewed the member that responded to the call 2. Reviewed the trouble ticket 3. Reviewed video that the reporting member made of the fence glowing Sequence of Events 1. On January 4, 2019 at 21:04, troubleman responded to a partial lights/line down call. 2. On this evening of January 4th, winter conditions had set in including ice buildup on the wires and devices on the poles in this area. 3. Upon arriving at 211 E. 4th Shamrock, Ok, troubleman found open wire secondary laying on a fence and still energized. 4. After investigating, he found the fuse to transformer 42859 had blown as he saw the fuse tail hanging out of the fuse barrel. 5. He then noticed the fuse barrel did not fall open when the fuse blew due to heavy ice buildup on the cutout. With the ice buildup, the let the electricity track over the fuse barrel which energize transformer 42859 energizing the downed secondary wire. 6. He then knocked the ice off the cutout which allowed the fuse barrel to drop de-energizing the transformer. 7. There was not enough fault current to blow the lateral fuse that served transformer 42859. 8. The troubleman then spliced the secondary and re-energized transformer 42859 at 23:12. Synopsis On January 4, 2019, troubleman responded to a partial power/line down call at 211 E. 4th Shamrock, Ok. Upon arrival, troubleman found an open wire secondary phase had fallen on a metal fence and still energized. One of the fence posts was glowing red. The troubleman noticed the fuse barrel was still closed and the fuse tail hanging out of the fuse barrel. The ice buildup was enough to prevent the fuse barrel from opening when the fuse blew. The ice buildup allowed the electricity to track over the ice which kept the transformer energized although laying on the fence. The troubleman knocked the ice off the cutout which let the fuse barrel fall open de-energizing the transformer. The troubleman then made the necessary repairs and restored power. Conclusion: The investigation has determined that the Basic Root Cause(s) to this incident are as follows: 1. Weather – Ice buildup on the open secondary wire and the cutout | 40. Weather Conditions | 12. Equipment Failure |  | I approve. | [90 empty] | PD-0104201900686
8661 | Northeast District Service Cen | 2019-01-04 21:00 | Member received trouble call and identified open wire secondary laying on fence still energized. No injury occurred. | Level 3 |  | TRUE | Member Injury |  | Lindle Coleman | Team Please work with appropriate resource from engineering | 2019-01-11 10:56 | Power Delivery | Randell Gilbert | 2019-02-08 10:45 | 2019-01-09 08:14 | 2019-01-09 08:13 | 2019-01-17 09:15 | 2019-01-18 21:00 | 2019-01-07 07:00 | 2019-01-21 14:24 | 2019-01-22 14:43 | 2019-01-17 09:34 | 211 E. 4th Shamrock, Ok |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Michael Gaunder |  | Completed: January 15, 2019 Incident: Member found downed open wire secondary still energized at 211 E. 4th Shamrock, Ok. On this date, there was a winter storm in effect. There was icing buildup on the cutout. The fuse did blow when the secondary wire contacted the fence as the tail of the fuse was hanging out of the fuse barrel, however the fuse barrel did not fall out of the cutout due to heavy ice. With the ice on the cutout, this allowed the electricity to track over the fuse barrel energizing transformer 42859 which energized the down secondary wire. There was not enough fault current to blow the lateral fuse feeding the transformer so the secondary remained energized until the ice was knocked off the fuse barrel which allowed the barrel to fall de-energizing the secondary. As part of this investigation, the following actions were taken: 1. Interviewed the member that responded to the call 2. Reviewed the trouble ticket 3. Reviewed video that the reporting member made of the fence glowing Sequence of Events 1. On January 4, 2019 at 21:04, troubleman responded to a partial lights/line down call. 2. On this evening of January 4th, winter conditions had set in including ice buildup on the wires and devices on the poles in this area. 3. Upon arriving at 211 E. 4th Shamrock, Ok, troubleman found open wire secondary laying on a fence and still energized. 4. After investigating, he found the fuse to transformer 42859 had blown as he saw the fuse tail hanging out of the fuse barrel. 5. He then noticed the fuse barrel did not fall open when the fuse blew due to heavy ice buildup on the cutout. With the ice buildup, the let the electricity track over the fuse barrel which energize transformer 42859 energizing the downed secondary wire. 6. He then knocked the ice off the cutout which allowed the fuse barrel to drop de-energizing the transformer. 7. There was not enough fault current to blow the lateral fuse that served transformer 42859. 8. The troubleman then spliced the secondary and re-energized transformer 42859 at 23:12. Synopsis On January 4, 2019, troubleman responded to a partial power/line down call at 211 E. 4th Shamrock, Ok. Upon arrival, troubleman found an open wire secondary phase had fallen on a metal fence and still energized. One of the fence posts was glowing red. The troubleman noticed the fuse barrel was still closed and the fuse tail hanging out of the fuse barrel. The ice buildup was enough to prevent the fuse barrel from opening when the fuse blew. The ice buildup allowed the electricity to track over the ice which kept the transformer energized although laying on the fence. The troubleman knocked the ice off the cutout which let the fuse barrel fall open de-energizing the transformer. The troubleman then made the necessary repairs and restored power. Conclusion: The investigation has determined that the Basic Root Cause(s) to this incident are as follows: 1. Weather – Ice buildup on the open secondary wire and the cutout | Randell Gilbert | Michael Gaunder |  | Northeast District Service Cen | FALSE |  | TRUE | Construction Services |  | Nicholas Manion | Randell Gilbert |  | Michael Fox | I approve. | Michael Fox | Lindle Coleman | High | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | Incident: Member found downed open wire secondary still energized at 211 E. 4th Shamrock, Ok. On this date, there was a winter storm in effect. There was icing buildup on the cutout. The fuse did blow when the secondary wire contacted the fence as the tail of the fuse was hanging out of the fuse barrel, however the fuse barrel did not fall out of the cutout due to heavy ice. With the ice on the cutout, this allowed the electricity to track over the fuse barrel energizing transformer 42859 which energized the down secondary wire. There was not enough fault current to blow the lateral fuse feeding the transformer so the secondary remained energized until the ice was knocked off the fuse barrel which allowed the barrel to fall de-energizing the secondary. As part of this investigation, the following actions were taken: 1. Interviewed the member that responded to the call 2. Reviewed the trouble ticket 3. Reviewed video that the reporting member made of the fence glowing Sequence of Events 1. On January 4, 2019 at 21:04, troubleman responded to a partial lights/line down call. 2. On this evening of January 4th, winter conditions had set in including ice buildup on the wires and devices on the poles in this area. 3. Upon arriving at 211 E. 4th Shamrock, Ok, troubleman found open wire secondary laying on a fence and still energized. 4. After investigating, he found the fuse to transformer 42859 had blown as he saw the fuse tail hanging out of the fuse barrel. 5. He then noticed the fuse barrel did not fall open when the fuse blew due to heavy ice buildup on the cutout. With the ice buildup, the let the electricity track over the fuse barrel which energize transformer 42859 energizing the downed secondary wire. 6. He then knocked the ice off the cutout which allowed the fuse barrel to drop de-energizing the transformer. 7. There was not enough fault current to blow the lateral fuse that served transformer 42859. 8. The troubleman then spliced the secondary and re-energized transformer 42859 at 23:12. Synopsis On January 4, 2019, troubleman responded to a partial power/line down call at 211 E. 4th Shamrock, Ok. Upon arrival, troubleman found an open wire secondary phase had fallen on a metal fence and still energized. One of the fence posts was glowing red. The troubleman noticed the fuse barrel was still closed and the fuse tail hanging out of the fuse barrel. The ice buildup was enough to prevent the fuse barrel from opening when the fuse blew. The ice buildup allowed the electricity to track over the ice which kept the transformer energized although laying on the fence. The troubleman knocked the ice off the cutout which let the fuse barrel fall open de-energizing the transformer. The troubleman then made the necessary repairs and restored power. Conclusion: The investigation has determined that the Basic Root Cause(s) to this incident are as follows: 1. Weather – Ice buildup on the open secondary wire and the cutout | 40. Weather Conditions | 12. Equipment Failure |  | I approve. | [90 empty] | PD-0104201900686
8661 | Northeast District Service Cen | 2019-01-04 21:00 | Member received trouble call and identified open wire secondary laying on fence still energized. No injury occurred. | Level 3 |  | TRUE | Member Injury |  | Lindle Coleman | Team Please work with appropriate resource from engineering | 2019-01-11 10:56 | Power Delivery | Randell Gilbert | 2019-02-08 10:45 | 2019-01-09 08:14 | 2019-01-09 08:13 | 2019-01-17 09:15 | 2019-01-18 21:00 | 2019-01-07 07:00 | 2019-01-21 14:24 | 2019-01-22 14:43 | 2019-01-17 09:34 | 211 E. 4th Shamrock, Ok |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Michael Gaunder |  | Completed: January 15, 2019 Incident: Member found downed open wire secondary still energized at 211 E. 4th Shamrock, Ok. On this date, there was a winter storm in effect. There was icing buildup on the cutout. The fuse did blow when the secondary wire contacted the fence as the tail of the fuse was hanging out of the fuse barrel, however the fuse barrel did not fall out of the cutout due to heavy ice. With the ice on the cutout, this allowed the electricity to track over the fuse barrel energizing transformer 42859 which energized the down secondary wire. There was not enough fault current to blow the lateral fuse feeding the transformer so the secondary remained energized until the ice was knocked off the fuse barrel which allowed the barrel to fall de-energizing the secondary. As part of this investigation, the following actions were taken: 1. Interviewed the member that responded to the call 2. Reviewed the trouble ticket 3. Reviewed video that the reporting member made of the fence glowing Sequence of Events 1. On January 4, 2019 at 21:04, troubleman responded to a partial lights/line down call. 2. On this evening of January 4th, winter conditions had set in including ice buildup on the wires and devices on the poles in this area. 3. Upon arriving at 211 E. 4th Shamrock, Ok, troubleman found open wire secondary laying on a fence and still energized. 4. After investigating, he found the fuse to transformer 42859 had blown as he saw the fuse tail hanging out of the fuse barrel. 5. He then noticed the fuse barrel did not fall open when the fuse blew due to heavy ice buildup on the cutout. With the ice buildup, the let the electricity track over the fuse barrel which energize transformer 42859 energizing the downed secondary wire. 6. He then knocked the ice off the cutout which allowed the fuse barrel to drop de-energizing the transformer. 7. There was not enough fault current to blow the lateral fuse that served transformer 42859. 8. The troubleman then spliced the secondary and re-energized transformer 42859 at 23:12. Synopsis On January 4, 2019, troubleman responded to a partial power/line down call at 211 E. 4th Shamrock, Ok. Upon arrival, troubleman found an open wire secondary phase had fallen on a metal fence and still energized. One of the fence posts was glowing red. The troubleman noticed the fuse barrel was still closed and the fuse tail hanging out of the fuse barrel. The ice buildup was enough to prevent the fuse barrel from opening when the fuse blew. The ice buildup allowed the electricity to track over the ice which kept the transformer energized although laying on the fence. The troubleman knocked the ice off the cutout which let the fuse barrel fall open de-energizing the transformer. The troubleman then made the necessary repairs and restored power. Conclusion: The investigation has determined that the Basic Root Cause(s) to this incident are as follows: 1. Weather – Ice buildup on the open secondary wire and the cutout | Hannah Everett | Michael Gaunder |  | Northeast District Service Cen | FALSE |  | TRUE | Construction Services |  | Nicholas Manion | Randell Gilbert |  | Michael Fox | I approve. | Michael Fox | Lindle Coleman | High | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | Incident: Member found downed open wire secondary still energized at 211 E. 4th Shamrock, Ok. On this date, there was a winter storm in effect. There was icing buildup on the cutout. The fuse did blow when the secondary wire contacted the fence as the tail of the fuse was hanging out of the fuse barrel, however the fuse barrel did not fall out of the cutout due to heavy ice. With the ice on the cutout, this allowed the electricity to track over the fuse barrel energizing transformer 42859 which energized the down secondary wire. There was not enough fault current to blow the lateral fuse feeding the transformer so the secondary remained energized until the ice was knocked off the fuse barrel which allowed the barrel to fall de-energizing the secondary. As part of this investigation, the following actions were taken: 1. Interviewed the member that responded to the call 2. Reviewed the trouble ticket 3. Reviewed video that the reporting member made of the fence glowing Sequence of Events 1. On January 4, 2019 at 21:04, troubleman responded to a partial lights/line down call. 2. On this evening of January 4th, winter conditions had set in including ice buildup on the wires and devices on the poles in this area. 3. Upon arriving at 211 E. 4th Shamrock, Ok, troubleman found open wire secondary laying on a fence and still energized. 4. After investigating, he found the fuse to transformer 42859 had blown as he saw the fuse tail hanging out of the fuse barrel. 5. He then noticed the fuse barrel did not fall open when the fuse blew due to heavy ice buildup on the cutout. With the ice buildup, the let the electricity track over the fuse barrel which energize transformer 42859 energizing the downed secondary wire. 6. He then knocked the ice off the cutout which allowed the fuse barrel to drop de-energizing the transformer. 7. There was not enough fault current to blow the lateral fuse that served transformer 42859. 8. The troubleman then spliced the secondary and re-energized transformer 42859 at 23:12. Synopsis On January 4, 2019, troubleman responded to a partial power/line down call at 211 E. 4th Shamrock, Ok. Upon arrival, troubleman found an open wire secondary phase had fallen on a metal fence and still energized. One of the fence posts was glowing red. The troubleman noticed the fuse barrel was still closed and the fuse tail hanging out of the fuse barrel. The ice buildup was enough to prevent the fuse barrel from opening when the fuse blew. The ice buildup allowed the electricity to track over the ice which kept the transformer energized although laying on the fence. The troubleman knocked the ice off the cutout which let the fuse barrel fall open de-energizing the transformer. The troubleman then made the necessary repairs and restored power. Conclusion: The investigation has determined that the Basic Root Cause(s) to this incident are as follows: 1. Weather – Ice buildup on the open secondary wire and the cutout | 40. Weather Conditions | 12. Equipment Failure |  | I approve. | [90 empty] | PD-0104201900686
8662 | McClain Power Plant | 2019-01-07 16:00 | OGE member was installing maintenance shop band saw. Member was moving the band saws(old and new). While moving a band saw the member drove the fork lift over the underground tornado shelter. The tornado shelter does not have a known load rate or is not rated to support load. | Level 3 |  | TRUE | Member Injury | Donnie Jones | Jesse Murray | Assigned Team Per Tony Shook | 2019-01-21 07:09 | Power Supply | Jeremy Loper | 2019-02-07 15:32 | 2019-01-09 15:29 | 2019-01-09 15:29 | 2019-01-23 09:52 | 2019-01-21 16:00 | 2019-01-09 15:19 | 2019-01-23 10:20 | 2019-02-04 08:14 | 2019-01-23 10:07 | McClain Plant Tornado Shelter (below) Skid-0130 |  |  | Donnie Jones | Appreciate the reporting of this incident and quick action taken to resolve. | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | TRUE |  | FALSE | TRUE | Jimmy Green |  | It was reported by the plant director that there were tire marks on the top of the underground storm shelter. The concern is whether the top of the underground storm shelter can support the weight of a forklift and load. The underground storm shelter was installed in 2001. The area around the underground storm shelter was gravel and about 6" lower than top of the storm shelter. An above ground storm shelter was installed next to the underground shelter in 2016. The area around both shelters was still gravel. In 2017 the area around both shelters was covered with concrete. Purpose for covering the area in concrete was to eliminate trip hazards when walking out of the administration building and to give easier access to the above ground shelter. Covering the area between the storm shelters and the road made it possible to drive on top of the underground storm shelter. This was not recognized as a hazard at the time the concrete was installed. A replacement band saw was purchased and delivered to the plant the first week of January. In the process of maneuvering the forklift to place the bandsaw, the wheels of the forklift crossed the top of the underground storm shelter. | Nolan Armstrong | Jimmy Green |  | McClain Power Plant | FALSE |  | TRUE | Maintenance |  | Jeremy Loper | Jeremy Loper |  | Jimmy Green | No comments | Jimmy Green | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | [7 empty] | Forklift was operated on the top of the underground storm shelter. Top of the underground shelter has no load rating. | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level | I Approve. Jesse Murray | Investigation was completed. This was a good catch. We have reviewed the incident with the plant and have also spoke on hazard recognition. Quote has been received for bollards. Will install bollards upon arrival. | [90 empty] | 615511
8662 | McClain Power Plant | 2019-01-07 16:00 | OGE member was installing maintenance shop band saw. Member was moving the band saws(old and new). While moving a band saw the member drove the fork lift over the underground tornado shelter. The tornado shelter does not have a known load rate or is not rated to support load. | Level 3 |  | TRUE | Member Injury | Donnie Jones | Jesse Murray | Assigned Team Per Tony Shook | 2019-01-21 07:09 | Power Supply | Jeremy Loper | 2019-02-07 15:32 | 2019-01-09 15:29 | 2019-01-09 15:29 | 2019-01-23 09:52 | 2019-01-21 16:00 | 2019-01-09 15:19 | 2019-01-23 10:20 | 2019-02-04 08:14 | 2019-01-23 10:07 | McClain Plant Tornado Shelter (below) Skid-0130 |  |  | Donnie Jones | Appreciate the reporting of this incident and quick action taken to resolve. | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | TRUE |  | FALSE | TRUE | Jimmy Green |  | It was reported by the plant director that there were tire marks on the top of the underground storm shelter. The concern is whether the top of the underground storm shelter can support the weight of a forklift and load. The underground storm shelter was installed in 2001. The area around the underground storm shelter was gravel and about 6" lower than top of the storm shelter. An above ground storm shelter was installed next to the underground shelter in 2016. The area around both shelters was still gravel. In 2017 the area around both shelters was covered with concrete. Purpose for covering the area in concrete was to eliminate trip hazards when walking out of the administration building and to give easier access to the above ground shelter. Covering the area between the storm shelters and the road made it possible to drive on top of the underground storm shelter. This was not recognized as a hazard at the time the concrete was installed. A replacement band saw was purchased and delivered to the plant the first week of January. In the process of maneuvering the forklift to place the bandsaw, the wheels of the forklift crossed the top of the underground storm shelter. | Tanner Brady | Jimmy Green |  | McClain Power Plant | FALSE |  | TRUE | Maintenance |  | Jeremy Loper | Jeremy Loper |  | Jimmy Green | No comments | Jimmy Green | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | [7 empty] | Forklift was operated on the top of the underground storm shelter. Top of the underground shelter has no load rating. | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level | I Approve. Jesse Murray | Investigation was completed. This was a good catch. We have reviewed the incident with the plant and have also spoke on hazard recognition. Quote has been received for bollards. Will install bollards upon arrival. | [90 empty] | 615511
8662 | McClain Power Plant | 2019-01-07 16:00 | OGE member was installing maintenance shop band saw. Member was moving the band saws(old and new). While moving a band saw the member drove the fork lift over the underground tornado shelter. The tornado shelter does not have a known load rate or is not rated to support load. | Level 3 |  | TRUE | Vehicle | Donnie Jones | Jesse Murray | Assigned Team Per Tony Shook | 2019-01-21 07:09 | Power Supply | Jeremy Loper | 2019-02-07 15:32 | 2019-01-09 15:29 | 2019-01-09 15:29 | 2019-01-23 09:52 | 2019-01-21 16:00 | 2019-01-09 15:19 | 2019-01-23 10:20 | 2019-02-04 08:14 | 2019-01-23 10:07 | McClain Plant Tornado Shelter (below) Skid-0130 |  |  | Donnie Jones | Appreciate the reporting of this incident and quick action taken to resolve. | Power Supply |  | Level 3 | Vehicle |  | FALSE | TRUE | TRUE |  | FALSE | TRUE | Jimmy Green |  | It was reported by the plant director that there were tire marks on the top of the underground storm shelter. The concern is whether the top of the underground storm shelter can support the weight of a forklift and load. The underground storm shelter was installed in 2001. The area around the underground storm shelter was gravel and about 6" lower than top of the storm shelter. An above ground storm shelter was installed next to the underground shelter in 2016. The area around both shelters was still gravel. In 2017 the area around both shelters was covered with concrete. Purpose for covering the area in concrete was to eliminate trip hazards when walking out of the administration building and to give easier access to the above ground shelter. Covering the area between the storm shelters and the road made it possible to drive on top of the underground storm shelter. This was not recognized as a hazard at the time the concrete was installed. A replacement band saw was purchased and delivered to the plant the first week of January. In the process of maneuvering the forklift to place the bandsaw, the wheels of the forklift crossed the top of the underground storm shelter. | Nolan Armstrong | Jimmy Green |  | McClain Power Plant | FALSE |  | TRUE | Maintenance |  | Jeremy Loper | Jeremy Loper |  | Jimmy Green | No comments | Jimmy Green | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | [7 empty] | Forklift was operated on the top of the underground storm shelter. Top of the underground shelter has no load rating. | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level | I Approve. Jesse Murray | Investigation was completed. This was a good catch. We have reviewed the incident with the plant and have also spoke on hazard recognition. Quote has been received for bollards. Will install bollards upon arrival. | [90 empty] | 615511
8662 | McClain Power Plant | 2019-01-07 16:00 | OGE member was installing maintenance shop band saw. Member was moving the band saws(old and new). While moving a band saw the member drove the fork lift over the underground tornado shelter. The tornado shelter does not have a known load rate or is not rated to support load. | Level 3 |  | TRUE | Vehicle | Donnie Jones | Jesse Murray | Assigned Team Per Tony Shook | 2019-01-21 07:09 | Power Supply | Jeremy Loper | 2019-02-07 15:32 | 2019-01-09 15:29 | 2019-01-09 15:29 | 2019-01-23 09:52 | 2019-01-21 16:00 | 2019-01-09 15:19 | 2019-01-23 10:20 | 2019-02-04 08:14 | 2019-01-23 10:07 | McClain Plant Tornado Shelter (below) Skid-0130 |  |  | Donnie Jones | Appreciate the reporting of this incident and quick action taken to resolve. | Power Supply |  | Level 3 | Vehicle |  | FALSE | TRUE | TRUE |  | FALSE | TRUE | Jimmy Green |  | It was reported by the plant director that there were tire marks on the top of the underground storm shelter. The concern is whether the top of the underground storm shelter can support the weight of a forklift and load. The underground storm shelter was installed in 2001. The area around the underground storm shelter was gravel and about 6" lower than top of the storm shelter. An above ground storm shelter was installed next to the underground shelter in 2016. The area around both shelters was still gravel. In 2017 the area around both shelters was covered with concrete. Purpose for covering the area in concrete was to eliminate trip hazards when walking out of the administration building and to give easier access to the above ground shelter. Covering the area between the storm shelters and the road made it possible to drive on top of the underground storm shelter. This was not recognized as a hazard at the time the concrete was installed. A replacement band saw was purchased and delivered to the plant the first week of January. In the process of maneuvering the forklift to place the bandsaw, the wheels of the forklift crossed the top of the underground storm shelter. | Tanner Brady | Jimmy Green |  | McClain Power Plant | FALSE |  | TRUE | Maintenance |  | Jeremy Loper | Jeremy Loper |  | Jimmy Green | No comments | Jimmy Green | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | [7 empty] | Forklift was operated on the top of the underground storm shelter. Top of the underground shelter has no load rating. | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level | I Approve. Jesse Murray | Investigation was completed. This was a good catch. We have reviewed the incident with the plant and have also spoke on hazard recognition. Quote has been received for bollards. Will install bollards upon arrival. | [90 empty] | 615511
8662 | McClain Power Plant | 2019-01-07 16:00 | OGE member was installing maintenance shop band saw. Member was moving the band saws(old and new). While moving a band saw the member drove the fork lift over the underground tornado shelter. The tornado shelter does not have a known load rate or is not rated to support load. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | Assigned Team Per Tony Shook | 2019-01-21 07:09 | Power Supply | Jeremy Loper | 2019-02-07 15:32 | 2019-01-09 15:29 | 2019-01-09 15:29 | 2019-01-23 09:52 | 2019-01-21 16:00 | 2019-01-09 15:19 | 2019-01-23 10:20 | 2019-02-04 08:14 | 2019-01-23 10:07 | McClain Plant Tornado Shelter (below) Skid-0130 |  |  | Donnie Jones | Appreciate the reporting of this incident and quick action taken to resolve. | Power Supply |  | Level 3 | Property Damage |  | FALSE | TRUE | TRUE |  | FALSE | TRUE | Jimmy Green |  | It was reported by the plant director that there were tire marks on the top of the underground storm shelter. The concern is whether the top of the underground storm shelter can support the weight of a forklift and load. The underground storm shelter was installed in 2001. The area around the underground storm shelter was gravel and about 6" lower than top of the storm shelter. An above ground storm shelter was installed next to the underground shelter in 2016. The area around both shelters was still gravel. In 2017 the area around both shelters was covered with concrete. Purpose for covering the area in concrete was to eliminate trip hazards when walking out of the administration building and to give easier access to the above ground shelter. Covering the area between the storm shelters and the road made it possible to drive on top of the underground storm shelter. This was not recognized as a hazard at the time the concrete was installed. A replacement band saw was purchased and delivered to the plant the first week of January. In the process of maneuvering the forklift to place the bandsaw, the wheels of the forklift crossed the top of the underground storm shelter. | Nolan Armstrong | Jimmy Green |  | McClain Power Plant | FALSE |  | TRUE | Maintenance |  | Jeremy Loper | Jeremy Loper |  | Jimmy Green | No comments | Jimmy Green | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | [7 empty] | Forklift was operated on the top of the underground storm shelter. Top of the underground shelter has no load rating. | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level | I Approve. Jesse Murray | Investigation was completed. This was a good catch. We have reviewed the incident with the plant and have also spoke on hazard recognition. Quote has been received for bollards. Will install bollards upon arrival. | [90 empty] | 615511
8662 | McClain Power Plant | 2019-01-07 16:00 | OGE member was installing maintenance shop band saw. Member was moving the band saws(old and new). While moving a band saw the member drove the fork lift over the underground tornado shelter. The tornado shelter does not have a known load rate or is not rated to support load. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | Assigned Team Per Tony Shook | 2019-01-21 07:09 | Power Supply | Jeremy Loper | 2019-02-07 15:32 | 2019-01-09 15:29 | 2019-01-09 15:29 | 2019-01-23 09:52 | 2019-01-21 16:00 | 2019-01-09 15:19 | 2019-01-23 10:20 | 2019-02-04 08:14 | 2019-01-23 10:07 | McClain Plant Tornado Shelter (below) Skid-0130 |  |  | Donnie Jones | Appreciate the reporting of this incident and quick action taken to resolve. | Power Supply |  | Level 3 | Property Damage |  | FALSE | TRUE | TRUE |  | FALSE | TRUE | Jimmy Green |  | It was reported by the plant director that there were tire marks on the top of the underground storm shelter. The concern is whether the top of the underground storm shelter can support the weight of a forklift and load. The underground storm shelter was installed in 2001. The area around the underground storm shelter was gravel and about 6" lower than top of the storm shelter. An above ground storm shelter was installed next to the underground shelter in 2016. The area around both shelters was still gravel. In 2017 the area around both shelters was covered with concrete. Purpose for covering the area in concrete was to eliminate trip hazards when walking out of the administration building and to give easier access to the above ground shelter. Covering the area between the storm shelters and the road made it possible to drive on top of the underground storm shelter. This was not recognized as a hazard at the time the concrete was installed. A replacement band saw was purchased and delivered to the plant the first week of January. In the process of maneuvering the forklift to place the bandsaw, the wheels of the forklift crossed the top of the underground storm shelter. | Tanner Brady | Jimmy Green |  | McClain Power Plant | FALSE |  | TRUE | Maintenance |  | Jeremy Loper | Jeremy Loper |  | Jimmy Green | No comments | Jimmy Green | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | [7 empty] | Forklift was operated on the top of the underground storm shelter. Top of the underground shelter has no load rating. | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level | I Approve. Jesse Murray | Investigation was completed. This was a good catch. We have reviewed the incident with the plant and have also spoke on hazard recognition. Quote has been received for bollards. Will install bollards upon arrival. | [90 empty] | 615511
8663 | Muskogee Power Plant | 2019-01-09 14:00 | while performing filter frame maintenance a DeWalt drill was placed on catwalk and fell 10' to concrete pit bottom breaking drill caseing | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Daniel Moffett | 2019-05-14 09:42 | 2019-01-09 16:54 | 2019-01-09 16:54 | 2019-01-11 15:32 | 2019-01-23 14:00 | 2019-01-09 16:44 | 2019-04-22 15:50 |  | 2019-01-21 09:13 | Muskogee Unit 5 B Circulating water pump motor |  |  | Jesse Murray | I Approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Daniel Moffett |  | On 1/9/19 a member reported they had dropped and damaged their battery operated Dewalt drill. upon the investigation it was quickly noted the member had placed the drill in a unstable position on the grating where a small section of toe board was missing. the drill dropped 10' off the mezzanine platform to the concrete pit floor. there was two members on the job one doing the work and another passing tools and supplies to him and watching for traffic and access to the work area (human barricade) due to limited access to the lower level (the stairs right were they were working). Upon further questioning of the task it was of my opinion fall protection should have been used and possibly confined space considerations of the motor compartment. The motor compartment is not currently in our confined space inventory. A separate incident has been initiated based on these findings. Fall protection was marked off on the SWP but was utilized on the opposite side of the motor as it is clearly needed. The missing toe board was not caught on the SWP on this job and over looked. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Maintenance |  | Daniel Moffett | Daniel Moffett |  | Andy Hedge | Reviewed and approved. Andy Hedge 4/22/19 | Andy Hedge |  | Medium |  |  |  |  | 5.06 Lack of situational awareness |  |  |  |  | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks |  |  |  | Tool placed by missing toe board and fell | 21. Inadequate Guards or Barriers | 3. Fall from Elevation to Lower Level |  | I don't believe this is a part of the conversion project, but I don't have any comments. MLH 1/21/19 | [90 empty] | 9575374
8663 | Muskogee Power Plant | 2019-01-09 14:00 | while performing filter frame maintenance a DeWalt drill was placed on catwalk and fell 10' to concrete pit bottom breaking drill caseing | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Daniel Moffett | 2019-05-14 09:42 | 2019-01-09 16:54 | 2019-01-09 16:54 | 2019-01-11 15:32 | 2019-01-23 14:00 | 2019-01-09 16:44 | 2019-04-22 15:50 |  | 2019-01-21 09:13 | Muskogee Unit 5 B Circulating water pump motor |  |  | Jesse Murray | I Approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Daniel Moffett |  | On 1/9/19 a member reported they had dropped and damaged their battery operated Dewalt drill. upon the investigation it was quickly noted the member had placed the drill in a unstable position on the grating where a small section of toe board was missing. the drill dropped 10' off the mezzanine platform to the concrete pit floor. there was two members on the job one doing the work and another passing tools and supplies to him and watching for traffic and access to the work area (human barricade) due to limited access to the lower level (the stairs right were they were working). Upon further questioning of the task it was of my opinion fall protection should have been used and possibly confined space considerations of the motor compartment. The motor compartment is not currently in our confined space inventory. A separate incident has been initiated based on these findings. Fall protection was marked off on the SWP but was utilized on the opposite side of the motor as it is clearly needed. The missing toe board was not caught on the SWP on this job and over looked. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Maintenance |  | Daniel Moffett | Daniel Moffett |  | Andy Hedge | Reviewed and approved. Andy Hedge 4/22/19 | Andy Hedge |  | Medium |  |  |  |  | 5.06 Lack of situational awareness |  |  |  |  | 10.04 Inadequate monitoring of construction |  |  | 13.01 Inadequate assessment of needs and risks |  |  |  | Tool placed by missing toe board and fell | 21. Inadequate Guards or Barriers | 3. Fall from Elevation to Lower Level |  | I don't believe this is a part of the conversion project, but I don't have any comments. MLH 1/21/19 | [90 empty] | 9575374
8664 | Sooner Power Plant | 2019-01-08 01:30 | Shift Supervisor conducting plant walk-down noticed fire protection system PIV 15 was laying on its side. Rough terrain tire tracks leading to PIV and tire rubber on PIV suggest valve was driven or backed over. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Daniel Dickinson | 2019-01-30 09:26 | 2019-01-09 22:15 | 2019-01-09 22:15 | 2019-01-21 10:39 | 2019-01-22 01:30 | 2019-01-09 22:01 | 2019-01-21 10:41 |  |  | Sooner Power Plant, east of Unit #1 boiler, 3 feet south east of #1 fuel oil burner pumps, at fire protection system PIV 15. |  |  | Brady Sowell | Approved by Brady Sowell | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Alexander Taybah |  | During his plant walk around, a Shift Supervisor noticed #15 Post Indicating Valve (PIV) was bent over as a result of a vehicle (truck, sky track, crane, etc.) most likely attempted to pass through a narrow path and ended up damaging it. Many avenues were used to investigate who (plant personnel and contractors) might've been working in that heavily trafficked area with no resolution. The gate camera in that area points in a different direction and an inspection of the sky tracks and other vehicles didn't show any signs of impact. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Operations |  | Daniel Dickinson | Daniel Dickinson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [7 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | It appears that the PIV has been hit by a vehicle trying to squeeze into a narrow path. | 21. Inadequate Guards or Barriers | 1. Struck Against (Running or Bumping Into) | [68 empty] | fire protection system PIV 15 was driven or backed over and is laying on its side. I would assume it is broken off underground and will need replaced. | 1000 | unknown-not reported | Fixed Equipment | [20 empty] | 9579947
8665 | Redbud Plant | 2019-01-10 07:00 | Contractors repairing HRSG tube leak on the night shift failed to sign in and out of Non-Permit Confined Space as per OGE Policy. No Injuries occurred. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Grant Craft | 2019-01-25 15:09 | 2019-01-10 09:39 | 2019-01-10 09:39 | 2019-01-11 14:06 | 2019-01-24 07:00 | 2019-01-10 09:18 | 2019-01-14 13:44 |  |  | Redbud Power Plant. Unit #1 HRSG Gas Path |  |  | Guillermo Sarmiento | Reviewed incident and agree with the information. Added some corrective actions. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Grant Craft |  | Contractors were performing tube leak repair on Unit #1 HRSG. The contractors were working day and night 12 hour shifts. There was a dayshift Confined Space Permit and a different permit for the nightshift to ensure that Entry Supervisors (OGE Member) were on site. On the morning of January 10th 2019, OGE plant contact went to check the atmosphere readings for the Dayshift Confined Space Permit and also entered another reading on the nightshift permit that was at the entry location. The OGE member realized that nightshift Bremco contractors were in the Confined Space but were not signed in to the entry log. OGE member had a discussion with the contractors about the requirement to sign in/out of the space each time and directed them to correct the entry log for this entry. Through further discussions it was found that another contractor (Superheat) had also entered the space during the night and also failed to sign in/out of the space. This job had been in progress for four days prior to this occurring and the contractors had been adhering to our policy of signing in/out of the space prior to this occurrence. On this particular night the contractors stated that they had forgotten to sign into the entry log and apologized for failing to do so. |  |  |  | Redbud Plant | FALSE |  | TRUE | Operations |  | Grant Craft | Thomas Ward |  | Robert Doupe | I approve | Robert Doupe |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Contractors failed to sign in/out of Non-Permit Confined Space | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Grant Craft | [5 empty] | 9. Abnormal Operation | Grant Craft | Bremco, Superheat | Zach Osgood, Fermin Medina |  |  |  | Grant Craft | [71 empty] | 9579764
8666 | Centennial Wind Farm | 2019-01-09 10:30 | Contractor was removing concrete with a jackhammer and punctured a piece of conduit that was encased in the concrete that had a fiber optic line contained in it. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Scott Zigler | 2019-02-06 13:53 | 2019-01-10 11:12 | 2019-01-10 11:12 | 2019-01-29 14:24 | 2019-01-23 10:30 | 2019-01-10 10:27 | 2019-01-31 16:07 |  |  | Pedestal base of turbine 56 at Centennial Wind Farm |  |  | Guillermo Sarmiento | 01.29.2019-Reviewed and has some recommendations. Sent back to Jason to send back to Scott to provide more information. Email was drafted and sent to Jason and Scott which include my recommendations. 02/03/19-made changes with Scott Zigler. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Scott Zigler |  | On January 9th at approximately 0930, contractor was using jackhammers to demolish a 3-4' thick concrete pad that the pad-mount transformer was sitting on next to the wind turbine. Due to the scale and nature of the project; the transformer needed to be moved and re-located further from the turbine. This also required the removal of the pad underneath the transformer which had the underground transmission cables and fiber optic communication cables encased in the concrete pad. The contractor, (Mortenson) has done numerous retrofit modification projects like this in the past, however none of them had the cables actually encased in the concrete, most have a basement type area under the pad-mount transformer. The conduit containing the fiber optic line that was damaged couldn't be seen or located because it was encased in a block of concrete approximately 3' thick, and there are no tracer wires in the conduit that contained the fiber optic cable. They were using all of the appropriate PPE for the task at the time of the incident. A safe work plan was conducted prior to performing tasks. One way to keep this from occurring would be to relocated the pad-mount transformer onto a vault which would keep all wires and cables accessible and removal of concrete would not be necessary. Adding vaults has been proposed and reviewed. Due to time constraints and frequency of this task being performed is minimal, the proposal was declined at this time. |  |  |  | Centennial Wind Farm | FALSE |  | FALSE | Renewable Energy |  | Scott Zigler | Scott Zigler |  | Jason Thomas | The contractor did not have a specific location for the fiber. All cables other than the fiber were being replaced. The jack hammer was used to expose all other cables with the intent to utilize the original fiber cable. Once the contractor determined an approximate location for the fiber, there was an attempt to remove concrete in small pieces with the jack hammer in an attempt to expose the fiber conduit. However when the jack hammer was positioned on the concrete directly above the fiber conduit and activated it broke through the concrete, rupturing the conduit and falling 2" in the void of the conduit eventually striking the fiber resting on the bottom of the inside of the conduit which severed the fiber upon contact. | Jason Thomas |  | Low | [5 empty] | 6.03 Infrequent performance |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications | [7 empty] | Due to the way the site was constructed with no tracer wires in the conduit, this was unavoidable. | 16. Failure to Follow Procedure, Policy, Practice | 2. Struck By (Hit By Moving Object) | [5 empty] | Property Damage |  | Scott Zigler | Damage to fiber optic cable |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Scott Zigler | Mortenson | Omar Villasaez |  | Portable Tool |  | Scott Zigler |  |  |  |  | FALSE | [66 empty] | 9568523
8666 | Centennial Wind Farm | 2019-01-09 10:30 | Contractor was removing concrete with a jackhammer and punctured a piece of conduit that was encased in the concrete that had a fiber optic line contained in it. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Scott Zigler | 2019-02-06 13:53 | 2019-01-10 11:12 | 2019-01-10 11:12 | 2019-01-29 14:24 | 2019-01-23 10:30 | 2019-01-10 10:27 | 2019-01-31 16:07 |  |  | Pedestal base of turbine 56 at Centennial Wind Farm |  |  | Guillermo Sarmiento | 01.29.2019-Reviewed and has some recommendations. Sent back to Jason to send back to Scott to provide more information. Email was drafted and sent to Jason and Scott which include my recommendations. 02/03/19-made changes with Scott Zigler. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Scott Zigler |  | On January 9th at approximately 0930, contractor was using jackhammers to demolish a 3-4' thick concrete pad that the pad-mount transformer was sitting on next to the wind turbine. Due to the scale and nature of the project; the transformer needed to be moved and re-located further from the turbine. This also required the removal of the pad underneath the transformer which had the underground transmission cables and fiber optic communication cables encased in the concrete pad. The contractor, (Mortenson) has done numerous retrofit modification projects like this in the past, however none of them had the cables actually encased in the concrete, most have a basement type area under the pad-mount transformer. The conduit containing the fiber optic line that was damaged couldn't be seen or located because it was encased in a block of concrete approximately 3' thick, and there are no tracer wires in the conduit that contained the fiber optic cable. They were using all of the appropriate PPE for the task at the time of the incident. A safe work plan was conducted prior to performing tasks. One way to keep this from occurring would be to relocated the pad-mount transformer onto a vault which would keep all wires and cables accessible and removal of concrete would not be necessary. Adding vaults has been proposed and reviewed. Due to time constraints and frequency of this task being performed is minimal, the proposal was declined at this time. |  |  |  | Centennial Wind Farm | FALSE |  | FALSE | Renewable Energy |  | Scott Zigler | Scott Zigler |  | Jason Thomas | The contractor did not have a specific location for the fiber. All cables other than the fiber were being replaced. The jack hammer was used to expose all other cables with the intent to utilize the original fiber cable. Once the contractor determined an approximate location for the fiber, there was an attempt to remove concrete in small pieces with the jack hammer in an attempt to expose the fiber conduit. However when the jack hammer was positioned on the concrete directly above the fiber conduit and activated it broke through the concrete, rupturing the conduit and falling 2" in the void of the conduit eventually striking the fiber resting on the bottom of the inside of the conduit which severed the fiber upon contact. | Jason Thomas |  | Low |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming | 10.03 Inadequate standards, specifications and/or design criteria | [6 empty] | The area in question had been identified as an area to use caution as to not damage the cable. There was an inadequate procedure when the site was constructed by encasing all of these cables in concrete. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Property Damage |  | Scott Zigler | Damage to fiber optic cable |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Scott Zigler | Mortenson | Omar Villasaez |  | Portable Tool |  | Scott Zigler |  |  |  |  | FALSE | [66 empty] | 9568523
8667 | West Service Center | 2019-01-11 07:30 | Member was pulling a butterfly reel out from underneath shelf when he experienced a pop in his left elbow accompanied by some discomfort. No medical treatment required at this time. | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Joshua Robertson | 2019-01-18 09:31 | 2019-01-11 10:15 | 2019-01-11 10:15 | 2019-01-14 09:49 | 2019-01-25 07:30 | 2019-01-11 10:01 |  |  |  | West District storage area |  |  | Luke Kennedy | Another follow up with the member has been conducted and his elbow has greatly improved. He was reminded to use team lifts when necessary and avoid placing side strains when performing lifts. | T&D Ops |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE |  |  | On 1/11/19 at 7:30 AM Member was preparing the truck for the days work. He went to the west district storage area and pulle a butterfly reel out from underneath shelf when he experienced a pop in his left elbow accompanied by some discomfort. The member did not feel that his elbow required medical attention at that time. The following Monday the member said his elbow felt much better and had improved over the weekend. |  |  | FALSE | West Service Center | FALSE |  | FALSE | Construction Services |  | Brandon Streber | Joshua Robertson |  |  |  | Terry Garrett |  | Low | [9 empty] | 10.02 Inadequate consideration of human factors/ergonomics | [6 empty] | Member was pulling a butterfly reel out from underneath shelf when he experienced a pop in his left elbow accompanied by some discomfort. No medical treatment required at this time. | 11. Improper Position for Task | 11. Overstress, Overpressure, Overexertion, Ergonomic | [26 empty] | FALSE |  |  | 2007-10-15 | 1982-12-28 |  | 2019-01-11 07:00 | 0 | 0 |  | FALSE | Male | Member was pulling a butterfly reel out from underneath shelf when he experienced a pop in his left elbow accompanied by some discomfort. |  |  | Brandon Streber |  | First Aid | Brandon Streber |  |  |  |  | Sprain/Strain |  | FALSE |  | Lineman | Elbow |  |  | FALSE | Joshua Robertson | FALSE |  | 1/11/2019 7:00:00 AM |  | FALSE |  |  | the strain placed on the elbow
8668 | Muskogee Power Plant | 2019-01-09 14:30 | While performing incident investigation on incident 8663; it is determined that the member was potentially exposed to fall risk due to th access point to the motor housing | Level 3 |  | TRUE | Member Injury | Donnie Jones | Jesse Murray | Assigned Per Jon S. | 2019-01-14 07:01 | Power Supply | Daniel Moffett | 2019-07-15 10:54 | 2019-01-11 13:32 | 2019-01-11 13:32 | 2019-06-24 07:39 | 2019-01-23 14:30 | 2019-01-11 13:20 | 2019-06-24 15:39 | 2019-07-14 12:31 | 2019-06-24 12:25 | Unit 5 Circulating Water pump motor 5B filter housing |  |  | Donnie Jones | Approved - Donnie Jones | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Andy Hedge |  | While investigating a dropped object incident (#8663), supervisor observed member accessing the filter compartment of 5B circulating water pump motor without the use of fall protection. Supervisor immediately stopped the job, discussed the findings with the member, provided necessary coaching and allowed the member to continue the assignment with the use of fall protection. The approximate height from the ground to the access point of the filter compartment is 10 ft. Job being performed: Installing clips in the filter compartment of the motor cover to provide support for filters when motor is offline (the filters tend to fall over inside the compartment when the motor is not in service). Additional findings: Member had failed to recognize the hazard. The area beneath the motor compartment is congested with conduit and piping. Member chose to cross the handrail and climb up on the piping without giving much thought to the risk of a fall. Member did state that although he believed the risk to be minimal, a fall would result in serious injury. Member also accessed the opposite end of the compartment for the same task and chose to wear fall protection at that time due to the location of the junction box at that end (pic below). Member also stated in the investigation that he had been sick and fatigued and this order had been in the backlog for a long period of time. He was not taking any shortcuts but failed to realize he was exposing himself to any risks. Further Findings: Redbud Filter Company is contracted to perform routine filter changes on many of the large motors throughout Muskogee Plant. In a meeting with them, we learned that this is one of 2 motors that they do not change filters on due to the risk of a fall. We also asked if they perform this work at any of the other plants in the fleet. Muskogee is currently the only plant they provide this service to. | Robert Wright | Andy Hedge |  | Muskogee Power Plant | FALSE |  | TRUE | Maintenance |  | Daniel Moffett | Daniel Moffett |  | Andy Hedge | Reviewed and approved. Andy Hedge 6/24/19 | Andy Hedge | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Member failed to use fall protection where required. | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level | Approved. Jesse Murray | I have reviewed this incident. The corrective actions address the causal factors of the incident. Bob Wright | [90 empty] | 9575374
8668 | Muskogee Power Plant | 2019-01-09 14:30 | While performing incident investigation on incident 8663; it is determined that the member was potentially exposed to fall risk due to th access point to the motor housing | Level 3 |  | TRUE | Member Injury | Donnie Jones | Jesse Murray | Assigned Per Jon S. | 2019-01-14 07:01 | Power Supply | Daniel Moffett | 2019-07-15 10:54 | 2019-01-11 13:32 | 2019-01-11 13:32 | 2019-06-24 07:39 | 2019-01-23 14:30 | 2019-01-11 13:20 | 2019-06-24 15:39 | 2019-07-14 12:31 | 2019-06-24 12:25 | Unit 5 Circulating Water pump motor 5B filter housing |  |  | Donnie Jones | Approved - Donnie Jones | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Andy Hedge |  | While investigating a dropped object incident (#8663), supervisor observed member accessing the filter compartment of 5B circulating water pump motor without the use of fall protection. Supervisor immediately stopped the job, discussed the findings with the member, provided necessary coaching and allowed the member to continue the assignment with the use of fall protection. The approximate height from the ground to the access point of the filter compartment is 10 ft. Job being performed: Installing clips in the filter compartment of the motor cover to provide support for filters when motor is offline (the filters tend to fall over inside the compartment when the motor is not in service). Additional findings: Member had failed to recognize the hazard. The area beneath the motor compartment is congested with conduit and piping. Member chose to cross the handrail and climb up on the piping without giving much thought to the risk of a fall. Member did state that although he believed the risk to be minimal, a fall would result in serious injury. Member also accessed the opposite end of the compartment for the same task and chose to wear fall protection at that time due to the location of the junction box at that end (pic below). Member also stated in the investigation that he had been sick and fatigued and this order had been in the backlog for a long period of time. He was not taking any shortcuts but failed to realize he was exposing himself to any risks. Further Findings: Redbud Filter Company is contracted to perform routine filter changes on many of the large motors throughout Muskogee Plant. In a meeting with them, we learned that this is one of 2 motors that they do not change filters on due to the risk of a fall. We also asked if they perform this work at any of the other plants in the fleet. Muskogee is currently the only plant they provide this service to. | Jerry Knight | Andy Hedge |  | Muskogee Power Plant | FALSE |  | TRUE | Maintenance |  | Daniel Moffett | Daniel Moffett |  | Andy Hedge | Reviewed and approved. Andy Hedge 6/24/19 | Andy Hedge | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Member failed to use fall protection where required. | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level | Approved. Jesse Murray | I have reviewed this incident. The corrective actions address the causal factors of the incident. Bob Wright | [90 empty] | 9575374
8668 | Muskogee Power Plant | 2019-01-09 14:30 | While performing incident investigation on incident 8663; it is determined that the member was potentially exposed to fall risk due to th access point to the motor housing | Level 3 |  | TRUE | Member Injury | Donnie Jones | Jesse Murray | Assigned Per Jon S. | 2019-01-14 07:01 | Power Supply | Daniel Moffett | 2019-07-15 10:54 | 2019-01-11 13:32 | 2019-01-11 13:32 | 2019-06-24 07:39 | 2019-01-23 14:30 | 2019-01-11 13:20 | 2019-06-24 15:39 | 2019-07-14 12:31 | 2019-06-24 12:25 | Unit 5 Circulating Water pump motor 5B filter housing |  |  | Donnie Jones | Approved - Donnie Jones | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Andy Hedge |  | While investigating a dropped object incident (#8663), supervisor observed member accessing the filter compartment of 5B circulating water pump motor without the use of fall protection. Supervisor immediately stopped the job, discussed the findings with the member, provided necessary coaching and allowed the member to continue the assignment with the use of fall protection. The approximate height from the ground to the access point of the filter compartment is 10 ft. Job being performed: Installing clips in the filter compartment of the motor cover to provide support for filters when motor is offline (the filters tend to fall over inside the compartment when the motor is not in service). Additional findings: Member had failed to recognize the hazard. The area beneath the motor compartment is congested with conduit and piping. Member chose to cross the handrail and climb up on the piping without giving much thought to the risk of a fall. Member did state that although he believed the risk to be minimal, a fall would result in serious injury. Member also accessed the opposite end of the compartment for the same task and chose to wear fall protection at that time due to the location of the junction box at that end (pic below). Member also stated in the investigation that he had been sick and fatigued and this order had been in the backlog for a long period of time. He was not taking any shortcuts but failed to realize he was exposing himself to any risks. Further Findings: Redbud Filter Company is contracted to perform routine filter changes on many of the large motors throughout Muskogee Plant. In a meeting with them, we learned that this is one of 2 motors that they do not change filters on due to the risk of a fall. We also asked if they perform this work at any of the other plants in the fleet. Muskogee is currently the only plant they provide this service to. | Michael Pugh | Andy Hedge |  | Muskogee Power Plant | FALSE |  | TRUE | Maintenance |  | Daniel Moffett | Daniel Moffett |  | Andy Hedge | Reviewed and approved. Andy Hedge 6/24/19 | Andy Hedge | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Member failed to use fall protection where required. | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level | Approved. Jesse Murray | I have reviewed this incident. The corrective actions address the causal factors of the incident. Bob Wright | [90 empty] | 9575374
8669 | Sooner Power Plant | 2019-01-11 08:30 | Metal from dumper got lodged in "C" feeder belt causing belt to be damaged | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Glen Hughes | 2019-04-11 11:17 | 2019-01-13 17:09 | 2019-01-13 17:09 | 2019-03-27 11:55 | 2019-01-25 08:30 | 2019-01-13 17:04 | 2019-03-29 09:36 |  |  | SoonerPP Dumper feeder belt "C". |  |  | Brady Sowell | Approved by Brady Sowell on 3/29/2019 | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Glen Hughes |  | While dumping a train on January 11, 2019 a Structural Cross Member from the rail car passed through the grizzlies lodging through "C" Dumper Feeder Belt, causing the belt to tear apart making it inoperable. The problem was assessed by Fuel Supply and it was determine to lock this belt out and continue to finish dumping the train and the trains following so there are no interruptions while AQCS (Scrubber) testing was being performed on Unit 2. It was known that this would slow the dumper feed rate and take longer to dump the trains until the belt could be replaced. On February 11, 2019 Evergreen was contracted to remove the coal over this belt so the cross member could be removed. On February 13, 2019 the cross member was removed from the belt so that we could determine its origin. (See attached pics “Structural Cross Member Lodged thru Dumper C Feeder Belt” and “Damaged Structural Cross Member”). IBT (Belt provider and Belt installer) immediately removed the damaged belt and replaced it with a new belt. It was assumed that this rail car cross member came from one of the last few cars from a borrowed BNSF train set that was the last train to dump prior to this incident, due to the cross members still being intact on the train being dumped when the incident occurred. This lead us to believe the cross member came the borrowed BSNF train set. After further investigation it was determined that the cross member did not come from the borrowed BNSF train set, based on the fact that the rail cars from BNSF have a completely different cross member design and configuration compared to the cross member retrieved from the Dumper Feeder Belt. This can be observed by looking at attached pictures “BNSF Cross Members” VS. “Structural Cross Member in OGE Rail Car”). Attached is an overall view of the Cross Member still intact on an OGE Rail Car (See “Structural Cross Member in Rail Car1”). It is clear that one side of the cross member had become fatigue and had been broken from the rail car structure for quite some time based on the foreign material that is on the break (see attached pic “Cross Member End that Initially Broke”). The evidence supports that while loading coal into the car at the coal mine is where the cross member that was initially broken got forced downward from the weight of coal being loaded. When this occurred it put other side of the cross member in a lot of stress causing it to partially separate further from the car structure. Once the rail car arrived at Sooner Plant to be emptied the cross member experience an upward force from the coal being emptied causing the cross member to tear completely from the rail car structure allowing it go through the Dumper grizzlies (see attached pic “Cross Member End that Allowed it to Leave the Car”). It is also became evident that the cross member got temporarily lodged cross ways in the chute leading to the belt. The cross member was lodged in its location when unloading the borrowed BNSF train set and did not become un-lodged until unloading the next train which created the incident. Fuel Supply is now looking for the OGE rail car with a missing cross member so rail car can be taken from the train set to be repaired. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Fuel Supply |  | Marcus McKiddy | Glen Hughes |  | Glen Hughes | Investigation is complete. The car that is missing a cross member will be identified and repaired. | Glen Hughes |  | Low | [14 empty] | 15.03 Inadequate inspection and/or monitoring |  | Structural Metal from rail car lost its structural integrity and was dumped with coal during unloading of a train | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure | [68 empty] | Piece of structural metal made it to the belt while belt was running tearing. The belt was torn. | 6500 | contracotr | Structural | [20 empty] | 9580138
8670 | Metro Service Center | 2019-01-05 09:30 | Driveway to house shaded by carport and inclined, sloping to the street. What happened - Slipped on inclined driveway covered in thin layer of black ice and scraped knuckle. Why it happened - Unable to see thin layer of ice in shaded area of driveway by carport. Action taken - Employee called GF and Supervisor. Supervisor drove to meet with employee. Employee put a band-aid on finger and continued permitting. | Level 1 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Wesley Lanier | 2019-02-15 11:04 | 2019-01-14 17:17 | 2019-01-14 17:17 | 2019-02-13 08:25 | 2019-01-19 09:30 | 2019-01-14 16:59 | 2019-02-13 10:43 |  |  | Connie Dr. Del city |  |  | Jerrie Looney | Returning to have contractor's incident report attached. J. Looney Employee will walk on grass in snow/ice conditions to have greater traction. J. Looney, 2.15.19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Wesley Lanier |  | Employee slipped on black ice on a shaded driveway. The employee fell and scratched his knuckles on the concrete |  |  |  | Metro Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Wesley Lanier | Wesley Lanier |  |  | Have reviewed incident - logged for records. No further action anticipated. Cassada |  |  | Low | 1.08 Other sensory deficiency (touch, taste, smell, balance) |  | 3.06 Exposure to temperature extremes | [13 empty] | in attention | 19. Failure to React, Correct | 4. Fall on Same Level (Slip and Fall, Trip Over) | [5 empty] | Injury / Illness |  | Wesley Lanier |  | scratched hand | FALSE |  |  | 1. Struck Against (Running or Bumping Into) | Wesley Lanier | U.S. Applicators | U.S. Applicators | Abrasion |  | Hand | Wesley Lanier |  | FALSE | [69 empty] | n/a
8671 | Shawnee Service Center | 2019-01-14 09:00 | Changing the desiccant chamber in the rear of analyzer rack.The chamber was attached to the analyzer rail with a tie wrap and needed to beremoved to change dessicant. Memberattempted to cut tywrap off of canister, slipped and cut thumb. | Level 2 |  | FALSE | Member Injury |  |  |  |  | OG&E Corp Services | Ronald Madron | 2019-05-24 15:02 | 2019-01-15 15:26 | 2019-01-15 15:26 | 2019-02-20 16:00 | 2019-01-28 09:00 | 2019-01-15 15:05 | 2019-05-23 10:37 |  | 2019-02-21 12:38 | Mustang Energy PP, Unit 6 Stack, EnvOps Testing Trailer #2 analyzer rack. |  |  | William Young | Reviewed and approved. WCY 5-24-19 | UTS |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Ronald Madron |  | Changing the desiccant chamber in the rear of analyzer rack. The chamber was attached to the analyzer rail with a tie wrap and needed to be removed to change desiccant. Member attempted to cut tie wrap off of canister, slipped and cut thumb |  |  | FALSE | Shawnee Service Center | FALSE |  | FALSE | UTS - Envir. & Process Chem |  | Ronald Madron | Ronald Madron |  | Thomas Leach | Reviewed by T Leach | Thomas Leach |  | Medium | [6 empty] | 7.06 Improper attempt to save time or effort | [9 empty] | Should have been using cutters instead of a knife to remove tie wraps | 15. Using Equipment Improperly | 2. Struck By (Hit By Moving Object) |  | Approved, 2/21/19 | [24 empty] | FALSE |  |  | 2017-12-11 | 1984-09-19 |  | 2019-01-14 06:00 | 0 | 0 |  | FALSE | Male | The desiccant for NOx analyzer needed changed. The chamber was attached to the analyzer rail with a tie wrap and needed to be removed to change dessicant. Member attempted to cut tywrap off of canister, slipped and cut index finger. |  |  | Nathaniel Shepherd |  | First Aid | Nathaniel Shepherd |  |  |  |  | Laceration |  | FALSE |  | Testing Technician I | Finger |  | Left |  | Ronald Madron | FALSE |  | 1/14/2019 6:00:00 AM | 13 months | FALSE |  |  | Blade | Preparing equipment for stack test. | [24 empty] | 18835486
8672 | Sooner Power Plant | 2019-01-16 15:30 | When stepping off bottom step of ladder, member stepped on recess concrete, twisted ankle and cause swelling in shin. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Michael Dowell | 2019-03-08 11:02 | 2019-01-17 10:12 | 2019-01-17 10:12 | 2019-02-13 16:36 | 2019-01-30 15:30 | 2019-01-17 09:53 | 2019-02-18 11:37 |  | 2019-02-15 07:40 | Sooner PP Unit 1 Mill Room 1E Room |  |  | Jesse Murray | I Approve. Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Michael Dowell |  | Contract member was removing separator body bolts. When the task was completed, he descended the ladder which was being held by another contract member. As he was stepping off the ladder, he placed his left foot in a recessed area of the floor. As he turned away from the ladder he twisted his ankle. This twisting caused swelling and a not on his lower left leg. Member placed ice on he swollen area. Zachary supervisor and OGE Plant Contact had very good discussion about identifying hazards and preventing this type of incident in the future. See attached document. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Maintenance |  | Lance Lantz | Michael Dowell |  | Frank Brixey | We really need to challenge the contractor for better corrective actions and to think through this scenario. They were extremely close to a recordable injury. A simple stand down does not seem adequate. Why did 2 employees not notice the hazard? Does it need to be painted for in the future? Brixey 2/4/2019 Approve - Brixey 2/18/2019 | Frank Brixey |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Failure to identify hazard (recess in floor at bottom of ladder) in work area. | 09. Improper Placement | 4. Fall on Same Level (Slip and Fall, Trip Over) |  | Approved by Brady Sowell |  |  |  | Injury / Illness |  | Michael Dowell |  | Twisted ankle, bruised shin | FALSE |  |  | 4. Fall on Same Level (Slip and Fall, Trip Over) | Lance Lantz | Zachary | Ty Morgan | Contusion |  | Ankle | Michael Dowell | Lower | FALSE | [69 empty] | none
8673 | North Service Center | 2019-01-16 13:30 | While traveling south in far right lane, attempted to change lanes. Checked mirror. Passenger warned me of car in blind spot. Avoided collision by braking. | Level 1 |  | TRUE | Vehicle |  |  |  |  | Power Delivery | Mark Loveless | 2019-01-21 07:02 | 2019-01-18 12:58 | 2019-01-18 12:58 | 2019-01-18 13:16 | 2019-01-30 13:30 | 2019-01-18 12:49 | 2019-01-18 16:18 |  |  | South bound Broadway Extension near Hefner Road exit. |  |  | Luke Kennedy | I appreciate Mark for turning this in as a good reminder on engagement behind the wheel. Approved 1/21/19 | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Mark Loveless |  | While traveling south in far right lane, attempted to change lanes. Checked mirror. Passenger warned me of car in blind spot. Avoided collision by braking. |  |  |  | North Service Center | FALSE |  | TRUE | Distribution Eng & Tech Services |  | Mark Loveless | Ronald Griffin |  | Ronald Griffin | This incident indicates value of passengers assisting driver. | Ronald Griffin |  | Low | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | Blind spot | 25. Inadequate Warning System | 1. Struck Against (Running or Bumping Into) | [92 empty] | NA
8674 | Muskogee Power Plant | 2018-12-26 14:30 | The insulation contractor (Brock) was installing insulation on a pipe and nicked a heat trace wire. This caused a small acre and left a burn mark the size of the tip of a pencil. No one was hurt. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Bradley Greening | 2019-02-22 13:05 | 2019-01-22 08:48 | 2019-01-22 08:48 | 2019-01-28 14:57 | 2019-01-09 14:30 | 2018-12-26 14:30 | 2019-01-30 10:11 |  |  | Belt 14 Compressor Station East of the coal yard |  |  | Chrysty Dorsey | Reviewed. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Bradley Greening |  | Employee was cutting around pipe insulation with a key hole saw and nicked the insulation of the 6 watt electric trace. Area involved two inches of limited space and should have been precut vs. cut in place. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | Power Supply Services |  | Bradley Greening | Bradley Greening |  |  | I am satisfied with the investigation and results. |  |  | Low | [6 empty] | 7.07 Improper attempt to avoid discomfort | [9 empty] | Employee was cutting around pipe insulation with a key hole saw and nicked the insulation of the 6 watt electric trace. Area involved two inches of limited space and should have been precut vs. cut in place. | 11. Improper Position for Task | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Property Damage |  | Bradley Greening | Nicked a heat trace line |  |  |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Bradley Greening | Brock | Terry Moler |  | Fixed Equipment |  | Bradley Greening |  |  |  |  | FALSE | [66 empty] | 9574879
8674 | Muskogee Power Plant | 2018-12-26 14:30 | The insulation contractor (Brock) was installing insulation on a pipe and nicked a heat trace wire. This caused a small acre and left a burn mark the size of the tip of a pencil. No one was hurt. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Bradley Greening | 2019-02-22 13:05 | 2019-01-22 08:48 | 2019-01-22 08:48 | 2019-01-28 14:57 | 2019-01-09 14:30 | 2018-12-26 14:30 | 2019-01-30 10:11 |  |  | Belt 14 Compressor Station East of the coal yard |  |  | Chrysty Dorsey | Reviewed. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Bradley Greening |  | Employee was cutting around pipe insulation with a key hole saw and nicked the insulation of the 6 watt electric trace. Area involved two inches of limited space and should have been precut vs. cut in place. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | Power Supply Services |  | Bradley Greening | Bradley Greening |  |  | I am satisfied with the investigation and results. |  |  | Low | [6 empty] | 7.06 Improper attempt to save time or effort | [9 empty] | Employee was cutting around pipe insulation with a key hole saw and nicked the insulation of the 6 watt electric trace. Area involved two inches of limited space and should have been precut vs. cut in place. | 11. Improper Position for Task | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Property Damage |  | Bradley Greening | Nicked a heat trace line |  |  |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Bradley Greening | Brock | Terry Moler |  | Fixed Equipment |  | Bradley Greening |  |  |  |  | FALSE | [66 empty] | 9574879
8675 | Northeast District Service Cen | 2019-01-18 11:30 | Crew was finishing a re-conductor along 141st between Lewis and Harvard. The crews were letting down the old wire on layout arms and it was drooping to the ground as they cut sections of the wire down. A member was lifting the old wire over a service pole with his extendo stick and it contacted the new wire that was energized primary voltage. When it made contact it blew the fuse at 141st and Harvard which also opened the circuit that was on a hot line hold. No one was injured. | Level 3 |  | TRUE | Member Injury |  | Lindle Coleman | incident reviewed by Lindle Coleman and team identified below. this incident was originally assigned as a medium and after investigation we re-assigned it as a high losing all info previously entered into intelex. I am assigning Hannah as lead to complete the report and capture the findings. | 2019-02-08 14:24 | Power Delivery | Donald Melson | 2019-03-29 08:41 | 2019-01-22 09:13 | 2019-01-22 09:13 | 2019-02-08 14:58 | 2019-02-01 11:30 | 2019-01-18 12:00 | 2019-02-11 09:15 | 2019-02-11 09:33 | 2019-02-08 14:59 | 141st and Lewis East of Bixby |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | TRUE | FALSE | Hannah Everett |  | On Friday January 18, 2019 -Three crews were finishing a re-conductor on 141st between Harvard and Lewis they were working behind a fuse with a hot line hold. After their tailboard they had split up for crew assignments making up jumpers, letting down wire and rolling up wire. -This was a multiple span job of primary wire removal that was 1/2 mile long down 141st West of Harvard. -The foreman had told them not to let any wire down until he contacted them about it being de-energized and on the ground. When he contacted them that it was on the ground and de-energized the buckets started letting #4 ACSR wire down off of layout arms. -At the point of contact a lineman was attempting to get the wire (that was let down) up and over a service pole with an extendo stick, while positioned on the ground. As the lineman was pushing the wire over the pole it was sliding do to a plastic gut taped for protection at the service pole. The lineman kept lifting the wire to get it over the service pole and made contact with the energized 477 conductor. -This blew a 40 amp fuse at 141st and Harvard and opened a circuit as there was a hot line hold on Beeline 1626 for the crews to make up jumpers at that intersection. -There was no one in contact with the conductor at the time of the incident. -It was found that the service pole was 34" away from the energized conductor. | Michael Fox | Hannah Everett |  | Northeast District Service Cen | FALSE |  | TRUE | Construction Services |  | Norris Carrier | Donald Melson |  | Michael Fox | I agree | Michael Fox | Lindle Coleman | High | [6 empty] | 7.06 Improper attempt to save time or effort | [9 empty] | Member lifted the dead phase to high making contact with the energized phase | 18. Failure to Check, Monitor | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | approved | Returning to re-rank risk. | [90 empty] | 7380538
8675 | Northeast District Service Cen | 2019-01-18 11:30 | Crew was finishing a re-conductor along 141st between Lewis and Harvard. The crews were letting down the old wire on layout arms and it was drooping to the ground as they cut sections of the wire down. A member was lifting the old wire over a service pole with his extendo stick and it contacted the new wire that was energized primary voltage. When it made contact it blew the fuse at 141st and Harvard which also opened the circuit that was on a hot line hold. No one was injured. | Level 3 |  | TRUE | Member Injury |  | Lindle Coleman | incident reviewed by Lindle Coleman and team identified below. this incident was originally assigned as a medium and after investigation we re-assigned it as a high losing all info previously entered into intelex. I am assigning Hannah as lead to complete the report and capture the findings. | 2019-02-08 14:24 | Power Delivery | Donald Melson | 2019-03-29 08:41 | 2019-01-22 09:13 | 2019-01-22 09:13 | 2019-02-08 14:58 | 2019-02-01 11:30 | 2019-01-18 12:00 | 2019-02-11 09:15 | 2019-02-11 09:33 | 2019-02-08 14:59 | 141st and Lewis East of Bixby |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | TRUE | FALSE | Hannah Everett |  | On Friday January 18, 2019 -Three crews were finishing a re-conductor on 141st between Harvard and Lewis they were working behind a fuse with a hot line hold. After their tailboard they had split up for crew assignments making up jumpers, letting down wire and rolling up wire. -This was a multiple span job of primary wire removal that was 1/2 mile long down 141st West of Harvard. -The foreman had told them not to let any wire down until he contacted them about it being de-energized and on the ground. When he contacted them that it was on the ground and de-energized the buckets started letting #4 ACSR wire down off of layout arms. -At the point of contact a lineman was attempting to get the wire (that was let down) up and over a service pole with an extendo stick, while positioned on the ground. As the lineman was pushing the wire over the pole it was sliding do to a plastic gut taped for protection at the service pole. The lineman kept lifting the wire to get it over the service pole and made contact with the energized 477 conductor. -This blew a 40 amp fuse at 141st and Harvard and opened a circuit as there was a hot line hold on Beeline 1626 for the crews to make up jumpers at that intersection. -There was no one in contact with the conductor at the time of the incident. -It was found that the service pole was 34" away from the energized conductor. | Donald Melson | Hannah Everett |  | Northeast District Service Cen | FALSE |  | TRUE | Construction Services |  | Norris Carrier | Donald Melson |  | Michael Fox | I agree | Michael Fox | Lindle Coleman | High | [6 empty] | 7.06 Improper attempt to save time or effort | [9 empty] | Member lifted the dead phase to high making contact with the energized phase | 18. Failure to Check, Monitor | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | approved | Returning to re-rank risk. | [90 empty] | 7380538
8675 | Northeast District Service Cen | 2019-01-18 11:30 | Crew was finishing a re-conductor along 141st between Lewis and Harvard. The crews were letting down the old wire on layout arms and it was drooping to the ground as they cut sections of the wire down. A member was lifting the old wire over a service pole with his extendo stick and it contacted the new wire that was energized primary voltage. When it made contact it blew the fuse at 141st and Harvard which also opened the circuit that was on a hot line hold. No one was injured. | Level 3 |  | TRUE | Member Injury |  | Lindle Coleman | incident reviewed by Lindle Coleman and team identified below. this incident was originally assigned as a medium and after investigation we re-assigned it as a high losing all info previously entered into intelex. I am assigning Hannah as lead to complete the report and capture the findings. | 2019-02-08 14:24 | Power Delivery | Donald Melson | 2019-03-29 08:41 | 2019-01-22 09:13 | 2019-01-22 09:13 | 2019-02-08 14:58 | 2019-02-01 11:30 | 2019-01-18 12:00 | 2019-02-11 09:15 | 2019-02-11 09:33 | 2019-02-08 14:59 | 141st and Lewis East of Bixby |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | TRUE | FALSE | Hannah Everett |  | On Friday January 18, 2019 -Three crews were finishing a re-conductor on 141st between Harvard and Lewis they were working behind a fuse with a hot line hold. After their tailboard they had split up for crew assignments making up jumpers, letting down wire and rolling up wire. -This was a multiple span job of primary wire removal that was 1/2 mile long down 141st West of Harvard. -The foreman had told them not to let any wire down until he contacted them about it being de-energized and on the ground. When he contacted them that it was on the ground and de-energized the buckets started letting #4 ACSR wire down off of layout arms. -At the point of contact a lineman was attempting to get the wire (that was let down) up and over a service pole with an extendo stick, while positioned on the ground. As the lineman was pushing the wire over the pole it was sliding do to a plastic gut taped for protection at the service pole. The lineman kept lifting the wire to get it over the service pole and made contact with the energized 477 conductor. -This blew a 40 amp fuse at 141st and Harvard and opened a circuit as there was a hot line hold on Beeline 1626 for the crews to make up jumpers at that intersection. -There was no one in contact with the conductor at the time of the incident. -It was found that the service pole was 34" away from the energized conductor. | Hannah Everett | Hannah Everett |  | Northeast District Service Cen | FALSE |  | TRUE | Construction Services |  | Norris Carrier | Donald Melson |  | Michael Fox | I agree | Michael Fox | Lindle Coleman | High | [6 empty] | 7.06 Improper attempt to save time or effort | [9 empty] | Member lifted the dead phase to high making contact with the energized phase | 18. Failure to Check, Monitor | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | approved | Returning to re-rank risk. | [90 empty] | 7380538
8675 | Northeast District Service Cen | 2019-01-18 11:30 | Crew was finishing a re-conductor along 141st between Lewis and Harvard. The crews were letting down the old wire on layout arms and it was drooping to the ground as they cut sections of the wire down. A member was lifting the old wire over a service pole with his extendo stick and it contacted the new wire that was energized primary voltage. When it made contact it blew the fuse at 141st and Harvard which also opened the circuit that was on a hot line hold. No one was injured. | Level 3 |  | TRUE | System Operational Incident |  | Lindle Coleman | incident reviewed by Lindle Coleman and team identified below. this incident was originally assigned as a medium and after investigation we re-assigned it as a high losing all info previously entered into intelex. I am assigning Hannah as lead to complete the report and capture the findings. | 2019-02-08 14:24 | Power Delivery | Donald Melson | 2019-03-29 08:41 | 2019-01-22 09:13 | 2019-01-22 09:13 | 2019-02-08 14:58 | 2019-02-01 11:30 | 2019-01-18 12:00 | 2019-02-11 09:15 | 2019-02-11 09:33 | 2019-02-08 14:59 | 141st and Lewis East of Bixby |  |  |  | Approve | T&D Ops |  | Level 3 | System Operational Incident |  | FALSE | TRUE | FALSE |  | TRUE | FALSE | Hannah Everett |  | On Friday January 18, 2019 -Three crews were finishing a re-conductor on 141st between Harvard and Lewis they were working behind a fuse with a hot line hold. After their tailboard they had split up for crew assignments making up jumpers, letting down wire and rolling up wire. -This was a multiple span job of primary wire removal that was 1/2 mile long down 141st West of Harvard. -The foreman had told them not to let any wire down until he contacted them about it being de-energized and on the ground. When he contacted them that it was on the ground and de-energized the buckets started letting #4 ACSR wire down off of layout arms. -At the point of contact a lineman was attempting to get the wire (that was let down) up and over a service pole with an extendo stick, while positioned on the ground. As the lineman was pushing the wire over the pole it was sliding do to a plastic gut taped for protection at the service pole. The lineman kept lifting the wire to get it over the service pole and made contact with the energized 477 conductor. -This blew a 40 amp fuse at 141st and Harvard and opened a circuit as there was a hot line hold on Beeline 1626 for the crews to make up jumpers at that intersection. -There was no one in contact with the conductor at the time of the incident. -It was found that the service pole was 34" away from the energized conductor. | Michael Fox | Hannah Everett |  | Northeast District Service Cen | FALSE |  | TRUE | Construction Services |  | Norris Carrier | Donald Melson |  | Michael Fox | I agree | Michael Fox | Lindle Coleman | High | [6 empty] | 7.06 Improper attempt to save time or effort | [9 empty] | Member lifted the dead phase to high making contact with the energized phase | 18. Failure to Check, Monitor | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | approved | Returning to re-rank risk. | [90 empty] | 7380538
8675 | Northeast District Service Cen | 2019-01-18 11:30 | Crew was finishing a re-conductor along 141st between Lewis and Harvard. The crews were letting down the old wire on layout arms and it was drooping to the ground as they cut sections of the wire down. A member was lifting the old wire over a service pole with his extendo stick and it contacted the new wire that was energized primary voltage. When it made contact it blew the fuse at 141st and Harvard which also opened the circuit that was on a hot line hold. No one was injured. | Level 3 |  | TRUE | System Operational Incident |  | Lindle Coleman | incident reviewed by Lindle Coleman and team identified below. this incident was originally assigned as a medium and after investigation we re-assigned it as a high losing all info previously entered into intelex. I am assigning Hannah as lead to complete the report and capture the findings. | 2019-02-08 14:24 | Power Delivery | Donald Melson | 2019-03-29 08:41 | 2019-01-22 09:13 | 2019-01-22 09:13 | 2019-02-08 14:58 | 2019-02-01 11:30 | 2019-01-18 12:00 | 2019-02-11 09:15 | 2019-02-11 09:33 | 2019-02-08 14:59 | 141st and Lewis East of Bixby |  |  |  | Approve | T&D Ops |  | Level 3 | System Operational Incident |  | FALSE | TRUE | FALSE |  | TRUE | FALSE | Hannah Everett |  | On Friday January 18, 2019 -Three crews were finishing a re-conductor on 141st between Harvard and Lewis they were working behind a fuse with a hot line hold. After their tailboard they had split up for crew assignments making up jumpers, letting down wire and rolling up wire. -This was a multiple span job of primary wire removal that was 1/2 mile long down 141st West of Harvard. -The foreman had told them not to let any wire down until he contacted them about it being de-energized and on the ground. When he contacted them that it was on the ground and de-energized the buckets started letting #4 ACSR wire down off of layout arms. -At the point of contact a lineman was attempting to get the wire (that was let down) up and over a service pole with an extendo stick, while positioned on the ground. As the lineman was pushing the wire over the pole it was sliding do to a plastic gut taped for protection at the service pole. The lineman kept lifting the wire to get it over the service pole and made contact with the energized 477 conductor. -This blew a 40 amp fuse at 141st and Harvard and opened a circuit as there was a hot line hold on Beeline 1626 for the crews to make up jumpers at that intersection. -There was no one in contact with the conductor at the time of the incident. -It was found that the service pole was 34" away from the energized conductor. | Donald Melson | Hannah Everett |  | Northeast District Service Cen | FALSE |  | TRUE | Construction Services |  | Norris Carrier | Donald Melson |  | Michael Fox | I agree | Michael Fox | Lindle Coleman | High | [6 empty] | 7.06 Improper attempt to save time or effort | [9 empty] | Member lifted the dead phase to high making contact with the energized phase | 18. Failure to Check, Monitor | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | approved | Returning to re-rank risk. | [90 empty] | 7380538
8675 | Northeast District Service Cen | 2019-01-18 11:30 | Crew was finishing a re-conductor along 141st between Lewis and Harvard. The crews were letting down the old wire on layout arms and it was drooping to the ground as they cut sections of the wire down. A member was lifting the old wire over a service pole with his extendo stick and it contacted the new wire that was energized primary voltage. When it made contact it blew the fuse at 141st and Harvard which also opened the circuit that was on a hot line hold. No one was injured. | Level 3 |  | TRUE | System Operational Incident |  | Lindle Coleman | incident reviewed by Lindle Coleman and team identified below. this incident was originally assigned as a medium and after investigation we re-assigned it as a high losing all info previously entered into intelex. I am assigning Hannah as lead to complete the report and capture the findings. | 2019-02-08 14:24 | Power Delivery | Donald Melson | 2019-03-29 08:41 | 2019-01-22 09:13 | 2019-01-22 09:13 | 2019-02-08 14:58 | 2019-02-01 11:30 | 2019-01-18 12:00 | 2019-02-11 09:15 | 2019-02-11 09:33 | 2019-02-08 14:59 | 141st and Lewis East of Bixby |  |  |  | Approve | T&D Ops |  | Level 3 | System Operational Incident |  | FALSE | TRUE | FALSE |  | TRUE | FALSE | Hannah Everett |  | On Friday January 18, 2019 -Three crews were finishing a re-conductor on 141st between Harvard and Lewis they were working behind a fuse with a hot line hold. After their tailboard they had split up for crew assignments making up jumpers, letting down wire and rolling up wire. -This was a multiple span job of primary wire removal that was 1/2 mile long down 141st West of Harvard. -The foreman had told them not to let any wire down until he contacted them about it being de-energized and on the ground. When he contacted them that it was on the ground and de-energized the buckets started letting #4 ACSR wire down off of layout arms. -At the point of contact a lineman was attempting to get the wire (that was let down) up and over a service pole with an extendo stick, while positioned on the ground. As the lineman was pushing the wire over the pole it was sliding do to a plastic gut taped for protection at the service pole. The lineman kept lifting the wire to get it over the service pole and made contact with the energized 477 conductor. -This blew a 40 amp fuse at 141st and Harvard and opened a circuit as there was a hot line hold on Beeline 1626 for the crews to make up jumpers at that intersection. -There was no one in contact with the conductor at the time of the incident. -It was found that the service pole was 34" away from the energized conductor. | Hannah Everett | Hannah Everett |  | Northeast District Service Cen | FALSE |  | TRUE | Construction Services |  | Norris Carrier | Donald Melson |  | Michael Fox | I agree | Michael Fox | Lindle Coleman | High | [6 empty] | 7.06 Improper attempt to save time or effort | [9 empty] | Member lifted the dead phase to high making contact with the energized phase | 18. Failure to Check, Monitor | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | approved | Returning to re-rank risk. | [90 empty] | 7380538
8676 | Muskogee Power Plant | 2019-01-22 07:30 | Member was checking the fuel level in the portable air compressor at the dumper. He raised the compressor lid and believed the lid latches engaged. The lid then stuck the member in the forehead causing a small laceration. Member was taken to clinic for first aid treatment. | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Supply |  | 2019-01-31 15:24 | 2019-01-22 10:46 | 2019-01-22 10:46 | 2019-01-23 15:09 | 2019-02-05 13:30 | 2019-01-22 10:28 |  |  |  | Portable air compressor at MK Dumper. |  |  | Robert Wright | Reviewed Bob Wright / Hold until call | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE |  |  | Member was not engaged to perform the task at hand which was to service the portable air compressor at the dumper. Personal factors include being in a rush to get to a doctors appointment and thinking about an upcoming surgery for an immediate family member. Also it was discovered that the Quincy air compressor that serves the dust suppression at the dumper was not reliable thus creating the need for the portable compressor. Other finding member failed to don hardhat before servicing the portable air compressor |  |  | FALSE | Muskogee Power Plant | FALSE |  | FALSE | Fuel Supply |  | Charles Harris | [6 empty] | Low |  |  |  | 4.09 Preoccupation with problems | [8 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | Member not engaged while servicing portable air compressor. Received laceration to upper forehead. Member was not wearing hardhat | 07. Failing to Use PPE Properly | 2. Struck By (Hit By Moving Object) | [26 empty] | FALSE |  |  | 1986-04-07 | 1963-10-25 |  | 2019-01-22 05:00 | 0 | 0 | Doctor cleaned and examined laceration and determined that stitches were not needed. | FALSE | Male | The lid on the side of the compressor was not securely latched. (The latch worked as designed) When the member leaned in to check fuel level the lid came down and hit member on the forehead. |  | TRUE | Charles Harris |  | First Aid | Charles Harris | FALSE |  | Med-Now | Richard Holsopple | Laceration |  | FALSE |  | Foreman Fuel Supply | Forehead |  | Front | FALSE | Jonathan Stogsdill | FALSE |  | 1/22/2019 5:00:00 AM | 30 plus years | TRUE | FALSE | FALSE | The lid from the temporary portable air compressor. | Driving to the compressor.
8677 | Sooner Power Plant | 2019-01-21 14:30 | Member was taking trash to the dumpster with small forklift and after dumping trash the forklift became stuck. While removing forklift the backrest was bent. | Level 2 |  | FALSE | Property Damage |  |  |  |  | OGE Energy Corp | Reginald Sanders | 2019-02-22 15:27 | 2019-01-22 15:34 | 2019-01-22 15:33 | 2019-01-30 11:59 | 2019-02-04 14:30 | 2019-01-22 15:21 | 2019-02-21 10:17 |  | 2019-01-30 12:06 | Sooner Power Plant north side of warehouse 1. |  |  | William Young | Reviewed and approved. WCY 2/22/19 | Enterprise Services |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Reginald Sanders |  | The member loaded up the forklift (F30-975) with trash to take to the dumpster located north of warehouse 1. The member drove the forklift (F30-975) on asphalt around the east side of the fuel tank, once the member got to the north side of the fuel tank the member drove off the asphalt on the gravel and proceed to dump the trash. After dumping the trash the member drove the forklift (F30-975) around the west side of the fuel tank which consisted of damp gravel and dirt. While proceeding back to the warehouse the forklift (F30-975) became stuck in the dirt and gravel. The member got off of the forklift (F30-975) and went got another forklift (F30-935) to try to free the stuck forklift (F30-975). The member pulled the forklift (F30-935) towards the stuck Forklift (F30-975) and hooked a ratchet strap to the front of the forklift (F30-935) backrest, the member proceeded to hook the other end of the ratchet strap to the backrest of the forklift (F30-975). The member proceeded backing up forklift (F30-935) pull the stuck forklift (F30-975), the member pulled the stuck forklift approximately 15 feet before being approached by his co-worker which stop the member from pull on the forklift (F30-975). The co-worker notice the backrest on forklift (F30-975) being bent in the process of being pulled. A Sooner PP member requested a contractor at the plant to come help get forklift (F30-975) unstuck. The contractor ( Zachary) got a skytrak and proceeded to the rear of forklift (F30-975) and began pushing the rear of the forklift (F30-975) until it became unstuck. No damages occurred to F30-935. Forklift (F30-975) was removed from service until inspection is completed on the front lifting carriage. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Supply Chain |  |  | Reginald Sanders |  | George Wicks | Have reviewed with supervisor. | George Wicks |  | Medium |  |  |  |  | 5.01 Lack of experience |  | 7.06 Improper attempt to save time or effort | [9 empty] | Member was taking trash to the dumpster with small forklift and after dumping trash the forklift became stuck. While removing forklift the backrest was bent. | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation |  | Approved, Cody Vinyard. | [66 empty] | Bent backrest of the forklift. | 500 | Johnny Jones | Industrial/Heavy Equipment |  | F30-975 | [18 empty] | .
8677 | Sooner Power Plant | 2019-01-21 14:30 | Member was taking trash to the dumpster with small forklift and after dumping trash the forklift became stuck. While removing forklift the backrest was bent. | Level 2 |  | FALSE | Property Damage |  |  |  |  | OGE Energy Corp | Reginald Sanders | 2019-02-22 15:27 | 2019-01-22 15:34 | 2019-01-22 15:33 | 2019-01-30 11:59 | 2019-02-04 14:30 | 2019-01-22 15:21 | 2019-02-21 10:17 |  | 2019-01-30 12:06 | Sooner Power Plant north side of warehouse 1. |  |  | William Young | Reviewed and approved. WCY 2/22/19 | Enterprise Services |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Reginald Sanders |  | The member loaded up the forklift (F30-975) with trash to take to the dumpster located north of warehouse 1. The member drove the forklift (F30-975) on asphalt around the east side of the fuel tank, once the member got to the north side of the fuel tank the member drove off the asphalt on the gravel and proceed to dump the trash. After dumping the trash the member drove the forklift (F30-975) around the west side of the fuel tank which consisted of damp gravel and dirt. While proceeding back to the warehouse the forklift (F30-975) became stuck in the dirt and gravel. The member got off of the forklift (F30-975) and went got another forklift (F30-935) to try to free the stuck forklift (F30-975). The member pulled the forklift (F30-935) towards the stuck Forklift (F30-975) and hooked a ratchet strap to the front of the forklift (F30-935) backrest, the member proceeded to hook the other end of the ratchet strap to the backrest of the forklift (F30-975). The member proceeded backing up forklift (F30-935) pull the stuck forklift (F30-975), the member pulled the stuck forklift approximately 15 feet before being approached by his co-worker which stop the member from pull on the forklift (F30-975). The co-worker notice the backrest on forklift (F30-975) being bent in the process of being pulled. A Sooner PP member requested a contractor at the plant to come help get forklift (F30-975) unstuck. The contractor ( Zachary) got a skytrak and proceeded to the rear of forklift (F30-975) and began pushing the rear of the forklift (F30-975) until it became unstuck. No damages occurred to F30-935. Forklift (F30-975) was removed from service until inspection is completed on the front lifting carriage. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Supply Chain |  |  | Reginald Sanders |  | George Wicks | Have reviewed with supervisor. | George Wicks |  | Medium |  |  |  |  | 5.06 Lack of situational awareness |  | 7.06 Improper attempt to save time or effort | [9 empty] | Member was taking trash to the dumpster with small forklift and after dumping trash the forklift became stuck. While removing forklift the backrest was bent. | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation |  | Approved, Cody Vinyard. | [66 empty] | Bent backrest of the forklift. | 500 | Johnny Jones | Industrial/Heavy Equipment |  | F30-975 | [18 empty] | .
8678 | Shawnee Service Center | 2019-01-22 23:30 | While diving east bound on HWY 9 around midnight in route to a "call out", a deer ran from the side of the road and hit between the drivers side tire and fender. The impact resulted in a broken fender and the deer was dragged under the vehicle.. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Jeffrey Gleim | 2019-01-25 14:06 | 2019-01-23 11:34 | 2019-01-23 11:34 | 2019-01-23 11:38 | 2019-02-05 23:30 | 2019-01-23 11:29 |  |  |  | 2 miles east of Earlsboro on hwy 9 |  |  | Brent Perdue | approved. A more detailed description was added on 1/30/2019 | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE |  |  | No investigation was conducted due to the low risk ranking of the "Not at Fault" vehicle incident. Pictures have been added to this report in the "Document Attachments" section. |  |  |  | Shawnee Service Center | FALSE |  | FALSE | Construction Services |  |  | Jeffrey Gleim |  |  |  | Steve Watkins |  | Low | [93 empty] | FALSE |  | Earlsboro | Animal-related |  |  |  | FALSE |  |  | Night |  |  | Asphalt |  | Cloudy
8679 | Metro Service Center | 2019-01-17 15:00 | While attempting to open the cover of a disconnect switch, the operating handle of the switch fell open. This caused a transmission breaker to open. | Level 1 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | James Hutchison | 2019-03-25 08:27 | 2019-01-23 13:14 |  | 2019-03-20 08:02 | 2019-02-28 15:00 | 2019-01-17 16:00 | 2019-03-24 12:32 |  |  | Draper Lake Substation |  |  | Cody Magby | approve cm | T&D Ops |  | Level 1 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | James Hutchison |  | Operational Incident Summary On Thursday, January 17th at Draper Lake substation a maintenance technician was asked by a contractor who was working on site to look at a PT disconnect switch that might not have closed properly. While attempting to open the cover of the 4B35PT1 disconnect switch to determine the problem the operating handle of the switch opened. This caused the 138kv PCB 105 breaker to open due to a loss of voltage to the protection relays. The technician immediately closed the disconnect switch handle restoring voltage to the protection relays and PCB 105 reclosed. Due to the operation of the breaker the TCC operator contacted the technician and asked about the breaker operation. The cause of the operation was discussed, it was determined that conditions were safe to continue switching so the technician was given authorization to proceed with his switching. Chain of Events: • A two man maintenance crew arrived at Draper Lake substation to conduct switching that would place the 138kv Bus 2 back in service by performing SWO S002. • Once on site they contacted the TCC to get authorization to begin conducting SWO S0002. o While one technician was on the phone with TCC a contractor working at the substation approached the other technician and informed him that there was a PT disconnect switch that was not closed properly. The contractor asked if they would check the switch to ensure it was closed properly. • The technicians decided to check the PT disconnect switch before starting their switching. So, they proceeded to the area the contractor indicated the switch was located and began checking each PT disconnect switch along the way. When they arrived at PT disconnect switch 4B35PT1 and attempted to remove the cover to inspect the internal parts of the switch the disconnect handle opened. • When the 4B35PT1 disconnect switch opened PCB 105 tripped open. • The technician immediately closed the disconnect switch handle and PCB 105 reclosed. • Due to the operation of the breaker the TCC operator contacted the technician and inquired into the nature of the event that had just occurred. o The maintenance technician informed the TCC operator that while he was attempting to open the cover of the switch he “bumped the handle and tripped it off” when he “accidently hit the handle”. o The technician then stated he “grabbed the handle and threw it back” and the breaker reclosed. • After the incident the maintenance crew went to the contractor and asked him to properly identify which PT disconnect switch was not closed correctly. o The contractor took them to the 4B38PT1 disconnect switch. o The crew opened the cover and discovered that one of the blades was not seated in the jaw properly. They got a screw driver out and manually pushed the blade back into the jaw. • The maintenance crew then proceeded to complete their switching assignment. Incident Facts Ascertained: • The maintenance crew was comprised of two apprentices’. • The maintenance crew went to Draper Lake substation to conduct switching; their assignment was to place the 138kv Bus 2 back in service. • While one technician was on the phone with the TCC operator receiving permission to start SWO S002 the other technician was approached by a contractor working on site. o The contractor informed the technician that he believed there was a PT disconnect switch that was not closed properly and asked them to check the switch.  The contractor did not identify the PT disconnect switch by operating number, he pointed in a direction and stated the switch “was one over there”. At this time, the maintenance technician did not ask for any additional information that would have identified which switch the contractor was referring to that needed to be checked. • Without confirming which PT disconnect switch was in question the maintenance crew proceeded to check each disconnect switch that was in the direction that the contractor had pointed towards. o PT disconnect switch 4B35PT1 was the third switch they went to check but it was not the switch that the contractor intended them to check. o The cover to the 4B35PT1 disconnect switch was difficult to remove and the technician shook it in an attempt to get the cover opened. While moving the cover the handle was bumped and it came open. • When the PT disconnect was opened the restraint voltage was lost to the protection relays. This allowed PCB 105 to open, when the disconnect switch was closed back voltage was restored to the relays and the breaker reclosed. • PT disconnect switch 4B38PT1 was the switch that was not closed properly; the blade was not seated in the jaw correctly and had to be pushed in manually by the maintenance technician. • PT disconnect switch 4B38PT1 was taken out of service and inspected. o No damage to the switch was identified. o The switch operated and functioned properly. Causal Factors: • The PT disconnect switch handle was moved to the open position when it was bumped by the maintenance technician while he was attempting to remove the cover to allow the internal parts of the switch to be inspected. |  |  |  | Metro Service Center | FALSE |  | FALSE | System Operations |  | John Bull | James Hutchison |  | Andrea Dennis | I have reviewed the incident and agree with the investigation and the corrective actions. | Andrea Dennis |  | Low | [111 empty] | 1646061
8680 | General Service Center | 2019-01-22 10:00 | An Anixter employee was cleaning the west parking lot and entrance ramp of building B using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. | Level 4 |  | TRUE | Contractor | Stephen Merrill | Jerrod Moser | Please get investigation done within 30 days. | 2019-01-31 13:23 | OGE Energy Corp | Jeffery Richardson | 2019-04-08 15:24 | 2019-01-23 17:03 | 2019-01-23 | 2019-02-28 15:55 | 2019-02-28 | 2019-01-23 10:00 | 2019-03-18 10:33 |  |  | General Service Center Building B |  |  | Jerrod Moser | Approved | Enterprise Services |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Cody Vinyard |  | An Anixter employee was cleaning the west parking lot and entrance ramp of building B at GSC using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. 01-22-19 (approximate time line) 9:55 a.m.-Anixter member was coming to the end of her sweeping routine when she pulls over toward NW side of building B, drives by the generator near the employee entrance and comes back to NW corner and makes a U turn and backs into gas pipe trying to readjust 10:00 a.m.-Anixter Member strikes gas pipe at the end of her sweeping route and calls Steven Dorsey because she smells gas 10:05 a.m.-Steven calls Dale Thompson (operations manager Anixter) 10:14 a.m. -Glen McClain calls OGE 2001 and no answer, then calls Phil Messer, buildings A,B,C evacuated 10:15 a.m. Phil Messer call ONG and directs Steve Smith to call OKC Fire Department 10:25 a.m.-ONG/Fire Department responds to GSC leak 10:30 a.m.-Fire Department checks for residual gas ppm 11:00 a.m.- GSC given permission to leave/return by 1:00 p.m. 1:00 p.m.-Leak isolated/mitigated, fans running, employees return to work. Interview with Anixter Member: Dawn Smith Generally sweep every other day, minimum once a week. Very Detailed Sweep Path that reaches all areas of warehouse and areas throughout the yard and parking lots. Bill Bain(retired OGE)-initial orientation (7 years ago) on Armadillo Diesel Sweeper usage (operation and dump). Dawn currently gives majority of “orientation” to employees who use sweeper. Float on Armadillo Sweeper does not work currently (has been called in but, never repaired) Never required to do pre-op inspection. Dawn stated: “I wish I had know that was a gas pipe and I would have never come anywhere near close.” No labeling or identification of pipe. Gas Line description: 2” GAS LINE THAT FEEDS –HEATERS IN THE WAREHOUSE, Building B Facility Generator. Armadillo strikes ¾” pressure gauge on bottom of gas line 29” from ground. Gas Line PSI 10-14 PSIG Gas Line is painted same color as building with no exterior labeling Diesel Sweeper Findings: No Operator Manual Present No Pre-Operational Inspection Float did not work, called in but never repaired correctly. Operator (Dawn) Findings: No formal training Last “training” was given seven years ago, upon purchase of sweeper by now retired OGE Member OGE (retired) “trainer” was never formally trained. Prior knowledge was used for training to Anixter members. Very good process used for work path flow (sweeping facility), employee takes the same route every time the task is performed. Operator is the agreed trainer for Anixter on the Armadillo Sweeper Primary operator of sweeper Gas hazard had not been identified by operator or facility. | Glen McClain | Cody Vinyard |  | General Service Center | FALSE |  | TRUE | Supply Chain |  | Jeffery Richardson | Jeffery Richardson |  | Stephen Merrill | ` |  |  | Very High | [9 empty] | 10.08 Inadequate evaluation of changes |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | An Anixter employee was cleaning the west parking lot and entrance ramp of building B using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Jeffery Richardson | [5 empty] | 1. Struck Against (Running or Bumping Into) | Jeffery Richardson | Anixter | Dawn Smith |  |  |  | Jeffery Richardson | [71 empty] | .
8680 | General Service Center | 2019-01-22 10:00 | An Anixter employee was cleaning the west parking lot and entrance ramp of building B using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. | Level 4 |  | TRUE | Contractor | Stephen Merrill | Jerrod Moser | Please get investigation done within 30 days. | 2019-01-31 13:23 | OGE Energy Corp | Jeffery Richardson | 2019-04-08 15:24 | 2019-01-23 17:03 | 2019-01-23 | 2019-02-28 15:55 | 2019-02-28 | 2019-01-23 10:00 | 2019-03-18 10:33 |  |  | General Service Center Building B |  |  | Jerrod Moser | Approved | Enterprise Services |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Cody Vinyard |  | An Anixter employee was cleaning the west parking lot and entrance ramp of building B at GSC using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. 01-22-19 (approximate time line) 9:55 a.m.-Anixter member was coming to the end of her sweeping routine when she pulls over toward NW side of building B, drives by the generator near the employee entrance and comes back to NW corner and makes a U turn and backs into gas pipe trying to readjust 10:00 a.m.-Anixter Member strikes gas pipe at the end of her sweeping route and calls Steven Dorsey because she smells gas 10:05 a.m.-Steven calls Dale Thompson (operations manager Anixter) 10:14 a.m. -Glen McClain calls OGE 2001 and no answer, then calls Phil Messer, buildings A,B,C evacuated 10:15 a.m. Phil Messer call ONG and directs Steve Smith to call OKC Fire Department 10:25 a.m.-ONG/Fire Department responds to GSC leak 10:30 a.m.-Fire Department checks for residual gas ppm 11:00 a.m.- GSC given permission to leave/return by 1:00 p.m. 1:00 p.m.-Leak isolated/mitigated, fans running, employees return to work. Interview with Anixter Member: Dawn Smith Generally sweep every other day, minimum once a week. Very Detailed Sweep Path that reaches all areas of warehouse and areas throughout the yard and parking lots. Bill Bain(retired OGE)-initial orientation (7 years ago) on Armadillo Diesel Sweeper usage (operation and dump). Dawn currently gives majority of “orientation” to employees who use sweeper. Float on Armadillo Sweeper does not work currently (has been called in but, never repaired) Never required to do pre-op inspection. Dawn stated: “I wish I had know that was a gas pipe and I would have never come anywhere near close.” No labeling or identification of pipe. Gas Line description: 2” GAS LINE THAT FEEDS –HEATERS IN THE WAREHOUSE, Building B Facility Generator. Armadillo strikes ¾” pressure gauge on bottom of gas line 29” from ground. Gas Line PSI 10-14 PSIG Gas Line is painted same color as building with no exterior labeling Diesel Sweeper Findings: No Operator Manual Present No Pre-Operational Inspection Float did not work, called in but never repaired correctly. Operator (Dawn) Findings: No formal training Last “training” was given seven years ago, upon purchase of sweeper by now retired OGE Member OGE (retired) “trainer” was never formally trained. Prior knowledge was used for training to Anixter members. Very good process used for work path flow (sweeping facility), employee takes the same route every time the task is performed. Operator is the agreed trainer for Anixter on the Armadillo Sweeper Primary operator of sweeper Gas hazard had not been identified by operator or facility. | Glen McClain | Cody Vinyard |  | General Service Center | FALSE |  | TRUE | Supply Chain |  | Jeffery Richardson | Jeffery Richardson |  | Stephen Merrill | ` |  |  | Very High | [9 empty] | 10.08 Inadequate evaluation of changes |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | An Anixter employee was cleaning the west parking lot and entrance ramp of building B using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Jeffery Richardson | [5 empty] | 1. Struck Against (Running or Bumping Into) | Jeffery Richardson | Anixter | Dawn Smith |  |  |  | Jeffery Richardson | [71 empty] | .
8680 | General Service Center | 2019-01-22 10:00 | An Anixter employee was cleaning the west parking lot and entrance ramp of building B using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. | Level 4 |  | TRUE | Contractor | Stephen Merrill | Jerrod Moser | Please get investigation done within 30 days. | 2019-01-31 13:23 | OGE Energy Corp | Jeffery Richardson | 2019-04-08 15:24 | 2019-01-23 17:03 | 2019-01-23 | 2019-02-28 15:55 | 2019-02-28 | 2019-01-23 10:00 | 2019-03-18 10:33 |  |  | General Service Center Building B |  |  | Jerrod Moser | Approved | Enterprise Services |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Cody Vinyard |  | An Anixter employee was cleaning the west parking lot and entrance ramp of building B at GSC using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. 01-22-19 (approximate time line) 9:55 a.m.-Anixter member was coming to the end of her sweeping routine when she pulls over toward NW side of building B, drives by the generator near the employee entrance and comes back to NW corner and makes a U turn and backs into gas pipe trying to readjust 10:00 a.m.-Anixter Member strikes gas pipe at the end of her sweeping route and calls Steven Dorsey because she smells gas 10:05 a.m.-Steven calls Dale Thompson (operations manager Anixter) 10:14 a.m. -Glen McClain calls OGE 2001 and no answer, then calls Phil Messer, buildings A,B,C evacuated 10:15 a.m. Phil Messer call ONG and directs Steve Smith to call OKC Fire Department 10:25 a.m.-ONG/Fire Department responds to GSC leak 10:30 a.m.-Fire Department checks for residual gas ppm 11:00 a.m.- GSC given permission to leave/return by 1:00 p.m. 1:00 p.m.-Leak isolated/mitigated, fans running, employees return to work. Interview with Anixter Member: Dawn Smith Generally sweep every other day, minimum once a week. Very Detailed Sweep Path that reaches all areas of warehouse and areas throughout the yard and parking lots. Bill Bain(retired OGE)-initial orientation (7 years ago) on Armadillo Diesel Sweeper usage (operation and dump). Dawn currently gives majority of “orientation” to employees who use sweeper. Float on Armadillo Sweeper does not work currently (has been called in but, never repaired) Never required to do pre-op inspection. Dawn stated: “I wish I had know that was a gas pipe and I would have never come anywhere near close.” No labeling or identification of pipe. Gas Line description: 2” GAS LINE THAT FEEDS –HEATERS IN THE WAREHOUSE, Building B Facility Generator. Armadillo strikes ¾” pressure gauge on bottom of gas line 29” from ground. Gas Line PSI 10-14 PSIG Gas Line is painted same color as building with no exterior labeling Diesel Sweeper Findings: No Operator Manual Present No Pre-Operational Inspection Float did not work, called in but never repaired correctly. Operator (Dawn) Findings: No formal training Last “training” was given seven years ago, upon purchase of sweeper by now retired OGE Member OGE (retired) “trainer” was never formally trained. Prior knowledge was used for training to Anixter members. Very good process used for work path flow (sweeping facility), employee takes the same route every time the task is performed. Operator is the agreed trainer for Anixter on the Armadillo Sweeper Primary operator of sweeper Gas hazard had not been identified by operator or facility. | Glen McClain | Cody Vinyard |  | General Service Center | FALSE |  | TRUE | Supply Chain |  | Jeffery Richardson | Jeffery Richardson |  | Stephen Merrill | ` |  |  | Very High | [9 empty] | 10.02 Inadequate consideration of human factors/ergonomics |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | An Anixter employee was cleaning the west parking lot and entrance ramp of building B using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Jeffery Richardson | [5 empty] | 1. Struck Against (Running or Bumping Into) | Jeffery Richardson | Anixter | Dawn Smith |  |  |  | Jeffery Richardson | [71 empty] | .
8680 | General Service Center | 2019-01-22 10:00 | An Anixter employee was cleaning the west parking lot and entrance ramp of building B using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. | Level 4 |  | TRUE | Contractor | Stephen Merrill | Jerrod Moser | Please get investigation done within 30 days. | 2019-01-31 13:23 | OGE Energy Corp | Jeffery Richardson | 2019-04-08 15:24 | 2019-01-23 17:03 | 2019-01-23 | 2019-02-28 15:55 | 2019-02-28 | 2019-01-23 10:00 | 2019-03-18 10:33 |  |  | General Service Center Building B |  |  | Jerrod Moser | Approved | Enterprise Services |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Cody Vinyard |  | An Anixter employee was cleaning the west parking lot and entrance ramp of building B at GSC using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. 01-22-19 (approximate time line) 9:55 a.m.-Anixter member was coming to the end of her sweeping routine when she pulls over toward NW side of building B, drives by the generator near the employee entrance and comes back to NW corner and makes a U turn and backs into gas pipe trying to readjust 10:00 a.m.-Anixter Member strikes gas pipe at the end of her sweeping route and calls Steven Dorsey because she smells gas 10:05 a.m.-Steven calls Dale Thompson (operations manager Anixter) 10:14 a.m. -Glen McClain calls OGE 2001 and no answer, then calls Phil Messer, buildings A,B,C evacuated 10:15 a.m. Phil Messer call ONG and directs Steve Smith to call OKC Fire Department 10:25 a.m.-ONG/Fire Department responds to GSC leak 10:30 a.m.-Fire Department checks for residual gas ppm 11:00 a.m.- GSC given permission to leave/return by 1:00 p.m. 1:00 p.m.-Leak isolated/mitigated, fans running, employees return to work. Interview with Anixter Member: Dawn Smith Generally sweep every other day, minimum once a week. Very Detailed Sweep Path that reaches all areas of warehouse and areas throughout the yard and parking lots. Bill Bain(retired OGE)-initial orientation (7 years ago) on Armadillo Diesel Sweeper usage (operation and dump). Dawn currently gives majority of “orientation” to employees who use sweeper. Float on Armadillo Sweeper does not work currently (has been called in but, never repaired) Never required to do pre-op inspection. Dawn stated: “I wish I had know that was a gas pipe and I would have never come anywhere near close.” No labeling or identification of pipe. Gas Line description: 2” GAS LINE THAT FEEDS –HEATERS IN THE WAREHOUSE, Building B Facility Generator. Armadillo strikes ¾” pressure gauge on bottom of gas line 29” from ground. Gas Line PSI 10-14 PSIG Gas Line is painted same color as building with no exterior labeling Diesel Sweeper Findings: No Operator Manual Present No Pre-Operational Inspection Float did not work, called in but never repaired correctly. Operator (Dawn) Findings: No formal training Last “training” was given seven years ago, upon purchase of sweeper by now retired OGE Member OGE (retired) “trainer” was never formally trained. Prior knowledge was used for training to Anixter members. Very good process used for work path flow (sweeping facility), employee takes the same route every time the task is performed. Operator is the agreed trainer for Anixter on the Armadillo Sweeper Primary operator of sweeper Gas hazard had not been identified by operator or facility. | Glen McClain | Cody Vinyard |  | General Service Center | FALSE |  | TRUE | Supply Chain |  | Jeffery Richardson | Jeffery Richardson |  | Stephen Merrill | ` |  |  | Very High | [9 empty] | 10.02 Inadequate consideration of human factors/ergonomics |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | An Anixter employee was cleaning the west parking lot and entrance ramp of building B using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Jeffery Richardson | [5 empty] | 1. Struck Against (Running or Bumping Into) | Jeffery Richardson | Anixter | Dawn Smith |  |  |  | Jeffery Richardson | [71 empty] | .
8680 | General Service Center | 2019-01-22 10:00 | An Anixter employee was cleaning the west parking lot and entrance ramp of building B using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. | Level 4 |  | TRUE | Contractor | Stephen Merrill | Jerrod Moser | Please get investigation done within 30 days. | 2019-01-31 13:23 | OGE Energy Corp | Jeffery Richardson | 2019-04-08 15:24 | 2019-01-23 17:03 | 2019-01-23 | 2019-02-28 15:55 | 2019-02-28 | 2019-01-23 10:00 | 2019-03-18 10:33 |  |  | General Service Center Building B |  |  | Jerrod Moser | Approved | Enterprise Services |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Cody Vinyard |  | An Anixter employee was cleaning the west parking lot and entrance ramp of building B at GSC using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. 01-22-19 (approximate time line) 9:55 a.m.-Anixter member was coming to the end of her sweeping routine when she pulls over toward NW side of building B, drives by the generator near the employee entrance and comes back to NW corner and makes a U turn and backs into gas pipe trying to readjust 10:00 a.m.-Anixter Member strikes gas pipe at the end of her sweeping route and calls Steven Dorsey because she smells gas 10:05 a.m.-Steven calls Dale Thompson (operations manager Anixter) 10:14 a.m. -Glen McClain calls OGE 2001 and no answer, then calls Phil Messer, buildings A,B,C evacuated 10:15 a.m. Phil Messer call ONG and directs Steve Smith to call OKC Fire Department 10:25 a.m.-ONG/Fire Department responds to GSC leak 10:30 a.m.-Fire Department checks for residual gas ppm 11:00 a.m.- GSC given permission to leave/return by 1:00 p.m. 1:00 p.m.-Leak isolated/mitigated, fans running, employees return to work. Interview with Anixter Member: Dawn Smith Generally sweep every other day, minimum once a week. Very Detailed Sweep Path that reaches all areas of warehouse and areas throughout the yard and parking lots. Bill Bain(retired OGE)-initial orientation (7 years ago) on Armadillo Diesel Sweeper usage (operation and dump). Dawn currently gives majority of “orientation” to employees who use sweeper. Float on Armadillo Sweeper does not work currently (has been called in but, never repaired) Never required to do pre-op inspection. Dawn stated: “I wish I had know that was a gas pipe and I would have never come anywhere near close.” No labeling or identification of pipe. Gas Line description: 2” GAS LINE THAT FEEDS –HEATERS IN THE WAREHOUSE, Building B Facility Generator. Armadillo strikes ¾” pressure gauge on bottom of gas line 29” from ground. Gas Line PSI 10-14 PSIG Gas Line is painted same color as building with no exterior labeling Diesel Sweeper Findings: No Operator Manual Present No Pre-Operational Inspection Float did not work, called in but never repaired correctly. Operator (Dawn) Findings: No formal training Last “training” was given seven years ago, upon purchase of sweeper by now retired OGE Member OGE (retired) “trainer” was never formally trained. Prior knowledge was used for training to Anixter members. Very good process used for work path flow (sweeping facility), employee takes the same route every time the task is performed. Operator is the agreed trainer for Anixter on the Armadillo Sweeper Primary operator of sweeper Gas hazard had not been identified by operator or facility. | Elizabeth Gough | Cody Vinyard |  | General Service Center | FALSE |  | TRUE | Supply Chain |  | Jeffery Richardson | Jeffery Richardson |  | Stephen Merrill | ` |  |  | Very High | [9 empty] | 10.08 Inadequate evaluation of changes |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | An Anixter employee was cleaning the west parking lot and entrance ramp of building B using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Jeffery Richardson | [5 empty] | 1. Struck Against (Running or Bumping Into) | Jeffery Richardson | Anixter | Dawn Smith |  |  |  | Jeffery Richardson | [71 empty] | .
8680 | General Service Center | 2019-01-22 10:00 | An Anixter employee was cleaning the west parking lot and entrance ramp of building B using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. | Level 4 |  | TRUE | Contractor | Stephen Merrill | Jerrod Moser | Please get investigation done within 30 days. | 2019-01-31 13:23 | OGE Energy Corp | Jeffery Richardson | 2019-04-08 15:24 | 2019-01-23 17:03 | 2019-01-23 | 2019-02-28 15:55 | 2019-02-28 | 2019-01-23 10:00 | 2019-03-18 10:33 |  |  | General Service Center Building B |  |  | Jerrod Moser | Approved | Enterprise Services |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Cody Vinyard |  | An Anixter employee was cleaning the west parking lot and entrance ramp of building B at GSC using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. 01-22-19 (approximate time line) 9:55 a.m.-Anixter member was coming to the end of her sweeping routine when she pulls over toward NW side of building B, drives by the generator near the employee entrance and comes back to NW corner and makes a U turn and backs into gas pipe trying to readjust 10:00 a.m.-Anixter Member strikes gas pipe at the end of her sweeping route and calls Steven Dorsey because she smells gas 10:05 a.m.-Steven calls Dale Thompson (operations manager Anixter) 10:14 a.m. -Glen McClain calls OGE 2001 and no answer, then calls Phil Messer, buildings A,B,C evacuated 10:15 a.m. Phil Messer call ONG and directs Steve Smith to call OKC Fire Department 10:25 a.m.-ONG/Fire Department responds to GSC leak 10:30 a.m.-Fire Department checks for residual gas ppm 11:00 a.m.- GSC given permission to leave/return by 1:00 p.m. 1:00 p.m.-Leak isolated/mitigated, fans running, employees return to work. Interview with Anixter Member: Dawn Smith Generally sweep every other day, minimum once a week. Very Detailed Sweep Path that reaches all areas of warehouse and areas throughout the yard and parking lots. Bill Bain(retired OGE)-initial orientation (7 years ago) on Armadillo Diesel Sweeper usage (operation and dump). Dawn currently gives majority of “orientation” to employees who use sweeper. Float on Armadillo Sweeper does not work currently (has been called in but, never repaired) Never required to do pre-op inspection. Dawn stated: “I wish I had know that was a gas pipe and I would have never come anywhere near close.” No labeling or identification of pipe. Gas Line description: 2” GAS LINE THAT FEEDS –HEATERS IN THE WAREHOUSE, Building B Facility Generator. Armadillo strikes ¾” pressure gauge on bottom of gas line 29” from ground. Gas Line PSI 10-14 PSIG Gas Line is painted same color as building with no exterior labeling Diesel Sweeper Findings: No Operator Manual Present No Pre-Operational Inspection Float did not work, called in but never repaired correctly. Operator (Dawn) Findings: No formal training Last “training” was given seven years ago, upon purchase of sweeper by now retired OGE Member OGE (retired) “trainer” was never formally trained. Prior knowledge was used for training to Anixter members. Very good process used for work path flow (sweeping facility), employee takes the same route every time the task is performed. Operator is the agreed trainer for Anixter on the Armadillo Sweeper Primary operator of sweeper Gas hazard had not been identified by operator or facility. | Elizabeth Gough | Cody Vinyard |  | General Service Center | FALSE |  | TRUE | Supply Chain |  | Jeffery Richardson | Jeffery Richardson |  | Stephen Merrill | ` |  |  | Very High | [9 empty] | 10.08 Inadequate evaluation of changes |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | An Anixter employee was cleaning the west parking lot and entrance ramp of building B using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Jeffery Richardson | [5 empty] | 1. Struck Against (Running or Bumping Into) | Jeffery Richardson | Anixter | Dawn Smith |  |  |  | Jeffery Richardson | [71 empty] | .
8680 | General Service Center | 2019-01-22 10:00 | An Anixter employee was cleaning the west parking lot and entrance ramp of building B using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. | Level 4 |  | TRUE | Contractor | Stephen Merrill | Jerrod Moser | Please get investigation done within 30 days. | 2019-01-31 13:23 | OGE Energy Corp | Jeffery Richardson | 2019-04-08 15:24 | 2019-01-23 17:03 | 2019-01-23 | 2019-02-28 15:55 | 2019-02-28 | 2019-01-23 10:00 | 2019-03-18 10:33 |  |  | General Service Center Building B |  |  | Jerrod Moser | Approved | Enterprise Services |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Cody Vinyard |  | An Anixter employee was cleaning the west parking lot and entrance ramp of building B at GSC using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. 01-22-19 (approximate time line) 9:55 a.m.-Anixter member was coming to the end of her sweeping routine when she pulls over toward NW side of building B, drives by the generator near the employee entrance and comes back to NW corner and makes a U turn and backs into gas pipe trying to readjust 10:00 a.m.-Anixter Member strikes gas pipe at the end of her sweeping route and calls Steven Dorsey because she smells gas 10:05 a.m.-Steven calls Dale Thompson (operations manager Anixter) 10:14 a.m. -Glen McClain calls OGE 2001 and no answer, then calls Phil Messer, buildings A,B,C evacuated 10:15 a.m. Phil Messer call ONG and directs Steve Smith to call OKC Fire Department 10:25 a.m.-ONG/Fire Department responds to GSC leak 10:30 a.m.-Fire Department checks for residual gas ppm 11:00 a.m.- GSC given permission to leave/return by 1:00 p.m. 1:00 p.m.-Leak isolated/mitigated, fans running, employees return to work. Interview with Anixter Member: Dawn Smith Generally sweep every other day, minimum once a week. Very Detailed Sweep Path that reaches all areas of warehouse and areas throughout the yard and parking lots. Bill Bain(retired OGE)-initial orientation (7 years ago) on Armadillo Diesel Sweeper usage (operation and dump). Dawn currently gives majority of “orientation” to employees who use sweeper. Float on Armadillo Sweeper does not work currently (has been called in but, never repaired) Never required to do pre-op inspection. Dawn stated: “I wish I had know that was a gas pipe and I would have never come anywhere near close.” No labeling or identification of pipe. Gas Line description: 2” GAS LINE THAT FEEDS –HEATERS IN THE WAREHOUSE, Building B Facility Generator. Armadillo strikes ¾” pressure gauge on bottom of gas line 29” from ground. Gas Line PSI 10-14 PSIG Gas Line is painted same color as building with no exterior labeling Diesel Sweeper Findings: No Operator Manual Present No Pre-Operational Inspection Float did not work, called in but never repaired correctly. Operator (Dawn) Findings: No formal training Last “training” was given seven years ago, upon purchase of sweeper by now retired OGE Member OGE (retired) “trainer” was never formally trained. Prior knowledge was used for training to Anixter members. Very good process used for work path flow (sweeping facility), employee takes the same route every time the task is performed. Operator is the agreed trainer for Anixter on the Armadillo Sweeper Primary operator of sweeper Gas hazard had not been identified by operator or facility. | Elizabeth Gough | Cody Vinyard |  | General Service Center | FALSE |  | TRUE | Supply Chain |  | Jeffery Richardson | Jeffery Richardson |  | Stephen Merrill | ` |  |  | Very High | [9 empty] | 10.02 Inadequate consideration of human factors/ergonomics |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | An Anixter employee was cleaning the west parking lot and entrance ramp of building B using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Jeffery Richardson | [5 empty] | 1. Struck Against (Running or Bumping Into) | Jeffery Richardson | Anixter | Dawn Smith |  |  |  | Jeffery Richardson | [71 empty] | .
8680 | General Service Center | 2019-01-22 10:00 | An Anixter employee was cleaning the west parking lot and entrance ramp of building B using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. | Level 4 |  | TRUE | Contractor | Stephen Merrill | Jerrod Moser | Please get investigation done within 30 days. | 2019-01-31 13:23 | OGE Energy Corp | Jeffery Richardson | 2019-04-08 15:24 | 2019-01-23 17:03 | 2019-01-23 | 2019-02-28 15:55 | 2019-02-28 | 2019-01-23 10:00 | 2019-03-18 10:33 |  |  | General Service Center Building B |  |  | Jerrod Moser | Approved | Enterprise Services |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Cody Vinyard |  | An Anixter employee was cleaning the west parking lot and entrance ramp of building B at GSC using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. 01-22-19 (approximate time line) 9:55 a.m.-Anixter member was coming to the end of her sweeping routine when she pulls over toward NW side of building B, drives by the generator near the employee entrance and comes back to NW corner and makes a U turn and backs into gas pipe trying to readjust 10:00 a.m.-Anixter Member strikes gas pipe at the end of her sweeping route and calls Steven Dorsey because she smells gas 10:05 a.m.-Steven calls Dale Thompson (operations manager Anixter) 10:14 a.m. -Glen McClain calls OGE 2001 and no answer, then calls Phil Messer, buildings A,B,C evacuated 10:15 a.m. Phil Messer call ONG and directs Steve Smith to call OKC Fire Department 10:25 a.m.-ONG/Fire Department responds to GSC leak 10:30 a.m.-Fire Department checks for residual gas ppm 11:00 a.m.- GSC given permission to leave/return by 1:00 p.m. 1:00 p.m.-Leak isolated/mitigated, fans running, employees return to work. Interview with Anixter Member: Dawn Smith Generally sweep every other day, minimum once a week. Very Detailed Sweep Path that reaches all areas of warehouse and areas throughout the yard and parking lots. Bill Bain(retired OGE)-initial orientation (7 years ago) on Armadillo Diesel Sweeper usage (operation and dump). Dawn currently gives majority of “orientation” to employees who use sweeper. Float on Armadillo Sweeper does not work currently (has been called in but, never repaired) Never required to do pre-op inspection. Dawn stated: “I wish I had know that was a gas pipe and I would have never come anywhere near close.” No labeling or identification of pipe. Gas Line description: 2” GAS LINE THAT FEEDS –HEATERS IN THE WAREHOUSE, Building B Facility Generator. Armadillo strikes ¾” pressure gauge on bottom of gas line 29” from ground. Gas Line PSI 10-14 PSIG Gas Line is painted same color as building with no exterior labeling Diesel Sweeper Findings: No Operator Manual Present No Pre-Operational Inspection Float did not work, called in but never repaired correctly. Operator (Dawn) Findings: No formal training Last “training” was given seven years ago, upon purchase of sweeper by now retired OGE Member OGE (retired) “trainer” was never formally trained. Prior knowledge was used for training to Anixter members. Very good process used for work path flow (sweeping facility), employee takes the same route every time the task is performed. Operator is the agreed trainer for Anixter on the Armadillo Sweeper Primary operator of sweeper Gas hazard had not been identified by operator or facility. | Elizabeth Gough | Cody Vinyard |  | General Service Center | FALSE |  | TRUE | Supply Chain |  | Jeffery Richardson | Jeffery Richardson |  | Stephen Merrill | ` |  |  | Very High | [9 empty] | 10.02 Inadequate consideration of human factors/ergonomics |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | An Anixter employee was cleaning the west parking lot and entrance ramp of building B using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Jeffery Richardson | [5 empty] | 1. Struck Against (Running or Bumping Into) | Jeffery Richardson | Anixter | Dawn Smith |  |  |  | Jeffery Richardson | [71 empty] | .
8680 | General Service Center | 2019-01-22 10:00 | An Anixter employee was cleaning the west parking lot and entrance ramp of building B using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. | Level 4 |  | TRUE | Contractor | Stephen Merrill | Jerrod Moser | Please get investigation done within 30 days. | 2019-01-31 13:23 | OGE Energy Corp | Jeffery Richardson | 2019-04-08 15:24 | 2019-01-23 17:03 | 2019-01-23 | 2019-02-28 15:55 | 2019-02-28 | 2019-01-23 10:00 | 2019-03-18 10:33 |  |  | General Service Center Building B |  |  | Jerrod Moser | Approved | Enterprise Services |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Cody Vinyard |  | An Anixter employee was cleaning the west parking lot and entrance ramp of building B at GSC using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. 01-22-19 (approximate time line) 9:55 a.m.-Anixter member was coming to the end of her sweeping routine when she pulls over toward NW side of building B, drives by the generator near the employee entrance and comes back to NW corner and makes a U turn and backs into gas pipe trying to readjust 10:00 a.m.-Anixter Member strikes gas pipe at the end of her sweeping route and calls Steven Dorsey because she smells gas 10:05 a.m.-Steven calls Dale Thompson (operations manager Anixter) 10:14 a.m. -Glen McClain calls OGE 2001 and no answer, then calls Phil Messer, buildings A,B,C evacuated 10:15 a.m. Phil Messer call ONG and directs Steve Smith to call OKC Fire Department 10:25 a.m.-ONG/Fire Department responds to GSC leak 10:30 a.m.-Fire Department checks for residual gas ppm 11:00 a.m.- GSC given permission to leave/return by 1:00 p.m. 1:00 p.m.-Leak isolated/mitigated, fans running, employees return to work. Interview with Anixter Member: Dawn Smith Generally sweep every other day, minimum once a week. Very Detailed Sweep Path that reaches all areas of warehouse and areas throughout the yard and parking lots. Bill Bain(retired OGE)-initial orientation (7 years ago) on Armadillo Diesel Sweeper usage (operation and dump). Dawn currently gives majority of “orientation” to employees who use sweeper. Float on Armadillo Sweeper does not work currently (has been called in but, never repaired) Never required to do pre-op inspection. Dawn stated: “I wish I had know that was a gas pipe and I would have never come anywhere near close.” No labeling or identification of pipe. Gas Line description: 2” GAS LINE THAT FEEDS –HEATERS IN THE WAREHOUSE, Building B Facility Generator. Armadillo strikes ¾” pressure gauge on bottom of gas line 29” from ground. Gas Line PSI 10-14 PSIG Gas Line is painted same color as building with no exterior labeling Diesel Sweeper Findings: No Operator Manual Present No Pre-Operational Inspection Float did not work, called in but never repaired correctly. Operator (Dawn) Findings: No formal training Last “training” was given seven years ago, upon purchase of sweeper by now retired OGE Member OGE (retired) “trainer” was never formally trained. Prior knowledge was used for training to Anixter members. Very good process used for work path flow (sweeping facility), employee takes the same route every time the task is performed. Operator is the agreed trainer for Anixter on the Armadillo Sweeper Primary operator of sweeper Gas hazard had not been identified by operator or facility. | Phillip Messer | Cody Vinyard |  | General Service Center | FALSE |  | TRUE | Supply Chain |  | Jeffery Richardson | Jeffery Richardson |  | Stephen Merrill | ` |  |  | Very High | [9 empty] | 10.08 Inadequate evaluation of changes |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | An Anixter employee was cleaning the west parking lot and entrance ramp of building B using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Jeffery Richardson | [5 empty] | 1. Struck Against (Running or Bumping Into) | Jeffery Richardson | Anixter | Dawn Smith |  |  |  | Jeffery Richardson | [71 empty] | .
8680 | General Service Center | 2019-01-22 10:00 | An Anixter employee was cleaning the west parking lot and entrance ramp of building B using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. | Level 4 |  | TRUE | Contractor | Stephen Merrill | Jerrod Moser | Please get investigation done within 30 days. | 2019-01-31 13:23 | OGE Energy Corp | Jeffery Richardson | 2019-04-08 15:24 | 2019-01-23 17:03 | 2019-01-23 | 2019-02-28 15:55 | 2019-02-28 | 2019-01-23 10:00 | 2019-03-18 10:33 |  |  | General Service Center Building B |  |  | Jerrod Moser | Approved | Enterprise Services |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Cody Vinyard |  | An Anixter employee was cleaning the west parking lot and entrance ramp of building B at GSC using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. 01-22-19 (approximate time line) 9:55 a.m.-Anixter member was coming to the end of her sweeping routine when she pulls over toward NW side of building B, drives by the generator near the employee entrance and comes back to NW corner and makes a U turn and backs into gas pipe trying to readjust 10:00 a.m.-Anixter Member strikes gas pipe at the end of her sweeping route and calls Steven Dorsey because she smells gas 10:05 a.m.-Steven calls Dale Thompson (operations manager Anixter) 10:14 a.m. -Glen McClain calls OGE 2001 and no answer, then calls Phil Messer, buildings A,B,C evacuated 10:15 a.m. Phil Messer call ONG and directs Steve Smith to call OKC Fire Department 10:25 a.m.-ONG/Fire Department responds to GSC leak 10:30 a.m.-Fire Department checks for residual gas ppm 11:00 a.m.- GSC given permission to leave/return by 1:00 p.m. 1:00 p.m.-Leak isolated/mitigated, fans running, employees return to work. Interview with Anixter Member: Dawn Smith Generally sweep every other day, minimum once a week. Very Detailed Sweep Path that reaches all areas of warehouse and areas throughout the yard and parking lots. Bill Bain(retired OGE)-initial orientation (7 years ago) on Armadillo Diesel Sweeper usage (operation and dump). Dawn currently gives majority of “orientation” to employees who use sweeper. Float on Armadillo Sweeper does not work currently (has been called in but, never repaired) Never required to do pre-op inspection. Dawn stated: “I wish I had know that was a gas pipe and I would have never come anywhere near close.” No labeling or identification of pipe. Gas Line description: 2” GAS LINE THAT FEEDS –HEATERS IN THE WAREHOUSE, Building B Facility Generator. Armadillo strikes ¾” pressure gauge on bottom of gas line 29” from ground. Gas Line PSI 10-14 PSIG Gas Line is painted same color as building with no exterior labeling Diesel Sweeper Findings: No Operator Manual Present No Pre-Operational Inspection Float did not work, called in but never repaired correctly. Operator (Dawn) Findings: No formal training Last “training” was given seven years ago, upon purchase of sweeper by now retired OGE Member OGE (retired) “trainer” was never formally trained. Prior knowledge was used for training to Anixter members. Very good process used for work path flow (sweeping facility), employee takes the same route every time the task is performed. Operator is the agreed trainer for Anixter on the Armadillo Sweeper Primary operator of sweeper Gas hazard had not been identified by operator or facility. | Phillip Messer | Cody Vinyard |  | General Service Center | FALSE |  | TRUE | Supply Chain |  | Jeffery Richardson | Jeffery Richardson |  | Stephen Merrill | ` |  |  | Very High | [9 empty] | 10.08 Inadequate evaluation of changes |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | An Anixter employee was cleaning the west parking lot and entrance ramp of building B using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Jeffery Richardson | [5 empty] | 1. Struck Against (Running or Bumping Into) | Jeffery Richardson | Anixter | Dawn Smith |  |  |  | Jeffery Richardson | [71 empty] | .
8680 | General Service Center | 2019-01-22 10:00 | An Anixter employee was cleaning the west parking lot and entrance ramp of building B using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. | Level 4 |  | TRUE | Contractor | Stephen Merrill | Jerrod Moser | Please get investigation done within 30 days. | 2019-01-31 13:23 | OGE Energy Corp | Jeffery Richardson | 2019-04-08 15:24 | 2019-01-23 17:03 | 2019-01-23 | 2019-02-28 15:55 | 2019-02-28 | 2019-01-23 10:00 | 2019-03-18 10:33 |  |  | General Service Center Building B |  |  | Jerrod Moser | Approved | Enterprise Services |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Cody Vinyard |  | An Anixter employee was cleaning the west parking lot and entrance ramp of building B at GSC using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. 01-22-19 (approximate time line) 9:55 a.m.-Anixter member was coming to the end of her sweeping routine when she pulls over toward NW side of building B, drives by the generator near the employee entrance and comes back to NW corner and makes a U turn and backs into gas pipe trying to readjust 10:00 a.m.-Anixter Member strikes gas pipe at the end of her sweeping route and calls Steven Dorsey because she smells gas 10:05 a.m.-Steven calls Dale Thompson (operations manager Anixter) 10:14 a.m. -Glen McClain calls OGE 2001 and no answer, then calls Phil Messer, buildings A,B,C evacuated 10:15 a.m. Phil Messer call ONG and directs Steve Smith to call OKC Fire Department 10:25 a.m.-ONG/Fire Department responds to GSC leak 10:30 a.m.-Fire Department checks for residual gas ppm 11:00 a.m.- GSC given permission to leave/return by 1:00 p.m. 1:00 p.m.-Leak isolated/mitigated, fans running, employees return to work. Interview with Anixter Member: Dawn Smith Generally sweep every other day, minimum once a week. Very Detailed Sweep Path that reaches all areas of warehouse and areas throughout the yard and parking lots. Bill Bain(retired OGE)-initial orientation (7 years ago) on Armadillo Diesel Sweeper usage (operation and dump). Dawn currently gives majority of “orientation” to employees who use sweeper. Float on Armadillo Sweeper does not work currently (has been called in but, never repaired) Never required to do pre-op inspection. Dawn stated: “I wish I had know that was a gas pipe and I would have never come anywhere near close.” No labeling or identification of pipe. Gas Line description: 2” GAS LINE THAT FEEDS –HEATERS IN THE WAREHOUSE, Building B Facility Generator. Armadillo strikes ¾” pressure gauge on bottom of gas line 29” from ground. Gas Line PSI 10-14 PSIG Gas Line is painted same color as building with no exterior labeling Diesel Sweeper Findings: No Operator Manual Present No Pre-Operational Inspection Float did not work, called in but never repaired correctly. Operator (Dawn) Findings: No formal training Last “training” was given seven years ago, upon purchase of sweeper by now retired OGE Member OGE (retired) “trainer” was never formally trained. Prior knowledge was used for training to Anixter members. Very good process used for work path flow (sweeping facility), employee takes the same route every time the task is performed. Operator is the agreed trainer for Anixter on the Armadillo Sweeper Primary operator of sweeper Gas hazard had not been identified by operator or facility. | Phillip Messer | Cody Vinyard |  | General Service Center | FALSE |  | TRUE | Supply Chain |  | Jeffery Richardson | Jeffery Richardson |  | Stephen Merrill | ` |  |  | Very High | [9 empty] | 10.02 Inadequate consideration of human factors/ergonomics |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | An Anixter employee was cleaning the west parking lot and entrance ramp of building B using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Jeffery Richardson | [5 empty] | 1. Struck Against (Running or Bumping Into) | Jeffery Richardson | Anixter | Dawn Smith |  |  |  | Jeffery Richardson | [71 empty] | .
8680 | General Service Center | 2019-01-22 10:00 | An Anixter employee was cleaning the west parking lot and entrance ramp of building B using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. | Level 4 |  | TRUE | Contractor | Stephen Merrill | Jerrod Moser | Please get investigation done within 30 days. | 2019-01-31 13:23 | OGE Energy Corp | Jeffery Richardson | 2019-04-08 15:24 | 2019-01-23 17:03 | 2019-01-23 | 2019-02-28 15:55 | 2019-02-28 | 2019-01-23 10:00 | 2019-03-18 10:33 |  |  | General Service Center Building B |  |  | Jerrod Moser | Approved | Enterprise Services |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Cody Vinyard |  | An Anixter employee was cleaning the west parking lot and entrance ramp of building B at GSC using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. 01-22-19 (approximate time line) 9:55 a.m.-Anixter member was coming to the end of her sweeping routine when she pulls over toward NW side of building B, drives by the generator near the employee entrance and comes back to NW corner and makes a U turn and backs into gas pipe trying to readjust 10:00 a.m.-Anixter Member strikes gas pipe at the end of her sweeping route and calls Steven Dorsey because she smells gas 10:05 a.m.-Steven calls Dale Thompson (operations manager Anixter) 10:14 a.m. -Glen McClain calls OGE 2001 and no answer, then calls Phil Messer, buildings A,B,C evacuated 10:15 a.m. Phil Messer call ONG and directs Steve Smith to call OKC Fire Department 10:25 a.m.-ONG/Fire Department responds to GSC leak 10:30 a.m.-Fire Department checks for residual gas ppm 11:00 a.m.- GSC given permission to leave/return by 1:00 p.m. 1:00 p.m.-Leak isolated/mitigated, fans running, employees return to work. Interview with Anixter Member: Dawn Smith Generally sweep every other day, minimum once a week. Very Detailed Sweep Path that reaches all areas of warehouse and areas throughout the yard and parking lots. Bill Bain(retired OGE)-initial orientation (7 years ago) on Armadillo Diesel Sweeper usage (operation and dump). Dawn currently gives majority of “orientation” to employees who use sweeper. Float on Armadillo Sweeper does not work currently (has been called in but, never repaired) Never required to do pre-op inspection. Dawn stated: “I wish I had know that was a gas pipe and I would have never come anywhere near close.” No labeling or identification of pipe. Gas Line description: 2” GAS LINE THAT FEEDS –HEATERS IN THE WAREHOUSE, Building B Facility Generator. Armadillo strikes ¾” pressure gauge on bottom of gas line 29” from ground. Gas Line PSI 10-14 PSIG Gas Line is painted same color as building with no exterior labeling Diesel Sweeper Findings: No Operator Manual Present No Pre-Operational Inspection Float did not work, called in but never repaired correctly. Operator (Dawn) Findings: No formal training Last “training” was given seven years ago, upon purchase of sweeper by now retired OGE Member OGE (retired) “trainer” was never formally trained. Prior knowledge was used for training to Anixter members. Very good process used for work path flow (sweeping facility), employee takes the same route every time the task is performed. Operator is the agreed trainer for Anixter on the Armadillo Sweeper Primary operator of sweeper Gas hazard had not been identified by operator or facility. | Phillip Messer | Cody Vinyard |  | General Service Center | FALSE |  | TRUE | Supply Chain |  | Jeffery Richardson | Jeffery Richardson |  | Stephen Merrill | ` |  |  | Very High | [9 empty] | 10.02 Inadequate consideration of human factors/ergonomics |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | An Anixter employee was cleaning the west parking lot and entrance ramp of building B using a diesel powered sweeper. During a turn the sweeper contacted and damaged a gas line. | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Jeffery Richardson | [5 empty] | 1. Struck Against (Running or Bumping Into) | Jeffery Richardson | Anixter | Dawn Smith |  |  |  | Jeffery Richardson | [71 empty] | .
8681 | Horseshoe Lake Power Plant | 2019-01-24 11:30 | Member was breaking a flange lose on the fire systems and heard air leaking. Member stopped the job and notified OA. Member not in the line of fire. No injuries. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Guillermo Sarmiento | 2019-03-08 13:02 | 2019-01-25 09:13 | 2019-01-25 09:13 | 2019-02-20 13:52 | 2019-02-07 11:30 | 2019-01-25 08:18 | 2019-03-01 13:33 |  |  | Horseshoe Lake Unit 8 exciter cab |  |  | Guillermo Sarmiento | Report is complete. Covered on the call as a hot sheet. Covered with members. | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Kyle Thornton |  | An O/M Tech 1 was working with the turbine crew and was asked to work on Unit 8 exciter for the removal of the cab. The O/M Tech with A mechanic then went to sign on the LOTO for unit 8 exciter. At this time the only exciter LOTO was for the CCW. The mechanic had a conversation with the OA about the fire protection on the exciter. The OA thought that the mechanic was talking about the heat sensor wires that ICE disconnects because that was a conversation we had earlier in our morning meeting. The mechanic thought that the OA was talking about the fire line system. NOTE: Our fire system is maintained by 30 to 40 psi air. If the air drops it brings an alarm in the control room and Operations will check out the situation. If a fire is present the operator has to manually open the water valve to spray water on the turbine gen/exciter. The OA then called the ICE Foreman to verify that the wires to the heat sensor have been taken care of. The ICE Foreman verified back with the OA that the wires have been disconnected. So the OA the mechanic and O/M Tech thought they were good to work on the system. At this point the mechanic called the Maintenance Foreman. The Maintenance Foreman told the mechanic if the OA said we are okay than you are good to work on it. The O/M Tech and mechanic proceeded to work but did not look at the steps on the LOTO. The O/M Tech started to take the bolt out of the fire line flange and the mechanic went to work on the CCW piping. While taking the last bolt out the fire line flange the O/M tech heard an air leak. The O/M Tech then stopped the job and got the Mechanic. They both went to the operating Authority and told the story. At that point a LOTO was issued on the fire line system. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Maintenance |  | Christian Powell | Kyle Thornton |  | Michael Kennedy | I approve | Michael Kennedy |  | Low |  |  |  |  | 5.01 Lack of experience | [11 empty] | Member was breaking a flange lose on the fire systems and heard air leaking. | 20. Failure to Communicate, Coordinate | 2. Struck By (Hit By Moving Object) | [92 empty] | 9572080
8681 | Horseshoe Lake Power Plant | 2019-01-24 11:30 | Member was breaking a flange lose on the fire systems and heard air leaking. Member stopped the job and notified OA. Member not in the line of fire. No injuries. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Guillermo Sarmiento | 2019-03-08 13:02 | 2019-01-25 09:13 | 2019-01-25 09:13 | 2019-02-20 13:52 | 2019-02-07 11:30 | 2019-01-25 08:18 | 2019-03-01 13:33 |  |  | Horseshoe Lake Unit 8 exciter cab |  |  | Guillermo Sarmiento | Report is complete. Covered on the call as a hot sheet. Covered with members. | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Kyle Thornton |  | An O/M Tech 1 was working with the turbine crew and was asked to work on Unit 8 exciter for the removal of the cab. The O/M Tech with A mechanic then went to sign on the LOTO for unit 8 exciter. At this time the only exciter LOTO was for the CCW. The mechanic had a conversation with the OA about the fire protection on the exciter. The OA thought that the mechanic was talking about the heat sensor wires that ICE disconnects because that was a conversation we had earlier in our morning meeting. The mechanic thought that the OA was talking about the fire line system. NOTE: Our fire system is maintained by 30 to 40 psi air. If the air drops it brings an alarm in the control room and Operations will check out the situation. If a fire is present the operator has to manually open the water valve to spray water on the turbine gen/exciter. The OA then called the ICE Foreman to verify that the wires to the heat sensor have been taken care of. The ICE Foreman verified back with the OA that the wires have been disconnected. So the OA the mechanic and O/M Tech thought they were good to work on the system. At this point the mechanic called the Maintenance Foreman. The Maintenance Foreman told the mechanic if the OA said we are okay than you are good to work on it. The O/M Tech and mechanic proceeded to work but did not look at the steps on the LOTO. The O/M Tech started to take the bolt out of the fire line flange and the mechanic went to work on the CCW piping. While taking the last bolt out the fire line flange the O/M tech heard an air leak. The O/M Tech then stopped the job and got the Mechanic. They both went to the operating Authority and told the story. At that point a LOTO was issued on the fire line system. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Maintenance |  | Christian Powell | Kyle Thornton |  | Michael Kennedy | I approve | Michael Kennedy |  | Low | [15 empty] | 16.04 Inadequate communication between work groups | Miscommunication between operations and maintenance regarding the tasks being performed and the LOTO in place. | 20. Failure to Communicate, Coordinate | 2. Struck By (Hit By Moving Object) | [92 empty] | 9572080
8682 | Centennial Wind Farm | 2019-01-25 11:30 | He lost his grip on the cable while preparing an underground cable splice, and the cutting tool being used cut through his glove and caused a laceration on his hand. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Scott Zigler | 2019-02-25 08:13 | 2019-01-25 17:07 | 2019-01-25 17:07 | 2019-01-28 15:47 | 2019-02-08 11:30 | 2019-01-25 16:32 | 2019-02-08 10:27 |  | 2019-02-06 13:08 | Pedestal base of turbine 57 |  |  | Jesse Murray | Jesse Murray - I Approve | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Scott Zigler |  | On January 25th at approximately 1130, Mortenson contacted OGE site lead to report an injury while performing underground cable splicing. This contractor had made numerous splices in the past and was using the recommended tool from Klein Tools for this particular task. The contractor has been on-site for about a month performing various tasks. On January 25th, a crew of two contractors were working on this splice on an excavation approximate 3-foot deep and about 12-feet wide. The weather was approximately 22 degrees Fahrenheit. The Incident occurred when the contactor was attempting to remove the outer jacket off the cable utilizing a Klein Splicing tool/knife. It was reported that the contractor was making a cut horizontal to the cable in order to slide the outer jacket off. Due to the cold temperature, the outer jacket was stiffer than usual making it harder to cut. He was holding the cable with his left hand and cutting with his right. The splicing tool slipped of the cut and struck the top of his left hand. The contractor mistakenly cut towards his body rather than away. Contractor immediately stopped work and administered first aid procedures to stop the bleeding. As soon as safely possible, contractor contacted OGE site lead and reported the incident. Contractor was taken to urgent care in Woodward, Oklahoma. Contractor received 8 stitches as a result of the incident and was released back to work the same day. Incident was covered in the next morning meeting. A Safe work plan was completed before the job took place. |  |  |  | Centennial Wind Farm | FALSE |  | FALSE | Renewable Energy |  | Scott Zigler | Scott Zigler |  | Jason Thomas | Reviewing with Scott Z. | Jason Thomas |  | Medium |  |  |  |  | 5.06 Lack of situational awareness |  | 7.07 Improper attempt to avoid discomfort |  | 9.09 Inadequate identification and evaluation of loss exposures |  |  |  | 13.02 Inadequate human factors/ergonomics considerations | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  | 16.10 Inadequate communication of safety and health data, regulations or guidelines | Ambient temperature and worker discomfort due to the cold and wind played a role in this incident occurring. | 40. Weather Conditions | 2. Struck By (Hit By Moving Object) |  | reviewing incident, making some changes with help of Scott Zigler |  |  |  | Injury / Illness |  | Scott Zigler |  | 2.5" laceration | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Scott Zigler | Mortenson | Joshua Renfrow | Laceration |  | Hand | Scott Zigler | Left | FALSE | [69 empty] | 9568523
8682 | Centennial Wind Farm | 2019-01-25 11:30 | He lost his grip on the cable while preparing an underground cable splice, and the cutting tool being used cut through his glove and caused a laceration on his hand. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Scott Zigler | 2019-02-25 08:13 | 2019-01-25 17:07 | 2019-01-25 17:07 | 2019-01-28 15:47 | 2019-02-08 11:30 | 2019-01-25 16:32 | 2019-02-08 10:27 |  | 2019-02-06 13:08 | Pedestal base of turbine 57 |  |  | Jesse Murray | Jesse Murray - I Approve | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Scott Zigler |  | On January 25th at approximately 1130, Mortenson contacted OGE site lead to report an injury while performing underground cable splicing. This contractor had made numerous splices in the past and was using the recommended tool from Klein Tools for this particular task. The contractor has been on-site for about a month performing various tasks. On January 25th, a crew of two contractors were working on this splice on an excavation approximate 3-foot deep and about 12-feet wide. The weather was approximately 22 degrees Fahrenheit. The Incident occurred when the contactor was attempting to remove the outer jacket off the cable utilizing a Klein Splicing tool/knife. It was reported that the contractor was making a cut horizontal to the cable in order to slide the outer jacket off. Due to the cold temperature, the outer jacket was stiffer than usual making it harder to cut. He was holding the cable with his left hand and cutting with his right. The splicing tool slipped of the cut and struck the top of his left hand. The contractor mistakenly cut towards his body rather than away. Contractor immediately stopped work and administered first aid procedures to stop the bleeding. As soon as safely possible, contractor contacted OGE site lead and reported the incident. Contractor was taken to urgent care in Woodward, Oklahoma. Contractor received 8 stitches as a result of the incident and was released back to work the same day. Incident was covered in the next morning meeting. A Safe work plan was completed before the job took place. |  |  |  | Centennial Wind Farm | FALSE |  | FALSE | Renewable Energy |  | Scott Zigler | Scott Zigler |  | Jason Thomas | Reviewing with Scott Z. | Jason Thomas |  | Medium |  |  | 3.06 Exposure to temperature extremes |  | 5.06 Lack of situational awareness | [11 empty] | Contractor lacerated hand during cable splicing tasks. Failure to use proper procedures while using splicing tool. | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) |  | reviewing incident, making some changes with help of Scott Zigler |  |  |  | Injury / Illness |  | Scott Zigler |  | 2.5" laceration | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Scott Zigler | Mortenson | Joshua Renfrow | Laceration |  | Hand | Scott Zigler | Left | FALSE | [69 empty] | 9568523
8683 | Muskogee Power Plant | 2019-01-25 16:00 | A contracting member was modifying a scaffold. The the member bent over to move a piece of material he felt discomfort in his lower back. | Level 1 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services |  | 2019-02-18 10:51 | 2019-01-28 11:44 | 2019-01-28 11:44 | 2019-02-09 12:14 | 2019-02-08 22:00 | 2019-01-28 11:37 | 2019-02-11 07:41 |  |  | Muskogee PP Unit 4 Boiler Elevation 5 |  |  | Marcus Huddleston | Good with the corrective action, I want a copy of the safety meeting content. No additional comments. MLH 2/18/19 | UTS |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | On 01-25-19 at approximately 1345hrs. a Brock scaffold builder felt discomfort to his lower middle back while modifying scaffold in the unit #4 boiler. IP felt discomfort to his back while receiving a scaffold runner while modifying a scaffold deck for TEiC production. IP notified his supervisor immediately and was escorted to the HSE office. IP stated that he felt minor discomfort for a moment, in turn feeling no discomfort by the time he had reached the HSE office which was approximately 10 minutes from the initial issue. IP was evaluated by HSE, statements were taken, IP was released to full duty no restrictions. IP stated he did not request treatment, IP filled out and signed a release for no medical treatment. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | UTS - Project Mgmt |  |  |  |  | Christopher Lelak | No further comment - CBL 02/11/19 | Christopher Lelak |  | Low | 1.03 Limited ability to sustain body positions |  |  |  | 5.06 Lack of situational awareness | [11 empty] | The member hurt his back while lifting scaffolding material because he not in the proper position to lift the material. | 10. Improper Lifting | 11. Overstress, Overpressure, Overexertion, Ergonomic |  |  |  |  | MK Gas Conversion | Injury / Illness | [7 empty] | 11. Overstress, Overpressure, Overexertion, Ergonomic |  | Brock | Jose Galvan | [75 empty] | 1645831
8684 | Seminole PP; EGX Gath/Trans | 2019-01-29 09:00 | While installing new Federal and State Posters and OSHA 300A Logs, the last bulletin board fell. Because the members installing the signage were able to catch the bulletin board as it fell, it was not damaged. No injuries. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Chrysty Dorsey | 2019-02-04 11:44 | 2019-01-29 10:29 | 2019-01-29 10:29 | 2019-01-30 15:04 | 2019-02-12 09:00 | 2019-01-29 10:10 | 2019-02-04 08:45 |  |  | Seminole PP Welding Shop |  |  | Cody Vinyard | approved, Cody Vinyard | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chrysty Dorsey |  | Upon investigation, the bulletin board was secured to a wooden board at the top via a chain and two screws. The screw attached to the bulletin board was inserted on the top (see pictures of hole where screw was); thus, allowing the screw to back out/come out easily. See other picture of screw and chain still attached for an idea of how it was mounted. Bulletin board was removed and stored out of the way. The bulletin board was not secured at the bottom. No damage and no injuries. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | TRUE | Other |  | Chrysty Dorsey | Jesse Murray |  | Jesse Murray | I Approve. Jesse Murray 2-4-19 | Jesse Murray |  | Low | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | Bulletin board was secured improperly via a screw and chain mounted at the top allowing the screw to back out/come out easily. The bulletin board was not secured at the bottom. | 23. Defective Tools, Equipment or Materials | 2. Struck By (Hit By Moving Object) | [92 empty] | None
8685 | Metro Service Center | 2019-01-29 10:00 | Crew was wrecking out transmission line. While spreading the center phase of 795 conductor to pull a pole, the glass standoff broke on the next structure. This resulted in a domino effect where 10 spans of insulators broke. The conductor momentarily contacted a three phase distribution circuit and tripped it out. HLHO was in place. All personnel was clear of the bite. No injuries. | Level 3 |  | TRUE | Member Injury |  | Lindle Coleman | Assigned in partnership with operations leadership | 2019-01-31 15:08 | Power Delivery | Jimmy Combs | 2019-03-29 08:43 | 2019-01-29 13:50 | 2019-01-29 13:50 | 2019-02-12 15:01 | 2019-02-12 10:00 | 2019-01-29 13:31 | 2019-02-19 13:31 | 2019-02-19 14:37 | 2019-02-12 15:06 | Hwy 152 and council road widening job |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Kenny La Ferney |  | Crew was wrecking out transmission line. While spreading the center phase of 795 conductor to pull a pole, the glass standoff broke on the next structure. This resulted in a domino effect where 10 spans of insulators broke. The conductor recoiled and momentarily contacted a three phase distribution circuit and tripped it out. HLHO was in place. All personnel was clear of the bite. No injuries. Facts Ascertained: Foreman requested and received approval from DOT to stop all work activities in the area of the circuit that was being wrecked out prior to work beginning on the day of the close call. Wacey Harrell conducted the tailboard which included the mitigation steps for falling loads and/or conductor (see attached) HLHO Requested and issued at 9:31 am on Circuit Sarah 5862 Center Phase was spread approximately 3' which should not cause porcelain stand off to break Work was stopped, DCC was notified, and new tailboard was conducted In light of the incident and as an added precaution the crew secured the phases on each side of the distribution crossing and ensured no personnel was in the bite of the line. | Jimmy Combs | Kenny La Ferney |  | Metro Service Center | FALSE |  | TRUE | Construction Services |  | Hershel Goodson | Jimmy Combs |  | Gary Lassley | This is a great example of why it is so important to conduct a detailed Tail Board. The Transmission Crew did everything right.........because of the due diligence taken by the Transmission Crew this ended up being a Near Miss instead of an Injury Accident. | Gary Lassley | Lindle Coleman | High | [14 empty] | 15.04 Improper loading or rate of use |  | Porcelain insulators broke causing conductor to fall to the ground. | 23. Defective Tools, Equipment or Materials | 2. Struck By (Hit By Moving Object) |  | Reviewed/Approved | [90 empty] | na
8685 | Metro Service Center | 2019-01-29 10:00 | Crew was wrecking out transmission line. While spreading the center phase of 795 conductor to pull a pole, the glass standoff broke on the next structure. This resulted in a domino effect where 10 spans of insulators broke. The conductor momentarily contacted a three phase distribution circuit and tripped it out. HLHO was in place. All personnel was clear of the bite. No injuries. | Level 3 |  | TRUE | Member Injury |  | Lindle Coleman | Assigned in partnership with operations leadership | 2019-01-31 15:08 | Power Delivery | Jimmy Combs | 2019-03-29 08:43 | 2019-01-29 13:50 | 2019-01-29 13:50 | 2019-02-12 15:01 | 2019-02-12 10:00 | 2019-01-29 13:31 | 2019-02-19 13:31 | 2019-02-19 14:37 | 2019-02-12 15:06 | Hwy 152 and council road widening job |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Kenny La Ferney |  | Crew was wrecking out transmission line. While spreading the center phase of 795 conductor to pull a pole, the glass standoff broke on the next structure. This resulted in a domino effect where 10 spans of insulators broke. The conductor recoiled and momentarily contacted a three phase distribution circuit and tripped it out. HLHO was in place. All personnel was clear of the bite. No injuries. Facts Ascertained: Foreman requested and received approval from DOT to stop all work activities in the area of the circuit that was being wrecked out prior to work beginning on the day of the close call. Wacey Harrell conducted the tailboard which included the mitigation steps for falling loads and/or conductor (see attached) HLHO Requested and issued at 9:31 am on Circuit Sarah 5862 Center Phase was spread approximately 3' which should not cause porcelain stand off to break Work was stopped, DCC was notified, and new tailboard was conducted In light of the incident and as an added precaution the crew secured the phases on each side of the distribution crossing and ensured no personnel was in the bite of the line. | Jimmy Combs | Kenny La Ferney |  | Metro Service Center | FALSE |  | TRUE | Construction Services |  | Hershel Goodson | Jimmy Combs |  | Gary Lassley | This is a great example of why it is so important to conduct a detailed Tail Board. The Transmission Crew did everything right.........because of the due diligence taken by the Transmission Crew this ended up being a Near Miss instead of an Injury Accident. | Gary Lassley | Lindle Coleman | High | [14 empty] | 15.03 Inadequate inspection and/or monitoring |  | Porcelain insulators broke causing conductor to fall to the ground. | 23. Defective Tools, Equipment or Materials | 2. Struck By (Hit By Moving Object) |  | Reviewed/Approved | [90 empty] | na
8685 | Metro Service Center | 2019-01-29 10:00 | Crew was wrecking out transmission line. While spreading the center phase of 795 conductor to pull a pole, the glass standoff broke on the next structure. This resulted in a domino effect where 10 spans of insulators broke. The conductor momentarily contacted a three phase distribution circuit and tripped it out. HLHO was in place. All personnel was clear of the bite. No injuries. | Level 3 |  | TRUE | Member Injury |  | Lindle Coleman | Assigned in partnership with operations leadership | 2019-01-31 15:08 | Power Delivery | Jimmy Combs | 2019-03-29 08:43 | 2019-01-29 13:50 | 2019-01-29 13:50 | 2019-02-12 15:01 | 2019-02-12 10:00 | 2019-01-29 13:31 | 2019-02-19 13:31 | 2019-02-19 14:37 | 2019-02-12 15:06 | Hwy 152 and council road widening job |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Kenny La Ferney |  | Crew was wrecking out transmission line. While spreading the center phase of 795 conductor to pull a pole, the glass standoff broke on the next structure. This resulted in a domino effect where 10 spans of insulators broke. The conductor recoiled and momentarily contacted a three phase distribution circuit and tripped it out. HLHO was in place. All personnel was clear of the bite. No injuries. Facts Ascertained: Foreman requested and received approval from DOT to stop all work activities in the area of the circuit that was being wrecked out prior to work beginning on the day of the close call. Wacey Harrell conducted the tailboard which included the mitigation steps for falling loads and/or conductor (see attached) HLHO Requested and issued at 9:31 am on Circuit Sarah 5862 Center Phase was spread approximately 3' which should not cause porcelain stand off to break Work was stopped, DCC was notified, and new tailboard was conducted In light of the incident and as an added precaution the crew secured the phases on each side of the distribution crossing and ensured no personnel was in the bite of the line. | Terry Hackett | Kenny La Ferney |  | Metro Service Center | FALSE |  | TRUE | Construction Services |  | Hershel Goodson | Jimmy Combs |  | Gary Lassley | This is a great example of why it is so important to conduct a detailed Tail Board. The Transmission Crew did everything right.........because of the due diligence taken by the Transmission Crew this ended up being a Near Miss instead of an Injury Accident. | Gary Lassley | Lindle Coleman | High | [14 empty] | 15.04 Improper loading or rate of use |  | Porcelain insulators broke causing conductor to fall to the ground. | 23. Defective Tools, Equipment or Materials | 2. Struck By (Hit By Moving Object) |  | Reviewed/Approved | [90 empty] | na
8685 | Metro Service Center | 2019-01-29 10:00 | Crew was wrecking out transmission line. While spreading the center phase of 795 conductor to pull a pole, the glass standoff broke on the next structure. This resulted in a domino effect where 10 spans of insulators broke. The conductor momentarily contacted a three phase distribution circuit and tripped it out. HLHO was in place. All personnel was clear of the bite. No injuries. | Level 3 |  | TRUE | Member Injury |  | Lindle Coleman | Assigned in partnership with operations leadership | 2019-01-31 15:08 | Power Delivery | Jimmy Combs | 2019-03-29 08:43 | 2019-01-29 13:50 | 2019-01-29 13:50 | 2019-02-12 15:01 | 2019-02-12 10:00 | 2019-01-29 13:31 | 2019-02-19 13:31 | 2019-02-19 14:37 | 2019-02-12 15:06 | Hwy 152 and council road widening job |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Kenny La Ferney |  | Crew was wrecking out transmission line. While spreading the center phase of 795 conductor to pull a pole, the glass standoff broke on the next structure. This resulted in a domino effect where 10 spans of insulators broke. The conductor recoiled and momentarily contacted a three phase distribution circuit and tripped it out. HLHO was in place. All personnel was clear of the bite. No injuries. Facts Ascertained: Foreman requested and received approval from DOT to stop all work activities in the area of the circuit that was being wrecked out prior to work beginning on the day of the close call. Wacey Harrell conducted the tailboard which included the mitigation steps for falling loads and/or conductor (see attached) HLHO Requested and issued at 9:31 am on Circuit Sarah 5862 Center Phase was spread approximately 3' which should not cause porcelain stand off to break Work was stopped, DCC was notified, and new tailboard was conducted In light of the incident and as an added precaution the crew secured the phases on each side of the distribution crossing and ensured no personnel was in the bite of the line. | Terry Hackett | Kenny La Ferney |  | Metro Service Center | FALSE |  | TRUE | Construction Services |  | Hershel Goodson | Jimmy Combs |  | Gary Lassley | This is a great example of why it is so important to conduct a detailed Tail Board. The Transmission Crew did everything right.........because of the due diligence taken by the Transmission Crew this ended up being a Near Miss instead of an Injury Accident. | Gary Lassley | Lindle Coleman | High | [14 empty] | 15.03 Inadequate inspection and/or monitoring |  | Porcelain insulators broke causing conductor to fall to the ground. | 23. Defective Tools, Equipment or Materials | 2. Struck By (Hit By Moving Object) |  | Reviewed/Approved | [90 empty] | na
8686 | Seminole PP; EGX Gath/Trans | 2019-01-29 15:00 | While removing cement pump base and grout member struck electrical conduit for freeze protection. Freeze protection conduit broke and pinched wire. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Kelly Casey | 2019-03-08 11:13 | 2019-01-29 15:54 | 2019-01-29 15:54 | 2019-02-11 06:09 | 2019-02-12 15:00 | 2019-01-29 15:47 | 2019-02-19 05:59 |  | 2019-02-18 15:10 | Seminole PP Unit 1 Screen Wash Pump on the intake |  |  | Jesse Murray | I Approve. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Kelly Casey |  | Members were assigned task of removing existing pump base and excavating existing structure to prepare for new base and grout. While using jackhammer member felt bit pinch on what he thought was rebar and used leverage of jackhammer to free the bit. Once jackhammer was free member noticed that the pinch was the result of the conduit that he did not expect to be that shallow. Work was stopped and supervisor was contacted. Electricians were notified to verify cable and clear out the energized wires. The conduit was below grade less than 2" from surface and that member needed to excavate for anchor bolt to around 4". Clearance and replacement of wire and repair of conduit is planned prior to further excavation work resuming. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | Special Services |  | Randy Ellis | Kelly Casey |  | Kelly Casey | Incident was reviewed and discussed. Future cement demolition should be looked at on a case by case basis to ensure all potential hazards are identified and possible solutions are looked at. | Kelly Casey |  | Medium | [8 empty] | 9.08 Providing inadequate reference documents, directives and guidance publications | [7 empty] | Jackhammer contacted unknown / recognized electrical conduit | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Reviewed | [66 empty] | Electrical conduit was damaged. Wire was broken. | 500 | Randy Ellis | Utility Strike | Tommy Deaton | [19 empty] | 9577225
8687 | Metro Service Center | 2019-01-17 13:00 | Sub -Contractor was moving ballistic wall from around the control house with fork lift and the wall made contact with control house guttering. Minor damage reported to the corner of gutter. Contractor will perform investigation and report findings and corrective actions. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Delivery | Cody Magby | 2019-02-21 07:37 | 2019-01-30 15:09 | 2019-01-30 15:09 | 2019-02-11 10:07 | 2019-01-31 13:00 | 2019-01-28 09:00 | 2019-02-20 15:02 |  |  | Belle Isle Substation |  |  | Cody Magby | Will continue to work with Kenny La Ferney to determine actual weight of the wall and what the best lifting method is. Will also ask construction coordinator to ask contractors to provide incident investigation. | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Cody Magby |  | AIMS Relocators Inc. was contracted to move a ballistic wall so a wire ditch could be opened up to the control house. The contract crew was on location with OGE construction crew but working independently. The contractor was using a forklift to move the wall and due to the terrain needed to set the load down to reposition. They set the wall down on 6X6 blocks to reposition, while setting the blocks began to sink in the ground causing the wall to lean into the control house guttering. About 2-3 feet of guttering was damaged which OESCO is fixing Project management has met with contractor and contractors feel the proper devices were used for lift. Safety met and discussed incident with OESCO, project management, and substation construction supervisor. John Burns, the project manager, has met with contractors and safety to review incident. Lindle Coleman was consulted on the incident and he met with Project Management manager, PM Manager feels appropriate actions have been taken at this time. |  |  |  | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Kenny La Ferney | Cody Magby |  | Gary Lassley | The Investigating Team is going to contact the vendor of the wall to get proper lifting procedures. | Gary Lassley |  | Low |  |  |  |  | 5.06 Lack of situational awareness |  |  |  |  | 10.06 Inadequate or improper controls | 11.07 Improper handling of materials |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Due to the load size and shape and the terrain of the substation it made for a particularly odd lift. The forklift was at an angle on a slope. Should have assessed and relocated before ever lifting. | 08. Improper Loading | 2. Struck By (Hit By Moving Object) | [5 empty] | Property Damage |  | Cody Magby | Gutter on control house bent |  |  |  |  | 2. Struck By (Hit By Moving Object) | Kenny La Ferney | AIMS | Curtis Markoon |  | Structural |  | John Burns |  |  |  |  | FALSE | [66 empty] | 1646243
8687 | Metro Service Center | 2019-01-17 13:00 | Sub -Contractor was moving ballistic wall from around the control house with fork lift and the wall made contact with control house guttering. Minor damage reported to the corner of gutter. Contractor will perform investigation and report findings and corrective actions. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Delivery | Cody Magby | 2019-02-21 07:37 | 2019-01-30 15:09 | 2019-01-30 15:09 | 2019-02-11 10:07 | 2019-01-31 13:00 | 2019-01-28 09:00 | 2019-02-20 15:02 |  |  | Belle Isle Substation |  |  | Cody Magby | Will continue to work with Kenny La Ferney to determine actual weight of the wall and what the best lifting method is. Will also ask construction coordinator to ask contractors to provide incident investigation. | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Cody Magby |  | AIMS Relocators Inc. was contracted to move a ballistic wall so a wire ditch could be opened up to the control house. The contract crew was on location with OGE construction crew but working independently. The contractor was using a forklift to move the wall and due to the terrain needed to set the load down to reposition. They set the wall down on 6X6 blocks to reposition, while setting the blocks began to sink in the ground causing the wall to lean into the control house guttering. About 2-3 feet of guttering was damaged which OESCO is fixing Project management has met with contractor and contractors feel the proper devices were used for lift. Safety met and discussed incident with OESCO, project management, and substation construction supervisor. John Burns, the project manager, has met with contractors and safety to review incident. Lindle Coleman was consulted on the incident and he met with Project Management manager, PM Manager feels appropriate actions have been taken at this time. |  |  |  | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Kenny La Ferney | Cody Magby |  | Gary Lassley | The Investigating Team is going to contact the vendor of the wall to get proper lifting procedures. | Gary Lassley |  | Low |  |  |  |  | 5.06 Lack of situational awareness |  |  |  |  | 10.03 Inadequate standards, specifications and/or design criteria | 11.07 Improper handling of materials |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Due to the load size and shape and the terrain of the substation it made for a particularly odd lift. The forklift was at an angle on a slope. Should have assessed and relocated before ever lifting. | 08. Improper Loading | 2. Struck By (Hit By Moving Object) | [5 empty] | Property Damage |  | Cody Magby | Gutter on control house bent |  |  |  |  | 2. Struck By (Hit By Moving Object) | Kenny La Ferney | AIMS | Curtis Markoon |  | Structural |  | John Burns |  |  |  |  | FALSE | [66 empty] | 1646243
8687 | Metro Service Center | 2019-01-17 13:00 | Sub -Contractor was moving ballistic wall from around the control house with fork lift and the wall made contact with control house guttering. Minor damage reported to the corner of gutter. Contractor will perform investigation and report findings and corrective actions. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Delivery | Cody Magby | 2019-02-21 07:37 | 2019-01-30 15:09 | 2019-01-30 15:09 | 2019-02-11 10:07 | 2019-01-31 13:00 | 2019-01-28 09:00 | 2019-02-20 15:02 |  |  | Belle Isle Substation |  |  | Cody Magby | Will continue to work with Kenny La Ferney to determine actual weight of the wall and what the best lifting method is. Will also ask construction coordinator to ask contractors to provide incident investigation. | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Cody Magby |  | AIMS Relocators Inc. was contracted to move a ballistic wall so a wire ditch could be opened up to the control house. The contract crew was on location with OGE construction crew but working independently. The contractor was using a forklift to move the wall and due to the terrain needed to set the load down to reposition. They set the wall down on 6X6 blocks to reposition, while setting the blocks began to sink in the ground causing the wall to lean into the control house guttering. About 2-3 feet of guttering was damaged which OESCO is fixing Project management has met with contractor and contractors feel the proper devices were used for lift. Safety met and discussed incident with OESCO, project management, and substation construction supervisor. John Burns, the project manager, has met with contractors and safety to review incident. Lindle Coleman was consulted on the incident and he met with Project Management manager, PM Manager feels appropriate actions have been taken at this time. |  |  |  | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Kenny La Ferney | Cody Magby |  | Gary Lassley | The Investigating Team is going to contact the vendor of the wall to get proper lifting procedures. | Gary Lassley |  | Low |  |  |  |  | 5.06 Lack of situational awareness |  |  |  |  | 10.04 Inadequate monitoring of construction | 11.07 Improper handling of materials |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Due to the load size and shape and the terrain of the substation it made for a particularly odd lift. The forklift was at an angle on a slope. Should have assessed and relocated before ever lifting. | 08. Improper Loading | 2. Struck By (Hit By Moving Object) | [5 empty] | Property Damage |  | Cody Magby | Gutter on control house bent |  |  |  |  | 2. Struck By (Hit By Moving Object) | Kenny La Ferney | AIMS | Curtis Markoon |  | Structural |  | John Burns |  |  |  |  | FALSE | [66 empty] | 1646243
8687 | Metro Service Center | 2019-01-17 13:00 | Sub -Contractor was moving ballistic wall from around the control house with fork lift and the wall made contact with control house guttering. Minor damage reported to the corner of gutter. Contractor will perform investigation and report findings and corrective actions. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Delivery | Cody Magby | 2019-02-21 07:37 | 2019-01-30 15:09 | 2019-01-30 15:09 | 2019-02-11 10:07 | 2019-01-31 13:00 | 2019-01-28 09:00 | 2019-02-20 15:02 |  |  | Belle Isle Substation |  |  | Cody Magby | Will continue to work with Kenny La Ferney to determine actual weight of the wall and what the best lifting method is. Will also ask construction coordinator to ask contractors to provide incident investigation. | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Cody Magby |  | AIMS Relocators Inc. was contracted to move a ballistic wall so a wire ditch could be opened up to the control house. The contract crew was on location with OGE construction crew but working independently. The contractor was using a forklift to move the wall and due to the terrain needed to set the load down to reposition. They set the wall down on 6X6 blocks to reposition, while setting the blocks began to sink in the ground causing the wall to lean into the control house guttering. About 2-3 feet of guttering was damaged which OESCO is fixing Project management has met with contractor and contractors feel the proper devices were used for lift. Safety met and discussed incident with OESCO, project management, and substation construction supervisor. John Burns, the project manager, has met with contractors and safety to review incident. Lindle Coleman was consulted on the incident and he met with Project Management manager, PM Manager feels appropriate actions have been taken at this time. |  |  |  | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Kenny La Ferney | Cody Magby |  | Gary Lassley | The Investigating Team is going to contact the vendor of the wall to get proper lifting procedures. | Gary Lassley |  | Low |  |  |  |  | 5.06 Lack of situational awareness |  |  |  |  | 10.08 Inadequate evaluation of changes | 11.07 Improper handling of materials |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Due to the load size and shape and the terrain of the substation it made for a particularly odd lift. The forklift was at an angle on a slope. Should have assessed and relocated before ever lifting. | 08. Improper Loading | 2. Struck By (Hit By Moving Object) | [5 empty] | Property Damage |  | Cody Magby | Gutter on control house bent |  |  |  |  | 2. Struck By (Hit By Moving Object) | Kenny La Ferney | AIMS | Curtis Markoon |  | Structural |  | John Burns |  |  |  |  | FALSE | [66 empty] | 1646243
8689 | Muskogee Power Plant | 2019-01-31 08:30 | Contract dump truck driver was dumping ash at the Muskogee landfill. After raising dump bed trailer became unstable and turned over on it's side. The truck did not turn over and driver was not injured | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Robert Wright | 2019-03-08 12:59 | 2019-01-31 15:58 | 2019-01-31 15:58 | 2019-02-05 14:30 | 2019-02-14 08:30 | 2019-01-31 15:33 | 2019-02-22 15:31 |  | 2019-02-05 14:31 | Incident occurred at the Muskogee Landfill |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Robert Wright |  | While unloading CCR at the Muskogee Landfill, the end-dump trailer attached to truck #189 driven by Mr. Northrup fell over. The trailer was loaded at the time and caused significant damage to the structural braces. Brad Brittain and Vernon Liles went immediately to the landfill to inspect. The trailer was laying on its side. The truck was upright, however the passenger side duals were off the ground due to the trailer still being attached. Inspection of the tail gate showed the passenger side gate latch was bent. There were no releases of hydraulic oil or diesel fuel during the incident. Pictures attached. Causal factors: The tail latch did not open as a result of a combination of the following factors. Cold temperatures may have caused the hydraulic system to seize or the latch failed mechanically in some other way. The truck was slightly overloaded (approx. 2 tons), and the extra weight may have contributed to the latch sticking. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | Power Supply Services |  | Robert Wright | Robert Wright |  | Jonathan Stogsdill | Reviewed. No comments. JHS | Jonathan Stogsdill |  | Medium | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | As the load of material was being lifted to dump the tail gate on the trailer did not open causing the trailer to become unstable. The trailer started to lean causing the lifting ram to break on the trailer end. The trailer full of ash hit the ground. The trailer was laying on its side and the truck was still upright. | 06. Using Defective Equipment | 12. Equipment Failure |  | Reviewed Bob Wright |  |  |  | Vehicle |  | Robbie Gildenblatt | [5 empty] | 12. Equipment Failure | Robbie Gildenblatt | Yokum Trucking | Leon Northrup |  |  |  | Robbie Gildenblatt |  |  |  |  | FALSE | [66 empty] | 9576806
8690 | Muskogee Power Plant | 2019-01-29 16:30 | A contracted employee was witnessed standing inside a hard barricaded area with out fall protection. The barricaded area had a 2 by 2 1/2 foot opening that was exposed to a potential fall area. The contractor was escorted down by the contracting safety professional. | Level 1 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services |  | 2019-02-25 15:31 | 2019-01-31 17:36 | 2019-01-31 17:36 | 2019-02-18 10:44 | 2019-02-12 22:30 | 2019-01-31 17:23 | 2019-02-21 15:26 |  |  | Muskogee PP Unit 4 Floor 5 |  |  | Marcus Huddleston | No additional comments. MLH 2/25/19 | UTS |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | Brian Evans was observed by a TEIC safety representative not tied off or wearing a harness inside a hard barricade around a floor penetration. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | UTS - Capital Projects |  |  |  |  | Christopher Lelak | The contract employee was released by his contracting company. - CBL 02/21/19 | Christopher Lelak |  | Low |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction | [10 empty] | Contractor willfully entered a fall protection isolated location without proper PPE. | 17. Failure to Identify Hazard, Risk | 9. Abnormal Operation |  |  |  |  | MK Gas Conversion | Injury / Illness | [7 empty] | 3. Fall from Elevation to Lower Level |  | TEIC | Brian Evans |  |  |  | Marcus Huddleston | [71 empty] | 1645831
8691 | Durant Service Center | 2019-01-31 12:30 | Tree crew dropped branch causing phase to phase fault and sustained outage | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services |  | 2019-06-20 11:29 | 2019-01-31 18:18 | 2019-01-31 18:18 | 2019-06-14 13:26 | 2019-02-14 18:30 | 2019-01-31 16:00 | 2019-06-18 14:23 |  | 2019-06-14 15:31 | Circuits Bodle 550661 and Durant 550522 - NE 5th and Lee in Durant |  |  | William Young | Returning for corrective actions to be added to incident. Understand Jarods's comment, "addressed in four actions they undertook, however, in order to be able to query or mind data in Intelex we need to have the CA's inputted into the CA fields. WCY 4/4/19 | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | Worker on crew did not follow job briefing or instructions from foreman. Cut branch without controls causing outage and damage to customer equipment. After creating the outage, the employee walked off the job site and the vendor has not been able to contact him. |  |  |  | Durant Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Danny Coffey |  |  |  | This was addressed in their four actions they undertook. |  |  | Medium |  | 2.04 Intelligence level |  |  | 5.06 Lack of situational awareness |  | 7.08 Improper attempt to gain attention |  | 9.11 Inadequate matching of individual qualifications and job/task requirements | [7 empty] | Tree trimmer caused outage by failing to control material being cut | 16. Failure to Follow Procedure, Policy, Practice | 2. Struck By (Hit By Moving Object) |  | Corrective Actions added. Approve, J. Looney, 6/14/19 |  |  |  | Property Damage |  |  | Industrial and Residential electrical equipment |  |  |  |  | 2. Struck By (Hit By Moving Object) | Danny Coffey | Whitmire Line Clearance | David Peasley |  | 3rd Party Property/Equipment |  | Danny Coffey |  |  |  |  | FALSE | [66 empty] | none
8691 | Durant Service Center | 2019-01-31 12:30 | Tree crew dropped branch causing phase to phase fault and sustained outage | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services |  | 2019-06-20 11:29 | 2019-01-31 18:18 | 2019-01-31 18:18 | 2019-06-14 13:26 | 2019-02-14 18:30 | 2019-01-31 16:00 | 2019-06-18 14:23 |  | 2019-06-14 15:31 | Circuits Bodle 550661 and Durant 550522 - NE 5th and Lee in Durant |  |  | William Young | Returning for corrective actions to be added to incident. Understand Jarods's comment, "addressed in four actions they undertook, however, in order to be able to query or mind data in Intelex we need to have the CA's inputted into the CA fields. WCY 4/4/19 | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | Worker on crew did not follow job briefing or instructions from foreman. Cut branch without controls causing outage and damage to customer equipment. After creating the outage, the employee walked off the job site and the vendor has not been able to contact him. |  |  |  | Durant Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Danny Coffey |  |  |  | This was addressed in their four actions they undertook. |  |  | Medium |  | 2.04 Intelligence level |  |  | 5.06 Lack of situational awareness |  | 7.08 Improper attempt to gain attention |  | 9.11 Inadequate matching of individual qualifications and job/task requirements | [7 empty] | Tree trimmer caused outage by failing to control material being cut | 16. Failure to Follow Procedure, Policy, Practice | 2. Struck By (Hit By Moving Object) |  | Corrective Actions added. Approve, J. Looney, 6/14/19 |  |  |  | System Outage |  |  | Industrial and Residential electrical equipment |  |  |  |  | 2. Struck By (Hit By Moving Object) | Danny Coffey | Whitmire Line Clearance | David Peasley |  | 3rd Party Property/Equipment |  | Danny Coffey |  |  |  |  | FALSE | [66 empty] | none
8692 | Enid Service Center | 2019-01-31 12:00 | My personal vehicle had received front end work the night before. at lunch I did a 360 around my vehicle and noticed the lug nuts appeared to be loose. I jacked the front end up and the lug nuts were backed off half way. tightened lug nuts and took the vehicle back to the shop along with a video of the loose wheel. I was given a new wheel due to the studs wearing on the inside of the holes in the wheel and being damaged | Level 2 |  | TRUE | Vehicle |  |  |  |  | Power Delivery | Kelly Powell | 2019-02-18 08:30 | 2019-02-01 09:49 | 2019-02-01 09:49 | 2019-02-15 11:06 | 2019-02-14 12:00 | 2019-02-01 09:21 | 2019-02-17 15:10 |  | 2019-02-15 11:30 | Enid service center parking lot (Personal vehicle ) |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Kelly Powell |  | My personal vehicle had received front end work the night before. at lunch I did a 360 around my vehicle and noticed the lug nuts appeared to be loose. I jacked the front end up and the lug nuts were backed off half way. tightened lug nuts and took the vehicle back to the shop along with a video of the loose wheel. I was given a new wheel due to the studs wearing on the inside of the holes in the wheel and being damaged. Later that evening I received a text from the shop wanting me to bring the vehicle in at my conveince to check all work done on the vehicle and that the employee who had did the work was no longer with them as this was so far from there standard of work. |  |  |  | Enid Service Center | FALSE |  | TRUE | Distribution Eng & Tech Services |  | Kelly Powell | Kelly Powell |  | Brian Routh | Member had received a safety recognition for his diligence in performing 360s for work and personal vehicles. I approve of the investigation. | Brian Routh |  | Medium | [6 empty] | 7.06 Improper attempt to save time or effort | [9 empty] | lug nuts not being tightened properly | 16. Failure to Follow Procedure, Policy, Practice | 12. Equipment Failure |  | Member took appropriate steps to ensure that the company responsible for this oversight was aware of the mishap and would mitigate this hazard in the future. | [90 empty] | none
8693 | Muskogee Power Plant | 2019-02-01 08:00 | Contract dump truck driver was dumping ash at the Muskogee landfill. After raising dump bed trailer became unstable and turned over on it's side. The truck did not turn over and driver was not injured | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Joel Leavell | 2019-02-25 08:17 | 2019-02-01 14:21 | 2019-02-01 14:21 | 2019-02-05 15:14 | 2019-02-15 08:00 | 2019-02-01 14:12 | 2019-02-07 10:46 |  | 2019-02-05 15:15 | Incident occurred at the Muskogee Landfill |  |  | Jesse Murray | I Approve. Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Robert Wright |  | The truck / trailer was under loaded so weight was not likely a direct cause to the failure. Inspection of the breaks in the A-frame showed there may have been some hairline fractures in the metal. These were located on the inside of the frame in a location that would be difficult to see during a normal pre- or post-trip inspection. The failing component was the base of the hydraulic dump ram |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | Other |  | Joel Leavell | Joel Leavell |  | Carol Rollins | inspections of trailers performed. but not in the corrective actions | Carol Rollins |  | Medium | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | The base of the hydraulic lifting ram broke under load during the dump | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure |  | Reviewed Bob Wright |  |  |  | Vehicle |  | Robbie Gildenblatt | [5 empty] | 12. Equipment Failure | Robbie Gildenblatt | Yokum Trucking | Leon Northrup |  |  |  | Robbie Gildenblatt |  |  |  |  | FALSE | [66 empty] | Na
8694 | Sooner Power Plant | 2019-01-31 20:10 | Aerotek Custodian fell down the stairway leading out of the contractor trailer after completing cleaning duties. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Supply | Brady Sowell | 2019-02-25 08:19 | 2019-02-01 20:03 | 2019-02-01 20:03 | 2019-02-12 09:32 | 2019-02-14 20:10 | 2019-02-01 15:00 | 2019-02-17 10:20 |  | 2019-02-15 07:39 | Contractor Trailer Stairway |  |  | Jesse Murray | Jesse Murray - Approved | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Schnelle Broome |  | On 1/31/19 around 8:10 pm Aerotek Custodian fell down the scaffold staircase leading out of the contractor trailer after completing cleaning duties. The light was out in that area and scaffold staircase did not have accurate handrail. (See Picture) An order was written 11/05/2018 to fix staircase # 9577926. The Aerotek Custodians at Sooner went through a proper orientation with their supervisor and completed the training assigned to them according to their student group. Opportunities Identified: - Aerotek Custodians work alone and no one knows where they are currently working at. - The Custodians had no notification system to the control room if they were injured or in an emergency situation. - 1 custodian had difficulty recalling shelter area. She stated she would not have found it in an emergency. - The Aerotek member did not report the incident until they arrived for their shift the next day. |  |  | FALSE | Sooner Power Plant | FALSE |  | FALSE | Other |  | Shawndra Sheik | Brady Sowell |  | Kent Wilson | Approved | Kent Wilson |  | Medium | [9 empty] | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.01 Inadequate assessment of needs and risks |  |  |  | Poor lighting and inadequate handrail. | 21. Inadequate Guards or Barriers | 3. Fall from Elevation to Lower Level |  | Approved by Brady Sowell on 2/15/2019 | [24 empty] | FALSE |  |  | 2018-11-29 |  |  | 2019-01-31 14:30 | 0 | 0 |  | FALSE | Female | Aerotek Member was traveling down stairs in a poorly lit area and fell down the stairs. |  | FALSE | Ethel Brewer |  | First Aid | Ethel Brewer |  |  |  |  | Sprain/Strain |  | FALSE |  | Custodian | Knee |  | Right | FALSE | Schnelle Broome | FALSE |  | 1/31/2019 2:30:00 PM | 3 months | FALSE |  |  | Stairs and ground | Aerotek member was cleaning contractor trailer | [24 empty] | None
8694 | Sooner Power Plant | 2019-01-31 20:10 | Aerotek Custodian fell down the stairway leading out of the contractor trailer after completing cleaning duties. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Supply | Brady Sowell | 2019-02-25 08:19 | 2019-02-01 20:03 | 2019-02-01 20:03 | 2019-02-12 09:32 | 2019-02-14 20:10 | 2019-02-01 15:00 | 2019-02-17 10:20 |  | 2019-02-15 07:39 | Contractor Trailer Stairway |  |  | Jesse Murray | Jesse Murray - Approved | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Schnelle Broome |  | On 1/31/19 around 8:10 pm Aerotek Custodian fell down the scaffold staircase leading out of the contractor trailer after completing cleaning duties. The light was out in that area and scaffold staircase did not have accurate handrail. (See Picture) An order was written 11/05/2018 to fix staircase # 9577926. The Aerotek Custodians at Sooner went through a proper orientation with their supervisor and completed the training assigned to them according to their student group. Opportunities Identified: - Aerotek Custodians work alone and no one knows where they are currently working at. - The Custodians had no notification system to the control room if they were injured or in an emergency situation. - 1 custodian had difficulty recalling shelter area. She stated she would not have found it in an emergency. - The Aerotek member did not report the incident until they arrived for their shift the next day. |  |  | FALSE | Sooner Power Plant | FALSE |  | FALSE | Other |  | Shawndra Sheik | Brady Sowell |  | Kent Wilson | Approved | Kent Wilson |  | Medium | [9 empty] | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.03 Inadequate standards or specifications |  |  |  | Poor lighting and inadequate handrail. | 21. Inadequate Guards or Barriers | 3. Fall from Elevation to Lower Level |  | Approved by Brady Sowell on 2/15/2019 | [24 empty] | FALSE |  |  | 2018-11-29 |  |  | 2019-01-31 14:30 | 0 | 0 |  | FALSE | Female | Aerotek Member was traveling down stairs in a poorly lit area and fell down the stairs. |  | FALSE | Ethel Brewer |  | First Aid | Ethel Brewer |  |  |  |  | Sprain/Strain |  | FALSE |  | Custodian | Knee |  | Right | FALSE | Schnelle Broome | FALSE |  | 1/31/2019 2:30:00 PM | 3 months | FALSE |  |  | Stairs and ground | Aerotek member was cleaning contractor trailer | [24 empty] | None
8695 | Sooner Power Plant | 2019-02-03 16:00 | Member in Pickup truck pulled up to water treatment building, stopped truck, opened door, wind caught door and sprung the hinges. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Daniel Dickinson | 2019-02-15 07:26 | 2019-02-03 18:24 | 2019-02-03 18:24 | 2019-02-05 05:27 | 2019-02-17 16:00 | 2019-02-03 18:20 | 2019-02-08 14:07 |  |  | Sooner PP, Water treatment building |  |  | Brady Sowell | approved by brady sowell | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Daniel Dickinson |  | on Sunday, Feb 3rd at 1600, weather is clear with a strong South wind and frequent gusts, Scrubber Operator was driving silo truck North headed back to Scrubber and stopped at water treatment building to check equipment/take readings. Operator opened drivers side door and wind caught door and flung it open. Operator shut door and went into water treatment building, made his rounds and when he came back out and when he tried to open driver side door he could not get door open because hinges were sprung and front lip of door was contacting back edge of fender. Operator reported damage to Supervisor. Upon further investigation and comparing hinges to passenger side, it appears the spring that should be in drivers side lower hinge is missing. I believe this spring is meant to absorb some of the stress from the door getting flung open and since it was missing the hinges took all of the force when the wind caught the door. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Operations |  | Blake Underwood | Daniel Dickinson |  | Alexander Taybah | I highly recommend working with OGE Fleet on a solution for this type of incident to prevent them from re-occurring. There is nothing like an engaged driver but I feel frustrated since such incidents keep on happening. | Alexander Taybah |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [6 empty] | 12.02.3 Inadequate reparative examination of units | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | wind caught pickup truck door and sprung hinges | 09. Improper Placement | 9. Abnormal Operation | [68 empty] | silo truck driver side door hinges are sprung, paint is chipped off of door. | 200 | Blake Underwood | Vehicle (not related to operation of vehicle) |  | FO3-1240 | [18 empty] | none
8696 | Metro Service Center | 2019-02-01 14:00 | While traveling down Interstate 240 bin door of flatbed truck bounced open from rough roadway. Aluminum Dolly fell out onto the road. A portion of the dolly shattered and the remainder of the dolly ended up in the median. No injury or damage to vehicles. | Level 3 |  | TRUE | Vehicle |  | Lindle Coleman | assigned | 2019-02-04 09:28 | Power Delivery | Quay Prough | 2019-03-01 10:59 | 2019-02-04 08:43 | 2019-02-04 08:43 | 2019-02-12 15:44 | 2019-02-15 14:00 | 2019-02-01 14:00 | 2019-02-19 13:32 | 2019-02-19 14:39 | 2019-02-13 09:31 | I-240 east bound at Bryant bridge. |  |  |  | approve | T&D Ops |  | Level 3 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Kenny La Ferney |  | o The crew, driving a flatbed truck and pulling a trailer, had just dropped off an empty reel at Metro and was heading back to Air Depot Sub to pick up another full reel. They travelled down I-35 and merged on to east bound I-240. While crossing the Eastern Avenue Bridge in the right hand lane they drove across a rough spot in the road. The driver maintained control of the vehicle and checked his mirrors to ensure the trailer was not affected by the shaking of the vehicle. When checking the mirrors, the driver saw the bin door open and the dolly fall out. The dolly hit the trailer tire, and shot across the left hand lane into the median. Part of the dolly shattered when it hit the road. There was public vehicles behind our company vehicle, but there was no damage to public vehicles. The crew members pulled off the road in a safe position and walked back to pick up the dolly. • FACTS GATHERED FROM INVESTIGATION o How fast was the vehicle travelling?  Speed limit (55-60 mph) o Is this the proper place to store the dolly?  Yes. It is the most secure place to store the dolly on the vehicle. o Has this happened before?  There have not been any issues reported with the flatbed vehicle.  This is a shared vehicle by the department. It is not assigned to any particular member or crew. o Is the bin overloaded (too full)?  No, only basic material is in the bin. o Has Fleet inspected the latch?  Yes, Fleet has repaired all failed parts of the latch.  Fleet found that the latching rod fell apart, due to a loose nut.  Lock-tite was used when repairing latch.  New locks are ordered.  Latch still will not come to the proper position when closed.  There are still unresolved issues with the vehicle. o What else is stored in the bin?  Basic pulling blocks, chains, and slings. o Would locking the bin prevent it from popping open?  Due to the mechanical failure, the likelihood of locking the bin making a difference is minimal.  Locking a bin door before travelling is still beneficial for preventing this from happening again.  The locks are non-functioning on the bins. o What are some options for preventing this from happening again?  Make sure all locks/latches are inspected  Lock doors before travelling  Store excess material in better location  Install secondary latch. o How long was bin door open before driver noticed?  Member seen the bin door open. o Was DOT pre-trip conducted?  Yes. | Brent Perdue | Kenny La Ferney |  | Metro Service Center | FALSE |  | TRUE | Construction Services |  | Adam Carey | Brent Boles |  | Gary Lassley | Good investigation. I concur with the proposed corrective actions | Gary Lassley | Lindle Coleman | High | [7 empty] | 8.1.2 Improper conduct that is condoned: Unintentional |  |  |  |  | 13.05 Inadequate adjustment/repair/maintenance |  | 15.03 Inadequate inspection and/or monitoring |  | bin door latch failed | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure |  | Reviewed/Approved | [90 empty] | none
8696 | Metro Service Center | 2019-02-01 14:00 | While traveling down Interstate 240 bin door of flatbed truck bounced open from rough roadway. Aluminum Dolly fell out onto the road. A portion of the dolly shattered and the remainder of the dolly ended up in the median. No injury or damage to vehicles. | Level 3 |  | TRUE | Vehicle |  | Lindle Coleman | assigned | 2019-02-04 09:28 | Power Delivery | Quay Prough | 2019-03-01 10:59 | 2019-02-04 08:43 | 2019-02-04 08:43 | 2019-02-12 15:44 | 2019-02-15 14:00 | 2019-02-01 14:00 | 2019-02-19 13:32 | 2019-02-19 14:39 | 2019-02-13 09:31 | I-240 east bound at Bryant bridge. |  |  |  | approve | T&D Ops |  | Level 3 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Kenny La Ferney |  | o The crew, driving a flatbed truck and pulling a trailer, had just dropped off an empty reel at Metro and was heading back to Air Depot Sub to pick up another full reel. They travelled down I-35 and merged on to east bound I-240. While crossing the Eastern Avenue Bridge in the right hand lane they drove across a rough spot in the road. The driver maintained control of the vehicle and checked his mirrors to ensure the trailer was not affected by the shaking of the vehicle. When checking the mirrors, the driver saw the bin door open and the dolly fall out. The dolly hit the trailer tire, and shot across the left hand lane into the median. Part of the dolly shattered when it hit the road. There was public vehicles behind our company vehicle, but there was no damage to public vehicles. The crew members pulled off the road in a safe position and walked back to pick up the dolly. • FACTS GATHERED FROM INVESTIGATION o How fast was the vehicle travelling?  Speed limit (55-60 mph) o Is this the proper place to store the dolly?  Yes. It is the most secure place to store the dolly on the vehicle. o Has this happened before?  There have not been any issues reported with the flatbed vehicle.  This is a shared vehicle by the department. It is not assigned to any particular member or crew. o Is the bin overloaded (too full)?  No, only basic material is in the bin. o Has Fleet inspected the latch?  Yes, Fleet has repaired all failed parts of the latch.  Fleet found that the latching rod fell apart, due to a loose nut.  Lock-tite was used when repairing latch.  New locks are ordered.  Latch still will not come to the proper position when closed.  There are still unresolved issues with the vehicle. o What else is stored in the bin?  Basic pulling blocks, chains, and slings. o Would locking the bin prevent it from popping open?  Due to the mechanical failure, the likelihood of locking the bin making a difference is minimal.  Locking a bin door before travelling is still beneficial for preventing this from happening again.  The locks are non-functioning on the bins. o What are some options for preventing this from happening again?  Make sure all locks/latches are inspected  Lock doors before travelling  Store excess material in better location  Install secondary latch. o How long was bin door open before driver noticed?  Member seen the bin door open. o Was DOT pre-trip conducted?  Yes. | Brent Perdue | Kenny La Ferney |  | Metro Service Center | FALSE |  | TRUE | Construction Services |  | Adam Carey | Brent Boles |  | Gary Lassley | Good investigation. I concur with the proposed corrective actions | Gary Lassley | Lindle Coleman | High | [7 empty] | 8.1.2 Improper conduct that is condoned: Unintentional |  |  |  |  | 13.01 Inadequate assessment of needs and risks |  | 15.03 Inadequate inspection and/or monitoring |  | bin door latch failed | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure |  | Reviewed/Approved | [90 empty] | none
8696 | Metro Service Center | 2019-02-01 14:00 | While traveling down Interstate 240 bin door of flatbed truck bounced open from rough roadway. Aluminum Dolly fell out onto the road. A portion of the dolly shattered and the remainder of the dolly ended up in the median. No injury or damage to vehicles. | Level 3 |  | TRUE | Vehicle |  | Lindle Coleman | assigned | 2019-02-04 09:28 | Power Delivery | Quay Prough | 2019-03-01 10:59 | 2019-02-04 08:43 | 2019-02-04 08:43 | 2019-02-12 15:44 | 2019-02-15 14:00 | 2019-02-01 14:00 | 2019-02-19 13:32 | 2019-02-19 14:39 | 2019-02-13 09:31 | I-240 east bound at Bryant bridge. |  |  |  | approve | T&D Ops |  | Level 3 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Kenny La Ferney |  | o The crew, driving a flatbed truck and pulling a trailer, had just dropped off an empty reel at Metro and was heading back to Air Depot Sub to pick up another full reel. They travelled down I-35 and merged on to east bound I-240. While crossing the Eastern Avenue Bridge in the right hand lane they drove across a rough spot in the road. The driver maintained control of the vehicle and checked his mirrors to ensure the trailer was not affected by the shaking of the vehicle. When checking the mirrors, the driver saw the bin door open and the dolly fall out. The dolly hit the trailer tire, and shot across the left hand lane into the median. Part of the dolly shattered when it hit the road. There was public vehicles behind our company vehicle, but there was no damage to public vehicles. The crew members pulled off the road in a safe position and walked back to pick up the dolly. • FACTS GATHERED FROM INVESTIGATION o How fast was the vehicle travelling?  Speed limit (55-60 mph) o Is this the proper place to store the dolly?  Yes. It is the most secure place to store the dolly on the vehicle. o Has this happened before?  There have not been any issues reported with the flatbed vehicle.  This is a shared vehicle by the department. It is not assigned to any particular member or crew. o Is the bin overloaded (too full)?  No, only basic material is in the bin. o Has Fleet inspected the latch?  Yes, Fleet has repaired all failed parts of the latch.  Fleet found that the latching rod fell apart, due to a loose nut.  Lock-tite was used when repairing latch.  New locks are ordered.  Latch still will not come to the proper position when closed.  There are still unresolved issues with the vehicle. o What else is stored in the bin?  Basic pulling blocks, chains, and slings. o Would locking the bin prevent it from popping open?  Due to the mechanical failure, the likelihood of locking the bin making a difference is minimal.  Locking a bin door before travelling is still beneficial for preventing this from happening again.  The locks are non-functioning on the bins. o What are some options for preventing this from happening again?  Make sure all locks/latches are inspected  Lock doors before travelling  Store excess material in better location  Install secondary latch. o How long was bin door open before driver noticed?  Member seen the bin door open. o Was DOT pre-trip conducted?  Yes. | Nathan Gooch | Kenny La Ferney |  | Metro Service Center | FALSE |  | TRUE | Construction Services |  | Adam Carey | Brent Boles |  | Gary Lassley | Good investigation. I concur with the proposed corrective actions | Gary Lassley | Lindle Coleman | High | [7 empty] | 8.1.2 Improper conduct that is condoned: Unintentional |  |  |  |  | 13.05 Inadequate adjustment/repair/maintenance |  | 15.03 Inadequate inspection and/or monitoring |  | bin door latch failed | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure |  | Reviewed/Approved | [90 empty] | none
8696 | Metro Service Center | 2019-02-01 14:00 | While traveling down Interstate 240 bin door of flatbed truck bounced open from rough roadway. Aluminum Dolly fell out onto the road. A portion of the dolly shattered and the remainder of the dolly ended up in the median. No injury or damage to vehicles. | Level 3 |  | TRUE | Vehicle |  | Lindle Coleman | assigned | 2019-02-04 09:28 | Power Delivery | Quay Prough | 2019-03-01 10:59 | 2019-02-04 08:43 | 2019-02-04 08:43 | 2019-02-12 15:44 | 2019-02-15 14:00 | 2019-02-01 14:00 | 2019-02-19 13:32 | 2019-02-19 14:39 | 2019-02-13 09:31 | I-240 east bound at Bryant bridge. |  |  |  | approve | T&D Ops |  | Level 3 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Kenny La Ferney |  | o The crew, driving a flatbed truck and pulling a trailer, had just dropped off an empty reel at Metro and was heading back to Air Depot Sub to pick up another full reel. They travelled down I-35 and merged on to east bound I-240. While crossing the Eastern Avenue Bridge in the right hand lane they drove across a rough spot in the road. The driver maintained control of the vehicle and checked his mirrors to ensure the trailer was not affected by the shaking of the vehicle. When checking the mirrors, the driver saw the bin door open and the dolly fall out. The dolly hit the trailer tire, and shot across the left hand lane into the median. Part of the dolly shattered when it hit the road. There was public vehicles behind our company vehicle, but there was no damage to public vehicles. The crew members pulled off the road in a safe position and walked back to pick up the dolly. • FACTS GATHERED FROM INVESTIGATION o How fast was the vehicle travelling?  Speed limit (55-60 mph) o Is this the proper place to store the dolly?  Yes. It is the most secure place to store the dolly on the vehicle. o Has this happened before?  There have not been any issues reported with the flatbed vehicle.  This is a shared vehicle by the department. It is not assigned to any particular member or crew. o Is the bin overloaded (too full)?  No, only basic material is in the bin. o Has Fleet inspected the latch?  Yes, Fleet has repaired all failed parts of the latch.  Fleet found that the latching rod fell apart, due to a loose nut.  Lock-tite was used when repairing latch.  New locks are ordered.  Latch still will not come to the proper position when closed.  There are still unresolved issues with the vehicle. o What else is stored in the bin?  Basic pulling blocks, chains, and slings. o Would locking the bin prevent it from popping open?  Due to the mechanical failure, the likelihood of locking the bin making a difference is minimal.  Locking a bin door before travelling is still beneficial for preventing this from happening again.  The locks are non-functioning on the bins. o What are some options for preventing this from happening again?  Make sure all locks/latches are inspected  Lock doors before travelling  Store excess material in better location  Install secondary latch. o How long was bin door open before driver noticed?  Member seen the bin door open. o Was DOT pre-trip conducted?  Yes. | Nathan Gooch | Kenny La Ferney |  | Metro Service Center | FALSE |  | TRUE | Construction Services |  | Adam Carey | Brent Boles |  | Gary Lassley | Good investigation. I concur with the proposed corrective actions | Gary Lassley | Lindle Coleman | High | [7 empty] | 8.1.2 Improper conduct that is condoned: Unintentional |  |  |  |  | 13.01 Inadequate assessment of needs and risks |  | 15.03 Inadequate inspection and/or monitoring |  | bin door latch failed | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure |  | Reviewed/Approved | [90 empty] | none
8697 | Muskogee Service Center | 2019-01-31 | On Wednesday 1/30/2019, at Sapulpa substation the 125 dc volt battery set was replaced due to age and deterioration by a contractor. On Thursday, 1/31/2019 the entire customer load at the substation had to be transferred when it was determined that an insufficient number of replacement batteries were installed which resulted in an inadequate DC voltage supply to permit the proper possible operation of the protective relays. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Delivery | John Burns | 2019-08-02 07:23 | 2019-02-04 09:26 | 2019-02-04 09:26 | 2019-07-26 08:12 | 2019-02-14 | 2019-02-01 09:11 | 2019-08-02 07:03 |  | 2019-08-01 14:08 | Sapulpa Substation |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | TRUE | FALSE | Jeffrey Uhls |  | Operational Incident Summary On Thursday, 1/31/2019 the entire customer load at Sapulpa substation had to be transferred or dropped when it was determined that an insufficient number of replacement batteries were installed. This resulted in an inadequate DC voltage and current capacity supply to permit the proper possible operation of protective equipment within the substation if a fault condition occurred. During the week the 125Vdc battery bank at the substation was being replaced due to age and deterioration by a contractor. Twelve batteries; totaling thirty-six cells were installed by the contractor and placed in service with a measured voltage of 74Vdc. Chain of Events: • In September 2018 a single pallet containing 12 battery jars and its associated hardware were picked up from the Anixter warehouse located at the General Service Center by a contractor and taken to their shop for storage until the job could be worked. Monday 1/28/2019 • A two man contractor crew picked up the prints for the job, then loaded material and equipment from their shop in Oklahoma City for the battery replacement job and traveled to Sapulpa substation to being work. o The contractor foreman was informed by his supervisor that an OGE crew would come to the substation and connect the Barrington DC power supply unit to the substation DC distribution box. o Upon arrival at the substation, the contractor crew unloaded the batteries and material from the truck; they then started to assemble the battery rack in the control room.  There were no instructions for assembling the rack so the crew went to another substation to view an assembled rack, but they did not find a similar rack at the other substation so they returned to Sapulpa substation and resumed working on assembling the rack. • An OGE Muskogee substation relay crew was contacted and asked to go to Sapulpa substation and connect the Barrington DC power supply unit for the contractors. o When the crew arrived, they connected the Barrington DC power supply unit to the buss bar of the substation DC distribution box.  The substation battery charger ac and dc breakers were turned off and the cables to the disconnect box were lifted when the Barrington device was connected and turned on. • The cables between the battery charger and the battery disconnect box were lifted at both ends by the crew to isolate the charger from the DC system while the Barrington was connected. • The contractor continued to work on assembling the battery rack inside the control room for the remainder of the day. Tuesday 1/29/2019 • The Contractor Project Manager arrives on site and helps with the assembly of the battery rack. o He brought some additional missing parts for the battery rack. • After completing the assembly of the new battery rack the contractor crew disconnected and removed the old batteries and rack from the battery room in preparation for the installation of the new batteries and rack. o The new rack was moved into the battery room from the control room once the old batteries and rack were disassembled and removed. o The old batteries were placed on a pallet to be taken away for disposal. o The old #2 cables from the DC disconnect box located in the control house to the battery rack in the battery room were removed. • The contractor crew placed the new batteries on the rack, placing 6 batteries on the top tier of the rack and 6 batteries on the bottom tier. o The contractor apprenticed asked why there were only 12 batteries being installed when there were 20 batteries being removed.  An assumption was made that because the new batteries were larger in physical size that not as many batteries were necessary for the installation. • The contractor crew started connecting the battery jars together in series using the cable straps provided for the installation. Wednesday 1/30/2019 • The contractor crew completed the connections of the cable straps for the new batteries. o The DC voltage measurement taken at this time was 74Vdc. o The Barrington DC power supply was still connected to DC distribution box with DC disconnect in the open position. • That afternoon the contractor crew transported the old batteries to Oklahoma City for disposal. Thursday 1/31/2019 • The contractor crew pulled in new #2 cables between the batteries in the battery room and the DC disconnect box in the control room. • After completing the installation of the batteries and new cables the contractor foreman informed the contractor project manager that he measured 74Vdc on the new batteries and asked if they needed to be charged before placing them online. o The foreman was told by the project manager to put them on charge and he would have OGE personnel come out and check everything. o An assumption by the foreman was made that the Barrington unit would be used to charge the new batteries. • The contractor proceeded to closed the DC disconnect attempting to charge the batteries with the Barrington unit while also still connected to the DC distribution box. o The substation battery charger was still isolated from the DC disconnect box. • When the foreman closed the DC disconnect the Barrington unit failed. o The DC disconnect was opened and the Barrington DC power supply unit was disconnected from the DC distribution box. • The foreman contacted his office and informed them of the situation. He was told to get the substation charger back in service to charge the batteries. • The contractor crew then reconnected the substation battery charger and closed the DC disconnect to charge the batteries while also supplying DC voltage to the DC distribution box. o The DC voltage of the batteries was checked, the batteries measured 74Vdc. • The contractor’s office contacted a sub-contractor and asked them to go to Sapulpa substation because they had a “loss of power.” He was informed that a new set of batteries were placed online and was asked to assess the situation and provide assistance to the contractor crew working on site. • The sub-contractor arrived on site and noticed the substation battery charger was powered up but was reading about 70Vdc on the DC volt meter. • The sub-contractor went to check the battery voltage at the batteries, as he entered the battery room he noticed that there were only 36 cells installed, that 24 cells were missing in the newly installed battery bank. o He also noticed the batteries were bubbling excessively, as if they were “boiling”. o He asked the contractor foreman if he knew this was a 120Vdc system. The foreman said he did but thought the voltage was low because the batteries needed to be charged. • The sub-contractor contacted his supervisor who contacted the OGE Protection and Control Substation Engineer and apprised him of the situation. It was determined the batteries needed to be taken off line due to the potential hazards being created from the overcharging of the partial set of batteries. o Hydrogen gasses were being produced inside the batteries due to the chemical reactions taking place due to the overcharging of the partial set of batteries. • The OGE Protection and Control Substation Engineer had a discussion with the TCC Manger and it was determined the substation needed to be cleared until the DC system could be placed back into a normal operating state because currently there was inadequate DC current capacity available to permit the proper tripping of protection equipment if a fault condition occurred. • Switching was written by TCC and DCC operators and switching was conducted by OGE members to transfer residential load in the field and shed the load from the Glass factory. o While performing this switching it was discovered that the trip coil on PCB 81 was burnt and not operational. This was found when the crew went to manually open the breaker during switching. • The Contractor Project Manager returned with the old batteries which were reinstalled to provide the necessary dc voltage and current to allow proper equipment operation in the event of a fault. • The OGE relay technician connected an external ac power supply to the substation battery charger to allow the reinstalled batteries to be charged. o The charger was placed on equalize for approximately 35 minutes, the battery voltage was then checked to ensure that the dc system was in proper operating condition. • Switching to restore load back onto the substation was started once the dc system was determined to be operating in a normal state. o PCB 81 was left out of service until the burnt trip coil could be replaced. |  |  |  | Muskogee Service Center | FALSE |  | FALSE | PD Operations Services |  | James Hutchison | Jeffrey Uhls |  | James Hutchison | I have reviewed this report and support the findings reported. I also support and have already covered the battery installation process and contractor to be used to perform this type of work. | James Hutchison |  | Medium |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.11 Inadequate matching of individual qualifications and job/task requirements | [7 empty] | Causal Factors: • During installation the contractor performing the work installed only 12 of the 20 batteries; 36 cells of the 60 cells required for a 125Vdc battery bank. As a result the DC voltage and current capacity was insufficient to provide proper tripping capability to the substation protection equipment if a fault condition occurred. o This condition resulted in the necessity to clear the load from the substation to protect the equipment and the members working in the substation until the DC system could be placed back to a proper operating condition. | 17. Failure to Identify Hazard, Risk | 9. Abnormal Operation |  | approved cm |  |  |  | System Outage |  | John Burns | [5 empty] | 12. Equipment Failure | James Hutchison | OESCO | Neil Mitchell |  |  |  | Jeffrey Uhls
8697 | Muskogee Service Center | 2019-01-31 | On Wednesday 1/30/2019, at Sapulpa substation the 125 dc volt battery set was replaced due to age and deterioration by a contractor. On Thursday, 1/31/2019 the entire customer load at the substation had to be transferred when it was determined that an insufficient number of replacement batteries were installed which resulted in an inadequate DC voltage supply to permit the proper possible operation of the protective relays. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Delivery | John Burns | 2019-08-02 07:23 | 2019-02-04 09:26 | 2019-02-04 09:26 | 2019-07-26 08:12 | 2019-02-14 | 2019-02-01 09:11 | 2019-08-02 07:03 |  | 2019-08-01 14:08 | Sapulpa Substation |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | TRUE | FALSE | Jeffrey Uhls |  | Operational Incident Summary On Thursday, 1/31/2019 the entire customer load at Sapulpa substation had to be transferred or dropped when it was determined that an insufficient number of replacement batteries were installed. This resulted in an inadequate DC voltage and current capacity supply to permit the proper possible operation of protective equipment within the substation if a fault condition occurred. During the week the 125Vdc battery bank at the substation was being replaced due to age and deterioration by a contractor. Twelve batteries; totaling thirty-six cells were installed by the contractor and placed in service with a measured voltage of 74Vdc. Chain of Events: • In September 2018 a single pallet containing 12 battery jars and its associated hardware were picked up from the Anixter warehouse located at the General Service Center by a contractor and taken to their shop for storage until the job could be worked. Monday 1/28/2019 • A two man contractor crew picked up the prints for the job, then loaded material and equipment from their shop in Oklahoma City for the battery replacement job and traveled to Sapulpa substation to being work. o The contractor foreman was informed by his supervisor that an OGE crew would come to the substation and connect the Barrington DC power supply unit to the substation DC distribution box. o Upon arrival at the substation, the contractor crew unloaded the batteries and material from the truck; they then started to assemble the battery rack in the control room.  There were no instructions for assembling the rack so the crew went to another substation to view an assembled rack, but they did not find a similar rack at the other substation so they returned to Sapulpa substation and resumed working on assembling the rack. • An OGE Muskogee substation relay crew was contacted and asked to go to Sapulpa substation and connect the Barrington DC power supply unit for the contractors. o When the crew arrived, they connected the Barrington DC power supply unit to the buss bar of the substation DC distribution box.  The substation battery charger ac and dc breakers were turned off and the cables to the disconnect box were lifted when the Barrington device was connected and turned on. • The cables between the battery charger and the battery disconnect box were lifted at both ends by the crew to isolate the charger from the DC system while the Barrington was connected. • The contractor continued to work on assembling the battery rack inside the control room for the remainder of the day. Tuesday 1/29/2019 • The Contractor Project Manager arrives on site and helps with the assembly of the battery rack. o He brought some additional missing parts for the battery rack. • After completing the assembly of the new battery rack the contractor crew disconnected and removed the old batteries and rack from the battery room in preparation for the installation of the new batteries and rack. o The new rack was moved into the battery room from the control room once the old batteries and rack were disassembled and removed. o The old batteries were placed on a pallet to be taken away for disposal. o The old #2 cables from the DC disconnect box located in the control house to the battery rack in the battery room were removed. • The contractor crew placed the new batteries on the rack, placing 6 batteries on the top tier of the rack and 6 batteries on the bottom tier. o The contractor apprenticed asked why there were only 12 batteries being installed when there were 20 batteries being removed.  An assumption was made that because the new batteries were larger in physical size that not as many batteries were necessary for the installation. • The contractor crew started connecting the battery jars together in series using the cable straps provided for the installation. Wednesday 1/30/2019 • The contractor crew completed the connections of the cable straps for the new batteries. o The DC voltage measurement taken at this time was 74Vdc. o The Barrington DC power supply was still connected to DC distribution box with DC disconnect in the open position. • That afternoon the contractor crew transported the old batteries to Oklahoma City for disposal. Thursday 1/31/2019 • The contractor crew pulled in new #2 cables between the batteries in the battery room and the DC disconnect box in the control room. • After completing the installation of the batteries and new cables the contractor foreman informed the contractor project manager that he measured 74Vdc on the new batteries and asked if they needed to be charged before placing them online. o The foreman was told by the project manager to put them on charge and he would have OGE personnel come out and check everything. o An assumption by the foreman was made that the Barrington unit would be used to charge the new batteries. • The contractor proceeded to closed the DC disconnect attempting to charge the batteries with the Barrington unit while also still connected to the DC distribution box. o The substation battery charger was still isolated from the DC disconnect box. • When the foreman closed the DC disconnect the Barrington unit failed. o The DC disconnect was opened and the Barrington DC power supply unit was disconnected from the DC distribution box. • The foreman contacted his office and informed them of the situation. He was told to get the substation charger back in service to charge the batteries. • The contractor crew then reconnected the substation battery charger and closed the DC disconnect to charge the batteries while also supplying DC voltage to the DC distribution box. o The DC voltage of the batteries was checked, the batteries measured 74Vdc. • The contractor’s office contacted a sub-contractor and asked them to go to Sapulpa substation because they had a “loss of power.” He was informed that a new set of batteries were placed online and was asked to assess the situation and provide assistance to the contractor crew working on site. • The sub-contractor arrived on site and noticed the substation battery charger was powered up but was reading about 70Vdc on the DC volt meter. • The sub-contractor went to check the battery voltage at the batteries, as he entered the battery room he noticed that there were only 36 cells installed, that 24 cells were missing in the newly installed battery bank. o He also noticed the batteries were bubbling excessively, as if they were “boiling”. o He asked the contractor foreman if he knew this was a 120Vdc system. The foreman said he did but thought the voltage was low because the batteries needed to be charged. • The sub-contractor contacted his supervisor who contacted the OGE Protection and Control Substation Engineer and apprised him of the situation. It was determined the batteries needed to be taken off line due to the potential hazards being created from the overcharging of the partial set of batteries. o Hydrogen gasses were being produced inside the batteries due to the chemical reactions taking place due to the overcharging of the partial set of batteries. • The OGE Protection and Control Substation Engineer had a discussion with the TCC Manger and it was determined the substation needed to be cleared until the DC system could be placed back into a normal operating state because currently there was inadequate DC current capacity available to permit the proper tripping of protection equipment if a fault condition occurred. • Switching was written by TCC and DCC operators and switching was conducted by OGE members to transfer residential load in the field and shed the load from the Glass factory. o While performing this switching it was discovered that the trip coil on PCB 81 was burnt and not operational. This was found when the crew went to manually open the breaker during switching. • The Contractor Project Manager returned with the old batteries which were reinstalled to provide the necessary dc voltage and current to allow proper equipment operation in the event of a fault. • The OGE relay technician connected an external ac power supply to the substation battery charger to allow the reinstalled batteries to be charged. o The charger was placed on equalize for approximately 35 minutes, the battery voltage was then checked to ensure that the dc system was in proper operating condition. • Switching to restore load back onto the substation was started once the dc system was determined to be operating in a normal state. o PCB 81 was left out of service until the burnt trip coil could be replaced. |  |  |  | Muskogee Service Center | FALSE |  | FALSE | PD Operations Services |  | James Hutchison | Jeffrey Uhls |  | James Hutchison | I have reviewed this report and support the findings reported. I also support and have already covered the battery installation process and contractor to be used to perform this type of work. | James Hutchison |  | Medium |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.11 Inadequate matching of individual qualifications and job/task requirements | [7 empty] | Causal Factors: • During installation the contractor performing the work installed only 12 of the 20 batteries; 36 cells of the 60 cells required for a 125Vdc battery bank. As a result the DC voltage and current capacity was insufficient to provide proper tripping capability to the substation protection equipment if a fault condition occurred. o This condition resulted in the necessity to clear the load from the substation to protect the equipment and the members working in the substation until the DC system could be placed back to a proper operating condition. | 17. Failure to Identify Hazard, Risk | 9. Abnormal Operation |  | approved cm |  |  |  | System Outage |  | John Burns | [5 empty] | 12. Equipment Failure | James Hutchison | OESCO | Neil Mitchell |  |  |  | Jeffrey Uhls
8697 | Muskogee Service Center | 2019-01-31 | On Wednesday 1/30/2019, at Sapulpa substation the 125 dc volt battery set was replaced due to age and deterioration by a contractor. On Thursday, 1/31/2019 the entire customer load at the substation had to be transferred when it was determined that an insufficient number of replacement batteries were installed which resulted in an inadequate DC voltage supply to permit the proper possible operation of the protective relays. | Level 2 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | John Burns | 2019-08-02 07:23 | 2019-02-04 09:26 | 2019-02-04 09:26 | 2019-07-26 08:12 | 2019-02-14 | 2019-02-01 09:11 | 2019-08-02 07:03 |  | 2019-08-01 14:08 | Sapulpa Substation |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | System Operational Incident |  | TRUE | FALSE | FALSE |  | TRUE | FALSE | Jeffrey Uhls |  | Operational Incident Summary On Thursday, 1/31/2019 the entire customer load at Sapulpa substation had to be transferred or dropped when it was determined that an insufficient number of replacement batteries were installed. This resulted in an inadequate DC voltage and current capacity supply to permit the proper possible operation of protective equipment within the substation if a fault condition occurred. During the week the 125Vdc battery bank at the substation was being replaced due to age and deterioration by a contractor. Twelve batteries; totaling thirty-six cells were installed by the contractor and placed in service with a measured voltage of 74Vdc. Chain of Events: • In September 2018 a single pallet containing 12 battery jars and its associated hardware were picked up from the Anixter warehouse located at the General Service Center by a contractor and taken to their shop for storage until the job could be worked. Monday 1/28/2019 • A two man contractor crew picked up the prints for the job, then loaded material and equipment from their shop in Oklahoma City for the battery replacement job and traveled to Sapulpa substation to being work. o The contractor foreman was informed by his supervisor that an OGE crew would come to the substation and connect the Barrington DC power supply unit to the substation DC distribution box. o Upon arrival at the substation, the contractor crew unloaded the batteries and material from the truck; they then started to assemble the battery rack in the control room.  There were no instructions for assembling the rack so the crew went to another substation to view an assembled rack, but they did not find a similar rack at the other substation so they returned to Sapulpa substation and resumed working on assembling the rack. • An OGE Muskogee substation relay crew was contacted and asked to go to Sapulpa substation and connect the Barrington DC power supply unit for the contractors. o When the crew arrived, they connected the Barrington DC power supply unit to the buss bar of the substation DC distribution box.  The substation battery charger ac and dc breakers were turned off and the cables to the disconnect box were lifted when the Barrington device was connected and turned on. • The cables between the battery charger and the battery disconnect box were lifted at both ends by the crew to isolate the charger from the DC system while the Barrington was connected. • The contractor continued to work on assembling the battery rack inside the control room for the remainder of the day. Tuesday 1/29/2019 • The Contractor Project Manager arrives on site and helps with the assembly of the battery rack. o He brought some additional missing parts for the battery rack. • After completing the assembly of the new battery rack the contractor crew disconnected and removed the old batteries and rack from the battery room in preparation for the installation of the new batteries and rack. o The new rack was moved into the battery room from the control room once the old batteries and rack were disassembled and removed. o The old batteries were placed on a pallet to be taken away for disposal. o The old #2 cables from the DC disconnect box located in the control house to the battery rack in the battery room were removed. • The contractor crew placed the new batteries on the rack, placing 6 batteries on the top tier of the rack and 6 batteries on the bottom tier. o The contractor apprenticed asked why there were only 12 batteries being installed when there were 20 batteries being removed.  An assumption was made that because the new batteries were larger in physical size that not as many batteries were necessary for the installation. • The contractor crew started connecting the battery jars together in series using the cable straps provided for the installation. Wednesday 1/30/2019 • The contractor crew completed the connections of the cable straps for the new batteries. o The DC voltage measurement taken at this time was 74Vdc. o The Barrington DC power supply was still connected to DC distribution box with DC disconnect in the open position. • That afternoon the contractor crew transported the old batteries to Oklahoma City for disposal. Thursday 1/31/2019 • The contractor crew pulled in new #2 cables between the batteries in the battery room and the DC disconnect box in the control room. • After completing the installation of the batteries and new cables the contractor foreman informed the contractor project manager that he measured 74Vdc on the new batteries and asked if they needed to be charged before placing them online. o The foreman was told by the project manager to put them on charge and he would have OGE personnel come out and check everything. o An assumption by the foreman was made that the Barrington unit would be used to charge the new batteries. • The contractor proceeded to closed the DC disconnect attempting to charge the batteries with the Barrington unit while also still connected to the DC distribution box. o The substation battery charger was still isolated from the DC disconnect box. • When the foreman closed the DC disconnect the Barrington unit failed. o The DC disconnect was opened and the Barrington DC power supply unit was disconnected from the DC distribution box. • The foreman contacted his office and informed them of the situation. He was told to get the substation charger back in service to charge the batteries. • The contractor crew then reconnected the substation battery charger and closed the DC disconnect to charge the batteries while also supplying DC voltage to the DC distribution box. o The DC voltage of the batteries was checked, the batteries measured 74Vdc. • The contractor’s office contacted a sub-contractor and asked them to go to Sapulpa substation because they had a “loss of power.” He was informed that a new set of batteries were placed online and was asked to assess the situation and provide assistance to the contractor crew working on site. • The sub-contractor arrived on site and noticed the substation battery charger was powered up but was reading about 70Vdc on the DC volt meter. • The sub-contractor went to check the battery voltage at the batteries, as he entered the battery room he noticed that there were only 36 cells installed, that 24 cells were missing in the newly installed battery bank. o He also noticed the batteries were bubbling excessively, as if they were “boiling”. o He asked the contractor foreman if he knew this was a 120Vdc system. The foreman said he did but thought the voltage was low because the batteries needed to be charged. • The sub-contractor contacted his supervisor who contacted the OGE Protection and Control Substation Engineer and apprised him of the situation. It was determined the batteries needed to be taken off line due to the potential hazards being created from the overcharging of the partial set of batteries. o Hydrogen gasses were being produced inside the batteries due to the chemical reactions taking place due to the overcharging of the partial set of batteries. • The OGE Protection and Control Substation Engineer had a discussion with the TCC Manger and it was determined the substation needed to be cleared until the DC system could be placed back into a normal operating state because currently there was inadequate DC current capacity available to permit the proper tripping of protection equipment if a fault condition occurred. • Switching was written by TCC and DCC operators and switching was conducted by OGE members to transfer residential load in the field and shed the load from the Glass factory. o While performing this switching it was discovered that the trip coil on PCB 81 was burnt and not operational. This was found when the crew went to manually open the breaker during switching. • The Contractor Project Manager returned with the old batteries which were reinstalled to provide the necessary dc voltage and current to allow proper equipment operation in the event of a fault. • The OGE relay technician connected an external ac power supply to the substation battery charger to allow the reinstalled batteries to be charged. o The charger was placed on equalize for approximately 35 minutes, the battery voltage was then checked to ensure that the dc system was in proper operating condition. • Switching to restore load back onto the substation was started once the dc system was determined to be operating in a normal state. o PCB 81 was left out of service until the burnt trip coil could be replaced. |  |  |  | Muskogee Service Center | FALSE |  | FALSE | PD Operations Services |  | James Hutchison | Jeffrey Uhls |  | James Hutchison | I have reviewed this report and support the findings reported. I also support and have already covered the battery installation process and contractor to be used to perform this type of work. | James Hutchison |  | Medium |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.11 Inadequate matching of individual qualifications and job/task requirements | [7 empty] | Causal Factors: • During installation the contractor performing the work installed only 12 of the 20 batteries; 36 cells of the 60 cells required for a 125Vdc battery bank. As a result the DC voltage and current capacity was insufficient to provide proper tripping capability to the substation protection equipment if a fault condition occurred. o This condition resulted in the necessity to clear the load from the substation to protect the equipment and the members working in the substation until the DC system could be placed back to a proper operating condition. | 17. Failure to Identify Hazard, Risk | 9. Abnormal Operation |  | approved cm |  |  |  | System Outage |  | John Burns | [5 empty] | 12. Equipment Failure | James Hutchison | OESCO | Neil Mitchell |  |  |  | Jeffrey Uhls
8697 | Muskogee Service Center | 2019-01-31 | On Wednesday 1/30/2019, at Sapulpa substation the 125 dc volt battery set was replaced due to age and deterioration by a contractor. On Thursday, 1/31/2019 the entire customer load at the substation had to be transferred when it was determined that an insufficient number of replacement batteries were installed which resulted in an inadequate DC voltage supply to permit the proper possible operation of the protective relays. | Level 2 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | John Burns | 2019-08-02 07:23 | 2019-02-04 09:26 | 2019-02-04 09:26 | 2019-07-26 08:12 | 2019-02-14 | 2019-02-01 09:11 | 2019-08-02 07:03 |  | 2019-08-01 14:08 | Sapulpa Substation |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | System Operational Incident |  | TRUE | FALSE | FALSE |  | TRUE | FALSE | Jeffrey Uhls |  | Operational Incident Summary On Thursday, 1/31/2019 the entire customer load at Sapulpa substation had to be transferred or dropped when it was determined that an insufficient number of replacement batteries were installed. This resulted in an inadequate DC voltage and current capacity supply to permit the proper possible operation of protective equipment within the substation if a fault condition occurred. During the week the 125Vdc battery bank at the substation was being replaced due to age and deterioration by a contractor. Twelve batteries; totaling thirty-six cells were installed by the contractor and placed in service with a measured voltage of 74Vdc. Chain of Events: • In September 2018 a single pallet containing 12 battery jars and its associated hardware were picked up from the Anixter warehouse located at the General Service Center by a contractor and taken to their shop for storage until the job could be worked. Monday 1/28/2019 • A two man contractor crew picked up the prints for the job, then loaded material and equipment from their shop in Oklahoma City for the battery replacement job and traveled to Sapulpa substation to being work. o The contractor foreman was informed by his supervisor that an OGE crew would come to the substation and connect the Barrington DC power supply unit to the substation DC distribution box. o Upon arrival at the substation, the contractor crew unloaded the batteries and material from the truck; they then started to assemble the battery rack in the control room.  There were no instructions for assembling the rack so the crew went to another substation to view an assembled rack, but they did not find a similar rack at the other substation so they returned to Sapulpa substation and resumed working on assembling the rack. • An OGE Muskogee substation relay crew was contacted and asked to go to Sapulpa substation and connect the Barrington DC power supply unit for the contractors. o When the crew arrived, they connected the Barrington DC power supply unit to the buss bar of the substation DC distribution box.  The substation battery charger ac and dc breakers were turned off and the cables to the disconnect box were lifted when the Barrington device was connected and turned on. • The cables between the battery charger and the battery disconnect box were lifted at both ends by the crew to isolate the charger from the DC system while the Barrington was connected. • The contractor continued to work on assembling the battery rack inside the control room for the remainder of the day. Tuesday 1/29/2019 • The Contractor Project Manager arrives on site and helps with the assembly of the battery rack. o He brought some additional missing parts for the battery rack. • After completing the assembly of the new battery rack the contractor crew disconnected and removed the old batteries and rack from the battery room in preparation for the installation of the new batteries and rack. o The new rack was moved into the battery room from the control room once the old batteries and rack were disassembled and removed. o The old batteries were placed on a pallet to be taken away for disposal. o The old #2 cables from the DC disconnect box located in the control house to the battery rack in the battery room were removed. • The contractor crew placed the new batteries on the rack, placing 6 batteries on the top tier of the rack and 6 batteries on the bottom tier. o The contractor apprenticed asked why there were only 12 batteries being installed when there were 20 batteries being removed.  An assumption was made that because the new batteries were larger in physical size that not as many batteries were necessary for the installation. • The contractor crew started connecting the battery jars together in series using the cable straps provided for the installation. Wednesday 1/30/2019 • The contractor crew completed the connections of the cable straps for the new batteries. o The DC voltage measurement taken at this time was 74Vdc. o The Barrington DC power supply was still connected to DC distribution box with DC disconnect in the open position. • That afternoon the contractor crew transported the old batteries to Oklahoma City for disposal. Thursday 1/31/2019 • The contractor crew pulled in new #2 cables between the batteries in the battery room and the DC disconnect box in the control room. • After completing the installation of the batteries and new cables the contractor foreman informed the contractor project manager that he measured 74Vdc on the new batteries and asked if they needed to be charged before placing them online. o The foreman was told by the project manager to put them on charge and he would have OGE personnel come out and check everything. o An assumption by the foreman was made that the Barrington unit would be used to charge the new batteries. • The contractor proceeded to closed the DC disconnect attempting to charge the batteries with the Barrington unit while also still connected to the DC distribution box. o The substation battery charger was still isolated from the DC disconnect box. • When the foreman closed the DC disconnect the Barrington unit failed. o The DC disconnect was opened and the Barrington DC power supply unit was disconnected from the DC distribution box. • The foreman contacted his office and informed them of the situation. He was told to get the substation charger back in service to charge the batteries. • The contractor crew then reconnected the substation battery charger and closed the DC disconnect to charge the batteries while also supplying DC voltage to the DC distribution box. o The DC voltage of the batteries was checked, the batteries measured 74Vdc. • The contractor’s office contacted a sub-contractor and asked them to go to Sapulpa substation because they had a “loss of power.” He was informed that a new set of batteries were placed online and was asked to assess the situation and provide assistance to the contractor crew working on site. • The sub-contractor arrived on site and noticed the substation battery charger was powered up but was reading about 70Vdc on the DC volt meter. • The sub-contractor went to check the battery voltage at the batteries, as he entered the battery room he noticed that there were only 36 cells installed, that 24 cells were missing in the newly installed battery bank. o He also noticed the batteries were bubbling excessively, as if they were “boiling”. o He asked the contractor foreman if he knew this was a 120Vdc system. The foreman said he did but thought the voltage was low because the batteries needed to be charged. • The sub-contractor contacted his supervisor who contacted the OGE Protection and Control Substation Engineer and apprised him of the situation. It was determined the batteries needed to be taken off line due to the potential hazards being created from the overcharging of the partial set of batteries. o Hydrogen gasses were being produced inside the batteries due to the chemical reactions taking place due to the overcharging of the partial set of batteries. • The OGE Protection and Control Substation Engineer had a discussion with the TCC Manger and it was determined the substation needed to be cleared until the DC system could be placed back into a normal operating state because currently there was inadequate DC current capacity available to permit the proper tripping of protection equipment if a fault condition occurred. • Switching was written by TCC and DCC operators and switching was conducted by OGE members to transfer residential load in the field and shed the load from the Glass factory. o While performing this switching it was discovered that the trip coil on PCB 81 was burnt and not operational. This was found when the crew went to manually open the breaker during switching. • The Contractor Project Manager returned with the old batteries which were reinstalled to provide the necessary dc voltage and current to allow proper equipment operation in the event of a fault. • The OGE relay technician connected an external ac power supply to the substation battery charger to allow the reinstalled batteries to be charged. o The charger was placed on equalize for approximately 35 minutes, the battery voltage was then checked to ensure that the dc system was in proper operating condition. • Switching to restore load back onto the substation was started once the dc system was determined to be operating in a normal state. o PCB 81 was left out of service until the burnt trip coil could be replaced. |  |  |  | Muskogee Service Center | FALSE |  | FALSE | PD Operations Services |  | James Hutchison | Jeffrey Uhls |  | James Hutchison | I have reviewed this report and support the findings reported. I also support and have already covered the battery installation process and contractor to be used to perform this type of work. | James Hutchison |  | Medium |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.11 Inadequate matching of individual qualifications and job/task requirements | [7 empty] | Causal Factors: • During installation the contractor performing the work installed only 12 of the 20 batteries; 36 cells of the 60 cells required for a 125Vdc battery bank. As a result the DC voltage and current capacity was insufficient to provide proper tripping capability to the substation protection equipment if a fault condition occurred. o This condition resulted in the necessity to clear the load from the substation to protect the equipment and the members working in the substation until the DC system could be placed back to a proper operating condition. | 17. Failure to Identify Hazard, Risk | 9. Abnormal Operation |  | approved cm |  |  |  | System Outage |  | John Burns | [5 empty] | 12. Equipment Failure | James Hutchison | OESCO | Neil Mitchell |  |  |  | Jeffrey Uhls
8698 | Corporate Headquarters Bldg | 2019-01-23 | Member reported discomfort in shoulder related to stamping invoices continuously. | Level 2 |  | FALSE | Member Injury |  |  |  |  | OGE Energy Corp | Melissa Smith | 2019-02-22 15:14 | 2019-02-04 09:53 | 2019-02-04 09:53 | 2019-02-04 10:38 | 2019-02-06 | 2019-01-23 10:00 | 2019-02-04 14:44 |  | 2019-02-04 11:06 | 8th floor CHQ |  |  | William Young | Reviewed and approved. WCY 2/22/19 | Enterprise Services |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Melissa Smith |  | Member's daily responsibility is to handle all incoming mail for the accounts payable department and date stamp each document. The complaint is that the repetitious stamping (approx. 350 documents per day) is causing some discomfort/pain in member's right shoulder. Stamping is a manual pushing down of a handheld ink pad stamper. To reduce amount of stamping, supervisor changed out the stamper being used. The change was from a long necked metal stamper (weighing 7.1oz) to a shorter necked plastic stamper (weighing 6.3oz) that required less pressure and is lighter weight. Also, supervisor instructed member to electronically stamp all electronically received mail (by email) to reduce by 2/3'rds the amount of manual stamping occurring. |  |  | FALSE | Corporate Headquarters Bldg | FALSE |  | FALSE | Other |  | Bernice Mills | Melissa Smith |  | Sherry Ryan | Should we look at rotating her duties within a day so that the stamping process is broken into smaller segments of time? | Sherry Ryan |  | Medium | [12 empty] | 13.02 Inadequate human factors/ergonomics considerations |  |  |  | Member reported discomfort in shoulder related to stamping invoices continuously. | 06. Using Defective Equipment | 11. Overstress, Overpressure, Overexertion, Ergonomic |  | Approved, Cody Vinyard | [24 empty] | FALSE |  |  | 2017-10-09 | 1961-06-30 |  | 2019-01-23 07:00 | 0 | 0 |  | FALSE | Female | Repetitive stamping of mail. |  | FALSE | Bernice Mills |  | First Aid | Bernice Mills | FALSE |  | McBride Orthopedic Hospital | Dr Rande lEstep | Sprain/Strain |  | FALSE |  | Accts Payable Clerk | Shoulder |  | Right | FALSE | Melissa Smith | FALSE |  | 1/23/2019 7:00:00 AM | approx 2 years | TRUE | FALSE | FALSE | repetitive movement | Member was doing daily routines which involves stamping mail as it arrives. | [24 empty] | .
8699 | Seminole PP; EGX Gath/Trans | 2019-02-02 17:00 | Contractor was working in the area of the instrument air valve when they reported that the valve blew off of the line. No injuries. | Level 1 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Paul Schoelen | 2019-02-21 15:13 | 2019-02-04 13:34 | 2019-02-04 13:34 | 2019-02-06 13:36 | 2019-02-16 17:00 | 2019-02-02 17:00 | 2019-02-11 11:51 |  |  | SMPP turbine floor at 2EA FWH |  |  | Chrysty Dorsey | Approved. | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Paul Schoelen |  | Scaffold crew was working in the area of 2EA feedwater heater staging material and heard an air release. They noticed a 1/2" valve had broken off of an instrument air line. Scaffold crew notified the control room and operations isolated the air line. Maintenance replaced the valve. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | TRUE | Operations |  | Jeffrey Misenheimer | Paul Schoelen |  | Scott Lee | I approve this incident report. | Scott Lee |  | Low | [14 empty] | 15.02 Improper extension of service life |  | Valve blew off air line. Solder joint appeared fatigued. | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure | [92 empty] | 9576978
8700 | Ada Service Center | 2019-02-01 17:30 | Member was using load break tool to open a fixed cap. station. He opened without an issue. Went to open next one and the load break tool did not function as designed and an arc occurred. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Delivery | Lyle Just | 2019-03-02 15:35 | 2019-02-05 07:21 | 2019-02-05 07:21 | 2019-02-18 10:57 | 2019-02-15 17:30 | 2019-02-05 07:07 | 2019-02-21 14:17 |  |  | Harden City Oil field. |  |  | Terry Hackett | Reviewed/Approved. Corrective action for member to share lessons learned and recommend/implement a mitigation control added per manager's request. | T&D Ops |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Lyle Just |  | Member was using load break tool to open a fixed cap. station. He opened without an issue. Went to open next one and the load break tool did not function as designed and an arc occurred. Load break is going to system lab to be looked at. The system lab found the Load break tool was unable to be fixed and was taken out of service. |  |  |  | Ada Service Center | FALSE |  | TRUE | Construction Services |  | Cameron Brady | Lyle Just |  | Chad Inman | I asked to have a Maintenance Schedule created and placed within the Live Line Tool SOP. Reviewed and Approved. | Chad Inman |  | Low | [14 empty] | 15.04 Improper loading or rate of use |  | Load break experienced an internal failure | 23. Defective Tools, Equipment or Materials | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [92 empty] | N/A
8700 | Ada Service Center | 2019-02-01 17:30 | Member was using load break tool to open a fixed cap. station. He opened without an issue. Went to open next one and the load break tool did not function as designed and an arc occurred. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Delivery | Lyle Just | 2019-03-02 15:35 | 2019-02-05 07:21 | 2019-02-05 07:21 | 2019-02-18 10:57 | 2019-02-15 17:30 | 2019-02-05 07:07 | 2019-02-21 14:17 |  |  | Harden City Oil field. |  |  | Terry Hackett | Reviewed/Approved. Corrective action for member to share lessons learned and recommend/implement a mitigation control added per manager's request. | T&D Ops |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Lyle Just |  | Member was using load break tool to open a fixed cap. station. He opened without an issue. Went to open next one and the load break tool did not function as designed and an arc occurred. Load break is going to system lab to be looked at. The system lab found the Load break tool was unable to be fixed and was taken out of service. |  |  |  | Ada Service Center | FALSE |  | TRUE | Construction Services |  | Cameron Brady | Lyle Just |  | Chad Inman | I asked to have a Maintenance Schedule created and placed within the Live Line Tool SOP. Reviewed and Approved. | Chad Inman |  | Low | [14 empty] | 15.05 Inadequate maintenance |  | Load break experienced an internal failure | 23. Defective Tools, Equipment or Materials | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [92 empty] | N/A
8701 | Shawnee Service Center | 2019-02-05 06:30 | Traveling north in route to Sooner Station when a deer came from the side of the road, entered the road way and was struck by the OGE vehicle. | Level 2 |  | FALSE | Vehicle |  |  |  |  | OG&E Corp Services | Ronald Madron | 2019-05-24 15:04 | 2019-02-06 09:09 | 2019-02-06 09:09 | 2019-02-20 16:28 | 2019-02-19 06:30 | 2019-02-06 08:12 | 2019-05-23 10:38 |  | 2019-02-21 12:35 | An OGE vehicle was traveling North on Highway 377, approximately 5 miles north of Prague a deer came from the side of the road, entered the road way and was struck by the OGE vehicle. |  |  | William Young | Reviewed and approved. WCY 5-24-19 | UTS |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Ronald Madron |  | An OGE vehicle was traveling North on Highway 377, approximately 5 miles north of Prague a deer came from the side of the road, entered the road way and was struck by the OGE vehicle. |  |  |  | Shawnee Service Center | FALSE |  | FALSE | UTS - Envir. & Process Chem |  | Ronald Madron | Ronald Madron |  | Thomas Leach | Reviewed by T. Leach | Thomas Leach |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Deer came from side and ran into vehicle | 39. Road Conditions | 2. Struck By (Hit By Moving Object) |  | Approved. J. Looney, 2/21/19 | [72 empty] | FALSE |  | Prague | Animal-related |  | 2016-09-25 19:00 |  | FALSE |  |  | Dawn |  |  | Asphalt |  | Cloudy |  |  | none
8702 | Enid Service Center | 2019-02-05 08:30 | Structure fell, 60' diverter structure fell in sub. No injury or equipment damage beside diverter pole. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Delivery | Dustin Kingcade | 2019-07-18 08:42 | 2019-02-06 14:07 | 2019-02-06 14:07 | 2019-02-28 09:09 | 2019-02-19 08:30 | 2019-02-06 13:53 | 2019-07-18 08:15 |  | 2019-03-01 09:59 | Enid Industrial Substation |  |  | Lindle Coleman | Process in place on vendor review of structure. This will drive the completion of this action item. Ok to close incident. | T&D Ops |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Dustin Kingcade |  | Structure fell, 60' diverter structure fell in sub. No injury or equipment damage beside diverter pole. Found that the welds on the diverter base failed to have proper penetration causing the structure to fall during high winds. manufacture of structure is performing QA investigation to find a root cause |  |  |  | Enid Service Center | FALSE |  | TRUE | PD Operations Services |  | Dustin Kingcade | Dustin Kingcade |  | Joseph Manseau | Vendor investigation is still not complete. Will update when report is returns. | Joseph Manseau |  | Medium | [9 empty] | 10.03 Inadequate standards, specifications and/or design criteria | [6 empty] | Found that the welds on the diverter base failed to have proper penetration causing the structure to fall during high winds. manufacture of structure is performing QA investigation to find a root cause. | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure |  | Wait on vendor to provide details from their investigation and open any follow up corrective actions if necessary | [90 empty] | 9090050
8703 | Sooner Power Plant | 2019-02-06 21:30 | On 2/6/2019 at 21:30, 1A flyash silo fluidizing blower caught on fire and burned the cable tray above it. No member injury. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Alexander Taybah | 2019-09-30 08:15 | 2019-02-07 01:33 | 2019-02-07 01:33 | 2019-09-10 15:32 | 2019-02-20 21:30 | 2019-02-07 00:40 | 2019-09-16 13:13 |  | 2019-09-12 07:59 | Sooner Power Plant; fly ash silo fluidizing blowers enclosure. |  |  | Jesse Murray | Approved- Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Alexander Taybah |  | on 2/6/19, a large group of ABB communication alarms related to ash systems came in on both units’ annunciators. Ash systems tripped on both units (unit 2 was in startup mode). After a brief discussion, AOs headed out in the field to investigate; the assumption was that rainwater had gotten into some electrical components related to ash systems in one of the fluidizing blower rooms. Operating Authority notified hot crew I&C tech and hot crew Electrician (both were already on standby for Unit 2 startup). After investigating, 2 AOs reported smoke coming from Unit 1’s fluidizing blower room, but all the doors appeared to be closed. Dispatch was notified and Unit 1 was derated to 200 NMW. Several more members headed to the silo area to help; an effort was made to open doors to allow smoke to ventilate. Due to extensive ice buildup on the grating, and the inability to easily access both east & west doors easily (unable to travel through blower room; had to go back to ground level and up a different set of stairs) it took a longer amount of time to get all available doors open. Upon opening the last door, a larger roll up style door on the east side of the room, it was discovered that 1A fluidizing blower and the electrical cables in the tray directly above it were on fire. Members immediately collected nearby fire extinguishers, and the OA directed the TG AO to locate the main and reserve 4.16kV breakers feeding all power to coalyard/silo areas; OA also notified coalyard members that electrical power to the coalyard area would possibly be cut. After assessing the condition of the area and fire, it was determined that fire was small, contained, and was well below the incipient stage as well as it did not involve any combustible dust. OA directed TG AO to open both main & reserve breakers to isolate all electrical power to silo area (by ABB alarms, this occurred at 2201), and OA and AOs proceeded to extinguish fire using class ABC dry chemical extinguishers. Fire was extinguished by multiple extinguishers (two to put out and eight more due to flare ups). Hot crew Tech & Electrician began assessing damage and working to see what power could be restored. At approximately 0100 on 2/7, various 480V and 120V breakers were opened to isolate power to individual components affected, and Main 4.16kV breaker was closed, restoring main electrical power to coalyard and silo areas. Communication was restored to both units’ ash systems, and coal conveying resumed. Hot crew Tech & Electrician had to leave site at 0200 to keep from exceeding consecutive work hours policy, and all activities related to Unit 2 startup were postponed until 0700. Unit 1 stayed derated at minimum load, as its ash systems could not be restarted until power was restored to at least 1 Flyash Vent Fan (1 vent fan was restarted at approximately 1930 on 2/7). |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Operations |  | Kellan Keeter | Alexander Taybah |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium | [11 empty] | 12.02.3 Inadequate reparative examination of units |  |  |  |  | Failure to follow OEM's inspection recommendation. | 18. Failure to Check, Monitor | 12. Equipment Failure |  | Approved on 9/12/2019 | [66 empty] | An RCA is being performed on this incident to figure out exactly what happened. Apparently 1A flyash silo fluidizing blower caught on fire damaging the cable tray above it and affecting other equipment. | 15000 | Blake Underwood | Fire | [20 empty] | 9581297
8703 | Sooner Power Plant | 2019-02-06 21:30 | On 2/6/2019 at 21:30, 1A flyash silo fluidizing blower caught on fire and burned the cable tray above it. No member injury. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Alexander Taybah | 2019-09-30 08:15 | 2019-02-07 01:33 | 2019-02-07 01:33 | 2019-09-10 15:32 | 2019-02-20 21:30 | 2019-02-07 00:40 | 2019-09-16 13:13 |  | 2019-09-12 07:59 | Sooner Power Plant; fly ash silo fluidizing blowers enclosure. |  |  | Jesse Murray | Approved- Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Alexander Taybah |  | on 2/6/19, a large group of ABB communication alarms related to ash systems came in on both units’ annunciators. Ash systems tripped on both units (unit 2 was in startup mode). After a brief discussion, AOs headed out in the field to investigate; the assumption was that rainwater had gotten into some electrical components related to ash systems in one of the fluidizing blower rooms. Operating Authority notified hot crew I&C tech and hot crew Electrician (both were already on standby for Unit 2 startup). After investigating, 2 AOs reported smoke coming from Unit 1’s fluidizing blower room, but all the doors appeared to be closed. Dispatch was notified and Unit 1 was derated to 200 NMW. Several more members headed to the silo area to help; an effort was made to open doors to allow smoke to ventilate. Due to extensive ice buildup on the grating, and the inability to easily access both east & west doors easily (unable to travel through blower room; had to go back to ground level and up a different set of stairs) it took a longer amount of time to get all available doors open. Upon opening the last door, a larger roll up style door on the east side of the room, it was discovered that 1A fluidizing blower and the electrical cables in the tray directly above it were on fire. Members immediately collected nearby fire extinguishers, and the OA directed the TG AO to locate the main and reserve 4.16kV breakers feeding all power to coalyard/silo areas; OA also notified coalyard members that electrical power to the coalyard area would possibly be cut. After assessing the condition of the area and fire, it was determined that fire was small, contained, and was well below the incipient stage as well as it did not involve any combustible dust. OA directed TG AO to open both main & reserve breakers to isolate all electrical power to silo area (by ABB alarms, this occurred at 2201), and OA and AOs proceeded to extinguish fire using class ABC dry chemical extinguishers. Fire was extinguished by multiple extinguishers (two to put out and eight more due to flare ups). Hot crew Tech & Electrician began assessing damage and working to see what power could be restored. At approximately 0100 on 2/7, various 480V and 120V breakers were opened to isolate power to individual components affected, and Main 4.16kV breaker was closed, restoring main electrical power to coalyard and silo areas. Communication was restored to both units’ ash systems, and coal conveying resumed. Hot crew Tech & Electrician had to leave site at 0200 to keep from exceeding consecutive work hours policy, and all activities related to Unit 2 startup were postponed until 0700. Unit 1 stayed derated at minimum load, as its ash systems could not be restarted until power was restored to at least 1 Flyash Vent Fan (1 vent fan was restarted at approximately 1930 on 2/7). |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Operations |  | Kellan Keeter | Alexander Taybah |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium | [13 empty] | 14.02.2 Inadequate communication of standards: distribution |  |  | Seal rings on rotor not sealing due to debris buildup. For details please refer to RCA #2326. | 34. Inadequate Instructions, Procedures | 12. Equipment Failure |  | Approved on 9/12/2019 | [66 empty] | An RCA is being performed on this incident to figure out exactly what happened. Apparently 1A flyash silo fluidizing blower caught on fire damaging the cable tray above it and affecting other equipment. | 15000 | Blake Underwood | Fire | [20 empty] | 9581297
8704 | Sooner Power Plant | 2019-02-07 10:00 | First Aid Only. Member fell on icy surface while returning from escorting semi driver out of Power Block gates. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Justin Buchanan | 2019-02-25 08:20 | 2019-02-07 11:49 | 2019-02-07 11:49 | 2019-02-07 12:30 | 2019-02-21 10:00 | 2019-02-07 11:24 | 2019-02-11 08:04 |  | 2019-02-07 14:22 | South of Sooner Unit 1 Crane Bay by Smoke Shack. |  |  | Jesse Murray | I Approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Justin Buchanan |  | Member was returning from letting the truck driver out of the power block gates South of Unit 1 Crane Bay when they slipped on the ice by the smoke shack and fell straight down. Member was travelling at an extremely slow pace due to cautions of ice and had very little forward momentum. Member fell straight down with no other forward movement. No further injuries are noted at this time and member explained that they have no pain or soreness at this time. Member was returning alone from opening and closing power block gates. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Francisco Aguilar | Justin Buchanan |  | Frank Brixey | Approve - Brixey - 2/11/2019 | Frank Brixey |  | Medium | [5 empty] | 6.02 Inadequate practice | [6 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | Member fell on icy surface when returning from letting semi truck out of South power block gates. Conditions were extremely slick and footing was hazardous. Member had recognized surface conditions but had not donned additional traction aids (Yaktrax) after loading journal and obtaining keys for gate access. Member did however slow pace when walking on ice to accommodate the hazardous conditions. | 19. Failure to React, Correct | 4. Fall on Same Level (Slip and Fall, Trip Over) |  | Approved by Brady Sowell on 2/7/2018 | [90 empty] | 759392
8705 | Horseshoe Lake Power Plant | 2019-02-08 09:00 | Member and contractor were measuring for scaffolding needed on upcoming job, contractor stepped on deteriorated tread plate cover for #7 screen wash strainer drain that goes below surface of floor. Tread plate gave way on corner and contractor caught himself without falling into drain trough. We replaced tread plate and member reported to plant leadership and wrote a notification for repair. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-03-13 13:17 | 2019-02-08 09:35 | 2019-02-08 09:35 | 2019-03-01 11:22 | 2019-02-22 09:00 | 2019-02-08 09:27 | 2019-03-11 16:46 |  | 2019-03-11 08:12 | Horseshoe Lake unit 7 crib house |  |  | Jesse Murray | `I Approve. Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | While measuring for upcoming scaffolding needs with contractor. Member witnessed contractor get off balance and both identified tread plate give way from deterioration. At the time of incident both member and contractor were measuring for needed scaffolding at head level and proper foot placement was not identified. Further investigation showed that additional tread plate has similar deterioration and needs to be addressed. This particular piece was only 4" x 12" and the weight of contractor pushed one corner up when his weight shifted to the plate and it crumbled the opposite corner. This tread plate was covering the screen wash drain piping that runs under floor in the #7 crib house. I believe this plate was originally galvanized coated but time and elements have rusted the material and made the plate unstable on the edges. Contractor did not fall but caught himself and stayed upright. Plate was identified as the tripping hazard and a notification was written and leadership onsite was briefed. Member reinstalled plate. Plant leadership installed a barricade until complete repair could be made. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Daniel Perry |  | Daniel Perry | I have reviewed this incident and I agree with the findings. | Daniel Perry |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [7 empty] | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.04 Improper loading or rate of use |  | Material had deteriorated over time and harsh environment. | 06. Using Defective Equipment | 12. Equipment Failure |  | Sent back for more information. |  |  |  | Property Damage |  | Kelly Casey | [5 empty] | 4. Fall on Same Level (Slip and Fall, Trip Over) | Kelly Casey | Brock | Julian Gonzalez |  |  |  | Kelly Casey | [71 empty] | 9581254
8705 | Horseshoe Lake Power Plant | 2019-02-08 09:00 | Member and contractor were measuring for scaffolding needed on upcoming job, contractor stepped on deteriorated tread plate cover for #7 screen wash strainer drain that goes below surface of floor. Tread plate gave way on corner and contractor caught himself without falling into drain trough. We replaced tread plate and member reported to plant leadership and wrote a notification for repair. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-03-13 13:17 | 2019-02-08 09:35 | 2019-02-08 09:35 | 2019-03-01 11:22 | 2019-02-22 09:00 | 2019-02-08 09:27 | 2019-03-11 16:46 |  | 2019-03-11 08:12 | Horseshoe Lake unit 7 crib house |  |  | Jesse Murray | `I Approve. Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | While measuring for upcoming scaffolding needs with contractor. Member witnessed contractor get off balance and both identified tread plate give way from deterioration. At the time of incident both member and contractor were measuring for needed scaffolding at head level and proper foot placement was not identified. Further investigation showed that additional tread plate has similar deterioration and needs to be addressed. This particular piece was only 4" x 12" and the weight of contractor pushed one corner up when his weight shifted to the plate and it crumbled the opposite corner. This tread plate was covering the screen wash drain piping that runs under floor in the #7 crib house. I believe this plate was originally galvanized coated but time and elements have rusted the material and made the plate unstable on the edges. Contractor did not fall but caught himself and stayed upright. Plate was identified as the tripping hazard and a notification was written and leadership onsite was briefed. Member reinstalled plate. Plant leadership installed a barricade until complete repair could be made. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Daniel Perry |  | Daniel Perry | I have reviewed this incident and I agree with the findings. | Daniel Perry |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [7 empty] | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life |  | Material had deteriorated over time and harsh environment. | 06. Using Defective Equipment | 12. Equipment Failure |  | Sent back for more information. |  |  |  | Property Damage |  | Kelly Casey | [5 empty] | 4. Fall on Same Level (Slip and Fall, Trip Over) | Kelly Casey | Brock | Julian Gonzalez |  |  |  | Kelly Casey | [71 empty] | 9581254
8706 | Sooner Power Plant | 2019-02-08 09:00 | Ice slide off roof and onto forklift cage. Contract member operating forklift was not injured. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Michael Dowell | 2019-03-08 13:46 | 2019-02-08 09:42 | 2019-02-08 12:49 | 2019-02-21 15:06 | 2019-02-22 09:00 | 2019-02-08 09:41 | 2019-02-26 12:57 |  | 2019-02-25 07:49 | Sooner Plant Unit #2 Mill Room Overhead Door |  |  | Jesse Murray | I Approve. Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Michael Dowell |  | While moving dumpster into mill room with forklift, ice fell from above and landed on the forklift cage. Cage prevented ice from hitting operator. Ice shattered when hitting fork lift, making it difficult to determine if it was an icicle or a sheet of ice. A SWP was in use, however the Falling Objects part of the form was checked NO. When Falling Objects are discussed, the discussion centers around dropping tools or equipment that are being worked on. Zachary's SWP (Daily Addendum) does not make mention of discussing weather conditions. Zachary recently updated their SWP and the Weather Hazard cell was left off. There is an area on the form that mentions high winds, this is an opportunity to discuss weather. Area was barricaded after incident until all ice on structure had melted. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Lance Lantz | Michael Dowell |  | Frank Brixey | Approved - Brixey | Frank Brixey |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Due to icy weather the plant structure had become coved with ice. As the outside temperatures began to rise, coupled with the sun shining on the structure, the ice began to melt and fall off the building. | 40. Weather Conditions | 2. Struck By (Hit By Moving Object) |  | Approved by Brady Sowell on 2/25/2019. |  |  |  | Injury / Illness |  | Michael Dowell | [5 empty] | 2. Struck By (Hit By Moving Object) | Lance Lantz | Zachry | Monty Brewer |  |  |  | Michael Dowell | [71 empty] | 615106
8707 | Muskogee Service Center | 2019-02-07 15:00 | Large bird flew into grill of truck while truck was traveling down hwy. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Brian McKinney | 2019-02-08 15:14 | 2019-02-08 10:55 | 2019-02-08 10:55 | 2019-02-08 12:28 | 2019-02-21 15:00 | 2019-02-08 10:46 |  |  |  | hwy 10 Braggs mountain |  |  | Hannah Everett | Approved. | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | [6 empty] | Muskogee Service Center | FALSE |  | FALSE | Construction Services |  | Gary Knupp | Brian McKinney |  |  |  | Michael Fox |  | Low | [87 empty] | front grill cracked | 441.26 | Dylan Rowan | Vehicle (not related to operation of vehicle) |  | F10-220 | FALSE |  | Braggs | Animal-related |  | 2016-01-17 18:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Cloudy |  |  | NA
8708 | West Service Center | 2019-02-08 10:30 | While member was backing his bucket truck, the front bumper struck a pole when turning during the backing process. The member was being directed by another member. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Joshua Robertson | 2019-02-20 14:39 | 2019-02-08 12:45 | 2019-02-08 12:45 | 2019-02-11 10:01 | 2019-02-22 10:30 | 2019-02-08 12:31 | 2019-02-12 07:16 |  |  | 17559 SW 44th Street |  |  | Brent Perdue | approved | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Joshua Robertson |  | While member was backing his bucket truck, the front left portion of the bumper struck a pole when turning during the backing process. The member was being directed by another member. Upon further investigation, it was determined that the two members did not properly position the truck before backing. The member driving did not maintain eye contact with the backer and did not see him attempting to stop the driver. |  |  |  | West Service Center | FALSE |  | FALSE | Construction Services |  | Casey Lee | Joshua Robertson |  | Terry Garrett | I approve | Terry Garrett |  | Low |  |  |  |  | 5.01 Lack of experience | [11 empty] | driver did not keep eye contact with backer. | 11. Improper Position for Task | 1. Struck Against (Running or Bumping Into) | [74 empty] | TRUE |  | Union City | Struck Fixed Object | Backing Related | 2018-07-01 19:00 |  | FALSE |  |  | Dawn |  |  | Dirt |  | Clear |  |  | N/A
8708 | West Service Center | 2019-02-08 10:30 | While member was backing his bucket truck, the front bumper struck a pole when turning during the backing process. The member was being directed by another member. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Joshua Robertson | 2019-02-20 14:39 | 2019-02-08 12:45 | 2019-02-08 12:45 | 2019-02-11 10:01 | 2019-02-22 10:30 | 2019-02-08 12:31 | 2019-02-12 07:16 |  |  | 17559 SW 44th Street |  |  | Brent Perdue | approved | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Joshua Robertson |  | While member was backing his bucket truck, the front left portion of the bumper struck a pole when turning during the backing process. The member was being directed by another member. Upon further investigation, it was determined that the two members did not properly position the truck before backing. The member driving did not maintain eye contact with the backer and did not see him attempting to stop the driver. |  |  |  | West Service Center | FALSE |  | FALSE | Construction Services |  | Casey Lee | Joshua Robertson |  | Terry Garrett | I approve | Terry Garrett |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | driver did not keep eye contact with backer. | 11. Improper Position for Task | 1. Struck Against (Running or Bumping Into) | [74 empty] | TRUE |  | Union City | Struck Fixed Object | Backing Related | 2018-07-01 19:00 |  | FALSE |  |  | Dawn |  |  | Dirt |  | Clear |  |  | N/A
8709 | Ft Smith Service Center | 2019-01-30 12:00 | Member was positioning truck to replace light. Member nosed truck up to fence and caused rock to roll underneath truck, damaging lower Intercooler and plastic shroud. Intercooler is 3" lower than bumper. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Sean Spicer | 2019-02-13 09:03 | 2019-02-08 13:24 | 2019-02-08 13:24 | 2019-02-08 13:44 | 2019-02-13 12:00 | 2019-02-08 12:26 |  |  |  | Ft Smith District. Mountain Burg, Ar. 11098 Canova TR. Gravel driveway, |  |  | Hannah Everett | Thank you for reporting, I approve. | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | [6 empty] | Ft Smith Service Center | FALSE |  | FALSE | Construction Services |  | Kristopher Halmes | Sean Spicer |  |  |  | Charles Kolp |  | Low | [93 empty] | FALSE |  | Mountain Burg | Other | Struck By Material/Debris | 2008-01-01 18:00 |  | FALSE |  |  | Day Light |  |  | Gravel |  | Clear
8710 | Horseshoe Lake Power Plant | 2019-02-07 21:30 | Steam release at approximately 1300 psi NOTE: this was a close call incident. No members were in the area when release occurred. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Michael Kennedy | 2019-06-20 11:08 | 2019-02-08 15:41 | 2019-02-08 15:41 | 2019-05-07 13:36 | 2019-02-21 21:30 | 2019-02-08 15:33 | 2019-06-10 08:25 |  | 2019-05-16 10:11 | North end of Unit 6 drum/Sight Glass |  |  | Jesse Murray | I approve. Jesse Murray 6-20-19 | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Michael Kennedy |  | At 2100 hours on February 7th there was an uncontrolled release of steam on Unit 6 at a recently installed level indication column (Fig 1&2, Photos Tab). The level indicator was installed as part of an initiative to automate drum level indication in an effort to keep members out of the line of fire. Currently, members must be stationed at the sight glass during key points of startup until steam is generated to fill the level transmitter leg. Had the event occurred at a time when the sight glass was being observed, serious injury or death could have occurred. The steam release occurred due to the failure of the lower gasket where the float column of the level indicator attaches to the bottom flange. This bottom flange has to be removed to install or service the float. The central causal factor has been identified as failure to properly spec the component. The investigation also found a number of secondary actions that could have mitigated the original failure. Failure to properly spec component It was determined during interviews that the measurements used to spec the operational conditions of the equipment were taken at the economizer inlet. This temperature was determined to be 400F and was recorded on a drawing provided by the supplier (Mag Gage Drawing Tab). However, drum readings suggest that operational temperatures reach 577 F or higher (Metal Temps Tab). Additionally, a quote provided by another company calls for much higher operational guidelines (Rosemont Quote Tab). This suggests an error in the spec’ing process on the OG&E side. To mitigate this issue in the future, it is suggested that the design criteria for the specific system be utilized when spec’ing new components. Improper Installation It cannot be ruled out that the gasket could have been installed improperly. While there is no direct evidence of this, it should be noted that ICE installed the gasket and installation of high pressure gaskets is outside of their normal scope. There are no known ‘gasket installation’ procedures or written best practice instructions. To mitigate this, training and/or written guidance should be developed and provided to members prior to installing critical gaskets. Additionally, no installation instructions were provided with the new part. A SCAR should be prepared, requesting the vendor supply installation instructions with any new parts. Defective Gasket While there was no indication that the gasket was physically damaged or otherwise unable to deliver its full engineered strength, there is no method for testing this type of equipment prior to putting it into service. A method for testing newly installed systems by bringing them online the first time in a carefully controlled manner that avoids putting members in the line of fire should be developed. Supplier Miscommunication When contacted after the event, the supplier stated that the gasket that came with the equipment was meant only as a “packing gasket,” one solely for the purpose of protecting the faces of the flange during shipment. While the gasket on Unit 6 was completely destroyed during the release, the one on Unit 7* was pulled and inspected under the reasonable assumption that it would be the same. It was clearly made of gasket material, though the specific kind has yet to be determined (Fig 3, Photos Tab). Additionally, the invoice receipt for the sight glass lists “Replacement Gasket” as a separate line item, indicating that the gasket was intended for use, despite what the supplier maintains (Vector Invoice Tab). It is the investigation team’s suggestion that a SCAR be prepared to request that if a gasket is intended for shipping purposes only, it be clearly labeled that way. It should be noted that the same equipment has been installed on 7&8. This was the first time Unit 6 was brought up to pressure since the installation of the level detector. Unit 7 has not been brought to pressure after the installation. Unit 8 was brought to pressure after the indicator was installed. However, it is suspected, but not conclusively proven, that the new level gage was isolated prior to any significant load or pressure being placed on the unit. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Operations |  | Peter Nowakowski | Michael Kennedy |  | Robert Doupe | I approve | Robert Doupe |  | Medium | [5 empty] | 6.02 Inadequate practice |  |  |  | 10.03 Inadequate standards, specifications and/or design criteria | [6 empty] | Gasket was not rated properly for its intended purpose. | 35. Inadequate Information, Data | 11. Overstress, Overpressure, Overexertion, Ergonomic |  | reviewed on 5/9/2019. Emailed Mike Kennedy about potential changes. Discussed potential changes with M. Kennedy on 5/9/19. | [90 empty] | 9581176
8710 | Horseshoe Lake Power Plant | 2019-02-07 21:30 | Steam release at approximately 1300 psi NOTE: this was a close call incident. No members were in the area when release occurred. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Michael Kennedy | 2019-06-20 11:08 | 2019-02-08 15:41 | 2019-02-08 15:41 | 2019-05-07 13:36 | 2019-02-21 21:30 | 2019-02-08 15:33 | 2019-06-10 08:25 |  | 2019-05-16 10:11 | North end of Unit 6 drum/Sight Glass |  |  | Jesse Murray | I approve. Jesse Murray 6-20-19 | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Michael Kennedy |  | At 2100 hours on February 7th there was an uncontrolled release of steam on Unit 6 at a recently installed level indication column (Fig 1&2, Photos Tab). The level indicator was installed as part of an initiative to automate drum level indication in an effort to keep members out of the line of fire. Currently, members must be stationed at the sight glass during key points of startup until steam is generated to fill the level transmitter leg. Had the event occurred at a time when the sight glass was being observed, serious injury or death could have occurred. The steam release occurred due to the failure of the lower gasket where the float column of the level indicator attaches to the bottom flange. This bottom flange has to be removed to install or service the float. The central causal factor has been identified as failure to properly spec the component. The investigation also found a number of secondary actions that could have mitigated the original failure. Failure to properly spec component It was determined during interviews that the measurements used to spec the operational conditions of the equipment were taken at the economizer inlet. This temperature was determined to be 400F and was recorded on a drawing provided by the supplier (Mag Gage Drawing Tab). However, drum readings suggest that operational temperatures reach 577 F or higher (Metal Temps Tab). Additionally, a quote provided by another company calls for much higher operational guidelines (Rosemont Quote Tab). This suggests an error in the spec’ing process on the OG&E side. To mitigate this issue in the future, it is suggested that the design criteria for the specific system be utilized when spec’ing new components. Improper Installation It cannot be ruled out that the gasket could have been installed improperly. While there is no direct evidence of this, it should be noted that ICE installed the gasket and installation of high pressure gaskets is outside of their normal scope. There are no known ‘gasket installation’ procedures or written best practice instructions. To mitigate this, training and/or written guidance should be developed and provided to members prior to installing critical gaskets. Additionally, no installation instructions were provided with the new part. A SCAR should be prepared, requesting the vendor supply installation instructions with any new parts. Defective Gasket While there was no indication that the gasket was physically damaged or otherwise unable to deliver its full engineered strength, there is no method for testing this type of equipment prior to putting it into service. A method for testing newly installed systems by bringing them online the first time in a carefully controlled manner that avoids putting members in the line of fire should be developed. Supplier Miscommunication When contacted after the event, the supplier stated that the gasket that came with the equipment was meant only as a “packing gasket,” one solely for the purpose of protecting the faces of the flange during shipment. While the gasket on Unit 6 was completely destroyed during the release, the one on Unit 7* was pulled and inspected under the reasonable assumption that it would be the same. It was clearly made of gasket material, though the specific kind has yet to be determined (Fig 3, Photos Tab). Additionally, the invoice receipt for the sight glass lists “Replacement Gasket” as a separate line item, indicating that the gasket was intended for use, despite what the supplier maintains (Vector Invoice Tab). It is the investigation team’s suggestion that a SCAR be prepared to request that if a gasket is intended for shipping purposes only, it be clearly labeled that way. It should be noted that the same equipment has been installed on 7&8. This was the first time Unit 6 was brought up to pressure since the installation of the level detector. Unit 7 has not been brought to pressure after the installation. Unit 8 was brought to pressure after the indicator was installed. However, it is suspected, but not conclusively proven, that the new level gage was isolated prior to any significant load or pressure being placed on the unit. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Operations |  | Peter Nowakowski | Michael Kennedy |  | Robert Doupe | I approve | Robert Doupe |  | Medium | [5 empty] | 6.03 Infrequent performance | [7 empty] | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.04 Inadequate communication between work groups | Lack of communication concerning proper installation of equipment provided by the manufacturer. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | reviewed on 5/9/2019. Emailed Mike Kennedy about potential changes. Discussed potential changes with M. Kennedy on 5/9/19. | [90 empty] | 9581176
8710 | Horseshoe Lake Power Plant | 2019-02-07 21:30 | Steam release at approximately 1300 psi NOTE: this was a close call incident. No members were in the area when release occurred. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Michael Kennedy | 2019-06-20 11:08 | 2019-02-08 15:41 | 2019-02-08 15:41 | 2019-05-07 13:36 | 2019-02-21 21:30 | 2019-02-08 15:33 | 2019-06-10 08:25 |  | 2019-05-16 10:11 | North end of Unit 6 drum/Sight Glass |  |  | Jesse Murray | I approve. Jesse Murray 6-20-19 | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Michael Kennedy |  | At 2100 hours on February 7th there was an uncontrolled release of steam on Unit 6 at a recently installed level indication column (Fig 1&2, Photos Tab). The level indicator was installed as part of an initiative to automate drum level indication in an effort to keep members out of the line of fire. Currently, members must be stationed at the sight glass during key points of startup until steam is generated to fill the level transmitter leg. Had the event occurred at a time when the sight glass was being observed, serious injury or death could have occurred. The steam release occurred due to the failure of the lower gasket where the float column of the level indicator attaches to the bottom flange. This bottom flange has to be removed to install or service the float. The central causal factor has been identified as failure to properly spec the component. The investigation also found a number of secondary actions that could have mitigated the original failure. Failure to properly spec component It was determined during interviews that the measurements used to spec the operational conditions of the equipment were taken at the economizer inlet. This temperature was determined to be 400F and was recorded on a drawing provided by the supplier (Mag Gage Drawing Tab). However, drum readings suggest that operational temperatures reach 577 F or higher (Metal Temps Tab). Additionally, a quote provided by another company calls for much higher operational guidelines (Rosemont Quote Tab). This suggests an error in the spec’ing process on the OG&E side. To mitigate this issue in the future, it is suggested that the design criteria for the specific system be utilized when spec’ing new components. Improper Installation It cannot be ruled out that the gasket could have been installed improperly. While there is no direct evidence of this, it should be noted that ICE installed the gasket and installation of high pressure gaskets is outside of their normal scope. There are no known ‘gasket installation’ procedures or written best practice instructions. To mitigate this, training and/or written guidance should be developed and provided to members prior to installing critical gaskets. Additionally, no installation instructions were provided with the new part. A SCAR should be prepared, requesting the vendor supply installation instructions with any new parts. Defective Gasket While there was no indication that the gasket was physically damaged or otherwise unable to deliver its full engineered strength, there is no method for testing this type of equipment prior to putting it into service. A method for testing newly installed systems by bringing them online the first time in a carefully controlled manner that avoids putting members in the line of fire should be developed. Supplier Miscommunication When contacted after the event, the supplier stated that the gasket that came with the equipment was meant only as a “packing gasket,” one solely for the purpose of protecting the faces of the flange during shipment. While the gasket on Unit 6 was completely destroyed during the release, the one on Unit 7* was pulled and inspected under the reasonable assumption that it would be the same. It was clearly made of gasket material, though the specific kind has yet to be determined (Fig 3, Photos Tab). Additionally, the invoice receipt for the sight glass lists “Replacement Gasket” as a separate line item, indicating that the gasket was intended for use, despite what the supplier maintains (Vector Invoice Tab). It is the investigation team’s suggestion that a SCAR be prepared to request that if a gasket is intended for shipping purposes only, it be clearly labeled that way. It should be noted that the same equipment has been installed on 7&8. This was the first time Unit 6 was brought up to pressure since the installation of the level detector. Unit 7 has not been brought to pressure after the installation. Unit 8 was brought to pressure after the indicator was installed. However, it is suspected, but not conclusively proven, that the new level gage was isolated prior to any significant load or pressure being placed on the unit. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Operations |  | Peter Nowakowski | Michael Kennedy |  | Robert Doupe | I approve | Robert Doupe |  | Medium | [5 empty] | 6.03 Infrequent performance | [7 empty] | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.03. Inadequate communication between different organizations | Lack of communication concerning proper installation of equipment provided by the manufacturer. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | reviewed on 5/9/2019. Emailed Mike Kennedy about potential changes. Discussed potential changes with M. Kennedy on 5/9/19. | [90 empty] | 9581176
8710 | Horseshoe Lake Power Plant | 2019-02-07 21:30 | Steam release at approximately 1300 psi NOTE: this was a close call incident. No members were in the area when release occurred. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Michael Kennedy | 2019-06-20 11:08 | 2019-02-08 15:41 | 2019-02-08 15:41 | 2019-05-07 13:36 | 2019-02-21 21:30 | 2019-02-08 15:33 | 2019-06-10 08:25 |  | 2019-05-16 10:11 | North end of Unit 6 drum/Sight Glass |  |  | Jesse Murray | I approve. Jesse Murray 6-20-19 | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Michael Kennedy |  | At 2100 hours on February 7th there was an uncontrolled release of steam on Unit 6 at a recently installed level indication column (Fig 1&2, Photos Tab). The level indicator was installed as part of an initiative to automate drum level indication in an effort to keep members out of the line of fire. Currently, members must be stationed at the sight glass during key points of startup until steam is generated to fill the level transmitter leg. Had the event occurred at a time when the sight glass was being observed, serious injury or death could have occurred. The steam release occurred due to the failure of the lower gasket where the float column of the level indicator attaches to the bottom flange. This bottom flange has to be removed to install or service the float. The central causal factor has been identified as failure to properly spec the component. The investigation also found a number of secondary actions that could have mitigated the original failure. Failure to properly spec component It was determined during interviews that the measurements used to spec the operational conditions of the equipment were taken at the economizer inlet. This temperature was determined to be 400F and was recorded on a drawing provided by the supplier (Mag Gage Drawing Tab). However, drum readings suggest that operational temperatures reach 577 F or higher (Metal Temps Tab). Additionally, a quote provided by another company calls for much higher operational guidelines (Rosemont Quote Tab). This suggests an error in the spec’ing process on the OG&E side. To mitigate this issue in the future, it is suggested that the design criteria for the specific system be utilized when spec’ing new components. Improper Installation It cannot be ruled out that the gasket could have been installed improperly. While there is no direct evidence of this, it should be noted that ICE installed the gasket and installation of high pressure gaskets is outside of their normal scope. There are no known ‘gasket installation’ procedures or written best practice instructions. To mitigate this, training and/or written guidance should be developed and provided to members prior to installing critical gaskets. Additionally, no installation instructions were provided with the new part. A SCAR should be prepared, requesting the vendor supply installation instructions with any new parts. Defective Gasket While there was no indication that the gasket was physically damaged or otherwise unable to deliver its full engineered strength, there is no method for testing this type of equipment prior to putting it into service. A method for testing newly installed systems by bringing them online the first time in a carefully controlled manner that avoids putting members in the line of fire should be developed. Supplier Miscommunication When contacted after the event, the supplier stated that the gasket that came with the equipment was meant only as a “packing gasket,” one solely for the purpose of protecting the faces of the flange during shipment. While the gasket on Unit 6 was completely destroyed during the release, the one on Unit 7* was pulled and inspected under the reasonable assumption that it would be the same. It was clearly made of gasket material, though the specific kind has yet to be determined (Fig 3, Photos Tab). Additionally, the invoice receipt for the sight glass lists “Replacement Gasket” as a separate line item, indicating that the gasket was intended for use, despite what the supplier maintains (Vector Invoice Tab). It is the investigation team’s suggestion that a SCAR be prepared to request that if a gasket is intended for shipping purposes only, it be clearly labeled that way. It should be noted that the same equipment has been installed on 7&8. This was the first time Unit 6 was brought up to pressure since the installation of the level detector. Unit 7 has not been brought to pressure after the installation. Unit 8 was brought to pressure after the indicator was installed. However, it is suspected, but not conclusively proven, that the new level gage was isolated prior to any significant load or pressure being placed on the unit. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Operations |  | Peter Nowakowski | Michael Kennedy |  | Robert Doupe | I approve | Robert Doupe |  | Medium | [5 empty] | 6.03 Infrequent performance | [7 empty] | 14.02.1 Inadequate communication of standards: publication |  | 16.04 Inadequate communication between work groups | Lack of communication concerning proper installation of equipment provided by the manufacturer. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | reviewed on 5/9/2019. Emailed Mike Kennedy about potential changes. Discussed potential changes with M. Kennedy on 5/9/19. | [90 empty] | 9581176
8710 | Horseshoe Lake Power Plant | 2019-02-07 21:30 | Steam release at approximately 1300 psi NOTE: this was a close call incident. No members were in the area when release occurred. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Michael Kennedy | 2019-06-20 11:08 | 2019-02-08 15:41 | 2019-02-08 15:41 | 2019-05-07 13:36 | 2019-02-21 21:30 | 2019-02-08 15:33 | 2019-06-10 08:25 |  | 2019-05-16 10:11 | North end of Unit 6 drum/Sight Glass |  |  | Jesse Murray | I approve. Jesse Murray 6-20-19 | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Michael Kennedy |  | At 2100 hours on February 7th there was an uncontrolled release of steam on Unit 6 at a recently installed level indication column (Fig 1&2, Photos Tab). The level indicator was installed as part of an initiative to automate drum level indication in an effort to keep members out of the line of fire. Currently, members must be stationed at the sight glass during key points of startup until steam is generated to fill the level transmitter leg. Had the event occurred at a time when the sight glass was being observed, serious injury or death could have occurred. The steam release occurred due to the failure of the lower gasket where the float column of the level indicator attaches to the bottom flange. This bottom flange has to be removed to install or service the float. The central causal factor has been identified as failure to properly spec the component. The investigation also found a number of secondary actions that could have mitigated the original failure. Failure to properly spec component It was determined during interviews that the measurements used to spec the operational conditions of the equipment were taken at the economizer inlet. This temperature was determined to be 400F and was recorded on a drawing provided by the supplier (Mag Gage Drawing Tab). However, drum readings suggest that operational temperatures reach 577 F or higher (Metal Temps Tab). Additionally, a quote provided by another company calls for much higher operational guidelines (Rosemont Quote Tab). This suggests an error in the spec’ing process on the OG&E side. To mitigate this issue in the future, it is suggested that the design criteria for the specific system be utilized when spec’ing new components. Improper Installation It cannot be ruled out that the gasket could have been installed improperly. While there is no direct evidence of this, it should be noted that ICE installed the gasket and installation of high pressure gaskets is outside of their normal scope. There are no known ‘gasket installation’ procedures or written best practice instructions. To mitigate this, training and/or written guidance should be developed and provided to members prior to installing critical gaskets. Additionally, no installation instructions were provided with the new part. A SCAR should be prepared, requesting the vendor supply installation instructions with any new parts. Defective Gasket While there was no indication that the gasket was physically damaged or otherwise unable to deliver its full engineered strength, there is no method for testing this type of equipment prior to putting it into service. A method for testing newly installed systems by bringing them online the first time in a carefully controlled manner that avoids putting members in the line of fire should be developed. Supplier Miscommunication When contacted after the event, the supplier stated that the gasket that came with the equipment was meant only as a “packing gasket,” one solely for the purpose of protecting the faces of the flange during shipment. While the gasket on Unit 6 was completely destroyed during the release, the one on Unit 7* was pulled and inspected under the reasonable assumption that it would be the same. It was clearly made of gasket material, though the specific kind has yet to be determined (Fig 3, Photos Tab). Additionally, the invoice receipt for the sight glass lists “Replacement Gasket” as a separate line item, indicating that the gasket was intended for use, despite what the supplier maintains (Vector Invoice Tab). It is the investigation team’s suggestion that a SCAR be prepared to request that if a gasket is intended for shipping purposes only, it be clearly labeled that way. It should be noted that the same equipment has been installed on 7&8. This was the first time Unit 6 was brought up to pressure since the installation of the level detector. Unit 7 has not been brought to pressure after the installation. Unit 8 was brought to pressure after the indicator was installed. However, it is suspected, but not conclusively proven, that the new level gage was isolated prior to any significant load or pressure being placed on the unit. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Operations |  | Peter Nowakowski | Michael Kennedy |  | Robert Doupe | I approve | Robert Doupe |  | Medium | [5 empty] | 6.03 Infrequent performance | [7 empty] | 14.02.1 Inadequate communication of standards: publication |  | 16.03. Inadequate communication between different organizations | Lack of communication concerning proper installation of equipment provided by the manufacturer. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | reviewed on 5/9/2019. Emailed Mike Kennedy about potential changes. Discussed potential changes with M. Kennedy on 5/9/19. | [90 empty] | 9581176
8711 | McClain Power Plant | 2019-02-11 09:30 | United Rental (Sub-contractor) was loading man lift on truck bed. The driver had was operating lift from man basket. The basket was low to ground for concern of overhead OEC power lines. Driver hit the corner fence post with basket knuckle. Security heard the impact and reported to plant members. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Jeremy Loper | 2019-03-04 08:56 | 2019-02-11 11:06 | 2019-02-11 11:06 | 2019-02-28 14:37 | 2019-02-25 09:30 | 2019-02-11 10:56 | 2019-02-28 15:54 |  |  | West side of contractor parking lot |  |  | Tanner Brady | Will review United Rentals investigation upon receiving it. Added corrective action 6212. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | TRUE |  | FALSE | FALSE | Jeremy Loper |  | United Rentals sub-contractor was loading man lift on flat bed. Contractor had concern for overhead power lines. This concern led the driver to keep the man basket low. He impacted the parameter fence with the man lift. United Rental has been contacted. We are waiting their investigation results. |  |  |  | McClain Power Plant | FALSE |  | FALSE | Other |  | Jeremy Loper | Jeremy Loper |  | Jimmy Green | 2/28/19 - United Rentals is still investigating this event. They expect a report will be ready the week of March 4th. Fence has been repaired by OGE. United Rentals is working with Facilities and AP to reimburse OGE for the cost of the fence repair. A SCAR was not submitted since United Rentals has been very cooperative in investigating the incident and paying for repairs. Rental equipment waiting for return is parked in the McClain contractor parking lot so the delivery drivers do not have to enter power block. The contractor parking lot is a very open area. There were only 2 cars in the parking lot at the time of the incident. It has not been standard practice for an OGE member to observe the loading of rental equipment. | Jimmy Green |  | Low | [8 empty] | 9.09 Inadequate identification and evaluation of loss exposures | [7 empty] | Failure to be aware of the distance | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) | [5 empty] | Property Damage |  | Jeremy Loper | Parameter Fence |  |  |  |  | 2. Struck By (Hit By Moving Object) | Jeremy Loper | United Rental Sub-Contractor | N/A |  | Fixed Equipment |  | Ralph Evans |  |  |  |  | FALSE | [42 empty] | Corner post is now leaning over by 20deg. The razor wire needs re-tension. The mid rail needs to be replaced. | 1500 | N/A | Fixed Equipment |  | Rental | [18 empty] | none
8711 | McClain Power Plant | 2019-02-11 09:30 | United Rental (Sub-contractor) was loading man lift on truck bed. The driver had was operating lift from man basket. The basket was low to ground for concern of overhead OEC power lines. Driver hit the corner fence post with basket knuckle. Security heard the impact and reported to plant members. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Jeremy Loper | 2019-03-04 08:56 | 2019-02-11 11:06 | 2019-02-11 11:06 | 2019-02-28 14:37 | 2019-02-25 09:30 | 2019-02-11 10:56 | 2019-02-28 15:54 |  |  | West side of contractor parking lot |  |  | Tanner Brady | Will review United Rentals investigation upon receiving it. Added corrective action 6212. | Power Supply |  | Level 1 | Property Damage |  | TRUE | FALSE | TRUE |  | FALSE | FALSE | Jeremy Loper |  | United Rentals sub-contractor was loading man lift on flat bed. Contractor had concern for overhead power lines. This concern led the driver to keep the man basket low. He impacted the parameter fence with the man lift. United Rental has been contacted. We are waiting their investigation results. |  |  |  | McClain Power Plant | FALSE |  | FALSE | Other |  | Jeremy Loper | Jeremy Loper |  | Jimmy Green | 2/28/19 - United Rentals is still investigating this event. They expect a report will be ready the week of March 4th. Fence has been repaired by OGE. United Rentals is working with Facilities and AP to reimburse OGE for the cost of the fence repair. A SCAR was not submitted since United Rentals has been very cooperative in investigating the incident and paying for repairs. Rental equipment waiting for return is parked in the McClain contractor parking lot so the delivery drivers do not have to enter power block. The contractor parking lot is a very open area. There were only 2 cars in the parking lot at the time of the incident. It has not been standard practice for an OGE member to observe the loading of rental equipment. | Jimmy Green |  | Low | [8 empty] | 9.09 Inadequate identification and evaluation of loss exposures | [7 empty] | Failure to be aware of the distance | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) | [5 empty] | Property Damage |  | Jeremy Loper | Parameter Fence |  |  |  |  | 2. Struck By (Hit By Moving Object) | Jeremy Loper | United Rental Sub-Contractor | N/A |  | Fixed Equipment |  | Ralph Evans |  |  |  |  | FALSE | [42 empty] | Corner post is now leaning over by 20deg. The razor wire needs re-tension. The mid rail needs to be replaced. | 1500 | N/A | Fixed Equipment |  | Rental | [18 empty] | none
8712 | Metro Service Center | 2019-02-05 13:30 | Member ran over gate stop in substation. | Level 1 |  | FALSE | Vehicle |  |  |  |  | OG&E Corp Services | Marcus Huddleston | 2019-02-18 10:50 | 2019-02-12 07:43 | 2019-02-12 07:43 | 2019-02-18 10:49 | 2019-02-19 13:30 | 2019-02-12 07:37 |  |  |  | Hunter Substation |  |  | Marcus Huddleston | No additional comments. MLH 2/18/19 | UTS |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | [6 empty] | Metro Service Center | FALSE |  | FALSE | UTS - Engineering & Planning |  | Keith Cook | Andrew Aston |  |  |  | Andrew Aston |  | Low | [93 empty] | FALSE |  | Hunter | Struck Fixed Object | Drove Forward Into Object | 2013-06-16 19:00 |  | FALSE |  |  | Day Light |  |  | Gravel |  | Rain
8713 | Sooner Power Plant | 2019-02-13 05:00 | Sooner unit 1 experienced a ruptured water wall tube on Sunday evening, Feb 10, 2019 forcing the unit off line. Dynamiting/shot-gunning was completed on Tue, Feb.12th during the day. While pulling bottom ash during the night shift to prevent the bottom ash from setting up in the bottom of the hoppers, the clinker grinder got jammed. Further follow up during the day revealed that one of the corner climber cables must've slipped through the throat scaffold and got into the clinker grinder. No members were onboard the climber since they were working days only. The cable needs to be replaced. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Alexander Taybah | 2019-03-21 08:43 | 2019-02-14 01:04 | 2019-02-14 01:04 | 2019-03-11 09:30 | 2019-02-27 05:00 | 2019-02-13 06:00 | 2019-03-17 17:11 |  | 2019-03-11 15:00 | Sooner PP, unit 1, bottom ash hoppers. |  |  | Jesse Murray | I Approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Alexander Taybah |  | Sooner unit 1 experienced a ruptured water wall tube leak on Sunday evening, Feb 10th forcing the unit off line. When the tube leak is on the burner side, pre-emptive dynamiting/shot-gunning must take place to eliminate any dangerous clinkers from falling down. This task was completed on Tue, Feb 12th in the afternoon. Best practice calls for the bottom ash to be pulled as soon as dynamiting/shot-gunning is done to prevent the ash from setting up in the bottom of the hoppers and while the night crew was doing so the clinker grinder got jammed. Further investigation the next day revealed that two of the corner climber cables (one safety and one motor cable) slipped through the throat scaffold and got into the clinker grinder causing it to jam. Risk Ranking: For this particular incident the risk ranking was high since the consequence could’ve been Severe if members were on the climber but it is Very Unlikely to occur. This is the first time such an incident had taken place at Sooner or Muskogee. The cables were pulled tight as they went through the clinker grinder. Fortunately no members were on the climber since there was a good chance the climber/members would be at a high risk. Going forward all measures will be taken where bottom ash will not be pulled when members are on the climbers. The reason the cables were able to reach the bottom of the boiler is that these cables can be used for different locations depending on where the tube leak is. In some instances the tube leak is on the pendant platens which requires longer cables. In this case, the leak was on one of the corners side of the furnace requiring level 7 access to be used which led to have an additional 250 feet laying at the bottom of the boiler on the throat scaffold. In general, the excess cables lay on the throat scaffold at the bottom of the furnace but clearly after two cables found their way between the tubes and recently purchased throat scaffold (refer to attached picture). |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Operations |  | Ronnie Fewell | Jimmie Allen |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | One of the cables used got through between the throat scaffold and boiler tubes. | 17. Failure to Identify Hazard, Risk | 6. Caught On (Snagged, Hung) |  | 2/27/2019 Brady Sowell Comments See my notes here and in the Workflow comments section. Detailed Description of Incident - Explain why the cable was able to reach clinker grinder - Explain why BA is pulled with the climber in the boiler - Discuss which cable was fed into the clinker grinder - Discuss the risk involved with cables getting into clinker grinders Immediate and Basic Causes - I believe 9.06 could be selected as well for a job system factor Corrective Actions - Discuss this option with Novotny before entering in Intellex. Develop a task list for installing climbers. This will ensure proper rigging is used every time and may help identify hazards like the one encountered in this incident. Document Attachment - IF we have any pictures of the cable or the climber at the time of the incident, we need to place them in the incident. | [90 empty] | 9580747
8713 | Sooner Power Plant | 2019-02-13 05:00 | Sooner unit 1 experienced a ruptured water wall tube on Sunday evening, Feb 10, 2019 forcing the unit off line. Dynamiting/shot-gunning was completed on Tue, Feb.12th during the day. While pulling bottom ash during the night shift to prevent the bottom ash from setting up in the bottom of the hoppers, the clinker grinder got jammed. Further follow up during the day revealed that one of the corner climber cables must've slipped through the throat scaffold and got into the clinker grinder. No members were onboard the climber since they were working days only. The cable needs to be replaced. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Alexander Taybah | 2019-03-21 08:43 | 2019-02-14 01:04 | 2019-02-14 01:04 | 2019-03-11 09:30 | 2019-02-27 05:00 | 2019-02-13 06:00 | 2019-03-17 17:11 |  | 2019-03-11 15:00 | Sooner PP, unit 1, bottom ash hoppers. |  |  | Jesse Murray | I Approve. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Alexander Taybah |  | Sooner unit 1 experienced a ruptured water wall tube leak on Sunday evening, Feb 10th forcing the unit off line. When the tube leak is on the burner side, pre-emptive dynamiting/shot-gunning must take place to eliminate any dangerous clinkers from falling down. This task was completed on Tue, Feb 12th in the afternoon. Best practice calls for the bottom ash to be pulled as soon as dynamiting/shot-gunning is done to prevent the ash from setting up in the bottom of the hoppers and while the night crew was doing so the clinker grinder got jammed. Further investigation the next day revealed that two of the corner climber cables (one safety and one motor cable) slipped through the throat scaffold and got into the clinker grinder causing it to jam. Risk Ranking: For this particular incident the risk ranking was high since the consequence could’ve been Severe if members were on the climber but it is Very Unlikely to occur. This is the first time such an incident had taken place at Sooner or Muskogee. The cables were pulled tight as they went through the clinker grinder. Fortunately no members were on the climber since there was a good chance the climber/members would be at a high risk. Going forward all measures will be taken where bottom ash will not be pulled when members are on the climbers. The reason the cables were able to reach the bottom of the boiler is that these cables can be used for different locations depending on where the tube leak is. In some instances the tube leak is on the pendant platens which requires longer cables. In this case, the leak was on one of the corners side of the furnace requiring level 7 access to be used which led to have an additional 250 feet laying at the bottom of the boiler on the throat scaffold. In general, the excess cables lay on the throat scaffold at the bottom of the furnace but clearly after two cables found their way between the tubes and recently purchased throat scaffold (refer to attached picture). |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Operations |  | Ronnie Fewell | Jimmie Allen |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | One of the cables used got through between the throat scaffold and boiler tubes. | 17. Failure to Identify Hazard, Risk | 6. Caught On (Snagged, Hung) |  | 2/27/2019 Brady Sowell Comments See my notes here and in the Workflow comments section. Detailed Description of Incident - Explain why the cable was able to reach clinker grinder - Explain why BA is pulled with the climber in the boiler - Discuss which cable was fed into the clinker grinder - Discuss the risk involved with cables getting into clinker grinders Immediate and Basic Causes - I believe 9.06 could be selected as well for a job system factor Corrective Actions - Discuss this option with Novotny before entering in Intellex. Develop a task list for installing climbers. This will ensure proper rigging is used every time and may help identify hazards like the one encountered in this incident. Document Attachment - IF we have any pictures of the cable or the climber at the time of the incident, we need to place them in the incident. | [90 empty] | 9580747
8714 | Sooner Power Plant | 2019-02-15 09:00 | Contractor heavily exposed to pebble lime during unloading operation. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Richard Wood | 2019-03-13 13:19 | 2019-02-15 13:05 | 2019-02-15 13:05 | 2019-03-02 07:41 | 2019-03-01 09:00 | 2019-02-15 12:40 | 2019-03-10 06:07 |  | 2019-03-04 15:49 | Pebble Lime Unloading Station |  |  | Jesse Murray | I Approve. Jesse Murray | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Richard Wood |  | Employees from JRT Trucking, the delivery subcontractor for US Lime came to the Station to offload lime from their truck into the Pebble Lime Silo. After notifying operations they attached their hose to the fill connection and began the offloading process. During the course of unloading a plug occurred in the unloading line. Although there is an unplugging procedure as well as a phone number to contact OGE Operations posted at the unloading station, one of the employees wearing a hard hat and safety glasses proceeded to remove the unloading hose from the fill connection apparently unaware that the line was pressurized. When the hose came off the fill connection under pressure, pebble lime and lime dust blew onto the employees upper body, face and eyes. The affected employee began to disrobe, but rather than going to the safety shower/eyewash station returned to the cab of his truck. When the operator assigned to monitor the operation returned from fueling his vehicle the driver stepped from the cab wrapped in a blanket and the operator drove him to the plant where he was showered, had his eyes washed and his condition evaluated. |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | UTS - Capital Projects |  | James Griffith | Richard Wood |  | Christopher Lelak | No further comments - CBL 03/10/2019 | Christopher Lelak |  | Medium |  |  |  |  | 5.04 Inadequate update training | 6.05 Inadequate review instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | [7 empty] | Employees from JRT Trucking, the delivery subcontractor for US Lime came to the Station to offload lime from their truck into the Pebble Lime Silo. After notifying operations they attached their hose to the fill connection and began the offloading process. During the course of unloading a plug occurred in the unloading line. Although there is an unplugging procedure as well as a phone number to contact OGE Operations posted at the unloading station, one of the employees wearing a hard hat and safety glasses proceeded to remove the unloading hose from the fill connection apparently unaware that the line was pressurized. When the hose came off the fill connection under pressure, pebble lime and lime dust blew onto the employees upper body, face and eyes. The affected employee began to disrobe, but rather than going to the safety shower/eyewash station returned to the cab of his truck. When the operator assigned to monitor the operation returned from fueling his vehicle the driver stepped from the cab wrapped in a blanket and the operator drove him to an the plant where he was showered, had his eyes washed and his condition evaluated. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 3/4/2019 |  |  | SO AQCS | Injury / Illness |  | Richard Wood |  | Irrritation | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | Nicholas Young | Burn: Chemical |  | Face | Richard Wood | Front | FALSE | [69 empty] | none
8714 | Sooner Power Plant | 2019-02-15 09:00 | Contractor heavily exposed to pebble lime during unloading operation. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Richard Wood | 2019-03-13 13:19 | 2019-02-15 13:05 | 2019-02-15 13:05 | 2019-03-02 07:41 | 2019-03-01 09:00 | 2019-02-15 12:40 | 2019-03-10 06:07 |  | 2019-03-04 15:49 | Pebble Lime Unloading Station |  |  | Jesse Murray | I Approve. Jesse Murray | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Richard Wood |  | Employees from JRT Trucking, the delivery subcontractor for US Lime came to the Station to offload lime from their truck into the Pebble Lime Silo. After notifying operations they attached their hose to the fill connection and began the offloading process. During the course of unloading a plug occurred in the unloading line. Although there is an unplugging procedure as well as a phone number to contact OGE Operations posted at the unloading station, one of the employees wearing a hard hat and safety glasses proceeded to remove the unloading hose from the fill connection apparently unaware that the line was pressurized. When the hose came off the fill connection under pressure, pebble lime and lime dust blew onto the employees upper body, face and eyes. The affected employee began to disrobe, but rather than going to the safety shower/eyewash station returned to the cab of his truck. When the operator assigned to monitor the operation returned from fueling his vehicle the driver stepped from the cab wrapped in a blanket and the operator drove him to the plant where he was showered, had his eyes washed and his condition evaluated. |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | UTS - Capital Projects |  | James Griffith | Richard Wood |  | Christopher Lelak | No further comments - CBL 03/10/2019 | Christopher Lelak |  | Medium |  |  |  |  | 5.04 Inadequate update training | 6.05 Inadequate review instruction |  |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Employees from JRT Trucking, the delivery subcontractor for US Lime came to the Station to offload lime from their truck into the Pebble Lime Silo. After notifying operations they attached their hose to the fill connection and began the offloading process. During the course of unloading a plug occurred in the unloading line. Although there is an unplugging procedure as well as a phone number to contact OGE Operations posted at the unloading station, one of the employees wearing a hard hat and safety glasses proceeded to remove the unloading hose from the fill connection apparently unaware that the line was pressurized. When the hose came off the fill connection under pressure, pebble lime and lime dust blew onto the employees upper body, face and eyes. The affected employee began to disrobe, but rather than going to the safety shower/eyewash station returned to the cab of his truck. When the operator assigned to monitor the operation returned from fueling his vehicle the driver stepped from the cab wrapped in a blanket and the operator drove him to an the plant where he was showered, had his eyes washed and his condition evaluated. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 3/4/2019 |  |  | SO AQCS | Injury / Illness |  | Richard Wood |  | Irrritation | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | Nicholas Young | Burn: Chemical |  | Face | Richard Wood | Front | FALSE | [69 empty] | none
8715 | Durant Service Center | 2019-02-15 11:30 | Crew completed job and was backing the bucket truck out of the site. Bucket contacted the eave of a house. This caused damage to the bucket and eave. Driver was utilizing backer, but the backer was not paying attention to the height of the truck and the overhead obstruction. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Lyle Just | 2019-03-04 13:56 | 2019-02-18 11:13 | 2019-02-18 11:13 | 2019-02-26 08:59 | 2019-03-01 11:30 | 2019-02-18 10:57 | 2019-02-28 15:21 |  |  | 1003 Christy Street, Calera Oklahoma |  |  | Terry Hackett | Reviewed/Approved TMH. Corrective action for operator added per Manager's request. | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Lyle Just |  | Crew completed job and was backing the bucket truck out of the site. Bucket contacted the eave of a house. This caused damage to the bucket and eave. Driver was utilizing backer, but the backer was not paying attention to the height of the truck and the overhead obstruction. Facts Ascertained: Driver stated that all he could see from his rear view mirrors were the two houses and that the edge of the house was in his blind spot. He was relying on the backer to direct him safely out of the site. Backer was an intern and had been through the 360 Backing WBT on 1-22-19 Backer stated he looked up at the eave and thought the bucket truck was going to clear it. Then he looked down at the bottom corner of the truck to ensure it was going to clear the house. During this time he was giving the operator the signal to continue backing up and the bucket struck the eave. Job site was muddy which caused truck to not turn as well while backing Truck was being backed between two houses (30 feet between the two houses) There was room to pull forward and maneuver Minor damage occurred to the eave of the house The bucket was totaled There were three members on site One driving the line truck, one backing the bucket, and the intern spotting See attached pictures and sketches for vehicle, building, and backer orientation |  |  |  | Durant Service Center | FALSE |  | FALSE | Construction Services |  | Michael Strohl | Lyle Just |  | Chad Inman | Need Member to gather information of driver responsibilities/lessons learned when backing, and then share with Southern Region. Propose a recommendation to eliminate backing incidents for Southern Region. | Chad Inman |  | Low |  |  |  |  | 5.01 Lack of experience | [11 empty] | Backer did not recognize overhead obstruction. | 02. Failure to Warn | 1. Struck Against (Running or Bumping Into) | [74 empty] | TRUE |  | Calera | Struck Fixed Object | Backing Related | 2007-01-21 18:00 |  | FALSE |  |  | Day Light |  |  | Mud |  | Cloudy |  |  | 7382328
8715 | Durant Service Center | 2019-02-15 11:30 | Crew completed job and was backing the bucket truck out of the site. Bucket contacted the eave of a house. This caused damage to the bucket and eave. Driver was utilizing backer, but the backer was not paying attention to the height of the truck and the overhead obstruction. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Lyle Just | 2019-03-04 13:56 | 2019-02-18 11:13 | 2019-02-18 11:13 | 2019-02-26 08:59 | 2019-03-01 11:30 | 2019-02-18 10:57 | 2019-02-28 15:21 |  |  | 1003 Christy Street, Calera Oklahoma |  |  | Terry Hackett | Reviewed/Approved TMH. Corrective action for operator added per Manager's request. | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Lyle Just |  | Crew completed job and was backing the bucket truck out of the site. Bucket contacted the eave of a house. This caused damage to the bucket and eave. Driver was utilizing backer, but the backer was not paying attention to the height of the truck and the overhead obstruction. Facts Ascertained: Driver stated that all he could see from his rear view mirrors were the two houses and that the edge of the house was in his blind spot. He was relying on the backer to direct him safely out of the site. Backer was an intern and had been through the 360 Backing WBT on 1-22-19 Backer stated he looked up at the eave and thought the bucket truck was going to clear it. Then he looked down at the bottom corner of the truck to ensure it was going to clear the house. During this time he was giving the operator the signal to continue backing up and the bucket struck the eave. Job site was muddy which caused truck to not turn as well while backing Truck was being backed between two houses (30 feet between the two houses) There was room to pull forward and maneuver Minor damage occurred to the eave of the house The bucket was totaled There were three members on site One driving the line truck, one backing the bucket, and the intern spotting See attached pictures and sketches for vehicle, building, and backer orientation |  |  |  | Durant Service Center | FALSE |  | FALSE | Construction Services |  | Michael Strohl | Lyle Just |  | Chad Inman | Need Member to gather information of driver responsibilities/lessons learned when backing, and then share with Southern Region. Propose a recommendation to eliminate backing incidents for Southern Region. | Chad Inman |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Backer did not recognize overhead obstruction. | 02. Failure to Warn | 1. Struck Against (Running or Bumping Into) | [74 empty] | TRUE |  | Calera | Struck Fixed Object | Backing Related | 2007-01-21 18:00 |  | FALSE |  |  | Day Light |  |  | Mud |  | Cloudy |  |  | 7382328
8716 | Ardmore Service Center | 2019-02-18 13:30 | Whitmire bucket truck hit wire going across 9th St and broke OG&E pole. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Danny Coffey | 2019-04-23 07:56 | 2019-02-18 14:50 | 2019-02-18 14:50 | 2019-04-01 08:26 | 2019-03-04 13:30 | 2019-02-18 14:24 | 2019-04-08 16:42 |  | 2019-04-01 11:24 | Hwy 48/S 9th St .1s Milburn OK |  |  | William Young | Will review with Danny and Jarod to ensure this is reviewed in staff mtg. for awareness and a reminder that we rank incidents on potential instead of outcome now. I recommend this incident be changed to L2, C4 due to the residential setting and nearby school - incident resulted in an uncontrolled pole falling in a potentially populated area. J. Looney, 3.26.19 | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Danny Coffey |  | A Whitmire bucket truck was travelling on S 9th St in Milburn Ok and hit a low hanging phone line that was attached to an OG&E pole. This resulted in the pole breaking off at ground level. The truck was of legal height and observing all traffic rules. The damage to OG&E facilities is no fault of the Whitmire tree crew based on the low hanging phone line that was below legal height across a roadway. |  |  |  | Ardmore Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Danny Coffey | Danny Coffey |  |  | Whitmire not at fault. Crossing not at appropriate height. Incident still indicates we should watch for unexpected hazards. No further action anticipated. Cassadjk |  |  | Medium |  |  |  | 4.04 Routine, monotony, demand for uneventful vigilance | [12 empty] | Vehicle driver didn't see low hanging wire in his path. | 17. Failure to Identify Hazard, Risk | 6. Caught On (Snagged, Hung) |  | Approved. J. Looney, 4.1.19 |  |  |  | Property Damage |  | Danny Coffey | Broke OG&E pole |  |  |  |  | 6. Caught On (Snagged, Hung) | Danny Coffey | Whitmire Line Clearance Inc | Elmonzo Onstott |  | Fixed Equipment |  | Danny Coffey |  |  |  | Broke OG&E pole | TRUE | [66 empty] | none
8716 | Ardmore Service Center | 2019-02-18 13:30 | Whitmire bucket truck hit wire going across 9th St and broke OG&E pole. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Danny Coffey | 2019-04-23 07:56 | 2019-02-18 14:50 | 2019-02-18 14:50 | 2019-04-01 08:26 | 2019-03-04 13:30 | 2019-02-18 14:24 | 2019-04-08 16:42 |  | 2019-04-01 11:24 | Hwy 48/S 9th St .1s Milburn OK |  |  | William Young | Will review with Danny and Jarod to ensure this is reviewed in staff mtg. for awareness and a reminder that we rank incidents on potential instead of outcome now. I recommend this incident be changed to L2, C4 due to the residential setting and nearby school - incident resulted in an uncontrolled pole falling in a potentially populated area. J. Looney, 3.26.19 | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Danny Coffey |  | A Whitmire bucket truck was travelling on S 9th St in Milburn Ok and hit a low hanging phone line that was attached to an OG&E pole. This resulted in the pole breaking off at ground level. The truck was of legal height and observing all traffic rules. The damage to OG&E facilities is no fault of the Whitmire tree crew based on the low hanging phone line that was below legal height across a roadway. |  |  |  | Ardmore Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Danny Coffey | Danny Coffey |  |  | Whitmire not at fault. Crossing not at appropriate height. Incident still indicates we should watch for unexpected hazards. No further action anticipated. Cassadjk |  |  | Medium |  |  |  | 4.04 Routine, monotony, demand for uneventful vigilance | [12 empty] | Vehicle driver didn't see low hanging wire in his path. | 17. Failure to Identify Hazard, Risk | 6. Caught On (Snagged, Hung) |  | Approved. J. Looney, 4.1.19 |  |  |  | Property Damage |  | Danny Coffey | Broke OG&E pole |  |  |  |  | 6. Caught On (Snagged, Hung) | Danny Coffey | Whitmire Line Clearance Inc | Elmonzo Onstott |  | Fixed Equipment |  | Danny Coffey |  |  |  | OG&E pole | TRUE | [66 empty] | none
8716 | Ardmore Service Center | 2019-02-18 13:30 | Whitmire bucket truck hit wire going across 9th St and broke OG&E pole. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Danny Coffey | 2019-04-23 07:56 | 2019-02-18 14:50 | 2019-02-18 14:50 | 2019-04-01 08:26 | 2019-03-04 13:30 | 2019-02-18 14:24 | 2019-04-08 16:42 |  | 2019-04-01 11:24 | Hwy 48/S 9th St .1s Milburn OK |  |  | William Young | Will review with Danny and Jarod to ensure this is reviewed in staff mtg. for awareness and a reminder that we rank incidents on potential instead of outcome now. I recommend this incident be changed to L2, C4 due to the residential setting and nearby school - incident resulted in an uncontrolled pole falling in a potentially populated area. J. Looney, 3.26.19 | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Danny Coffey |  | A Whitmire bucket truck was travelling on S 9th St in Milburn Ok and hit a low hanging phone line that was attached to an OG&E pole. This resulted in the pole breaking off at ground level. The truck was of legal height and observing all traffic rules. The damage to OG&E facilities is no fault of the Whitmire tree crew based on the low hanging phone line that was below legal height across a roadway. |  |  |  | Ardmore Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Danny Coffey | Danny Coffey |  |  | Whitmire not at fault. Crossing not at appropriate height. Incident still indicates we should watch for unexpected hazards. No further action anticipated. Cassadjk |  |  | Medium |  |  |  | 4.04 Routine, monotony, demand for uneventful vigilance | [12 empty] | Vehicle driver didn't see low hanging wire in his path. | 17. Failure to Identify Hazard, Risk | 6. Caught On (Snagged, Hung) |  | Approved. J. Looney, 4.1.19 |  |  |  | Property Damage |  | Danny Coffey | Broke OG&E pole |  |  |  |  | 6. Caught On (Snagged, Hung) | Danny Coffey | Whitmire Line Clearance Inc | Elmonzo Onstott |  | Fixed Equipment |  | Danny Coffey |  |  |  |  | TRUE | [66 empty] | none
8717 | Ft Smith Service Center | 2019-02-14 11:00 | During relay test of breaker C72 control relay at Branch the wrong FT was opened causing a breaker failure operation. | Level 2 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Eric Nipper | 2019-06-10 13:42 | 2019-02-18 15:15 |  | 2019-05-29 14:40 | 2019-03-28 11:00 | 2019-02-18 15:02 | 2019-06-10 11:37 |  | 2019-06-01 17:56 | Branch Substation |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Eric Nipper |  | Operational Incident Summary On Thursday, February 14th, 2019 while performing a relay calibration test at Branch substation on the Branch 69kv Capacitor C72 terminal a breaker failure operation inadvertently occurred on the 69kv Bus when the breaker failure FT switch was left closed during relay testing. Chain of Events: • The two man relay crew arrived at Branch substation to perform routine testing on the Branch 3701 terminal. o The relay foreman reviewed prints while the relay apprentice started to setup test equipment to perform the testing. • The relay foreman called out to the apprentice; who was standing in front of the panel, which FT switch he wanted him to open. o The relay apprentice repeated the numbers to confirm which FT switch to open and then opened the corresponding switch. o The relay foreman walked over to the panel and visually confirmed the apprentice had opened the FT switch as directed. • While performing the relay calibration test current initiated the operation of the breaker failure lockout relay and tripped PCB 4 and PCB 9 on the 69kv bus. o It was determined that the breaker failure lockout relay was not isolated while testing was conducted. • The TCC contacted the relay foreman and he informed them of the cause of the operation. It was determined the 69kv bus could be placed back to normal so switching was conducted and testing of C72 was completed. Incident Facts Ascertained: • Two man relay crew was tasked with conducting a calibration test on the C72 relay. • Only the relay foreman reviewed the prints to determine the FT switch to be opened. • The only FT switch opened during testing was for the C72 breaker lockout relay. o The FT switch for the C72 breaker failure lockout relay was not opened. |  |  |  | Ft Smith Service Center | FALSE |  | FALSE | PD Operations Services |  | Eric Nipper | Don Mantooth |  | Jeffrey Uhls | Investigation Completed | Jeffrey Uhls |  | Medium | [20 empty] | approved | [90 empty] | 7863081
8718 | South District Service Center | 2019-02-04 08:30 | Asplundh Tree Expert was flagging in work zone, public vehicle struck another vehicle from behind. | Level 1 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services | Richard Norton | 2019-03-18 09:40 | 2019-02-19 09:39 | 2019-02-19 09:39 | 2019-03-11 13:52 | 2019-02-18 08:30 | 2019-02-19 08:51 | 2019-03-12 16:09 |  |  | 5600 E. Etowah Rd. Noble Oklahoma |  |  | Jerrie Looney | Approved. J. Looney | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Richard Norton |  | Near Miss Report Company: Asplundh Tree Expert LLC Author: Damian Wisdom Date of Incident: 02/04/2019 Location: 5600 E. Etowah Rd. Noble, OK On Monday February 4th, 2019 we had crews working on Etowah Rd. in Noble, OK. Crews at location included two lift trucks and a manual crew to assist in flagging operations. Crews had set out three advanced warning signs ( Work Area Ahead, One Lane Road Ahead, Flagger Symbol) at both east and west end of job location. Flagger stations had also been established at both ends of work area with flagmen utilizing radios to communicate with one another. As lift crews where setting trucks up to operate the flagman at east end of work area informed other crews members an collision had taken place where he had traffic flow stopped. Eastbound traffic was stopped when a motorist traveling up to work zone neglected to notice the stopped cars and rear ended another motorist. The vehicle hit proceeded through the work zone and stopped on side of road adjacent of lift trucks. The two foreperson of lift crews made contact with drivers to ensure they were not injured. At this time the local police department was notified and shortly after arrived on scene. No citations were given to workers onsite due to traffic controls had been placed appropriately for work site location. At this time we do not have any information regarding if citations had been issued to motorists involved. There were no injuries reported to motorists and or crew members working the job location. If there is any other information that may need to be added or questions please feel free to contact me. Thank You Damian Wisdom General Foreperson Asplundh Tree Expert LLC (405)317-6576 |  |  |  | South District Service Center | FALSE |  | TRUE | PD - Resource Planning & Coord |  | Richard Norton | Danny Coffey |  |  | For records purposes and as a learning tool. No further action anticipated. Cassadjk |  |  | Low | [13 empty] | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  |  | Driver not paying attention | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) | [5 empty] | Vehicle |  | Richard Norton | [5 empty] | 1. Struck Against (Running or Bumping Into) | Richard Norton | Asplundh Tree Expert | Damian Wisdom |  |  |  | Danny Coffey | [71 empty] | None
8719 | Enid Service Center North | 2019-02-18 14:00 | Member was unloading large transformers off of an OGE heavy haul flatbed trailer when the member knocked a transformer off the opposite side of the flatbed trailer. | Level 2 |  | FALSE | Property Damage |  |  |  |  | OGE Energy Corp | Reginald Sanders | 2019-03-22 09:46 | 2019-02-19 13:42 | 2019-02-19 13:42 | 2019-03-04 13:49 | 2019-03-04 14:00 | 2019-02-19 13:26 | 2019-03-13 15:10 |  | 2019-03-05 08:27 | Enid warehouse yard |  |  | William Young | Incident returned to incorporate George's recommendation into a corrective action. WCY 3/11/2019 Reviewed and approved 3/22/19. WCY | Enterprise Services |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Reginald Sanders |  | Member was unloading a flatbed trailer that had 15 pole transformers, 6 reels of wire, a bundle of cross-arms, and 6 pallets of material. Heavy haul had sent a specific trailer for two large kited jobs. The jobs were 7381392 and 7381393. Member was unloading in the south area of the Enid yard, which is gravel/dirt mixture. It is a very flat area. Member was lifting a transformer, PN 919100, with the forklift F30-930 for unloading, Member failed to notice that the forks had pushed the third transformer very close to the edge. As member lifted the nearest transformer, the forks on the forklift caught the pallet of the third transformer across the trailer. This action tipped the third transformer over and off of the trailer. The transformer landed on the top side and on the insulator. The insulator was dislodged from the top and fluid started to leak out of the top of the transformer. The transformer was still attached to the pallet. The truck driver noticed the incident and moved the truck and trailer away from the spilling transformer. Once the trailer was out of the way, member up-righted the transformer. Member drove the forklift over to the truck dock to retrieve our spill kit. Member got a bag of dry absorbent and some “pig” absorbent sheet, (approx. 30). The truck driver damned up the liquid with the bag of dry absorbent to limit any liquid from spreading. The truck driver and member then placed the absorbent sheets on the spill. The truck driver called Tim Martin with Environmental to report the spill and have responsive action taken. After we contained and used the absorbent to soak up excess liquid, member finished unloading the trailer. The member thinks about 25 to 30 gallons spilled out of the transformer. The area of the spill was approximately 10 ft. by 25 ft. Member then called Reggie Sanders the supervisor, to report the incident. member was instructed to take pictures of the spill, and affected areas. Member also took pictures of the damaged transformer. Member placed the damaged transformer in the Enid TSA area. It is not leaking. Cal Services cleaned up the area. |  |  |  | Enid Service Center North | FALSE |  | FALSE | Supply Chain |  | John Roberts | Reginald Sanders |  | George Wicks | Supervisor recommended establishing a procedure for unloading oil filled equipment. | George Wicks |  | Medium | [10 empty] | 11.07 Improper handling of materials | [5 empty] | Member was unaware of the position of the forks on the forklift. | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) |  | Approved, Cody Vinyard | [66 empty] | Broken transformer bushing on top of transformer. | 1961.08 | John Roberts | Industrial/Heavy Equipment | [20 empty] | none
8720 | Metro Service Center | 2019-02-14 01:30 | While performing a breaker failure test at Cimarron substation on PCB 312 member inadvertently tripped breaker 302. | Level 1 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Joseph Manseau | 2019-04-10 12:13 | 2019-02-20 10:16 |  | 2019-04-03 07:50 | 2019-03-28 01:30 | 2019-02-20 10:09 | 2019-04-08 07:48 |  |  | Cimarron Substation |  |  | Cody Magby | Approved cm | T&D Ops |  | Level 1 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Joseph Manseau |  | During the course of testing breaker failure on PCB 312 member walked from the rear of the relay rack to the front of the relay rack to verify information. Upon returning to the rear of the rack to continue testing the member got off one rack. These racks are of similar build and physically look the same. After performing the test it was realized that he was on the wrong rack and tripped the wrong breaker. |  |  |  | Metro Service Center | FALSE |  | FALSE | PD Operations Services |  | Adam Auten | Joseph Manseau |  | James Hutchison | Please add a corrective action to this report it looks like it just got left off due to our conversation prior to investigating this incident. I have reviewed this incident and approve the corrective action as the team continues to develop best practices and necessary tools/equipment. | James Hutchison |  | Low | [111 empty] | 7848279
8721 | Metro Service Center | 2019-02-20 03:30 | OGE vehicle traveling north bound on I-35, traffic begin to slow down and trailing vehicle failed to slow down and rear ended the OGE vehicle. No injuries occurred. | Level 1 |  | FALSE | Vehicle |  |  |  |  | OG&E Corp Services | Johnny Whitfield | 2019-06-12 14:10 | 2019-02-20 17:13 | 2019-02-20 17:13 | 2019-06-12 13:26 | 2019-03-06 03:30 | 2019-02-20 16:56 |  |  |  | I 35 North and SE 89th St Exit |  |  | Jerrie Looney | Approved, J. Looney 6.12.19 | Enterprise Services |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | [6 empty] | Metro Service Center | FALSE |  | FALSE | Other |  | Johnny Whitfield | Johnny Whitfield |  |  |  | Jean Leger |  | Low | [93 empty] | FALSE |  | Oklahoma City | Public Vehicle Struck OGE | Public Driver Failed To Yield | 2011-08-07 19:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
8722 | General Service Center | 2019-02-20 12:00 | Truck driver attempted to pull in nose first in receiving area. In attempt to back out hit South wall with cab. | Level 1 |  | FALSE | Contractor |  |  |  |  | OGE Energy Corp | George Wicks | 2019-02-27 13:12 | 2019-02-21 10:13 | 2019-02-21 10:13 | 2019-02-21 12:25 | 2019-03-06 12:00 | 2019-02-21 10:04 | 2019-02-25 09:02 |  |  | South wall of receiving area at GSC high bay |  |  | Cody Vinyard | approved, cody vinyard | Enterprise Services |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | George Wicks |  | The Callaway driver was making a delivery to the receiving area of GSC at approximately 11:00 a.m. The driver pulled into receiving nose first and when in to check in with the Anixter receiving personnel. When he went back to his truck he had to turn around to unload. In the process of turning around in the very narrow receiving drive the tail of the trailer hit the wall causing the metal exterior to tear about 8 ft. vertical. |  |  |  | General Service Center | FALSE |  | FALSE | Supply Chain |  | Glen McClain | George Wicks |  | George Wicks | Signage will be moved today Feb 25th. | George Wicks |  | Low | [8 empty] | 9.06 Inadequate work planning or programming | [7 empty] | Driver was not aware of his surroundings. Driver did not read signage at entry of drive. | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) | [5 empty] | Vehicle |  | George Wicks | Damage to South Wall of high Bay warehouse at GSC |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Glen McClain | Callaway Carriers | Bryan Hugh Bolger |  | Structural |  | George Wicks |  |  |  |  | FALSE | [66 empty] | 1
8722 | General Service Center | 2019-02-20 12:00 | Truck driver attempted to pull in nose first in receiving area. In attempt to back out hit South wall with cab. | Level 1 |  | FALSE | Contractor |  |  |  |  | OGE Energy Corp | George Wicks | 2019-02-27 13:12 | 2019-02-21 10:13 | 2019-02-21 10:13 | 2019-02-21 12:25 | 2019-03-06 12:00 | 2019-02-21 10:04 | 2019-02-25 09:02 |  |  | South wall of receiving area at GSC high bay |  |  | Cody Vinyard | approved, cody vinyard | Enterprise Services |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | George Wicks |  | The Callaway driver was making a delivery to the receiving area of GSC at approximately 11:00 a.m. The driver pulled into receiving nose first and when in to check in with the Anixter receiving personnel. When he went back to his truck he had to turn around to unload. In the process of turning around in the very narrow receiving drive the tail of the trailer hit the wall causing the metal exterior to tear about 8 ft. vertical. |  |  |  | General Service Center | FALSE |  | FALSE | Supply Chain |  | Glen McClain | George Wicks |  | George Wicks | Signage will be moved today Feb 25th. | George Wicks |  | Low | [8 empty] | 9.06 Inadequate work planning or programming | [7 empty] | Driver was not aware of his surroundings. Driver did not read signage at entry of drive. | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | George Wicks | Damage to South Wall of high Bay warehouse at GSC |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Glen McClain | Callaway Carriers | Bryan Hugh Bolger |  | Structural |  | George Wicks |  |  |  |  | FALSE | [66 empty] | 1
8723 | Sooner Power Plant | 2019-02-21 04:00 | While moving tugger to job location, member moved to side of road to allow another vehicle to pass. During movement, wheel traveled off of pavement and struck hole. This caused the tugger to fall from forks of Rough Terrain Forklift. Tugger was damaged but is repairable. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Michael Dowell | 2019-03-26 09:02 | 2019-02-21 16:40 | 2019-02-21 16:39 | 2019-03-08 17:05 | 2019-03-07 04:00 | 2019-02-21 16:30 | 2019-03-12 07:32 |  |  | Sooner PP Service Road under belt 10&11 |  |  | Brady Sowell | Approved by Brady Sowell on 3/12/2019 | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Michael Dowell |  | Member was moving tugger from plant to ash silo. Tugger is stored on mobile cart. Member picked up cart with tugger sitting on top. Tugger is not mounted to cart as cart is used to move tugger short distances by hand. Member was enroute to destination when another vehicle approached. Member moved to side of road to give other vehicle room to pass. The road had recently been repaved and was much higher than the shoulder (8"). When the wheels of the Rough Terrain Forklift dropped off the tugger bounced off the cart and fell to the ground. The drum of the tugger was broken from the fall. The member stated that he feels like he does a good job securing loads. He has even stopped other members moving items and helped them secure their loads. This time however, he was focused on the job he was working on and not the task at hand. After reviewing the SWP it was determined that members did a good job of identifying the hazards related to the job they were working on. However, they failed to identify the hazards related to getting equipment and tools to the job site. The road shoulder is now level with the road surface. This was addressed by the AQCS project as they complete the road resufacing around the scrubber area. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Maintenance |  | Brian St Andrews | Michael Dowell |  | Frank Brixey | Approve - Brixey 3/12/19 | Frank Brixey |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Tugger and cart were not secured to the forklift | 08. Improper Loading | 2. Struck By (Hit By Moving Object) | [68 empty] | Drum was damaged on tugger after falling from pallet and landing on ground. | 1100 | Brian St Andrews | Portable Tool | [20 empty] | 9571297
8724 | Horseshoe Lake Power Plant | 2019-02-22 11:30 | WHILE REMOVING INSULATION BLANKETS A BREACHED AREA AROUND THE CROSSOVER PIPING WAS UNCOVERED NO INJURY OCCURED | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Wade Gabbert | 2019-04-01 07:40 | 2019-02-22 17:10 | 2019-02-22 17:10 | 2019-03-13 17:37 | 2019-03-08 11:30 | 2019-02-22 16:55 | 2019-03-26 09:32 |  | 2019-03-19 07:31 | UNIT 8 HP TURBINE |  |  | Jesse Murray | I Approve. Jesse Murray 4-1-19 | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Wade Gabbert |  | On 02/22/19 and EAI (Environmental Action Inc.) employee was tasked with removing the insulating blankets off of unit 8 cross over. While the removal was taking place, a HEPA vacuum was utilized to eliminate exposure to dust and fibers. During the process of EAI employees removing a portion of the blanket, an asbestos block became free and fell out of the old wrapping. The approximate size of the block was about 3”x3”x2.5”. Immediately upon occurrence, the work was stopped. The plant contact was notified. Personnel and other contractors working nearby were evacuated to prevent exposure. Clean up was immediately started. Clean up consisted of using the HEPA vacuum to pick up any fibers and debris. Repairs were also made to the insulation to prevent any further incidents. The OGE Asbestos Specialist was contact, Diana Edwards. The air quality was then tested to ensure no exposure would be present due to the incident. Testing came back negative. Diana Edwards came on site on 2/23/2019 to perform and investigation. Diana Edwards Report: A call from Wade Gabbert on 2-22-2019 at approximately 11:30 am, a small amount of ACM fell from under the blanket that was removed from Unit 8 cross over pipe. The amount of material that fell was approximately a sandwich baggy full. Bulk samples were taken on TSI prior to the start of the work in this area. It was confirmed that TSI was asbestos containing material (ACM). Procedures were being utilized to prevent exposure to ACM. All individuals working in the area were to wear PPE, protective clothing, and respiratory protection. A HEPA vacuum was to be used to capture any potential dust that may be present as the blanket was removed. EAI crew isolated the area (area surrounding unit 8 cross over on the turbine floor) and were beginning cleanup of the area. The isolation area was extended to the entire turbine floor. Contractors were not allowed to work on the turbine floor until the area is cleaned, repaired, and clearance samples completed. Darwin Chesnut was in agreement with this response action. Clean up included the disposal of the solid material that was dislodged and the area wet wiped. The mezzanine was also checked for visible material and cleanup of the area was performed as a precaution. Astech was contacted to perform clearance samples following the clean-up of the material. The clearance samples were analyzed and were found to be “below detectable limits”. This information was provided to Wade Gabbert along with verbal notification that the turbine floor could now be accessed by members and contractors. On February 23, 2019, a meeting was held with Wade Gabbert and EAI employees. We walked through the incident: • EAI members were to remove the blanket from around the pipe. • EAI was to repair or encapsulate any damaged insulation present under the blanket. • All individuals working on the pipe were wearing disposable suit and full face respirators. They were also wearing personal sampling monitors per their procedures. Test results for those units still need to be obtained. • At the time of the incident Ralph removed the blanket from the pipe and Richard Michael was a distance away assisting with the HEPA vac hose. • One Brock employee was in the area at the time (utilizing appropriate ppe and respiratory protection). • A piece of ACM located on the surface of the pipe fell from the pipe to the turbine floor. • There was not any scaffolding below the work area. • Nothing was in place below the work area to capture any material that might become dislodged while removing the blanket. • When the blanket was removed a piece of insulation located on the surface of the pipe was loose and fell out. • The material fell to the mezzanine. • The area around Unit 8 was cleared of all members and contractors and a barricade was established. • Clean-up procedures were immediately initiated with EAI. • The restricted area was extended to the entire turbine floor until such time clearance samples were available indicating there was not an exposure concern. There was no access to the turbine floor pending air sampling results. • The clearance samples were provided via email and were “Below Detectable Limits”. This information was forwarded to Wade Gabbert following a telephone call informing him the results were being emailed to him. Met with Darwin Chesnut, EAI, at HSL at 7am on Saturday, February 23, 2019 to determine the cause of the incident and discuss the incident and prevention strategies moving forward on the project. It appears that the heat from the pipe degraded (or burned away) the encapsulating material that had been used in the past to contain the asbestos. The layer of insulation material closest to the pipe was clearly no longer fully encapsulated and in a state that could become dislodged. The following prevention measures were implemented for the remaining project: • Scaffolding is to be built underneath the piping to allow a work surface below the pipe and blankets. • A mini containment or poly floor covering is to be utilized to capture any material that may become dislodged. • Any material captured will be properly handled and disposed of by EAI. • Continue to utilize PPE and respiratory protection. • Continue to utilize HEPA vacuum, approved cleaning methods, and patch and repair damaged material. • Encapsulate damaged material around pipe surface to prevent it from becoming loose and dislodged during future work. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Maintenance |  | Wade Gabbert | Wade Gabbert |  | Daniel Perry | Added comment on corrective action 6254 to describe the plan to abate the LP crossovers and remove the ACM. Sent back to have corrective action added for ensuring that moving forward some type of containment will be in place to capture any falling material. 3/26/19. I have reviewed this incident and I approve. | Daniel Perry |  | Medium | [14 empty] | 15.02 Improper extension of service life |  | incapsulating material was degraded | 23. Defective Tools, Equipment or Materials | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Filled out investigation with Wade Gabbert. 03/19/2019 - Consulted with Diana. Looks good and complete. |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Wade Gabbert | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Wade Gabbert | EAI | RICHARD MIKEL |  |  |  | Wade Gabbert | [71 empty] | TBD
8725 | Muskogee Power Plant | 2019-02-22 16:30 | During commissioning of unit 5 gas conversion the turbine was tripped for testing, the isolation valve separated from the control block. The isolation valve traveled across the turbine deck approximately 30 feet. There was a large release of hydraulic fluid. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | Assigned per Jon and Donnie. Jesse Murray 2-26-19 | 2019-02-26 13:28 | Power Supply | Randall Miller | 2019-06-10 13:48 | 2019-02-22 18:00 | 2019-02-22 18:00 | 2019-04-02 12:04 | 2019-03-08 16:30 | 2019-02-22 17:39 | 2019-04-22 15:54 | 2019-05-15 13:53 | 2019-04-04 13:02 | Muskogee Unit 5 Main Turbine, Left (#1) Throttle Valve. |  |  | Donnie Jones | Please quickly move to closing all action items. Thank you | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Unit 5 was undergoing MFT testing for gas conversion. Turbine tripped from boiler. Operations tripped second time due to showing left lower intercept valve closed but it was open. Re-latched and did not have open indication. Called techs. They discovered the linkage had disconnected on left lower intercept valve and the techs reattached the arm. The turbine re-latched and tripped to verify the closed limit. During the final trip the isolation valve was liberated from the block. The valve weighs about a pound and landed around 30 ft from its original location. EH fluid was observed streaming from the block. The block was removed and inspected in the shop. The isolation valve screws into a pressed fitting into the block. The fitting was on the isolation valve when recovered. The fitting was found to have an extrusion that appears to be a manufacturing defect in pressing it into the block. The isolation valve and o rings were recently replaced due to a leak. The replacement stopped the leak. We reviewed the operation history for the system at the time of the trips for abnormalities. This unit has a constant pressure EH system, so cycling is not suspected in the failure. No pressure or temperature excursions were noted in the trends reviewed. The block valve is primarily an oil path with other valves and checks inserted. Check valve for drain, trip header, servo, unloader valve and isolation valve are located on the block. Historically, covers were on the block. They were deemed unnecessary and were removed over 15 years ago. Approximately 7 years ago, safety representative identified hazard and stated need for a cover for wiring. Limited valves have covers. Covers could have mitigated the struck by hazard but still have EH leak. We reviewed the maintenance programs for the valve. No SAP history of rebuilding blocks. No SAP history of block failure. This is not currently part of the outage MI for the blocks and valves. Historically the o rings were replaced on the valves during outages, and valves are run to failure. | Randy Rigney | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Maintenance |  | Randall Miller | Andy Hedge |  | Andy Hedge | Reviewed and approved. Andy Hedge 4/22/19 | Andy Hedge | Jesse Murray | High | [9 empty] | 10.04 Inadequate monitoring of construction | [6 empty] | Defective equipment | 23. Defective Tools, Equipment or Materials | 2. Struck By (Hit By Moving Object) | Approved. Jesse Murray | Reviewed Bob Wright | [90 empty] | na
8725 | Muskogee Power Plant | 2019-02-22 16:30 | During commissioning of unit 5 gas conversion the turbine was tripped for testing, the isolation valve separated from the control block. The isolation valve traveled across the turbine deck approximately 30 feet. There was a large release of hydraulic fluid. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | Assigned per Jon and Donnie. Jesse Murray 2-26-19 | 2019-02-26 13:28 | Power Supply | Randall Miller | 2019-06-10 13:48 | 2019-02-22 18:00 | 2019-02-22 18:00 | 2019-04-02 12:04 | 2019-03-08 16:30 | 2019-02-22 17:39 | 2019-04-22 15:54 | 2019-05-15 13:53 | 2019-04-04 13:02 | Muskogee Unit 5 Main Turbine, Left (#1) Throttle Valve. |  |  | Donnie Jones | Please quickly move to closing all action items. Thank you | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Unit 5 was undergoing MFT testing for gas conversion. Turbine tripped from boiler. Operations tripped second time due to showing left lower intercept valve closed but it was open. Re-latched and did not have open indication. Called techs. They discovered the linkage had disconnected on left lower intercept valve and the techs reattached the arm. The turbine re-latched and tripped to verify the closed limit. During the final trip the isolation valve was liberated from the block. The valve weighs about a pound and landed around 30 ft from its original location. EH fluid was observed streaming from the block. The block was removed and inspected in the shop. The isolation valve screws into a pressed fitting into the block. The fitting was on the isolation valve when recovered. The fitting was found to have an extrusion that appears to be a manufacturing defect in pressing it into the block. The isolation valve and o rings were recently replaced due to a leak. The replacement stopped the leak. We reviewed the operation history for the system at the time of the trips for abnormalities. This unit has a constant pressure EH system, so cycling is not suspected in the failure. No pressure or temperature excursions were noted in the trends reviewed. The block valve is primarily an oil path with other valves and checks inserted. Check valve for drain, trip header, servo, unloader valve and isolation valve are located on the block. Historically, covers were on the block. They were deemed unnecessary and were removed over 15 years ago. Approximately 7 years ago, safety representative identified hazard and stated need for a cover for wiring. Limited valves have covers. Covers could have mitigated the struck by hazard but still have EH leak. We reviewed the maintenance programs for the valve. No SAP history of rebuilding blocks. No SAP history of block failure. This is not currently part of the outage MI for the blocks and valves. Historically the o rings were replaced on the valves during outages, and valves are run to failure. | Randy Rigney | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Maintenance |  | Randall Miller | Andy Hedge |  | Andy Hedge | Reviewed and approved. Andy Hedge 4/22/19 | Andy Hedge | Jesse Murray | High | [6 empty] | 7.06 Improper attempt to save time or effort |  | 9.10 Lack of supervisory/management job knowledge | 10.08 Inadequate evaluation of changes | [6 empty] | Inadequate guarding | 05. Making Safety Devices Inoperative | 2. Struck By (Hit By Moving Object) | Approved. Jesse Murray | Reviewed Bob Wright | [90 empty] | na
8725 | Muskogee Power Plant | 2019-02-22 16:30 | During commissioning of unit 5 gas conversion the turbine was tripped for testing, the isolation valve separated from the control block. The isolation valve traveled across the turbine deck approximately 30 feet. There was a large release of hydraulic fluid. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | Assigned per Jon and Donnie. Jesse Murray 2-26-19 | 2019-02-26 13:28 | Power Supply | Randall Miller | 2019-06-10 13:48 | 2019-02-22 18:00 | 2019-02-22 18:00 | 2019-04-02 12:04 | 2019-03-08 16:30 | 2019-02-22 17:39 | 2019-04-22 15:54 | 2019-05-15 13:53 | 2019-04-04 13:02 | Muskogee Unit 5 Main Turbine, Left (#1) Throttle Valve. |  |  | Donnie Jones | Please quickly move to closing all action items. Thank you | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Unit 5 was undergoing MFT testing for gas conversion. Turbine tripped from boiler. Operations tripped second time due to showing left lower intercept valve closed but it was open. Re-latched and did not have open indication. Called techs. They discovered the linkage had disconnected on left lower intercept valve and the techs reattached the arm. The turbine re-latched and tripped to verify the closed limit. During the final trip the isolation valve was liberated from the block. The valve weighs about a pound and landed around 30 ft from its original location. EH fluid was observed streaming from the block. The block was removed and inspected in the shop. The isolation valve screws into a pressed fitting into the block. The fitting was on the isolation valve when recovered. The fitting was found to have an extrusion that appears to be a manufacturing defect in pressing it into the block. The isolation valve and o rings were recently replaced due to a leak. The replacement stopped the leak. We reviewed the operation history for the system at the time of the trips for abnormalities. This unit has a constant pressure EH system, so cycling is not suspected in the failure. No pressure or temperature excursions were noted in the trends reviewed. The block valve is primarily an oil path with other valves and checks inserted. Check valve for drain, trip header, servo, unloader valve and isolation valve are located on the block. Historically, covers were on the block. They were deemed unnecessary and were removed over 15 years ago. Approximately 7 years ago, safety representative identified hazard and stated need for a cover for wiring. Limited valves have covers. Covers could have mitigated the struck by hazard but still have EH leak. We reviewed the maintenance programs for the valve. No SAP history of rebuilding blocks. No SAP history of block failure. This is not currently part of the outage MI for the blocks and valves. Historically the o rings were replaced on the valves during outages, and valves are run to failure. | Randy Rigney | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Maintenance |  | Randall Miller | Andy Hedge |  | Andy Hedge | Reviewed and approved. Andy Hedge 4/22/19 | Andy Hedge | Jesse Murray | High | [6 empty] | 7.06 Improper attempt to save time or effort |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.08 Inadequate evaluation of changes | [6 empty] | Inadequate guarding | 05. Making Safety Devices Inoperative | 2. Struck By (Hit By Moving Object) | Approved. Jesse Murray | Reviewed Bob Wright | [90 empty] | na
8725 | Muskogee Power Plant | 2019-02-22 16:30 | During commissioning of unit 5 gas conversion the turbine was tripped for testing, the isolation valve separated from the control block. The isolation valve traveled across the turbine deck approximately 30 feet. There was a large release of hydraulic fluid. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | Assigned per Jon and Donnie. Jesse Murray 2-26-19 | 2019-02-26 13:28 | Power Supply | Randall Miller | 2019-06-10 13:48 | 2019-02-22 18:00 | 2019-02-22 18:00 | 2019-04-02 12:04 | 2019-03-08 16:30 | 2019-02-22 17:39 | 2019-04-22 15:54 | 2019-05-15 13:53 | 2019-04-04 13:02 | Muskogee Unit 5 Main Turbine, Left (#1) Throttle Valve. |  |  | Donnie Jones | Please quickly move to closing all action items. Thank you | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Unit 5 was undergoing MFT testing for gas conversion. Turbine tripped from boiler. Operations tripped second time due to showing left lower intercept valve closed but it was open. Re-latched and did not have open indication. Called techs. They discovered the linkage had disconnected on left lower intercept valve and the techs reattached the arm. The turbine re-latched and tripped to verify the closed limit. During the final trip the isolation valve was liberated from the block. The valve weighs about a pound and landed around 30 ft from its original location. EH fluid was observed streaming from the block. The block was removed and inspected in the shop. The isolation valve screws into a pressed fitting into the block. The fitting was on the isolation valve when recovered. The fitting was found to have an extrusion that appears to be a manufacturing defect in pressing it into the block. The isolation valve and o rings were recently replaced due to a leak. The replacement stopped the leak. We reviewed the operation history for the system at the time of the trips for abnormalities. This unit has a constant pressure EH system, so cycling is not suspected in the failure. No pressure or temperature excursions were noted in the trends reviewed. The block valve is primarily an oil path with other valves and checks inserted. Check valve for drain, trip header, servo, unloader valve and isolation valve are located on the block. Historically, covers were on the block. They were deemed unnecessary and were removed over 15 years ago. Approximately 7 years ago, safety representative identified hazard and stated need for a cover for wiring. Limited valves have covers. Covers could have mitigated the struck by hazard but still have EH leak. We reviewed the maintenance programs for the valve. No SAP history of rebuilding blocks. No SAP history of block failure. This is not currently part of the outage MI for the blocks and valves. Historically the o rings were replaced on the valves during outages, and valves are run to failure. | Robert Wright | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Maintenance |  | Randall Miller | Andy Hedge |  | Andy Hedge | Reviewed and approved. Andy Hedge 4/22/19 | Andy Hedge | Jesse Murray | High | [9 empty] | 10.04 Inadequate monitoring of construction | [6 empty] | Defective equipment | 23. Defective Tools, Equipment or Materials | 2. Struck By (Hit By Moving Object) | Approved. Jesse Murray | Reviewed Bob Wright | [90 empty] | na
8725 | Muskogee Power Plant | 2019-02-22 16:30 | During commissioning of unit 5 gas conversion the turbine was tripped for testing, the isolation valve separated from the control block. The isolation valve traveled across the turbine deck approximately 30 feet. There was a large release of hydraulic fluid. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | Assigned per Jon and Donnie. Jesse Murray 2-26-19 | 2019-02-26 13:28 | Power Supply | Randall Miller | 2019-06-10 13:48 | 2019-02-22 18:00 | 2019-02-22 18:00 | 2019-04-02 12:04 | 2019-03-08 16:30 | 2019-02-22 17:39 | 2019-04-22 15:54 | 2019-05-15 13:53 | 2019-04-04 13:02 | Muskogee Unit 5 Main Turbine, Left (#1) Throttle Valve. |  |  | Donnie Jones | Please quickly move to closing all action items. Thank you | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Unit 5 was undergoing MFT testing for gas conversion. Turbine tripped from boiler. Operations tripped second time due to showing left lower intercept valve closed but it was open. Re-latched and did not have open indication. Called techs. They discovered the linkage had disconnected on left lower intercept valve and the techs reattached the arm. The turbine re-latched and tripped to verify the closed limit. During the final trip the isolation valve was liberated from the block. The valve weighs about a pound and landed around 30 ft from its original location. EH fluid was observed streaming from the block. The block was removed and inspected in the shop. The isolation valve screws into a pressed fitting into the block. The fitting was on the isolation valve when recovered. The fitting was found to have an extrusion that appears to be a manufacturing defect in pressing it into the block. The isolation valve and o rings were recently replaced due to a leak. The replacement stopped the leak. We reviewed the operation history for the system at the time of the trips for abnormalities. This unit has a constant pressure EH system, so cycling is not suspected in the failure. No pressure or temperature excursions were noted in the trends reviewed. The block valve is primarily an oil path with other valves and checks inserted. Check valve for drain, trip header, servo, unloader valve and isolation valve are located on the block. Historically, covers were on the block. They were deemed unnecessary and were removed over 15 years ago. Approximately 7 years ago, safety representative identified hazard and stated need for a cover for wiring. Limited valves have covers. Covers could have mitigated the struck by hazard but still have EH leak. We reviewed the maintenance programs for the valve. No SAP history of rebuilding blocks. No SAP history of block failure. This is not currently part of the outage MI for the blocks and valves. Historically the o rings were replaced on the valves during outages, and valves are run to failure. | Robert Wright | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Maintenance |  | Randall Miller | Andy Hedge |  | Andy Hedge | Reviewed and approved. Andy Hedge 4/22/19 | Andy Hedge | Jesse Murray | High | [6 empty] | 7.06 Improper attempt to save time or effort |  | 9.10 Lack of supervisory/management job knowledge | 10.08 Inadequate evaluation of changes | [6 empty] | Inadequate guarding | 05. Making Safety Devices Inoperative | 2. Struck By (Hit By Moving Object) | Approved. Jesse Murray | Reviewed Bob Wright | [90 empty] | na
8725 | Muskogee Power Plant | 2019-02-22 16:30 | During commissioning of unit 5 gas conversion the turbine was tripped for testing, the isolation valve separated from the control block. The isolation valve traveled across the turbine deck approximately 30 feet. There was a large release of hydraulic fluid. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | Assigned per Jon and Donnie. Jesse Murray 2-26-19 | 2019-02-26 13:28 | Power Supply | Randall Miller | 2019-06-10 13:48 | 2019-02-22 18:00 | 2019-02-22 18:00 | 2019-04-02 12:04 | 2019-03-08 16:30 | 2019-02-22 17:39 | 2019-04-22 15:54 | 2019-05-15 13:53 | 2019-04-04 13:02 | Muskogee Unit 5 Main Turbine, Left (#1) Throttle Valve. |  |  | Donnie Jones | Please quickly move to closing all action items. Thank you | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Unit 5 was undergoing MFT testing for gas conversion. Turbine tripped from boiler. Operations tripped second time due to showing left lower intercept valve closed but it was open. Re-latched and did not have open indication. Called techs. They discovered the linkage had disconnected on left lower intercept valve and the techs reattached the arm. The turbine re-latched and tripped to verify the closed limit. During the final trip the isolation valve was liberated from the block. The valve weighs about a pound and landed around 30 ft from its original location. EH fluid was observed streaming from the block. The block was removed and inspected in the shop. The isolation valve screws into a pressed fitting into the block. The fitting was on the isolation valve when recovered. The fitting was found to have an extrusion that appears to be a manufacturing defect in pressing it into the block. The isolation valve and o rings were recently replaced due to a leak. The replacement stopped the leak. We reviewed the operation history for the system at the time of the trips for abnormalities. This unit has a constant pressure EH system, so cycling is not suspected in the failure. No pressure or temperature excursions were noted in the trends reviewed. The block valve is primarily an oil path with other valves and checks inserted. Check valve for drain, trip header, servo, unloader valve and isolation valve are located on the block. Historically, covers were on the block. They were deemed unnecessary and were removed over 15 years ago. Approximately 7 years ago, safety representative identified hazard and stated need for a cover for wiring. Limited valves have covers. Covers could have mitigated the struck by hazard but still have EH leak. We reviewed the maintenance programs for the valve. No SAP history of rebuilding blocks. No SAP history of block failure. This is not currently part of the outage MI for the blocks and valves. Historically the o rings were replaced on the valves during outages, and valves are run to failure. | Robert Wright | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Maintenance |  | Randall Miller | Andy Hedge |  | Andy Hedge | Reviewed and approved. Andy Hedge 4/22/19 | Andy Hedge | Jesse Murray | High | [6 empty] | 7.06 Improper attempt to save time or effort |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.08 Inadequate evaluation of changes | [6 empty] | Inadequate guarding | 05. Making Safety Devices Inoperative | 2. Struck By (Hit By Moving Object) | Approved. Jesse Murray | Reviewed Bob Wright | [90 empty] | na
8726 | Metro Service Center | 2019-02-21 14:00 | While performing annual rescue training the retrieval device that was in use malfunctioned. Members were unable to raise the rescue dummy out of the vault. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Delivery | Terry Hackett | 2019-03-06 21:47 | 2019-02-25 08:09 | 2019-02-25 08:09 | 2019-03-04 15:47 | 2019-03-07 14:00 | 2019-02-25 07:55 | 2019-03-04 15:59 |  | 2019-03-04 15:48 | Norman Service Center Underground Training Vault |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Terry Hackett |  | Training department had requested that the Underground department bring a tripod and retrieval winch to the Norman Service Center for the CSE Rescue Training. The Underground group brought the equipment over and left it by the training vault. The equipment was there spare and was manufactured in 1994. Safety coordinator went down the morning of to inspect the equipment and did not notice any flaws that would cause the system to be unusable. The trainees went down the vault ladder, connected the rescue dummy, and started reeling him in with the winch handle. Members hand slipped off of the handle and it free spun prior to the SRL catching it. Once the SRL caught the dummy members were not able to get the device to lift or lower the dummy. The SRL rope had to be cut in order to get the dummy down. All members were cleared from the area prior to this taking place and Immediate control was in place. ANSI 359Z States SRL's including retrieval devices should be inspected/serviced on the below frequency: SRL with infrequent to light use: - Inspected by a Competent Person annually - Factory Authorized Inspection at least every 2-5 years SRL with moderate to heavy use: - Inspected by a Competent Person semi-annually to annually - Factory Authorized Inspection at least every 1-2 years SRL with severe/continuous use: - Inspected by a Competent Person quarterly to semi-annually - Factory Authorized Inspection at least annually Some SRL and Retrieval device vendors have a frequency called out in their user manual that the devices should be sent back to the manufacturer. The device used in underground are Miller and the user manual only requires they be sent back when a problem is identified during inspection or use. |  |  |  | Metro Service Center | FALSE |  | TRUE | Construction Services |  | Edward Bugby | Terry Hackett |  | Edward Bugby | .Reviewed and approved | Lindle Coleman |  | Medium | [8 empty] | 9.11 Inadequate matching of individual qualifications and job/task requirements | [7 empty] | Crew and trainers do not use the equipment frequent enough to be familiar with. | 23. Defective Tools, Equipment or Materials | 3. Fall from Elevation to Lower Level |  | Self reviewed | [90 empty] | NA
8726 | Metro Service Center | 2019-02-21 14:00 | While performing annual rescue training the retrieval device that was in use malfunctioned. Members were unable to raise the rescue dummy out of the vault. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Delivery | Terry Hackett | 2019-03-06 21:47 | 2019-02-25 08:09 | 2019-02-25 08:09 | 2019-03-04 15:47 | 2019-03-07 14:00 | 2019-02-25 07:55 | 2019-03-04 15:59 |  | 2019-03-04 15:48 | Norman Service Center Underground Training Vault |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Terry Hackett |  | Training department had requested that the Underground department bring a tripod and retrieval winch to the Norman Service Center for the CSE Rescue Training. The Underground group brought the equipment over and left it by the training vault. The equipment was there spare and was manufactured in 1994. Safety coordinator went down the morning of to inspect the equipment and did not notice any flaws that would cause the system to be unusable. The trainees went down the vault ladder, connected the rescue dummy, and started reeling him in with the winch handle. Members hand slipped off of the handle and it free spun prior to the SRL catching it. Once the SRL caught the dummy members were not able to get the device to lift or lower the dummy. The SRL rope had to be cut in order to get the dummy down. All members were cleared from the area prior to this taking place and Immediate control was in place. ANSI 359Z States SRL's including retrieval devices should be inspected/serviced on the below frequency: SRL with infrequent to light use: - Inspected by a Competent Person annually - Factory Authorized Inspection at least every 2-5 years SRL with moderate to heavy use: - Inspected by a Competent Person semi-annually to annually - Factory Authorized Inspection at least every 1-2 years SRL with severe/continuous use: - Inspected by a Competent Person quarterly to semi-annually - Factory Authorized Inspection at least annually Some SRL and Retrieval device vendors have a frequency called out in their user manual that the devices should be sent back to the manufacturer. The device used in underground are Miller and the user manual only requires they be sent back when a problem is identified during inspection or use. |  |  |  | Metro Service Center | FALSE |  | TRUE | Construction Services |  | Edward Bugby | Terry Hackett |  | Edward Bugby | .Reviewed and approved | Lindle Coleman |  | Medium | [11 empty] | 12.02.3 Inadequate reparative examination of units |  |  | 15.02 Improper extension of service life |  | Equipment was not in working order | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure |  | Self reviewed | [90 empty] | NA
8726 | Metro Service Center | 2019-02-21 14:00 | While performing annual rescue training the retrieval device that was in use malfunctioned. Members were unable to raise the rescue dummy out of the vault. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Delivery | Terry Hackett | 2019-03-06 21:47 | 2019-02-25 08:09 | 2019-02-25 08:09 | 2019-03-04 15:47 | 2019-03-07 14:00 | 2019-02-25 07:55 | 2019-03-04 15:59 |  | 2019-03-04 15:48 | Norman Service Center Underground Training Vault |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Terry Hackett |  | Training department had requested that the Underground department bring a tripod and retrieval winch to the Norman Service Center for the CSE Rescue Training. The Underground group brought the equipment over and left it by the training vault. The equipment was there spare and was manufactured in 1994. Safety coordinator went down the morning of to inspect the equipment and did not notice any flaws that would cause the system to be unusable. The trainees went down the vault ladder, connected the rescue dummy, and started reeling him in with the winch handle. Members hand slipped off of the handle and it free spun prior to the SRL catching it. Once the SRL caught the dummy members were not able to get the device to lift or lower the dummy. The SRL rope had to be cut in order to get the dummy down. All members were cleared from the area prior to this taking place and Immediate control was in place. ANSI 359Z States SRL's including retrieval devices should be inspected/serviced on the below frequency: SRL with infrequent to light use: - Inspected by a Competent Person annually - Factory Authorized Inspection at least every 2-5 years SRL with moderate to heavy use: - Inspected by a Competent Person semi-annually to annually - Factory Authorized Inspection at least every 1-2 years SRL with severe/continuous use: - Inspected by a Competent Person quarterly to semi-annually - Factory Authorized Inspection at least annually Some SRL and Retrieval device vendors have a frequency called out in their user manual that the devices should be sent back to the manufacturer. The device used in underground are Miller and the user manual only requires they be sent back when a problem is identified during inspection or use. |  |  |  | Metro Service Center | FALSE |  | TRUE | Construction Services |  | Edward Bugby | Terry Hackett |  | Edward Bugby | .Reviewed and approved | Lindle Coleman |  | Medium | [11 empty] | 12.01.2 Inadequate preventative lubrication and servicing |  |  | 15.02 Improper extension of service life |  | Equipment was not in working order | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure |  | Self reviewed | [90 empty] | NA
8726 | Metro Service Center | 2019-02-21 14:00 | While performing annual rescue training the retrieval device that was in use malfunctioned. Members were unable to raise the rescue dummy out of the vault. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Delivery | Terry Hackett | 2019-03-06 21:47 | 2019-02-25 08:09 | 2019-02-25 08:09 | 2019-03-04 15:47 | 2019-03-07 14:00 | 2019-02-25 07:55 | 2019-03-04 15:59 |  | 2019-03-04 15:48 | Norman Service Center Underground Training Vault |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Terry Hackett |  | Training department had requested that the Underground department bring a tripod and retrieval winch to the Norman Service Center for the CSE Rescue Training. The Underground group brought the equipment over and left it by the training vault. The equipment was there spare and was manufactured in 1994. Safety coordinator went down the morning of to inspect the equipment and did not notice any flaws that would cause the system to be unusable. The trainees went down the vault ladder, connected the rescue dummy, and started reeling him in with the winch handle. Members hand slipped off of the handle and it free spun prior to the SRL catching it. Once the SRL caught the dummy members were not able to get the device to lift or lower the dummy. The SRL rope had to be cut in order to get the dummy down. All members were cleared from the area prior to this taking place and Immediate control was in place. ANSI 359Z States SRL's including retrieval devices should be inspected/serviced on the below frequency: SRL with infrequent to light use: - Inspected by a Competent Person annually - Factory Authorized Inspection at least every 2-5 years SRL with moderate to heavy use: - Inspected by a Competent Person semi-annually to annually - Factory Authorized Inspection at least every 1-2 years SRL with severe/continuous use: - Inspected by a Competent Person quarterly to semi-annually - Factory Authorized Inspection at least annually Some SRL and Retrieval device vendors have a frequency called out in their user manual that the devices should be sent back to the manufacturer. The device used in underground are Miller and the user manual only requires they be sent back when a problem is identified during inspection or use. |  |  |  | Metro Service Center | FALSE |  | TRUE | Construction Services |  | Edward Bugby | Terry Hackett |  | Edward Bugby | .Reviewed and approved | Lindle Coleman |  | Medium | [11 empty] | 12.01.1 Inadequate preventative assessment of needs |  |  | 15.02 Improper extension of service life |  | Equipment was not in working order | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure |  | Self reviewed | [90 empty] | NA
8727 | Metro Service Center | 2019-02-13 12:00 | While tightening a fargo the contractor drill came in contact with streetlight wire causing sparks that ignited a grass fire. | Level 1 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Marcus Huddleston | 2019-03-13 09:58 | 2019-02-25 15:16 | 2019-02-25 15:16 | 2019-03-07 15:44 | 2019-02-27 12:00 | 2019-02-25 15:11 | 2019-03-12 22:52 |  |  | 4309 SE 35th Street, OKC |  |  | Marcus Huddleston | No additional comments. MLH // | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Melaina Moffatt |  | We had a 1 man hooking up a streetlight wire out of the bucket at 4309 SE 35th ST and while tightening the Fargo on the hot leg, the wind shifted the bucket and his drill touched the neutral on the streetlight wire and caused a spark that went to the ground and caught the grass on fire. He got down and put the fire out and spoke with the home owner and the home owner has no issues with it and doesn’t need anything fixed. No injuries or outages and the 1 man was wearing proper PPE. |  |  |  | Metro Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Melaina Moffatt | Melaina Moffatt |  | Nicole Rhodes | Reviewed. | Nicole Rhodes |  | Low |  |  |  |  | 5.06 Lack of situational awareness |  | 7.06 Improper attempt to save time or effort | [9 empty] | Gust of wind shifted the bucket while the one man was working on tightening the Fargo on the hot leg. | 40. Weather Conditions | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Marcus Huddleston | Burned grass |  |  |  |  | 9. Abnormal Operation | Melaina Moffatt | Davis H. Elliot Company | Jason Pritchett (Supervisor) |  | Fire |  | Melaina Moffatt |  |  |  |  | FALSE | [66 empty] | TBD
8728 | Ft Smith Service Center | 2019-02-25 10:30 | while traveling down highway a box of plastic coverup was blown out of the bed of the pickup by a passing semi. | Level 1 |  | TRUE | Vehicle |  |  |  |  | Power Delivery | Manuel Conley | 2019-03-13 08:13 | 2019-02-26 11:02 | 2019-02-26 11:02 | 2019-03-04 09:35 | 2019-03-11 10:30 | 2019-02-26 10:49 | 2019-03-04 10:23 |  |  | Interstate 540 near greenwood road exit |  |  | Cody Magby | Cargo netting was purchased for the area and has been in use since the incident with good success. Look at purchasing cargo nets for other areas is next step | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Manuel Conley |  | Substation maintenance member was transporting cover up to jobsite in the back up 3/4 ton pickup. Travelling down Interstate 540 when a semi truck passed the driver a cardboard box with some cover up material was blown out of the pickup bed. Driver found a safe spot to turn around and went to retrieve the box. The cover up material was still in the box when member got to it with minimal damage to the box, cover up was still in good condition. |  |  |  | Ft Smith Service Center | FALSE |  | TRUE | PD Operations Services |  | Manuel Conley | Don Mantooth |  | James Hutchison | I have reviewed this incident report and agree with the corrective actions. | James Hutchison |  | Low | [12 empty] | 13.04 Inadequate availability |  |  |  | There was not sufficient anchor points on the pickup bed. Straps for this abnormal load were insufficient, consider cargo nets. | 03. Failure to Secure | 9. Abnormal Operation | [92 empty] | 1646945
8729 | Metro Service Center | 2019-02-20 09:00 | Arborist dropped a log on the gas meter at this location. the crew was concerned the meter was damaged so they reported the incident to ONG and contacted reported the findings. | Level 1 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services | Wesley Lanier | 2019-03-20 17:35 | 2019-02-26 15:26 | 2019-02-26 15:26 | 2019-02-26 16:20 | 2019-03-06 09:00 | 2019-02-26 15:09 | 2019-03-12 16:04 |  |  | 2901 West Fairfield Ave OKC |  |  | Jerrie Looney | Approved. J. Looney | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Wesley Lanier |  | See attached document |  |  |  | Metro Service Center | FALSE |  | TRUE | PD - Resource Planning & Coord |  | Wesley Lanier | Wesley Lanier |  |  | Generally reported for tracking purposes. This is the second gas meter event for this vendor. Different crew, different supervisor. Records only. No further action anticipated. cassadjk |  |  | Low | 1.01 Inappropriate height, weight, size, strength, reach, etc. | [15 empty] | dropped log | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Wesley Lanier | [5 empty] | 2. Struck By (Hit By Moving Object) | Wesley Lanier | Asplundh Tree Expert Co. | Asplundh |  |  |  | Wesley Lanier | [71 empty] | N/A
8730 | Sooner Power Plant | 2019-02-27 08:00 | Member slipped on ice near east entrance of maintenance shop offices (old foremen's offices outside entrance). Member fell but was not injured. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply |  | 2019-03-13 13:20 | 2019-02-27 08:31 | 2019-02-27 08:31 | 2019-02-27 09:55 | 2019-03-13 14:00 | 2019-02-27 08:22 | 2019-03-07 12:15 |  | 2019-03-04 15:38 | Sooner PP. East side of maintenance shop near office entrance. |  |  | Jesse Murray | I Approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE |  |  | Member was walking to office area (new maintenance offices) to begin work day. Weather conditions: cold, 27 degrees, moderate mist. Member was taking precautions while walking from parking lot to office area. Member did not notice icy walkway until it was too late. Walkways before this location were not slick. Walkway from area of incident to new maintenance offices was slick and icy. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Engineering & Planning |  |  | Donald Wyckoff |  | Donald Wyckoff | Reviewed the investigation findings, agree that all building entrances should be treated with ice melt before beginning of the work day to prevent slipping hazards. 3/7/19 Donald E. Wyckoff. | Donald Wyckoff |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Icy conditions. | 17. Failure to Identify Hazard, Risk | 4. Fall on Same Level (Slip and Fall, Trip Over) |  | Approved by Brady Sowell | [90 empty] | None
8731 | Enid Service Center | 2019-02-26 12:00 | member struck pillar on right side of truck ( passenger side ) while driving forward to exit parking lot after completion of work | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Mark Hamm | 2019-03-07 12:59 | 2019-02-27 10:49 | 2019-02-27 10:49 | 2019-03-04 09:44 | 2019-03-12 12:00 | 2019-02-27 10:33 | 2019-03-04 12:50 |  |  | 113 e cottonwood Enid ,Ok in a parking lot |  |  | Luke Kennedy | I believe the corrective actions will prevent incidents similar to this one going forward. | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Mark Hamm |  | On Wednesday 2/27/19, Kevin Perryman received a job at 113 E Cottonwood replacing a security light. The location of the pole was somewhat congested and the member pulled straight in to perform the work. As the member left he walked out the area before safely backing up. Then as he went to leave he did a 2nd 360 before he pulled forward and turned to exit the parking lot. He did not realize he had not yet cleared the 2nd pillar and struck it on the passenger side causing some damage to the steps below the door. At this time the member stopped and reported it to his supervisor. Pictures of the job site are attached to the incident report. |  |  |  | Enid Service Center | FALSE |  | FALSE | Construction Services |  | Kevin Perryman | Mark Hamm |  | Christopher Bristol | We discussed this incident with the group Monday March 4th. I approve. | Christopher Bristol |  | Low |  |  |  |  | 5.01 Lack of experience | [11 empty] | member did not back in prior to work and did not identify the 2nd pillar as he was leaving | 11. Improper Position for Task | 1. Struck Against (Running or Bumping Into) | [74 empty] | TRUE |  | Enid | Struck Fixed Object | Turned Into Object | 2018-09-23 19:00 |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Rain |  |  | none
8731 | Enid Service Center | 2019-02-26 12:00 | member struck pillar on right side of truck ( passenger side ) while driving forward to exit parking lot after completion of work | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Mark Hamm | 2019-03-07 12:59 | 2019-02-27 10:49 | 2019-02-27 10:49 | 2019-03-04 09:44 | 2019-03-12 12:00 | 2019-02-27 10:33 | 2019-03-04 12:50 |  |  | 113 e cottonwood Enid ,Ok in a parking lot |  |  | Luke Kennedy | I believe the corrective actions will prevent incidents similar to this one going forward. | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Mark Hamm |  | On Wednesday 2/27/19, Kevin Perryman received a job at 113 E Cottonwood replacing a security light. The location of the pole was somewhat congested and the member pulled straight in to perform the work. As the member left he walked out the area before safely backing up. Then as he went to leave he did a 2nd 360 before he pulled forward and turned to exit the parking lot. He did not realize he had not yet cleared the 2nd pillar and struck it on the passenger side causing some damage to the steps below the door. At this time the member stopped and reported it to his supervisor. Pictures of the job site are attached to the incident report. |  |  |  | Enid Service Center | FALSE |  | FALSE | Construction Services |  | Kevin Perryman | Mark Hamm |  | Christopher Bristol | We discussed this incident with the group Monday March 4th. I approve. | Christopher Bristol |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | member did not back in prior to work and did not identify the 2nd pillar as he was leaving | 11. Improper Position for Task | 1. Struck Against (Running or Bumping Into) | [74 empty] | TRUE |  | Enid | Struck Fixed Object | Turned Into Object | 2018-09-23 19:00 |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Rain |  |  | none
8732 | Muskogee Power Plant | 2019-02-26 09:00 | Member was descending ladder to hot deck, stepped on the second rung and it broke. Member did not incur a fall. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Mark Graham | 2019-05-02 12:47 | 2019-02-27 15:08 | 2019-02-27 15:08 | 2019-03-08 14:43 | 2019-03-12 09:00 | 2019-02-27 15:01 | 2019-04-22 15:52 |  | 2019-03-08 14:56 | Unit 4 cooling tower F cell, ladder on hot deck. |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Gary Ridley |  | Mechanics had been replacing 4F CT motor and had the fan blades tied off with a rope. Member went back inside the CT cell to remove the rope. There is a short ladder (approx.. 7'-8' tall) going up to the gearbox area where the rope was tied off. After retrieving the rope, he rolled it up and stuck it in his pocket so he would have both hands free to descend the ladder. When he got all the way down to the 2nd rung from the bottom, the rung broke under his weight. He dropped approximately 16" but still had a hold of the ladder. Member did not fall, or get injured. He picked up the broken rung and brought it to a supervisor and reported the incident to him. There is a project in the works for this fall to do various repairs to unit 4 CT. I will make sure all the ladders get inspected and replaced as needed, including the one on 4F. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Maintenance |  | Dee Cookson | Mark Graham |  | Andy Hedge | Reviewed and approved. Andy Hedge 4/22/19 | Andy Hedge |  | Medium | [14 empty] | 15.02 Improper extension of service life |  | Ladder rung broke under weight of mechanic. | 23. Defective Tools, Equipment or Materials | 3. Fall from Elevation to Lower Level |  | good investigation Bob Wright | [90 empty] | 9574927
8733 | Seminole PP; EGX Gath/Trans | 2019-02-27 14:30 | 3A Condensate Pump coupling retaining nut was found off the shaft without set screws. Motor had been tested for rotation on 2/26/2019 and vibration on 2/27/2019. When members went to couple motor and pump, they discovered the retaining nut had spun off the shaft. | Level 3 |  | TRUE | Member Injury | Donnie Jones | Jesse Murray | Assigning to Stahl due to contractor issue with the parts. | 2019-03-05 13:00 | Power Supply | Justin Stahl | 2019-03-13 17:10 | 2019-02-27 15:20 | 2019-02-27 15:20 | 2019-03-05 14:33 | 2019-03-13 14:30 | 2019-02-27 15:08 | 2019-03-06 12:59 | 2019-03-13 13:21 | 2019-03-05 16:38 | SM03 Basement 3A Condensate Pump |  |  | Donnie Jones | Appreciate the action items you've identified - Donnie | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Justin Stahl |  | Around February 1, 2019 3A Condensate Pump was uncoupled and the motor was sent to Southwest Electric Co. for rebuild. Reliability Technician went to vendor on February 21 to perform FAT. On Friday, February 22, the motor arrived back onsite from vendor. On Thursday, February 26, motor and pump were installed and motor tested for rotation. The following day, Reliability Technician was asked to get baseline readings of motor uncoupled. After the baseline test, the clearance was reinstalled for SSG to set lift and couple motor and pump. Members found retaining nut inside pump can. There were two set screws for the retaining nut but were not found in the area. We reached out to Southwest Electric Co. and responded as follows: "I wanted to send the email and express my apologies for the set screws being left out of the coupling on the 900 hp we just returned to the Seminole power plant. I have reviewed the issue with the mechanics that installed the coupling the morning that it left out of here and they confirmed that we did in fact fail to install the set screws. I have attached a picture of the coupling that we took upon receipt of the motor for us to reference the position of the coupling on the shaft. This picture does not show well the set screws installed in the coupling. We failed to properly relay to the technician installing the coupling that the locking ring required two set screws to hold the ring in place. We will alter our picture documentation to show the full face of the coupling from a direct on angle to try and eliminate this from happening again. Please let me know if you have any other questions and I apologize again for any inconvenience this has caused. I have CC’d both of our VP’s of Sales and Production regarding this matter." | Kelly Casey | Justin Stahl |  | Seminole PP; EGX Gath/Trans | FALSE |  | TRUE | Maintenance |  | Matthew Cox | Justin Stahl |  | Paul Schoelen | Review Complete | Paul Schoelen | Jesse Murray | High | [11 empty] | 12.01.3 Inadequate preventative adjustment/assembly |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Retaining nut did not have set screws installed when returned from vendor. | 03. Failure to Secure | 9. Abnormal Operation | I Approve. Jesse Murray | Reviewed. | [90 empty] | 9580498
8733 | Seminole PP; EGX Gath/Trans | 2019-02-27 14:30 | 3A Condensate Pump coupling retaining nut was found off the shaft without set screws. Motor had been tested for rotation on 2/26/2019 and vibration on 2/27/2019. When members went to couple motor and pump, they discovered the retaining nut had spun off the shaft. | Level 3 |  | TRUE | Member Injury | Donnie Jones | Jesse Murray | Assigning to Stahl due to contractor issue with the parts. | 2019-03-05 13:00 | Power Supply | Justin Stahl | 2019-03-13 17:10 | 2019-02-27 15:20 | 2019-02-27 15:20 | 2019-03-05 14:33 | 2019-03-13 14:30 | 2019-02-27 15:08 | 2019-03-06 12:59 | 2019-03-13 13:21 | 2019-03-05 16:38 | SM03 Basement 3A Condensate Pump |  |  | Donnie Jones | Appreciate the action items you've identified - Donnie | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Justin Stahl |  | Around February 1, 2019 3A Condensate Pump was uncoupled and the motor was sent to Southwest Electric Co. for rebuild. Reliability Technician went to vendor on February 21 to perform FAT. On Friday, February 22, the motor arrived back onsite from vendor. On Thursday, February 26, motor and pump were installed and motor tested for rotation. The following day, Reliability Technician was asked to get baseline readings of motor uncoupled. After the baseline test, the clearance was reinstalled for SSG to set lift and couple motor and pump. Members found retaining nut inside pump can. There were two set screws for the retaining nut but were not found in the area. We reached out to Southwest Electric Co. and responded as follows: "I wanted to send the email and express my apologies for the set screws being left out of the coupling on the 900 hp we just returned to the Seminole power plant. I have reviewed the issue with the mechanics that installed the coupling the morning that it left out of here and they confirmed that we did in fact fail to install the set screws. I have attached a picture of the coupling that we took upon receipt of the motor for us to reference the position of the coupling on the shaft. This picture does not show well the set screws installed in the coupling. We failed to properly relay to the technician installing the coupling that the locking ring required two set screws to hold the ring in place. We will alter our picture documentation to show the full face of the coupling from a direct on angle to try and eliminate this from happening again. Please let me know if you have any other questions and I apologize again for any inconvenience this has caused. I have CC’d both of our VP’s of Sales and Production regarding this matter." | Chrysty Dorsey | Justin Stahl |  | Seminole PP; EGX Gath/Trans | FALSE |  | TRUE | Maintenance |  | Matthew Cox | Justin Stahl |  | Paul Schoelen | Review Complete | Paul Schoelen | Jesse Murray | High | [11 empty] | 12.01.3 Inadequate preventative adjustment/assembly |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Retaining nut did not have set screws installed when returned from vendor. | 03. Failure to Secure | 9. Abnormal Operation | I Approve. Jesse Murray | Reviewed. | [90 empty] | 9580498
8733 | Seminole PP; EGX Gath/Trans | 2019-02-27 14:30 | 3A Condensate Pump coupling retaining nut was found off the shaft without set screws. Motor had been tested for rotation on 2/26/2019 and vibration on 2/27/2019. When members went to couple motor and pump, they discovered the retaining nut had spun off the shaft. | Level 3 |  | TRUE | Member Injury | Donnie Jones | Jesse Murray | Assigning to Stahl due to contractor issue with the parts. | 2019-03-05 13:00 | Power Supply | Justin Stahl | 2019-03-13 17:10 | 2019-02-27 15:20 | 2019-02-27 15:20 | 2019-03-05 14:33 | 2019-03-13 14:30 | 2019-02-27 15:08 | 2019-03-06 12:59 | 2019-03-13 13:21 | 2019-03-05 16:38 | SM03 Basement 3A Condensate Pump |  |  | Donnie Jones | Appreciate the action items you've identified - Donnie | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Justin Stahl |  | Around February 1, 2019 3A Condensate Pump was uncoupled and the motor was sent to Southwest Electric Co. for rebuild. Reliability Technician went to vendor on February 21 to perform FAT. On Friday, February 22, the motor arrived back onsite from vendor. On Thursday, February 26, motor and pump were installed and motor tested for rotation. The following day, Reliability Technician was asked to get baseline readings of motor uncoupled. After the baseline test, the clearance was reinstalled for SSG to set lift and couple motor and pump. Members found retaining nut inside pump can. There were two set screws for the retaining nut but were not found in the area. We reached out to Southwest Electric Co. and responded as follows: "I wanted to send the email and express my apologies for the set screws being left out of the coupling on the 900 hp we just returned to the Seminole power plant. I have reviewed the issue with the mechanics that installed the coupling the morning that it left out of here and they confirmed that we did in fact fail to install the set screws. I have attached a picture of the coupling that we took upon receipt of the motor for us to reference the position of the coupling on the shaft. This picture does not show well the set screws installed in the coupling. We failed to properly relay to the technician installing the coupling that the locking ring required two set screws to hold the ring in place. We will alter our picture documentation to show the full face of the coupling from a direct on angle to try and eliminate this from happening again. Please let me know if you have any other questions and I apologize again for any inconvenience this has caused. I have CC’d both of our VP’s of Sales and Production regarding this matter." | Matthew Cox | Justin Stahl |  | Seminole PP; EGX Gath/Trans | FALSE |  | TRUE | Maintenance |  | Matthew Cox | Justin Stahl |  | Paul Schoelen | Review Complete | Paul Schoelen | Jesse Murray | High | [11 empty] | 12.01.3 Inadequate preventative adjustment/assembly |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Retaining nut did not have set screws installed when returned from vendor. | 03. Failure to Secure | 9. Abnormal Operation | I Approve. Jesse Murray | Reviewed. | [90 empty] | 9580498
8733 | Seminole PP; EGX Gath/Trans | 2019-02-27 14:30 | 3A Condensate Pump coupling retaining nut was found off the shaft without set screws. Motor had been tested for rotation on 2/26/2019 and vibration on 2/27/2019. When members went to couple motor and pump, they discovered the retaining nut had spun off the shaft. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | Assigning to Stahl due to contractor issue with the parts. | 2019-03-05 13:00 | Power Supply | Justin Stahl | 2019-03-13 17:10 | 2019-02-27 15:20 | 2019-02-27 15:20 | 2019-03-05 14:33 | 2019-03-13 14:30 | 2019-02-27 15:08 | 2019-03-06 12:59 | 2019-03-13 13:21 | 2019-03-05 16:38 | SM03 Basement 3A Condensate Pump |  |  | Donnie Jones | Appreciate the action items you've identified - Donnie | Power Supply |  | Level 3 | Property Damage |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Justin Stahl |  | Around February 1, 2019 3A Condensate Pump was uncoupled and the motor was sent to Southwest Electric Co. for rebuild. Reliability Technician went to vendor on February 21 to perform FAT. On Friday, February 22, the motor arrived back onsite from vendor. On Thursday, February 26, motor and pump were installed and motor tested for rotation. The following day, Reliability Technician was asked to get baseline readings of motor uncoupled. After the baseline test, the clearance was reinstalled for SSG to set lift and couple motor and pump. Members found retaining nut inside pump can. There were two set screws for the retaining nut but were not found in the area. We reached out to Southwest Electric Co. and responded as follows: "I wanted to send the email and express my apologies for the set screws being left out of the coupling on the 900 hp we just returned to the Seminole power plant. I have reviewed the issue with the mechanics that installed the coupling the morning that it left out of here and they confirmed that we did in fact fail to install the set screws. I have attached a picture of the coupling that we took upon receipt of the motor for us to reference the position of the coupling on the shaft. This picture does not show well the set screws installed in the coupling. We failed to properly relay to the technician installing the coupling that the locking ring required two set screws to hold the ring in place. We will alter our picture documentation to show the full face of the coupling from a direct on angle to try and eliminate this from happening again. Please let me know if you have any other questions and I apologize again for any inconvenience this has caused. I have CC’d both of our VP’s of Sales and Production regarding this matter." | Kelly Casey | Justin Stahl |  | Seminole PP; EGX Gath/Trans | FALSE |  | TRUE | Maintenance |  | Matthew Cox | Justin Stahl |  | Paul Schoelen | Review Complete | Paul Schoelen | Jesse Murray | High | [11 empty] | 12.01.3 Inadequate preventative adjustment/assembly |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Retaining nut did not have set screws installed when returned from vendor. | 03. Failure to Secure | 9. Abnormal Operation | I Approve. Jesse Murray | Reviewed. | [90 empty] | 9580498
8733 | Seminole PP; EGX Gath/Trans | 2019-02-27 14:30 | 3A Condensate Pump coupling retaining nut was found off the shaft without set screws. Motor had been tested for rotation on 2/26/2019 and vibration on 2/27/2019. When members went to couple motor and pump, they discovered the retaining nut had spun off the shaft. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | Assigning to Stahl due to contractor issue with the parts. | 2019-03-05 13:00 | Power Supply | Justin Stahl | 2019-03-13 17:10 | 2019-02-27 15:20 | 2019-02-27 15:20 | 2019-03-05 14:33 | 2019-03-13 14:30 | 2019-02-27 15:08 | 2019-03-06 12:59 | 2019-03-13 13:21 | 2019-03-05 16:38 | SM03 Basement 3A Condensate Pump |  |  | Donnie Jones | Appreciate the action items you've identified - Donnie | Power Supply |  | Level 3 | Property Damage |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Justin Stahl |  | Around February 1, 2019 3A Condensate Pump was uncoupled and the motor was sent to Southwest Electric Co. for rebuild. Reliability Technician went to vendor on February 21 to perform FAT. On Friday, February 22, the motor arrived back onsite from vendor. On Thursday, February 26, motor and pump were installed and motor tested for rotation. The following day, Reliability Technician was asked to get baseline readings of motor uncoupled. After the baseline test, the clearance was reinstalled for SSG to set lift and couple motor and pump. Members found retaining nut inside pump can. There were two set screws for the retaining nut but were not found in the area. We reached out to Southwest Electric Co. and responded as follows: "I wanted to send the email and express my apologies for the set screws being left out of the coupling on the 900 hp we just returned to the Seminole power plant. I have reviewed the issue with the mechanics that installed the coupling the morning that it left out of here and they confirmed that we did in fact fail to install the set screws. I have attached a picture of the coupling that we took upon receipt of the motor for us to reference the position of the coupling on the shaft. This picture does not show well the set screws installed in the coupling. We failed to properly relay to the technician installing the coupling that the locking ring required two set screws to hold the ring in place. We will alter our picture documentation to show the full face of the coupling from a direct on angle to try and eliminate this from happening again. Please let me know if you have any other questions and I apologize again for any inconvenience this has caused. I have CC’d both of our VP’s of Sales and Production regarding this matter." | Chrysty Dorsey | Justin Stahl |  | Seminole PP; EGX Gath/Trans | FALSE |  | TRUE | Maintenance |  | Matthew Cox | Justin Stahl |  | Paul Schoelen | Review Complete | Paul Schoelen | Jesse Murray | High | [11 empty] | 12.01.3 Inadequate preventative adjustment/assembly |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Retaining nut did not have set screws installed when returned from vendor. | 03. Failure to Secure | 9. Abnormal Operation | I Approve. Jesse Murray | Reviewed. | [90 empty] | 9580498
8733 | Seminole PP; EGX Gath/Trans | 2019-02-27 14:30 | 3A Condensate Pump coupling retaining nut was found off the shaft without set screws. Motor had been tested for rotation on 2/26/2019 and vibration on 2/27/2019. When members went to couple motor and pump, they discovered the retaining nut had spun off the shaft. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | Assigning to Stahl due to contractor issue with the parts. | 2019-03-05 13:00 | Power Supply | Justin Stahl | 2019-03-13 17:10 | 2019-02-27 15:20 | 2019-02-27 15:20 | 2019-03-05 14:33 | 2019-03-13 14:30 | 2019-02-27 15:08 | 2019-03-06 12:59 | 2019-03-13 13:21 | 2019-03-05 16:38 | SM03 Basement 3A Condensate Pump |  |  | Donnie Jones | Appreciate the action items you've identified - Donnie | Power Supply |  | Level 3 | Property Damage |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Justin Stahl |  | Around February 1, 2019 3A Condensate Pump was uncoupled and the motor was sent to Southwest Electric Co. for rebuild. Reliability Technician went to vendor on February 21 to perform FAT. On Friday, February 22, the motor arrived back onsite from vendor. On Thursday, February 26, motor and pump were installed and motor tested for rotation. The following day, Reliability Technician was asked to get baseline readings of motor uncoupled. After the baseline test, the clearance was reinstalled for SSG to set lift and couple motor and pump. Members found retaining nut inside pump can. There were two set screws for the retaining nut but were not found in the area. We reached out to Southwest Electric Co. and responded as follows: "I wanted to send the email and express my apologies for the set screws being left out of the coupling on the 900 hp we just returned to the Seminole power plant. I have reviewed the issue with the mechanics that installed the coupling the morning that it left out of here and they confirmed that we did in fact fail to install the set screws. I have attached a picture of the coupling that we took upon receipt of the motor for us to reference the position of the coupling on the shaft. This picture does not show well the set screws installed in the coupling. We failed to properly relay to the technician installing the coupling that the locking ring required two set screws to hold the ring in place. We will alter our picture documentation to show the full face of the coupling from a direct on angle to try and eliminate this from happening again. Please let me know if you have any other questions and I apologize again for any inconvenience this has caused. I have CC’d both of our VP’s of Sales and Production regarding this matter." | Matthew Cox | Justin Stahl |  | Seminole PP; EGX Gath/Trans | FALSE |  | TRUE | Maintenance |  | Matthew Cox | Justin Stahl |  | Paul Schoelen | Review Complete | Paul Schoelen | Jesse Murray | High | [11 empty] | 12.01.3 Inadequate preventative adjustment/assembly |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Retaining nut did not have set screws installed when returned from vendor. | 03. Failure to Secure | 9. Abnormal Operation | I Approve. Jesse Murray | Reviewed. | [90 empty] | 9580498
8734 | Enid Service Center | 2019-02-27 14:30 | Member driving POV on icy parking lot made contact with company vehicle F01-1069. While member was making turn to leave parking lot his POV lost traction on the ice and slid in to parked company vehicle. No injuries | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Dustin Kingcade | 2019-03-19 10:13 | 2019-02-27 15:28 | 2019-02-27 15:28 | 2019-03-18 11:27 | 2019-03-13 14:30 | 2019-02-27 14:57 | 2019-03-18 13:53 |  |  | Enid Service Center parking lots North gate. |  |  | Cody Magby | I approve cm | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | TRUE |  | FALSE | TRUE | Dustin Kingcade |  | Icy parking lot caused a loss of traction while making the turn out of parking area. This resulted in POV driven by member coming in contact with F01-1069. |  |  |  | Enid Service Center | FALSE |  | FALSE | PD Operations Services |  | Lee Olmstead | Dustin Kingcade |  | James Hutchison | I have reviewed this incident report and concur with it's findings and corrective actions. | James Hutchison |  | Low | [6 empty] | 7.03 Lack of incentives | [9 empty] | Member driving POV on icy parking lot made contact with company vehicle F01-1069. While member was making turn to leave parking lot his POV lost traction on the ice and slid in to parked company vehicle. No injuries | 39. Road Conditions | 1. Struck Against (Running or Bumping Into) | [68 empty] | Front Passenger side fender. | 1000 | Lee Olmstead | Vehicle (not related to operation of vehicle) |  | F01-1069 | FALSE |  | Enid | Public Vehicle Struck OGE | OGE Vehicle Stopped/Parked | 2017-08-27 19:00 |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Fog |  |  | none
8734 | Enid Service Center | 2019-02-27 14:30 | Member driving POV on icy parking lot made contact with company vehicle F01-1069. While member was making turn to leave parking lot his POV lost traction on the ice and slid in to parked company vehicle. No injuries | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Delivery | Dustin Kingcade | 2019-03-19 10:13 | 2019-02-27 15:28 | 2019-02-27 15:28 | 2019-03-18 11:27 | 2019-03-13 14:30 | 2019-02-27 14:57 | 2019-03-18 13:53 |  |  | Enid Service Center parking lots North gate. |  |  | Cody Magby | I approve cm | T&D Ops |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | TRUE | Dustin Kingcade |  | Icy parking lot caused a loss of traction while making the turn out of parking area. This resulted in POV driven by member coming in contact with F01-1069. |  |  |  | Enid Service Center | FALSE |  | FALSE | PD Operations Services |  | Lee Olmstead | Dustin Kingcade |  | James Hutchison | I have reviewed this incident report and concur with it's findings and corrective actions. | James Hutchison |  | Low | [6 empty] | 7.03 Lack of incentives | [9 empty] | Member driving POV on icy parking lot made contact with company vehicle F01-1069. While member was making turn to leave parking lot his POV lost traction on the ice and slid in to parked company vehicle. No injuries | 39. Road Conditions | 1. Struck Against (Running or Bumping Into) | [68 empty] | Front Passenger side fender. | 1000 | Lee Olmstead | Vehicle (not related to operation of vehicle) |  | F01-1069 | FALSE |  | Enid | Public Vehicle Struck OGE | OGE Vehicle Stopped/Parked | 2017-08-27 19:00 |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Fog |  |  | none
8735 | Metro Service Center | 2019-02-28 08:30 | Arc flash occurred while checking voltage. | Level 4 |  | FALSE | Member Injury |  | Jerrod Moser | This incident is being conducting at the direction of counsel. | 2019-03-04 07:33 | Power Delivery | Terry Hackett | 2019-04-12 14:24 | 2019-02-28 15:37 | 2019-02-28 15:37 | 2019-04-02 15:21 | 2019-04-08 | 2019-02-28 15:24 | 2019-04-10 14:06 |  |  | Tinker AFB B210 |  |  | Jerrod Moser | Approve | T&D Ops |  | Level 4 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Terry Hackett |  | Details of scenario preceding incident. Two OGE Journeymen linemen were performing the restoration phase of an outage request for building B210 at Tinker Air Force Base. Members completed tailboard for the job of energizing stepdown transformer 344755. Stepdown transformer 344755 which feeds building B210 was successfully energized by the members closing switches in cubicle 344790 SW#3. At this time members went beyond the point of demarcation into building B210 to perform voltage check on 4160 VAC Soft Starter. Member #1 used a 1000 VAC Fluke multimeter with his Class 2 (17KV) rubber gloves with class 2 leather protectors to check the voltage of the 4160 VAC equipment. The multimeter was destroyed due to being overloaded and a large phase to phase flash occurred in the equipment. This resulted in both members receiving 2nd degree burns, the equipment being damaged, and two blown fuses. Transformer 344755 steps down voltage from 12.5KV to 4160V. The transformer is labeled with the point of demarcation as the secondary spades of the transformer (see picture). Both members are journeymen linemen. Both members stated they thought the equipment was 480 volts which is common for our stepdown transformers and that is why the 1000-volt fluke multimeter was used. Members went beyond the point of demarcation into building B210. Shawver and Sons employee told member #1 that he did not have rubber glove to test the customer owned equipment. Member #1 felt like he was being asked to conduct the testing and proceeded to climb the 6’ A frame ladder that was set up in front of the equipment where the panel was removed. Member #1 pointed out the equipment did not have a neutral, so Member #2 looked into the equipment from the ground. At this time Member #1 touched his probes on one phase and then another. The multimeter shorted out and caused a phase to phase arc flash. Two Schawver employees were standing out of the Arc Flash Boundary. After the arc flash occurred the Schawver employees called 911. The injured members were transported by ambulance to the Integris Hospital. Where they were treated and released. Immediately Following the incident, OGE stopped all work, secured the scene, and made the area safe by isolating, grounding, locking, and tagging transformer 344755. Incident Details: Member #1 performing the testing was wearing HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans Class 2 (17KV) Rubber Gloves, Class 2 Leather Protectors, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #2 observing the testing was wearing HRC 2 Sleeveless Vest, HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans, HRC 2 Beanie, HRC2 Balaclava, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #1’s Class 2 rubber gloves (25489 & 25570) were dielectrically tested on 08-16-2018 Salisbury Model AS1000 Arc Rated 10 Cal face shield, Tyndale 11 Cal/CM2 Balaclava, and 20 cal/cm2 suit was readily available on the truck. Members had been trained on OGE SOP.TDO.015 Arc Flash Burn Prevention PPE and Clothing requirements, which prohibits working past the point of demarcation unless an arc flash study has been completed and members are wearing the appropriately rated category of FR clothing. This SOP also requires an arc rated face shield when working on 480 Volt cabinets that are a part of the OGE system. Member #1 Obtained journeyman status on 12/1/2009. Member #2 Obtained journeyman status on 7/29/2016. Member #1 used a 1000 Volt Fluke Multimeter to test voltage on the Customer Owned Benshaw 4160 VAC Soft Starter Model No: CFMVRMX18-3000-4160-12 Hard Hat: Bullard Classic Model C-33 Type 1 Leather protectors: Kunz Glove Size 10.5 #1005 Rubber Glove#’s: Salisbury size 10 class 2 (Internal ID# 25489 & 25570) Both members wore ANSI Z-87 Safety Glasses 1000 Volt Fluke Multimeter T5-1000 was used Documented work observations could not be provided Documented review of SOP.TDO.015 Arc Flash Burn Prevention could not be provided SOP.TDO.015 was set up to be an every other year review, but has not been on the SOP review calendar since 2014 Max incident energy was calculated at 1.9 cal/cm2 (see attachment FW: Tinker4_Arc Flash Results) | William Wilson | Terry Hackett | FALSE | Metro Service Center | TRUE |  | FALSE | Construction Services |  | Payton Martin | Carl Kemp |  |  | Approve |  |  | Very High | [7 empty] | 8.1.2 Improper conduct that is condoned: Unintentional | [5 empty] | 14.04 Inadequate monitoring of compliance |  |  | Supervisor did not have documentation for required annual work observations. Currently work observations are conducted in paper form and are stored in supervisors safety files. This makes it difficult for the company to verify full compliance. | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation | [26 empty] | FALSE |  | Days away from Work (H) | 2000-03-27 | 1978-05-15 |  | 2019-03-28 07:00 | 24 | 0 |  | FALSE | Male | 1000 volt fluke multimeter short circuited due to being overloaded by the 4160 VAC and caused a phase to phase Arc Flash |  | FALSE | James Caldwell |  | Days Away from Work | James Caldwell | TRUE |  | Baptist Hospital |  | Burn: Electrical | Released to full duty eff 3/25/19 per F. Davis. | TRUE |  | Lineman | Face | Injury | Multiple | TRUE | Carl Kemp | TRUE | 2019 | 3/28/2019 7:30:00 AM | 9 | TRUE | FALSE | TRUE | Arc Flash | Testing Voltage on 4160 VAC Soft Starter | [24 empty] | NA
8735 | Metro Service Center | 2019-02-28 08:30 | Arc flash occurred while checking voltage. | Level 4 |  | FALSE | Member Injury |  | Jerrod Moser | This incident is being conducting at the direction of counsel. | 2019-03-04 07:33 | Power Delivery | Terry Hackett | 2019-04-12 14:24 | 2019-02-28 15:37 | 2019-02-28 15:37 | 2019-04-02 15:21 | 2019-04-08 | 2019-02-28 15:24 | 2019-04-10 14:06 |  |  | Tinker AFB B210 |  |  | Jerrod Moser | Approve | T&D Ops |  | Level 4 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Terry Hackett |  | Details of scenario preceding incident. Two OGE Journeymen linemen were performing the restoration phase of an outage request for building B210 at Tinker Air Force Base. Members completed tailboard for the job of energizing stepdown transformer 344755. Stepdown transformer 344755 which feeds building B210 was successfully energized by the members closing switches in cubicle 344790 SW#3. At this time members went beyond the point of demarcation into building B210 to perform voltage check on 4160 VAC Soft Starter. Member #1 used a 1000 VAC Fluke multimeter with his Class 2 (17KV) rubber gloves with class 2 leather protectors to check the voltage of the 4160 VAC equipment. The multimeter was destroyed due to being overloaded and a large phase to phase flash occurred in the equipment. This resulted in both members receiving 2nd degree burns, the equipment being damaged, and two blown fuses. Transformer 344755 steps down voltage from 12.5KV to 4160V. The transformer is labeled with the point of demarcation as the secondary spades of the transformer (see picture). Both members are journeymen linemen. Both members stated they thought the equipment was 480 volts which is common for our stepdown transformers and that is why the 1000-volt fluke multimeter was used. Members went beyond the point of demarcation into building B210. Shawver and Sons employee told member #1 that he did not have rubber glove to test the customer owned equipment. Member #1 felt like he was being asked to conduct the testing and proceeded to climb the 6’ A frame ladder that was set up in front of the equipment where the panel was removed. Member #1 pointed out the equipment did not have a neutral, so Member #2 looked into the equipment from the ground. At this time Member #1 touched his probes on one phase and then another. The multimeter shorted out and caused a phase to phase arc flash. Two Schawver employees were standing out of the Arc Flash Boundary. After the arc flash occurred the Schawver employees called 911. The injured members were transported by ambulance to the Integris Hospital. Where they were treated and released. Immediately Following the incident, OGE stopped all work, secured the scene, and made the area safe by isolating, grounding, locking, and tagging transformer 344755. Incident Details: Member #1 performing the testing was wearing HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans Class 2 (17KV) Rubber Gloves, Class 2 Leather Protectors, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #2 observing the testing was wearing HRC 2 Sleeveless Vest, HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans, HRC 2 Beanie, HRC2 Balaclava, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #1’s Class 2 rubber gloves (25489 & 25570) were dielectrically tested on 08-16-2018 Salisbury Model AS1000 Arc Rated 10 Cal face shield, Tyndale 11 Cal/CM2 Balaclava, and 20 cal/cm2 suit was readily available on the truck. Members had been trained on OGE SOP.TDO.015 Arc Flash Burn Prevention PPE and Clothing requirements, which prohibits working past the point of demarcation unless an arc flash study has been completed and members are wearing the appropriately rated category of FR clothing. This SOP also requires an arc rated face shield when working on 480 Volt cabinets that are a part of the OGE system. Member #1 Obtained journeyman status on 12/1/2009. Member #2 Obtained journeyman status on 7/29/2016. Member #1 used a 1000 Volt Fluke Multimeter to test voltage on the Customer Owned Benshaw 4160 VAC Soft Starter Model No: CFMVRMX18-3000-4160-12 Hard Hat: Bullard Classic Model C-33 Type 1 Leather protectors: Kunz Glove Size 10.5 #1005 Rubber Glove#’s: Salisbury size 10 class 2 (Internal ID# 25489 & 25570) Both members wore ANSI Z-87 Safety Glasses 1000 Volt Fluke Multimeter T5-1000 was used Documented work observations could not be provided Documented review of SOP.TDO.015 Arc Flash Burn Prevention could not be provided SOP.TDO.015 was set up to be an every other year review, but has not been on the SOP review calendar since 2014 Max incident energy was calculated at 1.9 cal/cm2 (see attachment FW: Tinker4_Arc Flash Results) | William Wilson | Terry Hackett | FALSE | Metro Service Center | TRUE |  | FALSE | Construction Services |  | Payton Martin | Carl Kemp |  |  | Approve |  |  | Very High | [7 empty] | 8.1.2 Improper conduct that is condoned: Unintentional | [5 empty] | 14.04 Inadequate monitoring of compliance |  |  | Supervisor did not have documentation for required annual work observations. Currently work observations are conducted in paper form and are stored in supervisors safety files. This makes it difficult for the company to verify full compliance. | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation | [26 empty] | FALSE |  | Days away from Work (H) | 2008-04-21 | 1986-11-26 |  | 2019-03-28 07:00 | 31 | 78 |  | FALSE | Male | Arc Flash |  | FALSE | Payton Martin |  | Days Away from Work | Payton Martin | TRUE |  | Baptist Hospital Burn Unit |  | Burn: Electrical | Dr visit 3/29: Release to light duty eff 4/1/19 per F. Davis Released to full duty eff 6/18/19 | TRUE |  | Lineman | Hand | Injury | Left | TRUE | Carl Kemp | TRUE | 2019 | 3/28/2019 7:30:00 AM | 2.5 | TRUE | FALSE | TRUE | Arc Flash | Holding Ladder for member to test voltage in 4160 VAC Soft Starter | [24 empty] | NA
8735 | Metro Service Center | 2019-02-28 08:30 | Arc flash occurred while checking voltage. | Level 4 |  | FALSE | Member Injury |  | Jerrod Moser | This incident is being conducting at the direction of counsel. | 2019-03-04 07:33 | Power Delivery | Terry Hackett | 2019-04-12 14:24 | 2019-02-28 15:37 | 2019-02-28 15:37 | 2019-04-02 15:21 | 2019-04-08 | 2019-02-28 15:24 | 2019-04-10 14:06 |  |  | Tinker AFB B210 |  |  | Jerrod Moser | Approve | T&D Ops |  | Level 4 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Terry Hackett |  | Details of scenario preceding incident. Two OGE Journeymen linemen were performing the restoration phase of an outage request for building B210 at Tinker Air Force Base. Members completed tailboard for the job of energizing stepdown transformer 344755. Stepdown transformer 344755 which feeds building B210 was successfully energized by the members closing switches in cubicle 344790 SW#3. At this time members went beyond the point of demarcation into building B210 to perform voltage check on 4160 VAC Soft Starter. Member #1 used a 1000 VAC Fluke multimeter with his Class 2 (17KV) rubber gloves with class 2 leather protectors to check the voltage of the 4160 VAC equipment. The multimeter was destroyed due to being overloaded and a large phase to phase flash occurred in the equipment. This resulted in both members receiving 2nd degree burns, the equipment being damaged, and two blown fuses. Transformer 344755 steps down voltage from 12.5KV to 4160V. The transformer is labeled with the point of demarcation as the secondary spades of the transformer (see picture). Both members are journeymen linemen. Both members stated they thought the equipment was 480 volts which is common for our stepdown transformers and that is why the 1000-volt fluke multimeter was used. Members went beyond the point of demarcation into building B210. Shawver and Sons employee told member #1 that he did not have rubber glove to test the customer owned equipment. Member #1 felt like he was being asked to conduct the testing and proceeded to climb the 6’ A frame ladder that was set up in front of the equipment where the panel was removed. Member #1 pointed out the equipment did not have a neutral, so Member #2 looked into the equipment from the ground. At this time Member #1 touched his probes on one phase and then another. The multimeter shorted out and caused a phase to phase arc flash. Two Schawver employees were standing out of the Arc Flash Boundary. After the arc flash occurred the Schawver employees called 911. The injured members were transported by ambulance to the Integris Hospital. Where they were treated and released. Immediately Following the incident, OGE stopped all work, secured the scene, and made the area safe by isolating, grounding, locking, and tagging transformer 344755. Incident Details: Member #1 performing the testing was wearing HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans Class 2 (17KV) Rubber Gloves, Class 2 Leather Protectors, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #2 observing the testing was wearing HRC 2 Sleeveless Vest, HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans, HRC 2 Beanie, HRC2 Balaclava, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #1’s Class 2 rubber gloves (25489 & 25570) were dielectrically tested on 08-16-2018 Salisbury Model AS1000 Arc Rated 10 Cal face shield, Tyndale 11 Cal/CM2 Balaclava, and 20 cal/cm2 suit was readily available on the truck. Members had been trained on OGE SOP.TDO.015 Arc Flash Burn Prevention PPE and Clothing requirements, which prohibits working past the point of demarcation unless an arc flash study has been completed and members are wearing the appropriately rated category of FR clothing. This SOP also requires an arc rated face shield when working on 480 Volt cabinets that are a part of the OGE system. Member #1 Obtained journeyman status on 12/1/2009. Member #2 Obtained journeyman status on 7/29/2016. Member #1 used a 1000 Volt Fluke Multimeter to test voltage on the Customer Owned Benshaw 4160 VAC Soft Starter Model No: CFMVRMX18-3000-4160-12 Hard Hat: Bullard Classic Model C-33 Type 1 Leather protectors: Kunz Glove Size 10.5 #1005 Rubber Glove#’s: Salisbury size 10 class 2 (Internal ID# 25489 & 25570) Both members wore ANSI Z-87 Safety Glasses 1000 Volt Fluke Multimeter T5-1000 was used Documented work observations could not be provided Documented review of SOP.TDO.015 Arc Flash Burn Prevention could not be provided SOP.TDO.015 was set up to be an every other year review, but has not been on the SOP review calendar since 2014 Max incident energy was calculated at 1.9 cal/cm2 (see attachment FW: Tinker4_Arc Flash Results) | William Wilson | Terry Hackett | FALSE | Metro Service Center | TRUE |  | FALSE | Construction Services |  | Payton Martin | Carl Kemp |  |  | Approve |  |  | Very High | [6 empty] | 7.10 Inappropriate peer pressure | 8.1.2 Improper conduct that is condoned: Unintentional | [8 empty] | Member's went past the point of demarcation which was labeled as the secondary spades of the stepdown transformer. Member's felt pressure to assist customer. SOP.TDO.015 Arc Flash Burn Prevention and Clothing Requirements does not allow members to go past the point of demarcation without a formal arc flash study and the proper category of FR clothing. | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation | [26 empty] | FALSE |  | Days away from Work (H) | 2000-03-27 | 1978-05-15 |  | 2019-03-28 07:00 | 24 | 0 |  | FALSE | Male | 1000 volt fluke multimeter short circuited due to being overloaded by the 4160 VAC and caused a phase to phase Arc Flash |  | FALSE | James Caldwell |  | Days Away from Work | James Caldwell | TRUE |  | Baptist Hospital |  | Burn: Electrical | Released to full duty eff 3/25/19 per F. Davis. | TRUE |  | Lineman | Face | Injury | Multiple | TRUE | Carl Kemp | TRUE | 2019 | 3/28/2019 7:30:00 AM | 9 | TRUE | FALSE | TRUE | Arc Flash | Testing Voltage on 4160 VAC Soft Starter | [24 empty] | NA
8735 | Metro Service Center | 2019-02-28 08:30 | Arc flash occurred while checking voltage. | Level 4 |  | FALSE | Member Injury |  | Jerrod Moser | This incident is being conducting at the direction of counsel. | 2019-03-04 07:33 | Power Delivery | Terry Hackett | 2019-04-12 14:24 | 2019-02-28 15:37 | 2019-02-28 15:37 | 2019-04-02 15:21 | 2019-04-08 | 2019-02-28 15:24 | 2019-04-10 14:06 |  |  | Tinker AFB B210 |  |  | Jerrod Moser | Approve | T&D Ops |  | Level 4 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Terry Hackett |  | Details of scenario preceding incident. Two OGE Journeymen linemen were performing the restoration phase of an outage request for building B210 at Tinker Air Force Base. Members completed tailboard for the job of energizing stepdown transformer 344755. Stepdown transformer 344755 which feeds building B210 was successfully energized by the members closing switches in cubicle 344790 SW#3. At this time members went beyond the point of demarcation into building B210 to perform voltage check on 4160 VAC Soft Starter. Member #1 used a 1000 VAC Fluke multimeter with his Class 2 (17KV) rubber gloves with class 2 leather protectors to check the voltage of the 4160 VAC equipment. The multimeter was destroyed due to being overloaded and a large phase to phase flash occurred in the equipment. This resulted in both members receiving 2nd degree burns, the equipment being damaged, and two blown fuses. Transformer 344755 steps down voltage from 12.5KV to 4160V. The transformer is labeled with the point of demarcation as the secondary spades of the transformer (see picture). Both members are journeymen linemen. Both members stated they thought the equipment was 480 volts which is common for our stepdown transformers and that is why the 1000-volt fluke multimeter was used. Members went beyond the point of demarcation into building B210. Shawver and Sons employee told member #1 that he did not have rubber glove to test the customer owned equipment. Member #1 felt like he was being asked to conduct the testing and proceeded to climb the 6’ A frame ladder that was set up in front of the equipment where the panel was removed. Member #1 pointed out the equipment did not have a neutral, so Member #2 looked into the equipment from the ground. At this time Member #1 touched his probes on one phase and then another. The multimeter shorted out and caused a phase to phase arc flash. Two Schawver employees were standing out of the Arc Flash Boundary. After the arc flash occurred the Schawver employees called 911. The injured members were transported by ambulance to the Integris Hospital. Where they were treated and released. Immediately Following the incident, OGE stopped all work, secured the scene, and made the area safe by isolating, grounding, locking, and tagging transformer 344755. Incident Details: Member #1 performing the testing was wearing HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans Class 2 (17KV) Rubber Gloves, Class 2 Leather Protectors, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #2 observing the testing was wearing HRC 2 Sleeveless Vest, HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans, HRC 2 Beanie, HRC2 Balaclava, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #1’s Class 2 rubber gloves (25489 & 25570) were dielectrically tested on 08-16-2018 Salisbury Model AS1000 Arc Rated 10 Cal face shield, Tyndale 11 Cal/CM2 Balaclava, and 20 cal/cm2 suit was readily available on the truck. Members had been trained on OGE SOP.TDO.015 Arc Flash Burn Prevention PPE and Clothing requirements, which prohibits working past the point of demarcation unless an arc flash study has been completed and members are wearing the appropriately rated category of FR clothing. This SOP also requires an arc rated face shield when working on 480 Volt cabinets that are a part of the OGE system. Member #1 Obtained journeyman status on 12/1/2009. Member #2 Obtained journeyman status on 7/29/2016. Member #1 used a 1000 Volt Fluke Multimeter to test voltage on the Customer Owned Benshaw 4160 VAC Soft Starter Model No: CFMVRMX18-3000-4160-12 Hard Hat: Bullard Classic Model C-33 Type 1 Leather protectors: Kunz Glove Size 10.5 #1005 Rubber Glove#’s: Salisbury size 10 class 2 (Internal ID# 25489 & 25570) Both members wore ANSI Z-87 Safety Glasses 1000 Volt Fluke Multimeter T5-1000 was used Documented work observations could not be provided Documented review of SOP.TDO.015 Arc Flash Burn Prevention could not be provided SOP.TDO.015 was set up to be an every other year review, but has not been on the SOP review calendar since 2014 Max incident energy was calculated at 1.9 cal/cm2 (see attachment FW: Tinker4_Arc Flash Results) | William Wilson | Terry Hackett | FALSE | Metro Service Center | TRUE |  | FALSE | Construction Services |  | Payton Martin | Carl Kemp |  |  | Approve |  |  | Very High | [6 empty] | 7.10 Inappropriate peer pressure | 8.1.2 Improper conduct that is condoned: Unintentional | [8 empty] | Member's went past the point of demarcation which was labeled as the secondary spades of the stepdown transformer. Member's felt pressure to assist customer. SOP.TDO.015 Arc Flash Burn Prevention and Clothing Requirements does not allow members to go past the point of demarcation without a formal arc flash study and the proper category of FR clothing. | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation | [26 empty] | FALSE |  | Days away from Work (H) | 2008-04-21 | 1986-11-26 |  | 2019-03-28 07:00 | 31 | 78 |  | FALSE | Male | Arc Flash |  | FALSE | Payton Martin |  | Days Away from Work | Payton Martin | TRUE |  | Baptist Hospital Burn Unit |  | Burn: Electrical | Dr visit 3/29: Release to light duty eff 4/1/19 per F. Davis Released to full duty eff 6/18/19 | TRUE |  | Lineman | Hand | Injury | Left | TRUE | Carl Kemp | TRUE | 2019 | 3/28/2019 7:30:00 AM | 2.5 | TRUE | FALSE | TRUE | Arc Flash | Holding Ladder for member to test voltage in 4160 VAC Soft Starter | [24 empty] | NA
8735 | Metro Service Center | 2019-02-28 08:30 | Arc flash occurred while checking voltage. | Level 4 |  | FALSE | Member Injury |  | Jerrod Moser | This incident is being conducting at the direction of counsel. | 2019-03-04 07:33 | Power Delivery | Terry Hackett | 2019-04-12 14:24 | 2019-02-28 15:37 | 2019-02-28 15:37 | 2019-04-02 15:21 | 2019-04-08 | 2019-02-28 15:24 | 2019-04-10 14:06 |  |  | Tinker AFB B210 |  |  | Jerrod Moser | Approve | T&D Ops |  | Level 4 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Terry Hackett |  | Details of scenario preceding incident. Two OGE Journeymen linemen were performing the restoration phase of an outage request for building B210 at Tinker Air Force Base. Members completed tailboard for the job of energizing stepdown transformer 344755. Stepdown transformer 344755 which feeds building B210 was successfully energized by the members closing switches in cubicle 344790 SW#3. At this time members went beyond the point of demarcation into building B210 to perform voltage check on 4160 VAC Soft Starter. Member #1 used a 1000 VAC Fluke multimeter with his Class 2 (17KV) rubber gloves with class 2 leather protectors to check the voltage of the 4160 VAC equipment. The multimeter was destroyed due to being overloaded and a large phase to phase flash occurred in the equipment. This resulted in both members receiving 2nd degree burns, the equipment being damaged, and two blown fuses. Transformer 344755 steps down voltage from 12.5KV to 4160V. The transformer is labeled with the point of demarcation as the secondary spades of the transformer (see picture). Both members are journeymen linemen. Both members stated they thought the equipment was 480 volts which is common for our stepdown transformers and that is why the 1000-volt fluke multimeter was used. Members went beyond the point of demarcation into building B210. Shawver and Sons employee told member #1 that he did not have rubber glove to test the customer owned equipment. Member #1 felt like he was being asked to conduct the testing and proceeded to climb the 6’ A frame ladder that was set up in front of the equipment where the panel was removed. Member #1 pointed out the equipment did not have a neutral, so Member #2 looked into the equipment from the ground. At this time Member #1 touched his probes on one phase and then another. The multimeter shorted out and caused a phase to phase arc flash. Two Schawver employees were standing out of the Arc Flash Boundary. After the arc flash occurred the Schawver employees called 911. The injured members were transported by ambulance to the Integris Hospital. Where they were treated and released. Immediately Following the incident, OGE stopped all work, secured the scene, and made the area safe by isolating, grounding, locking, and tagging transformer 344755. Incident Details: Member #1 performing the testing was wearing HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans Class 2 (17KV) Rubber Gloves, Class 2 Leather Protectors, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #2 observing the testing was wearing HRC 2 Sleeveless Vest, HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans, HRC 2 Beanie, HRC2 Balaclava, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #1’s Class 2 rubber gloves (25489 & 25570) were dielectrically tested on 08-16-2018 Salisbury Model AS1000 Arc Rated 10 Cal face shield, Tyndale 11 Cal/CM2 Balaclava, and 20 cal/cm2 suit was readily available on the truck. Members had been trained on OGE SOP.TDO.015 Arc Flash Burn Prevention PPE and Clothing requirements, which prohibits working past the point of demarcation unless an arc flash study has been completed and members are wearing the appropriately rated category of FR clothing. This SOP also requires an arc rated face shield when working on 480 Volt cabinets that are a part of the OGE system. Member #1 Obtained journeyman status on 12/1/2009. Member #2 Obtained journeyman status on 7/29/2016. Member #1 used a 1000 Volt Fluke Multimeter to test voltage on the Customer Owned Benshaw 4160 VAC Soft Starter Model No: CFMVRMX18-3000-4160-12 Hard Hat: Bullard Classic Model C-33 Type 1 Leather protectors: Kunz Glove Size 10.5 #1005 Rubber Glove#’s: Salisbury size 10 class 2 (Internal ID# 25489 & 25570) Both members wore ANSI Z-87 Safety Glasses 1000 Volt Fluke Multimeter T5-1000 was used Documented work observations could not be provided Documented review of SOP.TDO.015 Arc Flash Burn Prevention could not be provided SOP.TDO.015 was set up to be an every other year review, but has not been on the SOP review calendar since 2014 Max incident energy was calculated at 1.9 cal/cm2 (see attachment FW: Tinker4_Arc Flash Results) | William Wilson | Terry Hackett | FALSE | Metro Service Center | TRUE |  | FALSE | Construction Services |  | Payton Martin | Carl Kemp |  |  | Approve |  |  | Very High |  |  |  | 4.05 Extreme concentration/perception demands | [9 empty] | 14.04 Inadequate monitoring of compliance |  |  | Arc Flash PPE and Clothing Requirements SOP was ranked as high priority and the determination to put it on the SOP Review calendar every other year was made. Building the SOP review calendar was contracted out and Arc Flash PPE and Clothing Requirements SOP was not added accordingly. Initial review was conducted in 2014. | 18. Failure to Check, Monitor | 9. Abnormal Operation | [26 empty] | FALSE |  | Days away from Work (H) | 2000-03-27 | 1978-05-15 |  | 2019-03-28 07:00 | 24 | 0 |  | FALSE | Male | 1000 volt fluke multimeter short circuited due to being overloaded by the 4160 VAC and caused a phase to phase Arc Flash |  | FALSE | James Caldwell |  | Days Away from Work | James Caldwell | TRUE |  | Baptist Hospital |  | Burn: Electrical | Released to full duty eff 3/25/19 per F. Davis. | TRUE |  | Lineman | Face | Injury | Multiple | TRUE | Carl Kemp | TRUE | 2019 | 3/28/2019 7:30:00 AM | 9 | TRUE | FALSE | TRUE | Arc Flash | Testing Voltage on 4160 VAC Soft Starter | [24 empty] | NA
8735 | Metro Service Center | 2019-02-28 08:30 | Arc flash occurred while checking voltage. | Level 4 |  | FALSE | Member Injury |  | Jerrod Moser | This incident is being conducting at the direction of counsel. | 2019-03-04 07:33 | Power Delivery | Terry Hackett | 2019-04-12 14:24 | 2019-02-28 15:37 | 2019-02-28 15:37 | 2019-04-02 15:21 | 2019-04-08 | 2019-02-28 15:24 | 2019-04-10 14:06 |  |  | Tinker AFB B210 |  |  | Jerrod Moser | Approve | T&D Ops |  | Level 4 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Terry Hackett |  | Details of scenario preceding incident. Two OGE Journeymen linemen were performing the restoration phase of an outage request for building B210 at Tinker Air Force Base. Members completed tailboard for the job of energizing stepdown transformer 344755. Stepdown transformer 344755 which feeds building B210 was successfully energized by the members closing switches in cubicle 344790 SW#3. At this time members went beyond the point of demarcation into building B210 to perform voltage check on 4160 VAC Soft Starter. Member #1 used a 1000 VAC Fluke multimeter with his Class 2 (17KV) rubber gloves with class 2 leather protectors to check the voltage of the 4160 VAC equipment. The multimeter was destroyed due to being overloaded and a large phase to phase flash occurred in the equipment. This resulted in both members receiving 2nd degree burns, the equipment being damaged, and two blown fuses. Transformer 344755 steps down voltage from 12.5KV to 4160V. The transformer is labeled with the point of demarcation as the secondary spades of the transformer (see picture). Both members are journeymen linemen. Both members stated they thought the equipment was 480 volts which is common for our stepdown transformers and that is why the 1000-volt fluke multimeter was used. Members went beyond the point of demarcation into building B210. Shawver and Sons employee told member #1 that he did not have rubber glove to test the customer owned equipment. Member #1 felt like he was being asked to conduct the testing and proceeded to climb the 6’ A frame ladder that was set up in front of the equipment where the panel was removed. Member #1 pointed out the equipment did not have a neutral, so Member #2 looked into the equipment from the ground. At this time Member #1 touched his probes on one phase and then another. The multimeter shorted out and caused a phase to phase arc flash. Two Schawver employees were standing out of the Arc Flash Boundary. After the arc flash occurred the Schawver employees called 911. The injured members were transported by ambulance to the Integris Hospital. Where they were treated and released. Immediately Following the incident, OGE stopped all work, secured the scene, and made the area safe by isolating, grounding, locking, and tagging transformer 344755. Incident Details: Member #1 performing the testing was wearing HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans Class 2 (17KV) Rubber Gloves, Class 2 Leather Protectors, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #2 observing the testing was wearing HRC 2 Sleeveless Vest, HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans, HRC 2 Beanie, HRC2 Balaclava, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #1’s Class 2 rubber gloves (25489 & 25570) were dielectrically tested on 08-16-2018 Salisbury Model AS1000 Arc Rated 10 Cal face shield, Tyndale 11 Cal/CM2 Balaclava, and 20 cal/cm2 suit was readily available on the truck. Members had been trained on OGE SOP.TDO.015 Arc Flash Burn Prevention PPE and Clothing requirements, which prohibits working past the point of demarcation unless an arc flash study has been completed and members are wearing the appropriately rated category of FR clothing. This SOP also requires an arc rated face shield when working on 480 Volt cabinets that are a part of the OGE system. Member #1 Obtained journeyman status on 12/1/2009. Member #2 Obtained journeyman status on 7/29/2016. Member #1 used a 1000 Volt Fluke Multimeter to test voltage on the Customer Owned Benshaw 4160 VAC Soft Starter Model No: CFMVRMX18-3000-4160-12 Hard Hat: Bullard Classic Model C-33 Type 1 Leather protectors: Kunz Glove Size 10.5 #1005 Rubber Glove#’s: Salisbury size 10 class 2 (Internal ID# 25489 & 25570) Both members wore ANSI Z-87 Safety Glasses 1000 Volt Fluke Multimeter T5-1000 was used Documented work observations could not be provided Documented review of SOP.TDO.015 Arc Flash Burn Prevention could not be provided SOP.TDO.015 was set up to be an every other year review, but has not been on the SOP review calendar since 2014 Max incident energy was calculated at 1.9 cal/cm2 (see attachment FW: Tinker4_Arc Flash Results) | William Wilson | Terry Hackett | FALSE | Metro Service Center | TRUE |  | FALSE | Construction Services |  | Payton Martin | Carl Kemp |  |  | Approve |  |  | Very High |  |  |  | 4.05 Extreme concentration/perception demands | [9 empty] | 14.04 Inadequate monitoring of compliance |  |  | Arc Flash PPE and Clothing Requirements SOP was ranked as high priority and the determination to put it on the SOP Review calendar every other year was made. Building the SOP review calendar was contracted out and Arc Flash PPE and Clothing Requirements SOP was not added accordingly. Initial review was conducted in 2014. | 18. Failure to Check, Monitor | 9. Abnormal Operation | [26 empty] | FALSE |  | Days away from Work (H) | 2008-04-21 | 1986-11-26 |  | 2019-03-28 07:00 | 31 | 78 |  | FALSE | Male | Arc Flash |  | FALSE | Payton Martin |  | Days Away from Work | Payton Martin | TRUE |  | Baptist Hospital Burn Unit |  | Burn: Electrical | Dr visit 3/29: Release to light duty eff 4/1/19 per F. Davis Released to full duty eff 6/18/19 | TRUE |  | Lineman | Hand | Injury | Left | TRUE | Carl Kemp | TRUE | 2019 | 3/28/2019 7:30:00 AM | 2.5 | TRUE | FALSE | TRUE | Arc Flash | Holding Ladder for member to test voltage in 4160 VAC Soft Starter | [24 empty] | NA
8735 | Metro Service Center | 2019-02-28 08:30 | Arc flash occurred while checking voltage. | Level 4 |  | FALSE | Member Injury |  | Jerrod Moser | This incident is being conducting at the direction of counsel. | 2019-03-04 07:33 | Power Delivery | Terry Hackett | 2019-04-12 14:24 | 2019-02-28 15:37 | 2019-02-28 15:37 | 2019-04-02 15:21 | 2019-04-08 | 2019-02-28 15:24 | 2019-04-10 14:06 |  |  | Tinker AFB B210 |  |  | Jerrod Moser | Approve | T&D Ops |  | Level 4 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Terry Hackett |  | Details of scenario preceding incident. Two OGE Journeymen linemen were performing the restoration phase of an outage request for building B210 at Tinker Air Force Base. Members completed tailboard for the job of energizing stepdown transformer 344755. Stepdown transformer 344755 which feeds building B210 was successfully energized by the members closing switches in cubicle 344790 SW#3. At this time members went beyond the point of demarcation into building B210 to perform voltage check on 4160 VAC Soft Starter. Member #1 used a 1000 VAC Fluke multimeter with his Class 2 (17KV) rubber gloves with class 2 leather protectors to check the voltage of the 4160 VAC equipment. The multimeter was destroyed due to being overloaded and a large phase to phase flash occurred in the equipment. This resulted in both members receiving 2nd degree burns, the equipment being damaged, and two blown fuses. Transformer 344755 steps down voltage from 12.5KV to 4160V. The transformer is labeled with the point of demarcation as the secondary spades of the transformer (see picture). Both members are journeymen linemen. Both members stated they thought the equipment was 480 volts which is common for our stepdown transformers and that is why the 1000-volt fluke multimeter was used. Members went beyond the point of demarcation into building B210. Shawver and Sons employee told member #1 that he did not have rubber glove to test the customer owned equipment. Member #1 felt like he was being asked to conduct the testing and proceeded to climb the 6’ A frame ladder that was set up in front of the equipment where the panel was removed. Member #1 pointed out the equipment did not have a neutral, so Member #2 looked into the equipment from the ground. At this time Member #1 touched his probes on one phase and then another. The multimeter shorted out and caused a phase to phase arc flash. Two Schawver employees were standing out of the Arc Flash Boundary. After the arc flash occurred the Schawver employees called 911. The injured members were transported by ambulance to the Integris Hospital. Where they were treated and released. Immediately Following the incident, OGE stopped all work, secured the scene, and made the area safe by isolating, grounding, locking, and tagging transformer 344755. Incident Details: Member #1 performing the testing was wearing HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans Class 2 (17KV) Rubber Gloves, Class 2 Leather Protectors, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #2 observing the testing was wearing HRC 2 Sleeveless Vest, HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans, HRC 2 Beanie, HRC2 Balaclava, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #1’s Class 2 rubber gloves (25489 & 25570) were dielectrically tested on 08-16-2018 Salisbury Model AS1000 Arc Rated 10 Cal face shield, Tyndale 11 Cal/CM2 Balaclava, and 20 cal/cm2 suit was readily available on the truck. Members had been trained on OGE SOP.TDO.015 Arc Flash Burn Prevention PPE and Clothing requirements, which prohibits working past the point of demarcation unless an arc flash study has been completed and members are wearing the appropriately rated category of FR clothing. This SOP also requires an arc rated face shield when working on 480 Volt cabinets that are a part of the OGE system. Member #1 Obtained journeyman status on 12/1/2009. Member #2 Obtained journeyman status on 7/29/2016. Member #1 used a 1000 Volt Fluke Multimeter to test voltage on the Customer Owned Benshaw 4160 VAC Soft Starter Model No: CFMVRMX18-3000-4160-12 Hard Hat: Bullard Classic Model C-33 Type 1 Leather protectors: Kunz Glove Size 10.5 #1005 Rubber Glove#’s: Salisbury size 10 class 2 (Internal ID# 25489 & 25570) Both members wore ANSI Z-87 Safety Glasses 1000 Volt Fluke Multimeter T5-1000 was used Documented work observations could not be provided Documented review of SOP.TDO.015 Arc Flash Burn Prevention could not be provided SOP.TDO.015 was set up to be an every other year review, but has not been on the SOP review calendar since 2014 Max incident energy was calculated at 1.9 cal/cm2 (see attachment FW: Tinker4_Arc Flash Results) | William Wilson | Terry Hackett | FALSE | Metro Service Center | TRUE |  | FALSE | Construction Services |  | Payton Martin | Carl Kemp |  |  | Approve |  |  | Very High | [5 empty] | 6.05 Inadequate review instruction | 7.13 Inadequate reinforcement of proper behavior |  | 9.06 Inadequate work planning or programming | [7 empty] | Member's failed to stop and evaluate the unplanned task of checking voltage. SOP Job Briefings requires that members stop and revisit the job briefing when task are added that were unplanned | 17. Failure to Identify Hazard, Risk | 9. Abnormal Operation | [26 empty] | FALSE |  | Days away from Work (H) | 2000-03-27 | 1978-05-15 |  | 2019-03-28 07:00 | 24 | 0 |  | FALSE | Male | 1000 volt fluke multimeter short circuited due to being overloaded by the 4160 VAC and caused a phase to phase Arc Flash |  | FALSE | James Caldwell |  | Days Away from Work | James Caldwell | TRUE |  | Baptist Hospital |  | Burn: Electrical | Released to full duty eff 3/25/19 per F. Davis. | TRUE |  | Lineman | Face | Injury | Multiple | TRUE | Carl Kemp | TRUE | 2019 | 3/28/2019 7:30:00 AM | 9 | TRUE | FALSE | TRUE | Arc Flash | Testing Voltage on 4160 VAC Soft Starter | [24 empty] | NA
8735 | Metro Service Center | 2019-02-28 08:30 | Arc flash occurred while checking voltage. | Level 4 |  | FALSE | Member Injury |  | Jerrod Moser | This incident is being conducting at the direction of counsel. | 2019-03-04 07:33 | Power Delivery | Terry Hackett | 2019-04-12 14:24 | 2019-02-28 15:37 | 2019-02-28 15:37 | 2019-04-02 15:21 | 2019-04-08 | 2019-02-28 15:24 | 2019-04-10 14:06 |  |  | Tinker AFB B210 |  |  | Jerrod Moser | Approve | T&D Ops |  | Level 4 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Terry Hackett |  | Details of scenario preceding incident. Two OGE Journeymen linemen were performing the restoration phase of an outage request for building B210 at Tinker Air Force Base. Members completed tailboard for the job of energizing stepdown transformer 344755. Stepdown transformer 344755 which feeds building B210 was successfully energized by the members closing switches in cubicle 344790 SW#3. At this time members went beyond the point of demarcation into building B210 to perform voltage check on 4160 VAC Soft Starter. Member #1 used a 1000 VAC Fluke multimeter with his Class 2 (17KV) rubber gloves with class 2 leather protectors to check the voltage of the 4160 VAC equipment. The multimeter was destroyed due to being overloaded and a large phase to phase flash occurred in the equipment. This resulted in both members receiving 2nd degree burns, the equipment being damaged, and two blown fuses. Transformer 344755 steps down voltage from 12.5KV to 4160V. The transformer is labeled with the point of demarcation as the secondary spades of the transformer (see picture). Both members are journeymen linemen. Both members stated they thought the equipment was 480 volts which is common for our stepdown transformers and that is why the 1000-volt fluke multimeter was used. Members went beyond the point of demarcation into building B210. Shawver and Sons employee told member #1 that he did not have rubber glove to test the customer owned equipment. Member #1 felt like he was being asked to conduct the testing and proceeded to climb the 6’ A frame ladder that was set up in front of the equipment where the panel was removed. Member #1 pointed out the equipment did not have a neutral, so Member #2 looked into the equipment from the ground. At this time Member #1 touched his probes on one phase and then another. The multimeter shorted out and caused a phase to phase arc flash. Two Schawver employees were standing out of the Arc Flash Boundary. After the arc flash occurred the Schawver employees called 911. The injured members were transported by ambulance to the Integris Hospital. Where they were treated and released. Immediately Following the incident, OGE stopped all work, secured the scene, and made the area safe by isolating, grounding, locking, and tagging transformer 344755. Incident Details: Member #1 performing the testing was wearing HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans Class 2 (17KV) Rubber Gloves, Class 2 Leather Protectors, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #2 observing the testing was wearing HRC 2 Sleeveless Vest, HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans, HRC 2 Beanie, HRC2 Balaclava, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #1’s Class 2 rubber gloves (25489 & 25570) were dielectrically tested on 08-16-2018 Salisbury Model AS1000 Arc Rated 10 Cal face shield, Tyndale 11 Cal/CM2 Balaclava, and 20 cal/cm2 suit was readily available on the truck. Members had been trained on OGE SOP.TDO.015 Arc Flash Burn Prevention PPE and Clothing requirements, which prohibits working past the point of demarcation unless an arc flash study has been completed and members are wearing the appropriately rated category of FR clothing. This SOP also requires an arc rated face shield when working on 480 Volt cabinets that are a part of the OGE system. Member #1 Obtained journeyman status on 12/1/2009. Member #2 Obtained journeyman status on 7/29/2016. Member #1 used a 1000 Volt Fluke Multimeter to test voltage on the Customer Owned Benshaw 4160 VAC Soft Starter Model No: CFMVRMX18-3000-4160-12 Hard Hat: Bullard Classic Model C-33 Type 1 Leather protectors: Kunz Glove Size 10.5 #1005 Rubber Glove#’s: Salisbury size 10 class 2 (Internal ID# 25489 & 25570) Both members wore ANSI Z-87 Safety Glasses 1000 Volt Fluke Multimeter T5-1000 was used Documented work observations could not be provided Documented review of SOP.TDO.015 Arc Flash Burn Prevention could not be provided SOP.TDO.015 was set up to be an every other year review, but has not been on the SOP review calendar since 2014 Max incident energy was calculated at 1.9 cal/cm2 (see attachment FW: Tinker4_Arc Flash Results) | William Wilson | Terry Hackett | FALSE | Metro Service Center | TRUE |  | FALSE | Construction Services |  | Payton Martin | Carl Kemp |  |  | Approve |  |  | Very High | [5 empty] | 6.05 Inadequate review instruction | 7.13 Inadequate reinforcement of proper behavior |  | 9.06 Inadequate work planning or programming | [7 empty] | Member's failed to stop and evaluate the unplanned task of checking voltage. SOP Job Briefings requires that members stop and revisit the job briefing when task are added that were unplanned | 17. Failure to Identify Hazard, Risk | 9. Abnormal Operation | [26 empty] | FALSE |  | Days away from Work (H) | 2008-04-21 | 1986-11-26 |  | 2019-03-28 07:00 | 31 | 78 |  | FALSE | Male | Arc Flash |  | FALSE | Payton Martin |  | Days Away from Work | Payton Martin | TRUE |  | Baptist Hospital Burn Unit |  | Burn: Electrical | Dr visit 3/29: Release to light duty eff 4/1/19 per F. Davis Released to full duty eff 6/18/19 | TRUE |  | Lineman | Hand | Injury | Left | TRUE | Carl Kemp | TRUE | 2019 | 3/28/2019 7:30:00 AM | 2.5 | TRUE | FALSE | TRUE | Arc Flash | Holding Ladder for member to test voltage in 4160 VAC Soft Starter | [24 empty] | NA
8735 | Metro Service Center | 2019-02-28 08:30 | Arc flash occurred while checking voltage. | Level 4 |  | FALSE | Member Injury |  | Jerrod Moser | This incident is being conducting at the direction of counsel. | 2019-03-04 07:33 | Power Delivery | Terry Hackett | 2019-04-12 14:24 | 2019-02-28 15:37 | 2019-02-28 15:37 | 2019-04-02 15:21 | 2019-04-08 | 2019-02-28 15:24 | 2019-04-10 14:06 |  |  | Tinker AFB B210 |  |  | Jerrod Moser | Approve | T&D Ops |  | Level 4 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Terry Hackett |  | Details of scenario preceding incident. Two OGE Journeymen linemen were performing the restoration phase of an outage request for building B210 at Tinker Air Force Base. Members completed tailboard for the job of energizing stepdown transformer 344755. Stepdown transformer 344755 which feeds building B210 was successfully energized by the members closing switches in cubicle 344790 SW#3. At this time members went beyond the point of demarcation into building B210 to perform voltage check on 4160 VAC Soft Starter. Member #1 used a 1000 VAC Fluke multimeter with his Class 2 (17KV) rubber gloves with class 2 leather protectors to check the voltage of the 4160 VAC equipment. The multimeter was destroyed due to being overloaded and a large phase to phase flash occurred in the equipment. This resulted in both members receiving 2nd degree burns, the equipment being damaged, and two blown fuses. Transformer 344755 steps down voltage from 12.5KV to 4160V. The transformer is labeled with the point of demarcation as the secondary spades of the transformer (see picture). Both members are journeymen linemen. Both members stated they thought the equipment was 480 volts which is common for our stepdown transformers and that is why the 1000-volt fluke multimeter was used. Members went beyond the point of demarcation into building B210. Shawver and Sons employee told member #1 that he did not have rubber glove to test the customer owned equipment. Member #1 felt like he was being asked to conduct the testing and proceeded to climb the 6’ A frame ladder that was set up in front of the equipment where the panel was removed. Member #1 pointed out the equipment did not have a neutral, so Member #2 looked into the equipment from the ground. At this time Member #1 touched his probes on one phase and then another. The multimeter shorted out and caused a phase to phase arc flash. Two Schawver employees were standing out of the Arc Flash Boundary. After the arc flash occurred the Schawver employees called 911. The injured members were transported by ambulance to the Integris Hospital. Where they were treated and released. Immediately Following the incident, OGE stopped all work, secured the scene, and made the area safe by isolating, grounding, locking, and tagging transformer 344755. Incident Details: Member #1 performing the testing was wearing HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans Class 2 (17KV) Rubber Gloves, Class 2 Leather Protectors, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #2 observing the testing was wearing HRC 2 Sleeveless Vest, HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans, HRC 2 Beanie, HRC2 Balaclava, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #1’s Class 2 rubber gloves (25489 & 25570) were dielectrically tested on 08-16-2018 Salisbury Model AS1000 Arc Rated 10 Cal face shield, Tyndale 11 Cal/CM2 Balaclava, and 20 cal/cm2 suit was readily available on the truck. Members had been trained on OGE SOP.TDO.015 Arc Flash Burn Prevention PPE and Clothing requirements, which prohibits working past the point of demarcation unless an arc flash study has been completed and members are wearing the appropriately rated category of FR clothing. This SOP also requires an arc rated face shield when working on 480 Volt cabinets that are a part of the OGE system. Member #1 Obtained journeyman status on 12/1/2009. Member #2 Obtained journeyman status on 7/29/2016. Member #1 used a 1000 Volt Fluke Multimeter to test voltage on the Customer Owned Benshaw 4160 VAC Soft Starter Model No: CFMVRMX18-3000-4160-12 Hard Hat: Bullard Classic Model C-33 Type 1 Leather protectors: Kunz Glove Size 10.5 #1005 Rubber Glove#’s: Salisbury size 10 class 2 (Internal ID# 25489 & 25570) Both members wore ANSI Z-87 Safety Glasses 1000 Volt Fluke Multimeter T5-1000 was used Documented work observations could not be provided Documented review of SOP.TDO.015 Arc Flash Burn Prevention could not be provided SOP.TDO.015 was set up to be an every other year review, but has not been on the SOP review calendar since 2014 Max incident energy was calculated at 1.9 cal/cm2 (see attachment FW: Tinker4_Arc Flash Results) | William Wilson | Terry Hackett | FALSE | Metro Service Center | TRUE |  | FALSE | Construction Services |  | Payton Martin | Carl Kemp |  |  | Approve |  |  | Very High |  |  |  | 4.04 Routine, monotony, demand for uneventful vigilance |  | 6.03 Infrequent performance | [10 empty] | Members were not familiar with the equipment and did not read equipment labels, due to belief that stepdown transformer had stepped the voltage down to 480 volts. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [26 empty] | FALSE |  | Days away from Work (H) | 2000-03-27 | 1978-05-15 |  | 2019-03-28 07:00 | 24 | 0 |  | FALSE | Male | 1000 volt fluke multimeter short circuited due to being overloaded by the 4160 VAC and caused a phase to phase Arc Flash |  | FALSE | James Caldwell |  | Days Away from Work | James Caldwell | TRUE |  | Baptist Hospital |  | Burn: Electrical | Released to full duty eff 3/25/19 per F. Davis. | TRUE |  | Lineman | Face | Injury | Multiple | TRUE | Carl Kemp | TRUE | 2019 | 3/28/2019 7:30:00 AM | 9 | TRUE | FALSE | TRUE | Arc Flash | Testing Voltage on 4160 VAC Soft Starter | [24 empty] | NA
8735 | Metro Service Center | 2019-02-28 08:30 | Arc flash occurred while checking voltage. | Level 4 |  | FALSE | Member Injury |  | Jerrod Moser | This incident is being conducting at the direction of counsel. | 2019-03-04 07:33 | Power Delivery | Terry Hackett | 2019-04-12 14:24 | 2019-02-28 15:37 | 2019-02-28 15:37 | 2019-04-02 15:21 | 2019-04-08 | 2019-02-28 15:24 | 2019-04-10 14:06 |  |  | Tinker AFB B210 |  |  | Jerrod Moser | Approve | T&D Ops |  | Level 4 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Terry Hackett |  | Details of scenario preceding incident. Two OGE Journeymen linemen were performing the restoration phase of an outage request for building B210 at Tinker Air Force Base. Members completed tailboard for the job of energizing stepdown transformer 344755. Stepdown transformer 344755 which feeds building B210 was successfully energized by the members closing switches in cubicle 344790 SW#3. At this time members went beyond the point of demarcation into building B210 to perform voltage check on 4160 VAC Soft Starter. Member #1 used a 1000 VAC Fluke multimeter with his Class 2 (17KV) rubber gloves with class 2 leather protectors to check the voltage of the 4160 VAC equipment. The multimeter was destroyed due to being overloaded and a large phase to phase flash occurred in the equipment. This resulted in both members receiving 2nd degree burns, the equipment being damaged, and two blown fuses. Transformer 344755 steps down voltage from 12.5KV to 4160V. The transformer is labeled with the point of demarcation as the secondary spades of the transformer (see picture). Both members are journeymen linemen. Both members stated they thought the equipment was 480 volts which is common for our stepdown transformers and that is why the 1000-volt fluke multimeter was used. Members went beyond the point of demarcation into building B210. Shawver and Sons employee told member #1 that he did not have rubber glove to test the customer owned equipment. Member #1 felt like he was being asked to conduct the testing and proceeded to climb the 6’ A frame ladder that was set up in front of the equipment where the panel was removed. Member #1 pointed out the equipment did not have a neutral, so Member #2 looked into the equipment from the ground. At this time Member #1 touched his probes on one phase and then another. The multimeter shorted out and caused a phase to phase arc flash. Two Schawver employees were standing out of the Arc Flash Boundary. After the arc flash occurred the Schawver employees called 911. The injured members were transported by ambulance to the Integris Hospital. Where they were treated and released. Immediately Following the incident, OGE stopped all work, secured the scene, and made the area safe by isolating, grounding, locking, and tagging transformer 344755. Incident Details: Member #1 performing the testing was wearing HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans Class 2 (17KV) Rubber Gloves, Class 2 Leather Protectors, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #2 observing the testing was wearing HRC 2 Sleeveless Vest, HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans, HRC 2 Beanie, HRC2 Balaclava, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #1’s Class 2 rubber gloves (25489 & 25570) were dielectrically tested on 08-16-2018 Salisbury Model AS1000 Arc Rated 10 Cal face shield, Tyndale 11 Cal/CM2 Balaclava, and 20 cal/cm2 suit was readily available on the truck. Members had been trained on OGE SOP.TDO.015 Arc Flash Burn Prevention PPE and Clothing requirements, which prohibits working past the point of demarcation unless an arc flash study has been completed and members are wearing the appropriately rated category of FR clothing. This SOP also requires an arc rated face shield when working on 480 Volt cabinets that are a part of the OGE system. Member #1 Obtained journeyman status on 12/1/2009. Member #2 Obtained journeyman status on 7/29/2016. Member #1 used a 1000 Volt Fluke Multimeter to test voltage on the Customer Owned Benshaw 4160 VAC Soft Starter Model No: CFMVRMX18-3000-4160-12 Hard Hat: Bullard Classic Model C-33 Type 1 Leather protectors: Kunz Glove Size 10.5 #1005 Rubber Glove#’s: Salisbury size 10 class 2 (Internal ID# 25489 & 25570) Both members wore ANSI Z-87 Safety Glasses 1000 Volt Fluke Multimeter T5-1000 was used Documented work observations could not be provided Documented review of SOP.TDO.015 Arc Flash Burn Prevention could not be provided SOP.TDO.015 was set up to be an every other year review, but has not been on the SOP review calendar since 2014 Max incident energy was calculated at 1.9 cal/cm2 (see attachment FW: Tinker4_Arc Flash Results) | William Wilson | Terry Hackett | FALSE | Metro Service Center | TRUE |  | FALSE | Construction Services |  | Payton Martin | Carl Kemp |  |  | Approve |  |  | Very High |  |  |  | 4.04 Routine, monotony, demand for uneventful vigilance |  | 6.03 Infrequent performance | [10 empty] | Members were not familiar with the equipment and did not read equipment labels, due to belief that stepdown transformer had stepped the voltage down to 480 volts. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [26 empty] | FALSE |  | Days away from Work (H) | 2008-04-21 | 1986-11-26 |  | 2019-03-28 07:00 | 31 | 78 |  | FALSE | Male | Arc Flash |  | FALSE | Payton Martin |  | Days Away from Work | Payton Martin | TRUE |  | Baptist Hospital Burn Unit |  | Burn: Electrical | Dr visit 3/29: Release to light duty eff 4/1/19 per F. Davis Released to full duty eff 6/18/19 | TRUE |  | Lineman | Hand | Injury | Left | TRUE | Carl Kemp | TRUE | 2019 | 3/28/2019 7:30:00 AM | 2.5 | TRUE | FALSE | TRUE | Arc Flash | Holding Ladder for member to test voltage in 4160 VAC Soft Starter | [24 empty] | NA
8735 | Metro Service Center | 2019-02-28 08:30 | Arc flash occurred while checking voltage. | Level 4 |  | FALSE | Member Injury |  | Jerrod Moser | This incident is being conducting at the direction of counsel. | 2019-03-04 07:33 | Power Delivery | Terry Hackett | 2019-04-12 14:24 | 2019-02-28 15:37 | 2019-02-28 15:37 | 2019-04-02 15:21 | 2019-04-08 | 2019-02-28 15:24 | 2019-04-10 14:06 |  |  | Tinker AFB B210 |  |  | Jerrod Moser | Approve | T&D Ops |  | Level 4 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Terry Hackett |  | Details of scenario preceding incident. Two OGE Journeymen linemen were performing the restoration phase of an outage request for building B210 at Tinker Air Force Base. Members completed tailboard for the job of energizing stepdown transformer 344755. Stepdown transformer 344755 which feeds building B210 was successfully energized by the members closing switches in cubicle 344790 SW#3. At this time members went beyond the point of demarcation into building B210 to perform voltage check on 4160 VAC Soft Starter. Member #1 used a 1000 VAC Fluke multimeter with his Class 2 (17KV) rubber gloves with class 2 leather protectors to check the voltage of the 4160 VAC equipment. The multimeter was destroyed due to being overloaded and a large phase to phase flash occurred in the equipment. This resulted in both members receiving 2nd degree burns, the equipment being damaged, and two blown fuses. Transformer 344755 steps down voltage from 12.5KV to 4160V. The transformer is labeled with the point of demarcation as the secondary spades of the transformer (see picture). Both members are journeymen linemen. Both members stated they thought the equipment was 480 volts which is common for our stepdown transformers and that is why the 1000-volt fluke multimeter was used. Members went beyond the point of demarcation into building B210. Shawver and Sons employee told member #1 that he did not have rubber glove to test the customer owned equipment. Member #1 felt like he was being asked to conduct the testing and proceeded to climb the 6’ A frame ladder that was set up in front of the equipment where the panel was removed. Member #1 pointed out the equipment did not have a neutral, so Member #2 looked into the equipment from the ground. At this time Member #1 touched his probes on one phase and then another. The multimeter shorted out and caused a phase to phase arc flash. Two Schawver employees were standing out of the Arc Flash Boundary. After the arc flash occurred the Schawver employees called 911. The injured members were transported by ambulance to the Integris Hospital. Where they were treated and released. Immediately Following the incident, OGE stopped all work, secured the scene, and made the area safe by isolating, grounding, locking, and tagging transformer 344755. Incident Details: Member #1 performing the testing was wearing HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans Class 2 (17KV) Rubber Gloves, Class 2 Leather Protectors, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #2 observing the testing was wearing HRC 2 Sleeveless Vest, HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans, HRC 2 Beanie, HRC2 Balaclava, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #1’s Class 2 rubber gloves (25489 & 25570) were dielectrically tested on 08-16-2018 Salisbury Model AS1000 Arc Rated 10 Cal face shield, Tyndale 11 Cal/CM2 Balaclava, and 20 cal/cm2 suit was readily available on the truck. Members had been trained on OGE SOP.TDO.015 Arc Flash Burn Prevention PPE and Clothing requirements, which prohibits working past the point of demarcation unless an arc flash study has been completed and members are wearing the appropriately rated category of FR clothing. This SOP also requires an arc rated face shield when working on 480 Volt cabinets that are a part of the OGE system. Member #1 Obtained journeyman status on 12/1/2009. Member #2 Obtained journeyman status on 7/29/2016. Member #1 used a 1000 Volt Fluke Multimeter to test voltage on the Customer Owned Benshaw 4160 VAC Soft Starter Model No: CFMVRMX18-3000-4160-12 Hard Hat: Bullard Classic Model C-33 Type 1 Leather protectors: Kunz Glove Size 10.5 #1005 Rubber Glove#’s: Salisbury size 10 class 2 (Internal ID# 25489 & 25570) Both members wore ANSI Z-87 Safety Glasses 1000 Volt Fluke Multimeter T5-1000 was used Documented work observations could not be provided Documented review of SOP.TDO.015 Arc Flash Burn Prevention could not be provided SOP.TDO.015 was set up to be an every other year review, but has not been on the SOP review calendar since 2014 Max incident energy was calculated at 1.9 cal/cm2 (see attachment FW: Tinker4_Arc Flash Results) |  | Terry Hackett | FALSE | Metro Service Center | TRUE |  | FALSE | Construction Services |  | Payton Martin | Carl Kemp |  |  | Approve |  |  | Very High | [7 empty] | 8.1.2 Improper conduct that is condoned: Unintentional | [5 empty] | 14.04 Inadequate monitoring of compliance |  |  | Supervisor did not have documentation for required annual work observations. Currently work observations are conducted in paper form and are stored in supervisors safety files. This makes it difficult for the company to verify full compliance. | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation | [26 empty] | FALSE |  | Days away from Work (H) | 2000-03-27 | 1978-05-15 |  | 2019-03-28 07:00 | 24 | 0 |  | FALSE | Male | 1000 volt fluke multimeter short circuited due to being overloaded by the 4160 VAC and caused a phase to phase Arc Flash |  | FALSE | James Caldwell |  | Days Away from Work | James Caldwell | TRUE |  | Baptist Hospital |  | Burn: Electrical | Released to full duty eff 3/25/19 per F. Davis. | TRUE |  | Lineman | Face | Injury | Multiple | TRUE | Carl Kemp | TRUE | 2019 | 3/28/2019 7:30:00 AM | 9 | TRUE | FALSE | TRUE | Arc Flash | Testing Voltage on 4160 VAC Soft Starter | [24 empty] | NA
8735 | Metro Service Center | 2019-02-28 08:30 | Arc flash occurred while checking voltage. | Level 4 |  | FALSE | Member Injury |  | Jerrod Moser | This incident is being conducting at the direction of counsel. | 2019-03-04 07:33 | Power Delivery | Terry Hackett | 2019-04-12 14:24 | 2019-02-28 15:37 | 2019-02-28 15:37 | 2019-04-02 15:21 | 2019-04-08 | 2019-02-28 15:24 | 2019-04-10 14:06 |  |  | Tinker AFB B210 |  |  | Jerrod Moser | Approve | T&D Ops |  | Level 4 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Terry Hackett |  | Details of scenario preceding incident. Two OGE Journeymen linemen were performing the restoration phase of an outage request for building B210 at Tinker Air Force Base. Members completed tailboard for the job of energizing stepdown transformer 344755. Stepdown transformer 344755 which feeds building B210 was successfully energized by the members closing switches in cubicle 344790 SW#3. At this time members went beyond the point of demarcation into building B210 to perform voltage check on 4160 VAC Soft Starter. Member #1 used a 1000 VAC Fluke multimeter with his Class 2 (17KV) rubber gloves with class 2 leather protectors to check the voltage of the 4160 VAC equipment. The multimeter was destroyed due to being overloaded and a large phase to phase flash occurred in the equipment. This resulted in both members receiving 2nd degree burns, the equipment being damaged, and two blown fuses. Transformer 344755 steps down voltage from 12.5KV to 4160V. The transformer is labeled with the point of demarcation as the secondary spades of the transformer (see picture). Both members are journeymen linemen. Both members stated they thought the equipment was 480 volts which is common for our stepdown transformers and that is why the 1000-volt fluke multimeter was used. Members went beyond the point of demarcation into building B210. Shawver and Sons employee told member #1 that he did not have rubber glove to test the customer owned equipment. Member #1 felt like he was being asked to conduct the testing and proceeded to climb the 6’ A frame ladder that was set up in front of the equipment where the panel was removed. Member #1 pointed out the equipment did not have a neutral, so Member #2 looked into the equipment from the ground. At this time Member #1 touched his probes on one phase and then another. The multimeter shorted out and caused a phase to phase arc flash. Two Schawver employees were standing out of the Arc Flash Boundary. After the arc flash occurred the Schawver employees called 911. The injured members were transported by ambulance to the Integris Hospital. Where they were treated and released. Immediately Following the incident, OGE stopped all work, secured the scene, and made the area safe by isolating, grounding, locking, and tagging transformer 344755. Incident Details: Member #1 performing the testing was wearing HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans Class 2 (17KV) Rubber Gloves, Class 2 Leather Protectors, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #2 observing the testing was wearing HRC 2 Sleeveless Vest, HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans, HRC 2 Beanie, HRC2 Balaclava, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #1’s Class 2 rubber gloves (25489 & 25570) were dielectrically tested on 08-16-2018 Salisbury Model AS1000 Arc Rated 10 Cal face shield, Tyndale 11 Cal/CM2 Balaclava, and 20 cal/cm2 suit was readily available on the truck. Members had been trained on OGE SOP.TDO.015 Arc Flash Burn Prevention PPE and Clothing requirements, which prohibits working past the point of demarcation unless an arc flash study has been completed and members are wearing the appropriately rated category of FR clothing. This SOP also requires an arc rated face shield when working on 480 Volt cabinets that are a part of the OGE system. Member #1 Obtained journeyman status on 12/1/2009. Member #2 Obtained journeyman status on 7/29/2016. Member #1 used a 1000 Volt Fluke Multimeter to test voltage on the Customer Owned Benshaw 4160 VAC Soft Starter Model No: CFMVRMX18-3000-4160-12 Hard Hat: Bullard Classic Model C-33 Type 1 Leather protectors: Kunz Glove Size 10.5 #1005 Rubber Glove#’s: Salisbury size 10 class 2 (Internal ID# 25489 & 25570) Both members wore ANSI Z-87 Safety Glasses 1000 Volt Fluke Multimeter T5-1000 was used Documented work observations could not be provided Documented review of SOP.TDO.015 Arc Flash Burn Prevention could not be provided SOP.TDO.015 was set up to be an every other year review, but has not been on the SOP review calendar since 2014 Max incident energy was calculated at 1.9 cal/cm2 (see attachment FW: Tinker4_Arc Flash Results) |  | Terry Hackett | FALSE | Metro Service Center | TRUE |  | FALSE | Construction Services |  | Payton Martin | Carl Kemp |  |  | Approve |  |  | Very High | [7 empty] | 8.1.2 Improper conduct that is condoned: Unintentional | [5 empty] | 14.04 Inadequate monitoring of compliance |  |  | Supervisor did not have documentation for required annual work observations. Currently work observations are conducted in paper form and are stored in supervisors safety files. This makes it difficult for the company to verify full compliance. | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation | [26 empty] | FALSE |  | Days away from Work (H) | 2008-04-21 | 1986-11-26 |  | 2019-03-28 07:00 | 31 | 78 |  | FALSE | Male | Arc Flash |  | FALSE | Payton Martin |  | Days Away from Work | Payton Martin | TRUE |  | Baptist Hospital Burn Unit |  | Burn: Electrical | Dr visit 3/29: Release to light duty eff 4/1/19 per F. Davis Released to full duty eff 6/18/19 | TRUE |  | Lineman | Hand | Injury | Left | TRUE | Carl Kemp | TRUE | 2019 | 3/28/2019 7:30:00 AM | 2.5 | TRUE | FALSE | TRUE | Arc Flash | Holding Ladder for member to test voltage in 4160 VAC Soft Starter | [24 empty] | NA
8735 | Metro Service Center | 2019-02-28 08:30 | Arc flash occurred while checking voltage. | Level 4 |  | FALSE | Member Injury |  | Jerrod Moser | This incident is being conducting at the direction of counsel. | 2019-03-04 07:33 | Power Delivery | Terry Hackett | 2019-04-12 14:24 | 2019-02-28 15:37 | 2019-02-28 15:37 | 2019-04-02 15:21 | 2019-04-08 | 2019-02-28 15:24 | 2019-04-10 14:06 |  |  | Tinker AFB B210 |  |  | Jerrod Moser | Approve | T&D Ops |  | Level 4 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Terry Hackett |  | Details of scenario preceding incident. Two OGE Journeymen linemen were performing the restoration phase of an outage request for building B210 at Tinker Air Force Base. Members completed tailboard for the job of energizing stepdown transformer 344755. Stepdown transformer 344755 which feeds building B210 was successfully energized by the members closing switches in cubicle 344790 SW#3. At this time members went beyond the point of demarcation into building B210 to perform voltage check on 4160 VAC Soft Starter. Member #1 used a 1000 VAC Fluke multimeter with his Class 2 (17KV) rubber gloves with class 2 leather protectors to check the voltage of the 4160 VAC equipment. The multimeter was destroyed due to being overloaded and a large phase to phase flash occurred in the equipment. This resulted in both members receiving 2nd degree burns, the equipment being damaged, and two blown fuses. Transformer 344755 steps down voltage from 12.5KV to 4160V. The transformer is labeled with the point of demarcation as the secondary spades of the transformer (see picture). Both members are journeymen linemen. Both members stated they thought the equipment was 480 volts which is common for our stepdown transformers and that is why the 1000-volt fluke multimeter was used. Members went beyond the point of demarcation into building B210. Shawver and Sons employee told member #1 that he did not have rubber glove to test the customer owned equipment. Member #1 felt like he was being asked to conduct the testing and proceeded to climb the 6’ A frame ladder that was set up in front of the equipment where the panel was removed. Member #1 pointed out the equipment did not have a neutral, so Member #2 looked into the equipment from the ground. At this time Member #1 touched his probes on one phase and then another. The multimeter shorted out and caused a phase to phase arc flash. Two Schawver employees were standing out of the Arc Flash Boundary. After the arc flash occurred the Schawver employees called 911. The injured members were transported by ambulance to the Integris Hospital. Where they were treated and released. Immediately Following the incident, OGE stopped all work, secured the scene, and made the area safe by isolating, grounding, locking, and tagging transformer 344755. Incident Details: Member #1 performing the testing was wearing HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans Class 2 (17KV) Rubber Gloves, Class 2 Leather Protectors, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #2 observing the testing was wearing HRC 2 Sleeveless Vest, HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans, HRC 2 Beanie, HRC2 Balaclava, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #1’s Class 2 rubber gloves (25489 & 25570) were dielectrically tested on 08-16-2018 Salisbury Model AS1000 Arc Rated 10 Cal face shield, Tyndale 11 Cal/CM2 Balaclava, and 20 cal/cm2 suit was readily available on the truck. Members had been trained on OGE SOP.TDO.015 Arc Flash Burn Prevention PPE and Clothing requirements, which prohibits working past the point of demarcation unless an arc flash study has been completed and members are wearing the appropriately rated category of FR clothing. This SOP also requires an arc rated face shield when working on 480 Volt cabinets that are a part of the OGE system. Member #1 Obtained journeyman status on 12/1/2009. Member #2 Obtained journeyman status on 7/29/2016. Member #1 used a 1000 Volt Fluke Multimeter to test voltage on the Customer Owned Benshaw 4160 VAC Soft Starter Model No: CFMVRMX18-3000-4160-12 Hard Hat: Bullard Classic Model C-33 Type 1 Leather protectors: Kunz Glove Size 10.5 #1005 Rubber Glove#’s: Salisbury size 10 class 2 (Internal ID# 25489 & 25570) Both members wore ANSI Z-87 Safety Glasses 1000 Volt Fluke Multimeter T5-1000 was used Documented work observations could not be provided Documented review of SOP.TDO.015 Arc Flash Burn Prevention could not be provided SOP.TDO.015 was set up to be an every other year review, but has not been on the SOP review calendar since 2014 Max incident energy was calculated at 1.9 cal/cm2 (see attachment FW: Tinker4_Arc Flash Results) |  | Terry Hackett | FALSE | Metro Service Center | TRUE |  | FALSE | Construction Services |  | Payton Martin | Carl Kemp |  |  | Approve |  |  | Very High | [6 empty] | 7.10 Inappropriate peer pressure | 8.1.2 Improper conduct that is condoned: Unintentional | [8 empty] | Member's went past the point of demarcation which was labeled as the secondary spades of the stepdown transformer. Member's felt pressure to assist customer. SOP.TDO.015 Arc Flash Burn Prevention and Clothing Requirements does not allow members to go past the point of demarcation without a formal arc flash study and the proper category of FR clothing. | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation | [26 empty] | FALSE |  | Days away from Work (H) | 2000-03-27 | 1978-05-15 |  | 2019-03-28 07:00 | 24 | 0 |  | FALSE | Male | 1000 volt fluke multimeter short circuited due to being overloaded by the 4160 VAC and caused a phase to phase Arc Flash |  | FALSE | James Caldwell |  | Days Away from Work | James Caldwell | TRUE |  | Baptist Hospital |  | Burn: Electrical | Released to full duty eff 3/25/19 per F. Davis. | TRUE |  | Lineman | Face | Injury | Multiple | TRUE | Carl Kemp | TRUE | 2019 | 3/28/2019 7:30:00 AM | 9 | TRUE | FALSE | TRUE | Arc Flash | Testing Voltage on 4160 VAC Soft Starter | [24 empty] | NA
8735 | Metro Service Center | 2019-02-28 08:30 | Arc flash occurred while checking voltage. | Level 4 |  | FALSE | Member Injury |  | Jerrod Moser | This incident is being conducting at the direction of counsel. | 2019-03-04 07:33 | Power Delivery | Terry Hackett | 2019-04-12 14:24 | 2019-02-28 15:37 | 2019-02-28 15:37 | 2019-04-02 15:21 | 2019-04-08 | 2019-02-28 15:24 | 2019-04-10 14:06 |  |  | Tinker AFB B210 |  |  | Jerrod Moser | Approve | T&D Ops |  | Level 4 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Terry Hackett |  | Details of scenario preceding incident. Two OGE Journeymen linemen were performing the restoration phase of an outage request for building B210 at Tinker Air Force Base. Members completed tailboard for the job of energizing stepdown transformer 344755. Stepdown transformer 344755 which feeds building B210 was successfully energized by the members closing switches in cubicle 344790 SW#3. At this time members went beyond the point of demarcation into building B210 to perform voltage check on 4160 VAC Soft Starter. Member #1 used a 1000 VAC Fluke multimeter with his Class 2 (17KV) rubber gloves with class 2 leather protectors to check the voltage of the 4160 VAC equipment. The multimeter was destroyed due to being overloaded and a large phase to phase flash occurred in the equipment. This resulted in both members receiving 2nd degree burns, the equipment being damaged, and two blown fuses. Transformer 344755 steps down voltage from 12.5KV to 4160V. The transformer is labeled with the point of demarcation as the secondary spades of the transformer (see picture). Both members are journeymen linemen. Both members stated they thought the equipment was 480 volts which is common for our stepdown transformers and that is why the 1000-volt fluke multimeter was used. Members went beyond the point of demarcation into building B210. Shawver and Sons employee told member #1 that he did not have rubber glove to test the customer owned equipment. Member #1 felt like he was being asked to conduct the testing and proceeded to climb the 6’ A frame ladder that was set up in front of the equipment where the panel was removed. Member #1 pointed out the equipment did not have a neutral, so Member #2 looked into the equipment from the ground. At this time Member #1 touched his probes on one phase and then another. The multimeter shorted out and caused a phase to phase arc flash. Two Schawver employees were standing out of the Arc Flash Boundary. After the arc flash occurred the Schawver employees called 911. The injured members were transported by ambulance to the Integris Hospital. Where they were treated and released. Immediately Following the incident, OGE stopped all work, secured the scene, and made the area safe by isolating, grounding, locking, and tagging transformer 344755. Incident Details: Member #1 performing the testing was wearing HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans Class 2 (17KV) Rubber Gloves, Class 2 Leather Protectors, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #2 observing the testing was wearing HRC 2 Sleeveless Vest, HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans, HRC 2 Beanie, HRC2 Balaclava, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #1’s Class 2 rubber gloves (25489 & 25570) were dielectrically tested on 08-16-2018 Salisbury Model AS1000 Arc Rated 10 Cal face shield, Tyndale 11 Cal/CM2 Balaclava, and 20 cal/cm2 suit was readily available on the truck. Members had been trained on OGE SOP.TDO.015 Arc Flash Burn Prevention PPE and Clothing requirements, which prohibits working past the point of demarcation unless an arc flash study has been completed and members are wearing the appropriately rated category of FR clothing. This SOP also requires an arc rated face shield when working on 480 Volt cabinets that are a part of the OGE system. Member #1 Obtained journeyman status on 12/1/2009. Member #2 Obtained journeyman status on 7/29/2016. Member #1 used a 1000 Volt Fluke Multimeter to test voltage on the Customer Owned Benshaw 4160 VAC Soft Starter Model No: CFMVRMX18-3000-4160-12 Hard Hat: Bullard Classic Model C-33 Type 1 Leather protectors: Kunz Glove Size 10.5 #1005 Rubber Glove#’s: Salisbury size 10 class 2 (Internal ID# 25489 & 25570) Both members wore ANSI Z-87 Safety Glasses 1000 Volt Fluke Multimeter T5-1000 was used Documented work observations could not be provided Documented review of SOP.TDO.015 Arc Flash Burn Prevention could not be provided SOP.TDO.015 was set up to be an every other year review, but has not been on the SOP review calendar since 2014 Max incident energy was calculated at 1.9 cal/cm2 (see attachment FW: Tinker4_Arc Flash Results) |  | Terry Hackett | FALSE | Metro Service Center | TRUE |  | FALSE | Construction Services |  | Payton Martin | Carl Kemp |  |  | Approve |  |  | Very High | [6 empty] | 7.10 Inappropriate peer pressure | 8.1.2 Improper conduct that is condoned: Unintentional | [8 empty] | Member's went past the point of demarcation which was labeled as the secondary spades of the stepdown transformer. Member's felt pressure to assist customer. SOP.TDO.015 Arc Flash Burn Prevention and Clothing Requirements does not allow members to go past the point of demarcation without a formal arc flash study and the proper category of FR clothing. | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation | [26 empty] | FALSE |  | Days away from Work (H) | 2008-04-21 | 1986-11-26 |  | 2019-03-28 07:00 | 31 | 78 |  | FALSE | Male | Arc Flash |  | FALSE | Payton Martin |  | Days Away from Work | Payton Martin | TRUE |  | Baptist Hospital Burn Unit |  | Burn: Electrical | Dr visit 3/29: Release to light duty eff 4/1/19 per F. Davis Released to full duty eff 6/18/19 | TRUE |  | Lineman | Hand | Injury | Left | TRUE | Carl Kemp | TRUE | 2019 | 3/28/2019 7:30:00 AM | 2.5 | TRUE | FALSE | TRUE | Arc Flash | Holding Ladder for member to test voltage in 4160 VAC Soft Starter | [24 empty] | NA
8735 | Metro Service Center | 2019-02-28 08:30 | Arc flash occurred while checking voltage. | Level 4 |  | FALSE | Member Injury |  | Jerrod Moser | This incident is being conducting at the direction of counsel. | 2019-03-04 07:33 | Power Delivery | Terry Hackett | 2019-04-12 14:24 | 2019-02-28 15:37 | 2019-02-28 15:37 | 2019-04-02 15:21 | 2019-04-08 | 2019-02-28 15:24 | 2019-04-10 14:06 |  |  | Tinker AFB B210 |  |  | Jerrod Moser | Approve | T&D Ops |  | Level 4 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Terry Hackett |  | Details of scenario preceding incident. Two OGE Journeymen linemen were performing the restoration phase of an outage request for building B210 at Tinker Air Force Base. Members completed tailboard for the job of energizing stepdown transformer 344755. Stepdown transformer 344755 which feeds building B210 was successfully energized by the members closing switches in cubicle 344790 SW#3. At this time members went beyond the point of demarcation into building B210 to perform voltage check on 4160 VAC Soft Starter. Member #1 used a 1000 VAC Fluke multimeter with his Class 2 (17KV) rubber gloves with class 2 leather protectors to check the voltage of the 4160 VAC equipment. The multimeter was destroyed due to being overloaded and a large phase to phase flash occurred in the equipment. This resulted in both members receiving 2nd degree burns, the equipment being damaged, and two blown fuses. Transformer 344755 steps down voltage from 12.5KV to 4160V. The transformer is labeled with the point of demarcation as the secondary spades of the transformer (see picture). Both members are journeymen linemen. Both members stated they thought the equipment was 480 volts which is common for our stepdown transformers and that is why the 1000-volt fluke multimeter was used. Members went beyond the point of demarcation into building B210. Shawver and Sons employee told member #1 that he did not have rubber glove to test the customer owned equipment. Member #1 felt like he was being asked to conduct the testing and proceeded to climb the 6’ A frame ladder that was set up in front of the equipment where the panel was removed. Member #1 pointed out the equipment did not have a neutral, so Member #2 looked into the equipment from the ground. At this time Member #1 touched his probes on one phase and then another. The multimeter shorted out and caused a phase to phase arc flash. Two Schawver employees were standing out of the Arc Flash Boundary. After the arc flash occurred the Schawver employees called 911. The injured members were transported by ambulance to the Integris Hospital. Where they were treated and released. Immediately Following the incident, OGE stopped all work, secured the scene, and made the area safe by isolating, grounding, locking, and tagging transformer 344755. Incident Details: Member #1 performing the testing was wearing HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans Class 2 (17KV) Rubber Gloves, Class 2 Leather Protectors, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #2 observing the testing was wearing HRC 2 Sleeveless Vest, HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans, HRC 2 Beanie, HRC2 Balaclava, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #1’s Class 2 rubber gloves (25489 & 25570) were dielectrically tested on 08-16-2018 Salisbury Model AS1000 Arc Rated 10 Cal face shield, Tyndale 11 Cal/CM2 Balaclava, and 20 cal/cm2 suit was readily available on the truck. Members had been trained on OGE SOP.TDO.015 Arc Flash Burn Prevention PPE and Clothing requirements, which prohibits working past the point of demarcation unless an arc flash study has been completed and members are wearing the appropriately rated category of FR clothing. This SOP also requires an arc rated face shield when working on 480 Volt cabinets that are a part of the OGE system. Member #1 Obtained journeyman status on 12/1/2009. Member #2 Obtained journeyman status on 7/29/2016. Member #1 used a 1000 Volt Fluke Multimeter to test voltage on the Customer Owned Benshaw 4160 VAC Soft Starter Model No: CFMVRMX18-3000-4160-12 Hard Hat: Bullard Classic Model C-33 Type 1 Leather protectors: Kunz Glove Size 10.5 #1005 Rubber Glove#’s: Salisbury size 10 class 2 (Internal ID# 25489 & 25570) Both members wore ANSI Z-87 Safety Glasses 1000 Volt Fluke Multimeter T5-1000 was used Documented work observations could not be provided Documented review of SOP.TDO.015 Arc Flash Burn Prevention could not be provided SOP.TDO.015 was set up to be an every other year review, but has not been on the SOP review calendar since 2014 Max incident energy was calculated at 1.9 cal/cm2 (see attachment FW: Tinker4_Arc Flash Results) |  | Terry Hackett | FALSE | Metro Service Center | TRUE |  | FALSE | Construction Services |  | Payton Martin | Carl Kemp |  |  | Approve |  |  | Very High |  |  |  | 4.05 Extreme concentration/perception demands | [9 empty] | 14.04 Inadequate monitoring of compliance |  |  | Arc Flash PPE and Clothing Requirements SOP was ranked as high priority and the determination to put it on the SOP Review calendar every other year was made. Building the SOP review calendar was contracted out and Arc Flash PPE and Clothing Requirements SOP was not added accordingly. Initial review was conducted in 2014. | 18. Failure to Check, Monitor | 9. Abnormal Operation | [26 empty] | FALSE |  | Days away from Work (H) | 2000-03-27 | 1978-05-15 |  | 2019-03-28 07:00 | 24 | 0 |  | FALSE | Male | 1000 volt fluke multimeter short circuited due to being overloaded by the 4160 VAC and caused a phase to phase Arc Flash |  | FALSE | James Caldwell |  | Days Away from Work | James Caldwell | TRUE |  | Baptist Hospital |  | Burn: Electrical | Released to full duty eff 3/25/19 per F. Davis. | TRUE |  | Lineman | Face | Injury | Multiple | TRUE | Carl Kemp | TRUE | 2019 | 3/28/2019 7:30:00 AM | 9 | TRUE | FALSE | TRUE | Arc Flash | Testing Voltage on 4160 VAC Soft Starter | [24 empty] | NA
8735 | Metro Service Center | 2019-02-28 08:30 | Arc flash occurred while checking voltage. | Level 4 |  | FALSE | Member Injury |  | Jerrod Moser | This incident is being conducting at the direction of counsel. | 2019-03-04 07:33 | Power Delivery | Terry Hackett | 2019-04-12 14:24 | 2019-02-28 15:37 | 2019-02-28 15:37 | 2019-04-02 15:21 | 2019-04-08 | 2019-02-28 15:24 | 2019-04-10 14:06 |  |  | Tinker AFB B210 |  |  | Jerrod Moser | Approve | T&D Ops |  | Level 4 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Terry Hackett |  | Details of scenario preceding incident. Two OGE Journeymen linemen were performing the restoration phase of an outage request for building B210 at Tinker Air Force Base. Members completed tailboard for the job of energizing stepdown transformer 344755. Stepdown transformer 344755 which feeds building B210 was successfully energized by the members closing switches in cubicle 344790 SW#3. At this time members went beyond the point of demarcation into building B210 to perform voltage check on 4160 VAC Soft Starter. Member #1 used a 1000 VAC Fluke multimeter with his Class 2 (17KV) rubber gloves with class 2 leather protectors to check the voltage of the 4160 VAC equipment. The multimeter was destroyed due to being overloaded and a large phase to phase flash occurred in the equipment. This resulted in both members receiving 2nd degree burns, the equipment being damaged, and two blown fuses. Transformer 344755 steps down voltage from 12.5KV to 4160V. The transformer is labeled with the point of demarcation as the secondary spades of the transformer (see picture). Both members are journeymen linemen. Both members stated they thought the equipment was 480 volts which is common for our stepdown transformers and that is why the 1000-volt fluke multimeter was used. Members went beyond the point of demarcation into building B210. Shawver and Sons employee told member #1 that he did not have rubber glove to test the customer owned equipment. Member #1 felt like he was being asked to conduct the testing and proceeded to climb the 6’ A frame ladder that was set up in front of the equipment where the panel was removed. Member #1 pointed out the equipment did not have a neutral, so Member #2 looked into the equipment from the ground. At this time Member #1 touched his probes on one phase and then another. The multimeter shorted out and caused a phase to phase arc flash. Two Schawver employees were standing out of the Arc Flash Boundary. After the arc flash occurred the Schawver employees called 911. The injured members were transported by ambulance to the Integris Hospital. Where they were treated and released. Immediately Following the incident, OGE stopped all work, secured the scene, and made the area safe by isolating, grounding, locking, and tagging transformer 344755. Incident Details: Member #1 performing the testing was wearing HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans Class 2 (17KV) Rubber Gloves, Class 2 Leather Protectors, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #2 observing the testing was wearing HRC 2 Sleeveless Vest, HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans, HRC 2 Beanie, HRC2 Balaclava, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #1’s Class 2 rubber gloves (25489 & 25570) were dielectrically tested on 08-16-2018 Salisbury Model AS1000 Arc Rated 10 Cal face shield, Tyndale 11 Cal/CM2 Balaclava, and 20 cal/cm2 suit was readily available on the truck. Members had been trained on OGE SOP.TDO.015 Arc Flash Burn Prevention PPE and Clothing requirements, which prohibits working past the point of demarcation unless an arc flash study has been completed and members are wearing the appropriately rated category of FR clothing. This SOP also requires an arc rated face shield when working on 480 Volt cabinets that are a part of the OGE system. Member #1 Obtained journeyman status on 12/1/2009. Member #2 Obtained journeyman status on 7/29/2016. Member #1 used a 1000 Volt Fluke Multimeter to test voltage on the Customer Owned Benshaw 4160 VAC Soft Starter Model No: CFMVRMX18-3000-4160-12 Hard Hat: Bullard Classic Model C-33 Type 1 Leather protectors: Kunz Glove Size 10.5 #1005 Rubber Glove#’s: Salisbury size 10 class 2 (Internal ID# 25489 & 25570) Both members wore ANSI Z-87 Safety Glasses 1000 Volt Fluke Multimeter T5-1000 was used Documented work observations could not be provided Documented review of SOP.TDO.015 Arc Flash Burn Prevention could not be provided SOP.TDO.015 was set up to be an every other year review, but has not been on the SOP review calendar since 2014 Max incident energy was calculated at 1.9 cal/cm2 (see attachment FW: Tinker4_Arc Flash Results) |  | Terry Hackett | FALSE | Metro Service Center | TRUE |  | FALSE | Construction Services |  | Payton Martin | Carl Kemp |  |  | Approve |  |  | Very High |  |  |  | 4.05 Extreme concentration/perception demands | [9 empty] | 14.04 Inadequate monitoring of compliance |  |  | Arc Flash PPE and Clothing Requirements SOP was ranked as high priority and the determination to put it on the SOP Review calendar every other year was made. Building the SOP review calendar was contracted out and Arc Flash PPE and Clothing Requirements SOP was not added accordingly. Initial review was conducted in 2014. | 18. Failure to Check, Monitor | 9. Abnormal Operation | [26 empty] | FALSE |  | Days away from Work (H) | 2008-04-21 | 1986-11-26 |  | 2019-03-28 07:00 | 31 | 78 |  | FALSE | Male | Arc Flash |  | FALSE | Payton Martin |  | Days Away from Work | Payton Martin | TRUE |  | Baptist Hospital Burn Unit |  | Burn: Electrical | Dr visit 3/29: Release to light duty eff 4/1/19 per F. Davis Released to full duty eff 6/18/19 | TRUE |  | Lineman | Hand | Injury | Left | TRUE | Carl Kemp | TRUE | 2019 | 3/28/2019 7:30:00 AM | 2.5 | TRUE | FALSE | TRUE | Arc Flash | Holding Ladder for member to test voltage in 4160 VAC Soft Starter | [24 empty] | NA
8735 | Metro Service Center | 2019-02-28 08:30 | Arc flash occurred while checking voltage. | Level 4 |  | FALSE | Member Injury |  | Jerrod Moser | This incident is being conducting at the direction of counsel. | 2019-03-04 07:33 | Power Delivery | Terry Hackett | 2019-04-12 14:24 | 2019-02-28 15:37 | 2019-02-28 15:37 | 2019-04-02 15:21 | 2019-04-08 | 2019-02-28 15:24 | 2019-04-10 14:06 |  |  | Tinker AFB B210 |  |  | Jerrod Moser | Approve | T&D Ops |  | Level 4 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Terry Hackett |  | Details of scenario preceding incident. Two OGE Journeymen linemen were performing the restoration phase of an outage request for building B210 at Tinker Air Force Base. Members completed tailboard for the job of energizing stepdown transformer 344755. Stepdown transformer 344755 which feeds building B210 was successfully energized by the members closing switches in cubicle 344790 SW#3. At this time members went beyond the point of demarcation into building B210 to perform voltage check on 4160 VAC Soft Starter. Member #1 used a 1000 VAC Fluke multimeter with his Class 2 (17KV) rubber gloves with class 2 leather protectors to check the voltage of the 4160 VAC equipment. The multimeter was destroyed due to being overloaded and a large phase to phase flash occurred in the equipment. This resulted in both members receiving 2nd degree burns, the equipment being damaged, and two blown fuses. Transformer 344755 steps down voltage from 12.5KV to 4160V. The transformer is labeled with the point of demarcation as the secondary spades of the transformer (see picture). Both members are journeymen linemen. Both members stated they thought the equipment was 480 volts which is common for our stepdown transformers and that is why the 1000-volt fluke multimeter was used. Members went beyond the point of demarcation into building B210. Shawver and Sons employee told member #1 that he did not have rubber glove to test the customer owned equipment. Member #1 felt like he was being asked to conduct the testing and proceeded to climb the 6’ A frame ladder that was set up in front of the equipment where the panel was removed. Member #1 pointed out the equipment did not have a neutral, so Member #2 looked into the equipment from the ground. At this time Member #1 touched his probes on one phase and then another. The multimeter shorted out and caused a phase to phase arc flash. Two Schawver employees were standing out of the Arc Flash Boundary. After the arc flash occurred the Schawver employees called 911. The injured members were transported by ambulance to the Integris Hospital. Where they were treated and released. Immediately Following the incident, OGE stopped all work, secured the scene, and made the area safe by isolating, grounding, locking, and tagging transformer 344755. Incident Details: Member #1 performing the testing was wearing HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans Class 2 (17KV) Rubber Gloves, Class 2 Leather Protectors, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #2 observing the testing was wearing HRC 2 Sleeveless Vest, HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans, HRC 2 Beanie, HRC2 Balaclava, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #1’s Class 2 rubber gloves (25489 & 25570) were dielectrically tested on 08-16-2018 Salisbury Model AS1000 Arc Rated 10 Cal face shield, Tyndale 11 Cal/CM2 Balaclava, and 20 cal/cm2 suit was readily available on the truck. Members had been trained on OGE SOP.TDO.015 Arc Flash Burn Prevention PPE and Clothing requirements, which prohibits working past the point of demarcation unless an arc flash study has been completed and members are wearing the appropriately rated category of FR clothing. This SOP also requires an arc rated face shield when working on 480 Volt cabinets that are a part of the OGE system. Member #1 Obtained journeyman status on 12/1/2009. Member #2 Obtained journeyman status on 7/29/2016. Member #1 used a 1000 Volt Fluke Multimeter to test voltage on the Customer Owned Benshaw 4160 VAC Soft Starter Model No: CFMVRMX18-3000-4160-12 Hard Hat: Bullard Classic Model C-33 Type 1 Leather protectors: Kunz Glove Size 10.5 #1005 Rubber Glove#’s: Salisbury size 10 class 2 (Internal ID# 25489 & 25570) Both members wore ANSI Z-87 Safety Glasses 1000 Volt Fluke Multimeter T5-1000 was used Documented work observations could not be provided Documented review of SOP.TDO.015 Arc Flash Burn Prevention could not be provided SOP.TDO.015 was set up to be an every other year review, but has not been on the SOP review calendar since 2014 Max incident energy was calculated at 1.9 cal/cm2 (see attachment FW: Tinker4_Arc Flash Results) |  | Terry Hackett | FALSE | Metro Service Center | TRUE |  | FALSE | Construction Services |  | Payton Martin | Carl Kemp |  |  | Approve |  |  | Very High | [5 empty] | 6.05 Inadequate review instruction | 7.13 Inadequate reinforcement of proper behavior |  | 9.06 Inadequate work planning or programming | [7 empty] | Member's failed to stop and evaluate the unplanned task of checking voltage. SOP Job Briefings requires that members stop and revisit the job briefing when task are added that were unplanned | 17. Failure to Identify Hazard, Risk | 9. Abnormal Operation | [26 empty] | FALSE |  | Days away from Work (H) | 2000-03-27 | 1978-05-15 |  | 2019-03-28 07:00 | 24 | 0 |  | FALSE | Male | 1000 volt fluke multimeter short circuited due to being overloaded by the 4160 VAC and caused a phase to phase Arc Flash |  | FALSE | James Caldwell |  | Days Away from Work | James Caldwell | TRUE |  | Baptist Hospital |  | Burn: Electrical | Released to full duty eff 3/25/19 per F. Davis. | TRUE |  | Lineman | Face | Injury | Multiple | TRUE | Carl Kemp | TRUE | 2019 | 3/28/2019 7:30:00 AM | 9 | TRUE | FALSE | TRUE | Arc Flash | Testing Voltage on 4160 VAC Soft Starter | [24 empty] | NA
8735 | Metro Service Center | 2019-02-28 08:30 | Arc flash occurred while checking voltage. | Level 4 |  | FALSE | Member Injury |  | Jerrod Moser | This incident is being conducting at the direction of counsel. | 2019-03-04 07:33 | Power Delivery | Terry Hackett | 2019-04-12 14:24 | 2019-02-28 15:37 | 2019-02-28 15:37 | 2019-04-02 15:21 | 2019-04-08 | 2019-02-28 15:24 | 2019-04-10 14:06 |  |  | Tinker AFB B210 |  |  | Jerrod Moser | Approve | T&D Ops |  | Level 4 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Terry Hackett |  | Details of scenario preceding incident. Two OGE Journeymen linemen were performing the restoration phase of an outage request for building B210 at Tinker Air Force Base. Members completed tailboard for the job of energizing stepdown transformer 344755. Stepdown transformer 344755 which feeds building B210 was successfully energized by the members closing switches in cubicle 344790 SW#3. At this time members went beyond the point of demarcation into building B210 to perform voltage check on 4160 VAC Soft Starter. Member #1 used a 1000 VAC Fluke multimeter with his Class 2 (17KV) rubber gloves with class 2 leather protectors to check the voltage of the 4160 VAC equipment. The multimeter was destroyed due to being overloaded and a large phase to phase flash occurred in the equipment. This resulted in both members receiving 2nd degree burns, the equipment being damaged, and two blown fuses. Transformer 344755 steps down voltage from 12.5KV to 4160V. The transformer is labeled with the point of demarcation as the secondary spades of the transformer (see picture). Both members are journeymen linemen. Both members stated they thought the equipment was 480 volts which is common for our stepdown transformers and that is why the 1000-volt fluke multimeter was used. Members went beyond the point of demarcation into building B210. Shawver and Sons employee told member #1 that he did not have rubber glove to test the customer owned equipment. Member #1 felt like he was being asked to conduct the testing and proceeded to climb the 6’ A frame ladder that was set up in front of the equipment where the panel was removed. Member #1 pointed out the equipment did not have a neutral, so Member #2 looked into the equipment from the ground. At this time Member #1 touched his probes on one phase and then another. The multimeter shorted out and caused a phase to phase arc flash. Two Schawver employees were standing out of the Arc Flash Boundary. After the arc flash occurred the Schawver employees called 911. The injured members were transported by ambulance to the Integris Hospital. Where they were treated and released. Immediately Following the incident, OGE stopped all work, secured the scene, and made the area safe by isolating, grounding, locking, and tagging transformer 344755. Incident Details: Member #1 performing the testing was wearing HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans Class 2 (17KV) Rubber Gloves, Class 2 Leather Protectors, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #2 observing the testing was wearing HRC 2 Sleeveless Vest, HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans, HRC 2 Beanie, HRC2 Balaclava, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #1’s Class 2 rubber gloves (25489 & 25570) were dielectrically tested on 08-16-2018 Salisbury Model AS1000 Arc Rated 10 Cal face shield, Tyndale 11 Cal/CM2 Balaclava, and 20 cal/cm2 suit was readily available on the truck. Members had been trained on OGE SOP.TDO.015 Arc Flash Burn Prevention PPE and Clothing requirements, which prohibits working past the point of demarcation unless an arc flash study has been completed and members are wearing the appropriately rated category of FR clothing. This SOP also requires an arc rated face shield when working on 480 Volt cabinets that are a part of the OGE system. Member #1 Obtained journeyman status on 12/1/2009. Member #2 Obtained journeyman status on 7/29/2016. Member #1 used a 1000 Volt Fluke Multimeter to test voltage on the Customer Owned Benshaw 4160 VAC Soft Starter Model No: CFMVRMX18-3000-4160-12 Hard Hat: Bullard Classic Model C-33 Type 1 Leather protectors: Kunz Glove Size 10.5 #1005 Rubber Glove#’s: Salisbury size 10 class 2 (Internal ID# 25489 & 25570) Both members wore ANSI Z-87 Safety Glasses 1000 Volt Fluke Multimeter T5-1000 was used Documented work observations could not be provided Documented review of SOP.TDO.015 Arc Flash Burn Prevention could not be provided SOP.TDO.015 was set up to be an every other year review, but has not been on the SOP review calendar since 2014 Max incident energy was calculated at 1.9 cal/cm2 (see attachment FW: Tinker4_Arc Flash Results) |  | Terry Hackett | FALSE | Metro Service Center | TRUE |  | FALSE | Construction Services |  | Payton Martin | Carl Kemp |  |  | Approve |  |  | Very High | [5 empty] | 6.05 Inadequate review instruction | 7.13 Inadequate reinforcement of proper behavior |  | 9.06 Inadequate work planning or programming | [7 empty] | Member's failed to stop and evaluate the unplanned task of checking voltage. SOP Job Briefings requires that members stop and revisit the job briefing when task are added that were unplanned | 17. Failure to Identify Hazard, Risk | 9. Abnormal Operation | [26 empty] | FALSE |  | Days away from Work (H) | 2008-04-21 | 1986-11-26 |  | 2019-03-28 07:00 | 31 | 78 |  | FALSE | Male | Arc Flash |  | FALSE | Payton Martin |  | Days Away from Work | Payton Martin | TRUE |  | Baptist Hospital Burn Unit |  | Burn: Electrical | Dr visit 3/29: Release to light duty eff 4/1/19 per F. Davis Released to full duty eff 6/18/19 | TRUE |  | Lineman | Hand | Injury | Left | TRUE | Carl Kemp | TRUE | 2019 | 3/28/2019 7:30:00 AM | 2.5 | TRUE | FALSE | TRUE | Arc Flash | Holding Ladder for member to test voltage in 4160 VAC Soft Starter | [24 empty] | NA
8735 | Metro Service Center | 2019-02-28 08:30 | Arc flash occurred while checking voltage. | Level 4 |  | FALSE | Member Injury |  | Jerrod Moser | This incident is being conducting at the direction of counsel. | 2019-03-04 07:33 | Power Delivery | Terry Hackett | 2019-04-12 14:24 | 2019-02-28 15:37 | 2019-02-28 15:37 | 2019-04-02 15:21 | 2019-04-08 | 2019-02-28 15:24 | 2019-04-10 14:06 |  |  | Tinker AFB B210 |  |  | Jerrod Moser | Approve | T&D Ops |  | Level 4 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Terry Hackett |  | Details of scenario preceding incident. Two OGE Journeymen linemen were performing the restoration phase of an outage request for building B210 at Tinker Air Force Base. Members completed tailboard for the job of energizing stepdown transformer 344755. Stepdown transformer 344755 which feeds building B210 was successfully energized by the members closing switches in cubicle 344790 SW#3. At this time members went beyond the point of demarcation into building B210 to perform voltage check on 4160 VAC Soft Starter. Member #1 used a 1000 VAC Fluke multimeter with his Class 2 (17KV) rubber gloves with class 2 leather protectors to check the voltage of the 4160 VAC equipment. The multimeter was destroyed due to being overloaded and a large phase to phase flash occurred in the equipment. This resulted in both members receiving 2nd degree burns, the equipment being damaged, and two blown fuses. Transformer 344755 steps down voltage from 12.5KV to 4160V. The transformer is labeled with the point of demarcation as the secondary spades of the transformer (see picture). Both members are journeymen linemen. Both members stated they thought the equipment was 480 volts which is common for our stepdown transformers and that is why the 1000-volt fluke multimeter was used. Members went beyond the point of demarcation into building B210. Shawver and Sons employee told member #1 that he did not have rubber glove to test the customer owned equipment. Member #1 felt like he was being asked to conduct the testing and proceeded to climb the 6’ A frame ladder that was set up in front of the equipment where the panel was removed. Member #1 pointed out the equipment did not have a neutral, so Member #2 looked into the equipment from the ground. At this time Member #1 touched his probes on one phase and then another. The multimeter shorted out and caused a phase to phase arc flash. Two Schawver employees were standing out of the Arc Flash Boundary. After the arc flash occurred the Schawver employees called 911. The injured members were transported by ambulance to the Integris Hospital. Where they were treated and released. Immediately Following the incident, OGE stopped all work, secured the scene, and made the area safe by isolating, grounding, locking, and tagging transformer 344755. Incident Details: Member #1 performing the testing was wearing HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans Class 2 (17KV) Rubber Gloves, Class 2 Leather Protectors, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #2 observing the testing was wearing HRC 2 Sleeveless Vest, HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans, HRC 2 Beanie, HRC2 Balaclava, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #1’s Class 2 rubber gloves (25489 & 25570) were dielectrically tested on 08-16-2018 Salisbury Model AS1000 Arc Rated 10 Cal face shield, Tyndale 11 Cal/CM2 Balaclava, and 20 cal/cm2 suit was readily available on the truck. Members had been trained on OGE SOP.TDO.015 Arc Flash Burn Prevention PPE and Clothing requirements, which prohibits working past the point of demarcation unless an arc flash study has been completed and members are wearing the appropriately rated category of FR clothing. This SOP also requires an arc rated face shield when working on 480 Volt cabinets that are a part of the OGE system. Member #1 Obtained journeyman status on 12/1/2009. Member #2 Obtained journeyman status on 7/29/2016. Member #1 used a 1000 Volt Fluke Multimeter to test voltage on the Customer Owned Benshaw 4160 VAC Soft Starter Model No: CFMVRMX18-3000-4160-12 Hard Hat: Bullard Classic Model C-33 Type 1 Leather protectors: Kunz Glove Size 10.5 #1005 Rubber Glove#’s: Salisbury size 10 class 2 (Internal ID# 25489 & 25570) Both members wore ANSI Z-87 Safety Glasses 1000 Volt Fluke Multimeter T5-1000 was used Documented work observations could not be provided Documented review of SOP.TDO.015 Arc Flash Burn Prevention could not be provided SOP.TDO.015 was set up to be an every other year review, but has not been on the SOP review calendar since 2014 Max incident energy was calculated at 1.9 cal/cm2 (see attachment FW: Tinker4_Arc Flash Results) |  | Terry Hackett | FALSE | Metro Service Center | TRUE |  | FALSE | Construction Services |  | Payton Martin | Carl Kemp |  |  | Approve |  |  | Very High |  |  |  | 4.04 Routine, monotony, demand for uneventful vigilance |  | 6.03 Infrequent performance | [10 empty] | Members were not familiar with the equipment and did not read equipment labels, due to belief that stepdown transformer had stepped the voltage down to 480 volts. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [26 empty] | FALSE |  | Days away from Work (H) | 2000-03-27 | 1978-05-15 |  | 2019-03-28 07:00 | 24 | 0 |  | FALSE | Male | 1000 volt fluke multimeter short circuited due to being overloaded by the 4160 VAC and caused a phase to phase Arc Flash |  | FALSE | James Caldwell |  | Days Away from Work | James Caldwell | TRUE |  | Baptist Hospital |  | Burn: Electrical | Released to full duty eff 3/25/19 per F. Davis. | TRUE |  | Lineman | Face | Injury | Multiple | TRUE | Carl Kemp | TRUE | 2019 | 3/28/2019 7:30:00 AM | 9 | TRUE | FALSE | TRUE | Arc Flash | Testing Voltage on 4160 VAC Soft Starter | [24 empty] | NA
8735 | Metro Service Center | 2019-02-28 08:30 | Arc flash occurred while checking voltage. | Level 4 |  | FALSE | Member Injury |  | Jerrod Moser | This incident is being conducting at the direction of counsel. | 2019-03-04 07:33 | Power Delivery | Terry Hackett | 2019-04-12 14:24 | 2019-02-28 15:37 | 2019-02-28 15:37 | 2019-04-02 15:21 | 2019-04-08 | 2019-02-28 15:24 | 2019-04-10 14:06 |  |  | Tinker AFB B210 |  |  | Jerrod Moser | Approve | T&D Ops |  | Level 4 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Terry Hackett |  | Details of scenario preceding incident. Two OGE Journeymen linemen were performing the restoration phase of an outage request for building B210 at Tinker Air Force Base. Members completed tailboard for the job of energizing stepdown transformer 344755. Stepdown transformer 344755 which feeds building B210 was successfully energized by the members closing switches in cubicle 344790 SW#3. At this time members went beyond the point of demarcation into building B210 to perform voltage check on 4160 VAC Soft Starter. Member #1 used a 1000 VAC Fluke multimeter with his Class 2 (17KV) rubber gloves with class 2 leather protectors to check the voltage of the 4160 VAC equipment. The multimeter was destroyed due to being overloaded and a large phase to phase flash occurred in the equipment. This resulted in both members receiving 2nd degree burns, the equipment being damaged, and two blown fuses. Transformer 344755 steps down voltage from 12.5KV to 4160V. The transformer is labeled with the point of demarcation as the secondary spades of the transformer (see picture). Both members are journeymen linemen. Both members stated they thought the equipment was 480 volts which is common for our stepdown transformers and that is why the 1000-volt fluke multimeter was used. Members went beyond the point of demarcation into building B210. Shawver and Sons employee told member #1 that he did not have rubber glove to test the customer owned equipment. Member #1 felt like he was being asked to conduct the testing and proceeded to climb the 6’ A frame ladder that was set up in front of the equipment where the panel was removed. Member #1 pointed out the equipment did not have a neutral, so Member #2 looked into the equipment from the ground. At this time Member #1 touched his probes on one phase and then another. The multimeter shorted out and caused a phase to phase arc flash. Two Schawver employees were standing out of the Arc Flash Boundary. After the arc flash occurred the Schawver employees called 911. The injured members were transported by ambulance to the Integris Hospital. Where they were treated and released. Immediately Following the incident, OGE stopped all work, secured the scene, and made the area safe by isolating, grounding, locking, and tagging transformer 344755. Incident Details: Member #1 performing the testing was wearing HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans Class 2 (17KV) Rubber Gloves, Class 2 Leather Protectors, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #2 observing the testing was wearing HRC 2 Sleeveless Vest, HRC 2 Hoody, HRC 2 Long Sleeve Shirt, HRC 2 Jeans, HRC 2 Beanie, HRC2 Balaclava, Hard Hat, Safety Glasses, and EH Rated Safety Toed Shoes. Member #1’s Class 2 rubber gloves (25489 & 25570) were dielectrically tested on 08-16-2018 Salisbury Model AS1000 Arc Rated 10 Cal face shield, Tyndale 11 Cal/CM2 Balaclava, and 20 cal/cm2 suit was readily available on the truck. Members had been trained on OGE SOP.TDO.015 Arc Flash Burn Prevention PPE and Clothing requirements, which prohibits working past the point of demarcation unless an arc flash study has been completed and members are wearing the appropriately rated category of FR clothing. This SOP also requires an arc rated face shield when working on 480 Volt cabinets that are a part of the OGE system. Member #1 Obtained journeyman status on 12/1/2009. Member #2 Obtained journeyman status on 7/29/2016. Member #1 used a 1000 Volt Fluke Multimeter to test voltage on the Customer Owned Benshaw 4160 VAC Soft Starter Model No: CFMVRMX18-3000-4160-12 Hard Hat: Bullard Classic Model C-33 Type 1 Leather protectors: Kunz Glove Size 10.5 #1005 Rubber Glove#’s: Salisbury size 10 class 2 (Internal ID# 25489 & 25570) Both members wore ANSI Z-87 Safety Glasses 1000 Volt Fluke Multimeter T5-1000 was used Documented work observations could not be provided Documented review of SOP.TDO.015 Arc Flash Burn Prevention could not be provided SOP.TDO.015 was set up to be an every other year review, but has not been on the SOP review calendar since 2014 Max incident energy was calculated at 1.9 cal/cm2 (see attachment FW: Tinker4_Arc Flash Results) |  | Terry Hackett | FALSE | Metro Service Center | TRUE |  | FALSE | Construction Services |  | Payton Martin | Carl Kemp |  |  | Approve |  |  | Very High |  |  |  | 4.04 Routine, monotony, demand for uneventful vigilance |  | 6.03 Infrequent performance | [10 empty] | Members were not familiar with the equipment and did not read equipment labels, due to belief that stepdown transformer had stepped the voltage down to 480 volts. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [26 empty] | FALSE |  | Days away from Work (H) | 2008-04-21 | 1986-11-26 |  | 2019-03-28 07:00 | 31 | 78 |  | FALSE | Male | Arc Flash |  | FALSE | Payton Martin |  | Days Away from Work | Payton Martin | TRUE |  | Baptist Hospital Burn Unit |  | Burn: Electrical | Dr visit 3/29: Release to light duty eff 4/1/19 per F. Davis Released to full duty eff 6/18/19 | TRUE |  | Lineman | Hand | Injury | Left | TRUE | Carl Kemp | TRUE | 2019 | 3/28/2019 7:30:00 AM | 2.5 | TRUE | FALSE | TRUE | Arc Flash | Holding Ladder for member to test voltage in 4160 VAC Soft Starter | [24 empty] | NA
8737 | Seminole PP; EGX Gath/Trans | 2019-02-20 14:00 | Crane subcontractor was performing lift in breezeway. Ground was barricaded, but the catwalks between the turbine and boiler were not. Another site contractor stepped outside plant door onto catwalk as hook moved toward catwalk. Contractor stopped and reported to plant personnel. | Level 2 |  | TRUE | Contractor | Donnie Jones |  |  |  | Power Supply | Patrick Coleman | 2019-04-13 14:21 | 2019-03-01 16:28 | 2019-03-01 16:28 | 2019-03-20 20:05 | 2019-03-06 14:00 | 2019-03-01 16:06 | 2019-03-28 07:24 |  | 2019-03-25 10:31 | Seminole PP, Unit 1, Breezeway Turbine-to-Boiler Catwalk Elev. 2 & 3 |  |  | Jesse Murray | I Approve. Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Patrick Coleman |  | The close call occurred on Wednesday, February 20, 2019. A Power Plant Services (PPS) contractor walked out onto a 3rd floor catwalk, connecting the turbine building and the boiler structure, for a smoke break. As he opened the door leading outside and walked onto the catwalk, he noticed a crane hook in his peripheral vision estimated at 6’-10’ from the handrail of the catwalk. When the PPS contractor walked out onto the catwalk, a ZACHRY contractor immediately saw him and let him know it was okay to be on the catwalk. The PPS contractor, however, left the catwalk to report an un-barricaded lifting zone to the control room. This crane was used to lift steel up to the top of the boiler structure through the openings in the stairwell. This close call occurred while the crane was being rigged down to leave the job site. At the time of the close call, all lifts had been completed following a pre-approved lift plan. None of the planned lifts involved lifting activities above the catwalk. According to the plan, steel was to be lifted from the ground up to the 6th floor of the boiler structure through the stair well. This level of the structure was barricaded and had spotters during the lift. The ground level was barricaded as well. Upon review, the crane truck was backed in and the boom rotated roughly 45°to the northeast to perform the lift. While the crane was rigging down, it was rotated back to a position 90° to the catwalk, where the hook would have been the closest to the catwalk at the time the PPS contractor walked out for his break. To clarify, following the investigation it was determined that the crane hook was not moving (initial reports were that it was moving towards the catwalk) when the PPS contractor accessed the catwalk and was only in close proximity. The risk assessment for this close call was re-evaluated to be medium, and not high. The reasoning being that based on the approved lifting plan, the lifting area was at least 15’ from the catwalk, reducing the likelihood of an incident occurring, while the consequences if there were to be an incident, remained the same. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | TRUE | Power Supply Services |  | Patrick Coleman | Patrick Coleman |  | Brian Huckabay | Approved no comments. | Brian Huckabay |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Situational awareness in regards to barricading pathways. | 21. Inadequate Guards or Barriers | 2. Struck By (Hit By Moving Object) |  | Reviewed |  |  |  | Injury / Illness |  | Patrick Coleman | [5 empty] | 2. Struck By (Hit By Moving Object) | Patrick Coleman | Power Plant Services (PPRS) | Jason Muehe |  |  |  | Patrick Coleman | [71 empty] | 615514
8738 | Horseshoe Lake Power Plant | 2019-03-01 15:00 | Siemens was unloading materials and equipment they had ordered from an enclosed truck. Siemens member was using the Horseshoe Lake rough terrain telescoping boom forklift to unload the truck. The load was near the front of the truck. While backing out, the rear of the forklift went down while following the terrain and the front came up and contacted the truck enclosure causing minor damage. Forklift was not damaged. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Daniel Perry | 2019-03-22 11:10 | 2019-03-02 14:26 | 2019-03-02 14:26 | 2019-03-13 16:46 | 2019-03-15 15:00 | 2019-03-01 18:00 | 2019-03-13 17:12 |  |  | Plant road on the North end of Unit 8. |  |  | Guillermo Sarmiento | 03/13/2019 - Had some questions. Send email to Dan. Also sent workflow back. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Daniel Perry |  | Siemens was unloading materials and equipment they had ordered from an enclosed truck. Siemens member was using the Horseshoe Lake rough terrain telescoping boom forklift to unload the truck. A spotter was utilized during the unloading of equipment. The load was near the front of the truck. While backing out, the rear of the forklift went down while following the terrain and the front came up and contacted the truck enclosure causing minor damage. Forklift was not damaged. During the investigation, it was found that: The contractor did perform a Take 5, which is the equivalent of our SWP. A spotter was used during unloading. The material to be unloaded was at the front of the box truck. Did not use a pallet jack to move it closer to the back to eliminate the distance to extend the boom. Employee's did have OGE training and authorized to use OGE Sky Track. Inspection was performed on the equipment prior to usage. Weather and lighting did not play a role in creating a hazardous condition. Contractor was reminded that incidents need to be reported as soon as safely possible. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Maintenance |  | Daniel Perry | Daniel Perry |  | Daniel Perry | I have reviewed this incident and I approve. | Daniel Perry |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | The truck delivering the tooling was an enclosed box truck. Tooling was moved to the rear to provide better access. Contractor was unloading the tooling using a rough terrain forklift. While backing out with the load, the operator stated that the rear tires went down in a low spot in the road causing the front of the boom to contact the top door frame area of the box truck. Contractor stated that a spotter was being used. Contractor had been trained on forklift operation. | 11. Improper Position for Task | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Daniel Perry | Damage |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Daniel Perry | Siemens | Steve Baker |  | 3rd Party Property/Equipment |  | Daniel Perry |  |  |  | F34-794 | TRUE | [66 empty] | 9581777
8739 | Muskogee Power Plant | 2019-03-02 16:00 | Ryan’s Trucking was coming through to load fly ash. Security took his drivers license, opened up the gate and turned to make the driver a OGE card. As Security Guard started to make the driver a card Security heard the truck driver hit his brakes. Security figured the gate started to shut and hit the open button again and truck driver stepped out of his truck and explained that the gate was closing and hit his truck. Security guard went and looked and the truck has a scrape on the fender but the gate doesn’t seem to have any damages. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Joel Leavell | 2019-03-21 08:51 | 2019-03-02 17:53 | 2019-03-02 17:53 | 2019-03-14 13:18 | 2019-03-16 16:00 | 2019-03-02 17:39 | 2019-03-15 14:45 |  | 2019-03-14 13:23 | Muskogee PP Plant Security Gate entrance. NE side of Plant campus. |  |  | Jesse Murray | I Approve Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Joel Leavell |  | The gate closed on the Fly Ash truck. The safety circuit should have opened the gate when photo eye detected the truck. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | Operations |  | Joel Leavell | Joel Leavell |  |  | Reviewed. SC |  |  | Medium | [7 empty] | 8.2.2 Improper conduct that is not condoned: Unintentional | [8 empty] | The safety circuit's photo did not prevent the gate from striking the Fly Ash Truck. | 23. Defective Tools, Equipment or Materials | 2. Struck By (Hit By Moving Object) |  | Reviewed Bob Wright |  |  |  | Vehicle |  | Joel Leavell | [5 empty] | 2. Struck By (Hit By Moving Object) | Joel Leavell | Ryan Trucking | Sammuel Barrett | [75 empty] | N/A
8740 | Redbud Plant | 2019-03-03 12:00 | Concrete was a slick and contractor slipped and fell and jammed finger. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Scott Carroll | 2019-04-17 08:17 | 2019-03-04 10:10 | 2019-03-04 10:10 | 2019-04-08 09:38 | 2019-03-17 12:00 | 2019-03-04 10:06 | 2019-04-08 09:54 |  |  | Unit 2 Power Block |  |  | Guillermo Sarmiento | Agree with report and findings. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Scott Carroll |  | While walking through the unit to job site, the forklift guide stepped on a slick spot on the concrete. Due to the weather conditions, ice melt has been applied frequently in order to reduce the risk of slips on slick surfaces. Contractor fell and put left hand down to catch himself. Did not notice any injury or issues at the time of the incident. Hazard was shared with other contract employees working in the area and is barricaded. Finger started hurting later that day. Finger was slightly swollen. Incident was then reported to plant contact. First aid was administered to contract employee. No serious injury was sustained. |  |  |  | Redbud Plant | FALSE |  | TRUE | Maintenance |  | Scott Carroll | Scott Carroll |  | Shawn Gribble | I agree with the corrective actions on this investigation. | Shawn Gribble |  | Low |  |  | 3.06 Exposure to temperature extremes | [13 empty] | CONTRACT MEMBER SLIPPED ON ICE | 17. Failure to Identify Hazard, Risk | 4. Fall on Same Level (Slip and Fall, Trip Over) | [5 empty] | Injury / Illness |  | Scott Carroll | [5 empty] | 4. Fall on Same Level (Slip and Fall, Trip Over) | Scott Carroll | TEAM | James Spell |  |  |  | Scott Carroll | [71 empty] | 9576226
8741 | Muskogee Service Center | 2019-02-20 | While member was unloading backhoe off trailer the backhoe slid and front tires came off of ramps. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Delivery | Brian McKinney | 2019-03-15 12:14 | 2019-03-04 13:46 | 2019-03-04 13:46 | 2019-03-13 15:36 | 2019-03-06 | 2019-03-04 13:29 | 2019-03-14 15:24 |  | 2019-03-14 05:33 | Kellyville service center |  |  | Lindle Coleman | Review risk ranking requested. A causal factor would be training. Member had not had a FPR completed the action item added will be to correct this training oversite. | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Brian McKinney |  | Member climbed onto backhoe seat and tried to buckle seat belt but it was locked and would not reach across the seat. So member then disengaged parking break and switched lever into reverse and placed gear shift into 1st gear. Member let off brake and backed off slowly until wheels climbed out of recessed holes as the front wheels reached the rear recessed holes and began to slide off the right side of the trailer, as the member pressed the brake it didn't stop and continued to slide till both front tires were on the ground and the machine is now horizontal to the trailer. Member did have backer present. Weather was cold and wet with a slight frost. |  |  |  | Muskogee Service Center | FALSE |  | TRUE | Construction Services |  | Aaron Thrall | Brian McKinney |  | Michael Fox | I approve | Michael Fox |  | Medium |  |  |  |  | 5.04 Inadequate update training | [8 empty] | 14.02.4 Inadequate communication of standards: training |  |  | Member climbed onto backhoe seat and tried to buckle seat belt but it was locked and would not reach across the seat. So member then disengaged parking break and switched lever into reverse and placed gear shift into 1st gear. Member let off brake and backed off slowly until wheels climbed out of recessed holes as the front wheels reached the rear recessed holes and began to slide off the right side of the trailer, as the member pressed the brake it didn't stop and continued to slide till both front tires were on the ground and the machine is now horizontal to the trailer. Member did have backer present. Weather was cold and wet with a slight frost. | 15. Using Equipment Improperly | 3. Fall from Elevation to Lower Level |  | I approve. | [90 empty] | NA
8741 | Muskogee Service Center | 2019-02-20 | While member was unloading backhoe off trailer the backhoe slid and front tires came off of ramps. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Delivery | Brian McKinney | 2019-03-15 12:14 | 2019-03-04 13:46 | 2019-03-04 13:46 | 2019-03-13 15:36 | 2019-03-06 | 2019-03-04 13:29 | 2019-03-14 15:24 |  | 2019-03-14 05:33 | Kellyville service center |  |  | Lindle Coleman | Review risk ranking requested. A causal factor would be training. Member had not had a FPR completed the action item added will be to correct this training oversite. | T&D Ops |  | Level 2 | Property Damage |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Brian McKinney |  | Member climbed onto backhoe seat and tried to buckle seat belt but it was locked and would not reach across the seat. So member then disengaged parking break and switched lever into reverse and placed gear shift into 1st gear. Member let off brake and backed off slowly until wheels climbed out of recessed holes as the front wheels reached the rear recessed holes and began to slide off the right side of the trailer, as the member pressed the brake it didn't stop and continued to slide till both front tires were on the ground and the machine is now horizontal to the trailer. Member did have backer present. Weather was cold and wet with a slight frost. |  |  |  | Muskogee Service Center | FALSE |  | TRUE | Construction Services |  | Aaron Thrall | Brian McKinney |  | Michael Fox | I approve | Michael Fox |  | Medium |  |  |  |  | 5.04 Inadequate update training | [8 empty] | 14.02.4 Inadequate communication of standards: training |  |  | Member climbed onto backhoe seat and tried to buckle seat belt but it was locked and would not reach across the seat. So member then disengaged parking break and switched lever into reverse and placed gear shift into 1st gear. Member let off brake and backed off slowly until wheels climbed out of recessed holes as the front wheels reached the rear recessed holes and began to slide off the right side of the trailer, as the member pressed the brake it didn't stop and continued to slide till both front tires were on the ground and the machine is now horizontal to the trailer. Member did have backer present. Weather was cold and wet with a slight frost. | 15. Using Equipment Improperly | 3. Fall from Elevation to Lower Level |  | I approve. | [90 empty] | NA
8742 | Metro Service Center | 2019-02-27 14:30 | Auger motor bled off and allowed safety mechanism that locks motor to the second stage of the boom to engage. When boom was telescoped out auger moved forward and bent auger stowing assembly. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Delivery | Hershel Goodson | 2019-04-25 12:54 | 2019-03-05 07:25 | 2019-03-05 07:25 | 2019-04-15 07:34 | 2019-03-13 14:30 | 2019-03-05 07:03 | 2019-04-24 13:19 |  | 2019-04-15 09:35 | Norman Road Widening North of Alameda and 24th St |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Hershel Goodson |  | Auger assembly was missing parts that enable the safety mechanism that locks the motor to the second stage of the boom to engage. When boom was telescoped out auger moved forward and bent auger stowing assembly. Facts ascertained: Truck was turned into fleet for repair in 2016 Per fleet all the parts that allow the safety latch to function properly were not installed (2016) After receiving line truck from the garage in 2016 primary operator was aware the auger safety latch would not disengage unless you rolled the auger up before telescoping out. Primary Operator was off work the day of the incident Member operating the line truck went to telescope out the boom and did not realize the hook was still engaged Safety latch cannot be seen from the operators seat |  |  |  | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Hershel Goodson | Jimmy Combs |  | Gary Lassley | The expectation has been set by operations management not to leave the yard with a piece of equipment that is not operating correctly. | Gary Lassley |  | Medium |  |  |  | 4.04 Routine, monotony, demand for uneventful vigilance |  | 6.03 Infrequent performance |  | 8.1.2 Improper conduct that is condoned: Unintentional |  | 10.05 Inadequate assessment of operational readiness |  |  | 13.02 Inadequate human factors/ergonomics considerations |  |  |  | Auger stow safety latch was not functioning properly 4.04: Telescoping the boom out on a line truck is a routine task 6.03 Member does not operated this line truck often (primary operator was off) 10.05 Fleet released truck with an operational issue 13.02 Safety latch cannot be seen from operator seat. 8.1.2 Unintentional make what you have work message | 06. Using Defective Equipment | 1. Struck Against (Running or Bumping Into) |  | Reviewed/Approved. The expectation has been set by operations management not to leave the yard with a piece of equipment that is not operating correctly. | [66 empty] | Auger stowing bracket bent. 6 bolts sheared off | 7000 | Hershel Goodson | Industrial/Heavy Equipment |  | F15-298 | [18 empty] | N/A
8743 | Muskogee Power Plant | 2019-03-05 19:00 | Member was removing personal items from trailer to transition to Muskogee plant where he is scheduled to report to tomorrow. He parked vehicle close to front door so he could transport items into company vehicle. When moving vehicle out of trailer area member turned vehicle too sharp and struck tree with rear driver quarter panel putting a small scratch on vehicle. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Supply | Kelly Casey | 2019-03-21 12:17 | 2019-03-05 21:03 | 2019-03-05 21:03 | 2019-03-08 10:19 | 2019-03-19 19:00 | 2019-03-05 19:00 | 2019-03-12 16:47 |  |  | Members off site temporary residence ( rv trailer ) parked at trailer park in Luther Ok. |  |  | Chrysty Dorsey | Approved to close. | Power Supply |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Kelly Casey |  | Member was removing personal items from trailer to transition to a different location for work the next day. Member backed into graveled parking area on a curved drive. The parking drive was not lighted and it was dark with only backing lights available, member did not judge distance from fixed object (tree) and made light contact with tree bark . After conversation with member he was attempting to get close to door of trailer to aid in transitioning belongings into vehicle. He thought he had enough clearance at the time to avoid contact with the tree. Fleet was contacted and instructed member to take vehicle to service center to evaluate. Fleet members inspected damage and instructed member to go back to work they would close the ticket as there was no lasting damage to property and the scratch would wipe out. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | Special Services |  | Brent Case | Kelly Casey |  | Brian Huckabay | Approved, in future it would be good to provide information such as had the member worked prior to the incident, if so how many hours. Was a 360 conducted and did he notice the tree then? Why not back in and walk around the truck. etc. What are the other contributing factors we should be aware of. Brian | Brian Huckabay |  | Low | [8 empty] | 9.12 Inadequate performance measurement and evaluation | [7 empty] | Member used poor judgement and distance to back into space. | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) | [74 empty] | TRUE |  | Luther | Struck Fixed Object | Turned Into Object | 2011-05-08 19:00 |  | FALSE |  |  | Night |  |  | Gravel |  | Clear |  |  | 615568
8744 | Shawnee Service Center | 2019-03-05 19:30 | An OGE fleet mechanic had completed a repair on unit F10/F28-271. F10/F28-271 is a mobile road crane. The member was backing the unit out of the service bay when the overhead crane control pendant cable got caught on F10/F28-271's boom. The member did not see the cable get caught. The control cable pendant was pulled out of the overhead crane. | Level 2 |  | FALSE | Vehicle |  |  |  |  | OG&E Corp Services | Nathan Gooch | 2019-05-10 10:46 | 2019-03-06 13:28 | 2019-03-06 13:27 | 2019-03-14 15:30 | 2019-03-19 19:30 | 2019-03-06 13:12 | 2019-04-29 13:22 |  | 2019-03-14 15:34 | The southwest bay in Shawnee Garage |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Nathan Gooch |  | An OGE fleet mechanic had completed a repair on unit F10/F28-271. F10/F28-271 is a mobile road crane. The member was backing the unit out of the service bay when the overhead crane control pendant cable got caught on F10/F28-271's boom. The member did not see the cable get caught. The control cable pendant was pulled out of the overhead crane. Upon investigation it was discovered that the control pendant was not pulled from the crane but the power cable from the cable retractor was what got caught. When the crane is at the north end of the track, the cable sagged roughly 2 to 3 feet below the beam. When the unit is moved into the bay the truck has to be positioned under the beam so that it misses the hoist chain box. Operator did 360 prior to backing unit out of the bay. Crane beam height is 15 ft. The hoist is approximately 2ft below the beam. The hoist is approximately 2 ft. above the truck boom. The cable sags lower than the hoist. There was no damage truck or the crane other than the cable being disconnected. |  |  |  | Shawnee Service Center | FALSE |  | FALSE | UTS - Asset & LC Mgmt |  | Lowell Jones | Nathan Gooch |  | Paul Jefferson | I approve the long term solution - 6307 | Paul Jefferson |  | Medium | [9 empty] | 10.08 Inadequate evaluation of changes |  |  | 13.01 Inadequate assessment of needs and risks |  |  |  | While backing vehicle out of the service bay the member did not identify the low hanging power cable on the overhead hoist. | 23. Defective Tools, Equipment or Materials | 1. Struck Against (Running or Bumping Into) |  | Approved, Cody Vinyard | [72 empty] | TRUE |  | Shawnee | Struck Fixed Object | Backing Related | 2012-06-10 19:00 |  | FALSE |  |  | Night |  |  | Concrete/Pavement |  | Clear |  |  | 0
8745 | Enid Service Center | 2019-03-06 13:30 | Arborist struck on wrist by branch last week. Sought medical attention this week for continued pain. treated and released with no restriction. | Level 1 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Christopher Martin | 2019-03-20 17:37 | 2019-03-06 14:48 | 2019-03-06 14:48 | 2019-03-20 15:56 | 2019-03-20 13:30 | 2019-03-06 14:42 | 2019-03-20 16:15 |  |  | Distribution right of way in the Enid area. |  |  | Jerrie Looney | J. Looney, 3.20.19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Christopher Martin |  | The employee was hit in the wrist by a branch while loading the chipper. He complained about it being painful but was able to move it freely so he continued to work the rest of the day. He had Friday (2/29) off and came back to work on Monday. He has worked all week but complained about how his wrist was still hurting him today. The GF took the worker to a clinic and the X-Ray did not reveal any broken bones. He was not prescribed any medication and was released with the direction of taking over the counter pain medication and no heavy lifting for a while. The doctor thought it was just bruised. |  |  |  | Enid Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Grant Ehlen | Christopher Martin |  |  | Another example of Wright reporting incidents regardless of severity. Good for them. Not recordable, but useful to capture for learning and reference. No further action anticipated. Cassada |  |  | Low |  | 2.07 Slow reaction time | [14 empty] | The employee was hit in the wrist by a branch while loading the chipper. He complained about it being painful but was able to move it freely so he continued to work the rest of the day. He had Friday (2/29) off and came back to work on Monday. He has worked all week but complained about how his wrist was still hurting him today. The GF took the worker to a clinic and the X-Ray did not reveal any broken bones. He was not prescribed any medication and was released with the direction of taking over the counter pain medication and no heavy lifting for a while. The doctor thought it was just bruised. | 19. Failure to React, Correct | 2. Struck By (Hit By Moving Object) | [5 empty] | Injury / Illness |  | Christopher Martin |  | Wrist smacked by branch | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Grant Ehlen | Wright Tree Service | Trimmer | Crush/Smash |  | Wrist | Christopher Martin |  | FALSE | [69 empty] | none
8746 | Woodward Service Center | 2019-03-06 11:00 | While positioning pole into grabbers pole contacted back of members leg leaving splinter lodged in members leg. | Level 3 |  | FALSE | Member Injury |  | Lindle Coleman | Assigned | 2019-03-12 12:38 | Power Delivery | Tyler Scott | 2019-04-10 14:04 | 2019-03-06 15:47 | 2019-03-06 15:47 | 2019-03-26 09:11 | 2019-03-20 11:00 | 2019-03-06 11:30 | 2019-04-01 10:33 | 2019-04-01 11:14 | 2019-03-29 12:17 | 182312 E county rd 50 Gage Ok |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Lewis Wilson |  | On March 6 2019, at 11:00 A.M. A Woodward crew was setting up on a job site to set a pole on a new single phase line. Crew had already framed poles and they had strung out the wire for the job. The crew had set up on the pole and moved it so they could slip tie the wire in before setting the pole. Hayden Bierig was operating the line truck. He began to lift the pole with the winch line/sling to grab ahold of it with the claws located on the end of the boom. Josiah Duncan was positioned over the butt of the pole to guide it as it was being lifted. At this point he put his weight on the butt of the pole to leverage the pole top higher. As he was pushing his weight down on the pole, the wire on the pole top became caught in some bushes. When the wire came free from the bush the pole slid approximately 1-2ft backwards against Jousiahs leg that was still placed over the butt of the pole. The contact between the members leg and a rough part of the pole caused a splinter to enter his leg through his jeans. After the incident the member felt some discomfort in his leg at which point he discovered the splinter and tried to remove it. When he could not remove the splinter he alerted his foreman. At this time his foreman transported him to the OGE McBride Clinic. The physician at Mcbride was able to remove the wood from the members leg and he was able to return to work. | Luke Kennedy | Lewis Wilson | FALSE | Woodward Service Center | FALSE |  | FALSE | Construction Services |  | Kevin Pettigrew | Tyler Scott |  | Chad Inman | I feel like the findings of the incident were very thorough and that the corrective actions are listed are appropriate. Thank you. | Chad Inman | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience |  |  |  |  | 10.08 Inadequate evaluation of changes | [6 empty] | Poor body positioning against the pole while it was being lifted into the jaws of the boom. | 09. Improper Placement | 6. Caught On (Snagged, Hung) | approved | I believe the corrective actions decided upon by the investigation team are the most effective means of mitigation at this time. | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2018-04-09 | 1997-06-11 |  | 2019-03-06 06:00 | 0 | 0 |  | FALSE | Male | Pole contacted the back of members leg and a shard of wood punctured the members skin. |  | FALSE | Josiah Duncan |  | Recordable | Josiah Duncan | FALSE |  |  |  | Puncture | No lost time per F. Davis 4/9/19. | TRUE |  | Lineman Appr | Thigh | Injury | Left | TRUE | Kevin Pettigrew | TRUE | 2019 | 3/6/2019 6:00:00 AM |  | TRUE | FALSE | FALSE | piece of wood | [25 empty] | N/A
8746 | Woodward Service Center | 2019-03-06 11:00 | While positioning pole into grabbers pole contacted back of members leg leaving splinter lodged in members leg. | Level 3 |  | FALSE | Member Injury |  | Lindle Coleman | Assigned | 2019-03-12 12:38 | Power Delivery | Tyler Scott | 2019-04-10 14:04 | 2019-03-06 15:47 | 2019-03-06 15:47 | 2019-03-26 09:11 | 2019-03-20 11:00 | 2019-03-06 11:30 | 2019-04-01 10:33 | 2019-04-01 11:14 | 2019-03-29 12:17 | 182312 E county rd 50 Gage Ok |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Lewis Wilson |  | On March 6 2019, at 11:00 A.M. A Woodward crew was setting up on a job site to set a pole on a new single phase line. Crew had already framed poles and they had strung out the wire for the job. The crew had set up on the pole and moved it so they could slip tie the wire in before setting the pole. Hayden Bierig was operating the line truck. He began to lift the pole with the winch line/sling to grab ahold of it with the claws located on the end of the boom. Josiah Duncan was positioned over the butt of the pole to guide it as it was being lifted. At this point he put his weight on the butt of the pole to leverage the pole top higher. As he was pushing his weight down on the pole, the wire on the pole top became caught in some bushes. When the wire came free from the bush the pole slid approximately 1-2ft backwards against Jousiahs leg that was still placed over the butt of the pole. The contact between the members leg and a rough part of the pole caused a splinter to enter his leg through his jeans. After the incident the member felt some discomfort in his leg at which point he discovered the splinter and tried to remove it. When he could not remove the splinter he alerted his foreman. At this time his foreman transported him to the OGE McBride Clinic. The physician at Mcbride was able to remove the wood from the members leg and he was able to return to work. | Luke Kennedy | Lewis Wilson | FALSE | Woodward Service Center | FALSE |  | FALSE | Construction Services |  | Kevin Pettigrew | Tyler Scott |  | Chad Inman | I feel like the findings of the incident were very thorough and that the corrective actions are listed are appropriate. Thank you. | Chad Inman | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  |  | 10.08 Inadequate evaluation of changes | [6 empty] | Poor body positioning against the pole while it was being lifted into the jaws of the boom. | 09. Improper Placement | 6. Caught On (Snagged, Hung) | approved | I believe the corrective actions decided upon by the investigation team are the most effective means of mitigation at this time. | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2018-04-09 | 1997-06-11 |  | 2019-03-06 06:00 | 0 | 0 |  | FALSE | Male | Pole contacted the back of members leg and a shard of wood punctured the members skin. |  | FALSE | Josiah Duncan |  | Recordable | Josiah Duncan | FALSE |  |  |  | Puncture | No lost time per F. Davis 4/9/19. | TRUE |  | Lineman Appr | Thigh | Injury | Left | TRUE | Kevin Pettigrew | TRUE | 2019 | 3/6/2019 6:00:00 AM |  | TRUE | FALSE | FALSE | piece of wood | [25 empty] | N/A
8746 | Woodward Service Center | 2019-03-06 11:00 | While positioning pole into grabbers pole contacted back of members leg leaving splinter lodged in members leg. | Level 3 |  | FALSE | Member Injury |  | Lindle Coleman | Assigned | 2019-03-12 12:38 | Power Delivery | Tyler Scott | 2019-04-10 14:04 | 2019-03-06 15:47 | 2019-03-06 15:47 | 2019-03-26 09:11 | 2019-03-20 11:00 | 2019-03-06 11:30 | 2019-04-01 10:33 | 2019-04-01 11:14 | 2019-03-29 12:17 | 182312 E county rd 50 Gage Ok |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Lewis Wilson |  | On March 6 2019, at 11:00 A.M. A Woodward crew was setting up on a job site to set a pole on a new single phase line. Crew had already framed poles and they had strung out the wire for the job. The crew had set up on the pole and moved it so they could slip tie the wire in before setting the pole. Hayden Bierig was operating the line truck. He began to lift the pole with the winch line/sling to grab ahold of it with the claws located on the end of the boom. Josiah Duncan was positioned over the butt of the pole to guide it as it was being lifted. At this point he put his weight on the butt of the pole to leverage the pole top higher. As he was pushing his weight down on the pole, the wire on the pole top became caught in some bushes. When the wire came free from the bush the pole slid approximately 1-2ft backwards against Jousiahs leg that was still placed over the butt of the pole. The contact between the members leg and a rough part of the pole caused a splinter to enter his leg through his jeans. After the incident the member felt some discomfort in his leg at which point he discovered the splinter and tried to remove it. When he could not remove the splinter he alerted his foreman. At this time his foreman transported him to the OGE McBride Clinic. The physician at Mcbride was able to remove the wood from the members leg and he was able to return to work. | David Fox | Lewis Wilson | FALSE | Woodward Service Center | FALSE |  | FALSE | Construction Services |  | Kevin Pettigrew | Tyler Scott |  | Chad Inman | I feel like the findings of the incident were very thorough and that the corrective actions are listed are appropriate. Thank you. | Chad Inman | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience |  |  |  |  | 10.08 Inadequate evaluation of changes | [6 empty] | Poor body positioning against the pole while it was being lifted into the jaws of the boom. | 09. Improper Placement | 6. Caught On (Snagged, Hung) | approved | I believe the corrective actions decided upon by the investigation team are the most effective means of mitigation at this time. | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2018-04-09 | 1997-06-11 |  | 2019-03-06 06:00 | 0 | 0 |  | FALSE | Male | Pole contacted the back of members leg and a shard of wood punctured the members skin. |  | FALSE | Josiah Duncan |  | Recordable | Josiah Duncan | FALSE |  |  |  | Puncture | No lost time per F. Davis 4/9/19. | TRUE |  | Lineman Appr | Thigh | Injury | Left | TRUE | Kevin Pettigrew | TRUE | 2019 | 3/6/2019 6:00:00 AM |  | TRUE | FALSE | FALSE | piece of wood | [25 empty] | N/A
8746 | Woodward Service Center | 2019-03-06 11:00 | While positioning pole into grabbers pole contacted back of members leg leaving splinter lodged in members leg. | Level 3 |  | FALSE | Member Injury |  | Lindle Coleman | Assigned | 2019-03-12 12:38 | Power Delivery | Tyler Scott | 2019-04-10 14:04 | 2019-03-06 15:47 | 2019-03-06 15:47 | 2019-03-26 09:11 | 2019-03-20 11:00 | 2019-03-06 11:30 | 2019-04-01 10:33 | 2019-04-01 11:14 | 2019-03-29 12:17 | 182312 E county rd 50 Gage Ok |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Lewis Wilson |  | On March 6 2019, at 11:00 A.M. A Woodward crew was setting up on a job site to set a pole on a new single phase line. Crew had already framed poles and they had strung out the wire for the job. The crew had set up on the pole and moved it so they could slip tie the wire in before setting the pole. Hayden Bierig was operating the line truck. He began to lift the pole with the winch line/sling to grab ahold of it with the claws located on the end of the boom. Josiah Duncan was positioned over the butt of the pole to guide it as it was being lifted. At this point he put his weight on the butt of the pole to leverage the pole top higher. As he was pushing his weight down on the pole, the wire on the pole top became caught in some bushes. When the wire came free from the bush the pole slid approximately 1-2ft backwards against Jousiahs leg that was still placed over the butt of the pole. The contact between the members leg and a rough part of the pole caused a splinter to enter his leg through his jeans. After the incident the member felt some discomfort in his leg at which point he discovered the splinter and tried to remove it. When he could not remove the splinter he alerted his foreman. At this time his foreman transported him to the OGE McBride Clinic. The physician at Mcbride was able to remove the wood from the members leg and he was able to return to work. | David Fox | Lewis Wilson | FALSE | Woodward Service Center | FALSE |  | FALSE | Construction Services |  | Kevin Pettigrew | Tyler Scott |  | Chad Inman | I feel like the findings of the incident were very thorough and that the corrective actions are listed are appropriate. Thank you. | Chad Inman | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  |  | 10.08 Inadequate evaluation of changes | [6 empty] | Poor body positioning against the pole while it was being lifted into the jaws of the boom. | 09. Improper Placement | 6. Caught On (Snagged, Hung) | approved | I believe the corrective actions decided upon by the investigation team are the most effective means of mitigation at this time. | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2018-04-09 | 1997-06-11 |  | 2019-03-06 06:00 | 0 | 0 |  | FALSE | Male | Pole contacted the back of members leg and a shard of wood punctured the members skin. |  | FALSE | Josiah Duncan |  | Recordable | Josiah Duncan | FALSE |  |  |  | Puncture | No lost time per F. Davis 4/9/19. | TRUE |  | Lineman Appr | Thigh | Injury | Left | TRUE | Kevin Pettigrew | TRUE | 2019 | 3/6/2019 6:00:00 AM |  | TRUE | FALSE | FALSE | piece of wood | [25 empty] | N/A
8747 | Metro Service Center | 2019-03-05 14:00 | While separating de-energized floating transmission phases to tie them into the structure, bottom phase recoiled and momentarily contacted the underbuilt distribution circuit. No members were in contact with the phase and the HLHO tripped the circuit out. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Delivery | Jimmy Combs | 2019-04-04 13:21 | 2019-03-07 06:31 | 2019-03-07 06:31 | 2019-03-26 07:09 | 2019-03-19 14:00 | 2019-03-07 06:18 | 2019-04-03 15:08 |  | 2019-04-01 07:40 | Norman road widening job 24 ave ne |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Jimmy Combs |  | Member operating elevator and working grounded transmission phases was on the road side. Member placed top phase in his material handler jib and proceeded to untie the rope that was holding the bottom phase to the middle. Foreman and Leadman communicated to member in the bucket via radio and by shouting to let him know that he needed to place the bottom and middle phases in the running lip hanging from the hook of the crane. By the time the member understood what was being communicated to him, he had already untied the bottom phase from the top and middle. Member was holding onto the rope that was tied to the bottom phase. Crane operator was in motion to bring the running lip to secure the bottom phase and then the middle. Prior to being able to get the crane into position the member in the bucket lost his grip on the rope, the bottom phase recoiled and contacted the distribution crossarm on the old structure below. The phase recoiled up then back down and contacted b phase locking out the circuit. B phase was contacted approximately 30’ to north of the structure that was being worked. Facts Ascertained: HLHO 0854 was in place and operated as designed 2nd HLHO 1412 was taken after the circuits were switched back in Tailboard was revisited and updated with new HLHO# after incident In the previous days the crew had set 7 structures and used the crane running lip to secure the phases Setting this pole was the only task for the day (no rush to complete). Foreman decided to let new member perform this task to gain experience. Crane operator, Foreman, Leadman, and New Member had radios to enable easy communication 4 insulated snakes per phase plus one on the neutral. 4 sliding insulators on C phase. 4 sliding insulators on b phase. 2 sliding insulators on A phase to protect crane boom and make phase visable (New pole being set is between B&C Phase) New pole was set approximately 3' west of the old pole Member in the elevator bucket working Transmission Phases is a step 4 lineman Step 9 Lineman was set up on the field side of new pole to remove cover up on the under build distribution (after phases were secured on transmission pole) New member hired on 01-07-2019 New member has 2 years experience working transmission |  |  |  | Metro Service Center | FALSE |  | TRUE | Construction Services |  | Hershel Goodson | Jimmy Combs |  | Gary Lassley | Communicate lessons learned with Transmission Construction Staff. When newer OG&E members are performing a tasks on their own for the first time communicate expectations, expected outcomes, and verify understanding prior to acting on tasks as well as discussing what could happen | Gary Lassley |  | Medium |  |  |  |  | 5.01 Lack of experience | [11 empty] | Member did not secure phase | 03. Failure to Secure | 9. Abnormal Operation |  | Reviewed/Approved TMH | [90 empty] | 1645883
8747 | Metro Service Center | 2019-03-05 14:00 | While separating de-energized floating transmission phases to tie them into the structure, bottom phase recoiled and momentarily contacted the underbuilt distribution circuit. No members were in contact with the phase and the HLHO tripped the circuit out. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Delivery | Jimmy Combs | 2019-04-04 13:21 | 2019-03-07 06:31 | 2019-03-07 06:31 | 2019-03-26 07:09 | 2019-03-19 14:00 | 2019-03-07 06:18 | 2019-04-03 15:08 |  | 2019-04-01 07:40 | Norman road widening job 24 ave ne |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Jimmy Combs |  | Member operating elevator and working grounded transmission phases was on the road side. Member placed top phase in his material handler jib and proceeded to untie the rope that was holding the bottom phase to the middle. Foreman and Leadman communicated to member in the bucket via radio and by shouting to let him know that he needed to place the bottom and middle phases in the running lip hanging from the hook of the crane. By the time the member understood what was being communicated to him, he had already untied the bottom phase from the top and middle. Member was holding onto the rope that was tied to the bottom phase. Crane operator was in motion to bring the running lip to secure the bottom phase and then the middle. Prior to being able to get the crane into position the member in the bucket lost his grip on the rope, the bottom phase recoiled and contacted the distribution crossarm on the old structure below. The phase recoiled up then back down and contacted b phase locking out the circuit. B phase was contacted approximately 30’ to north of the structure that was being worked. Facts Ascertained: HLHO 0854 was in place and operated as designed 2nd HLHO 1412 was taken after the circuits were switched back in Tailboard was revisited and updated with new HLHO# after incident In the previous days the crew had set 7 structures and used the crane running lip to secure the phases Setting this pole was the only task for the day (no rush to complete). Foreman decided to let new member perform this task to gain experience. Crane operator, Foreman, Leadman, and New Member had radios to enable easy communication 4 insulated snakes per phase plus one on the neutral. 4 sliding insulators on C phase. 4 sliding insulators on b phase. 2 sliding insulators on A phase to protect crane boom and make phase visable (New pole being set is between B&C Phase) New pole was set approximately 3' west of the old pole Member in the elevator bucket working Transmission Phases is a step 4 lineman Step 9 Lineman was set up on the field side of new pole to remove cover up on the under build distribution (after phases were secured on transmission pole) New member hired on 01-07-2019 New member has 2 years experience working transmission |  |  |  | Metro Service Center | FALSE |  | TRUE | Construction Services |  | Hershel Goodson | Jimmy Combs |  | Gary Lassley | Communicate lessons learned with Transmission Construction Staff. When newer OG&E members are performing a tasks on their own for the first time communicate expectations, expected outcomes, and verify understanding prior to acting on tasks as well as discussing what could happen | Gary Lassley |  | Medium | [13 empty] | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Task does not have an associate JHA | 03. Failure to Secure | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Reviewed/Approved TMH | [90 empty] | 1645883
8748 | Enid Service Center | 2019-03-05 13:30 | On Tuesday March 5 2019 breaker 1022 tripped open. This accrued during normal switching operation to place 1022 back in service after relay testing, switch 1072 a (SM5 fuse) B phase insulator broke allowing the hot line side of the fuse to make contact with ground causing the breaker to trip. | Level 1 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Dustin Kingcade | 2019-03-19 10:12 | 2019-03-07 10:43 | 2019-03-07 10:43 | 2019-03-18 11:43 | 2019-03-19 13:30 | 2019-03-07 09:59 | 2019-03-18 13:51 |  |  | Medford Substation, Medford OK |  |  | Cody Magby | approve cm | T&D Ops |  | Level 1 | System Operational Incident |  | FALSE | FALSE | TRUE |  | TRUE | FALSE | Dustin Kingcade |  | On Tuesday March 5 2019 breaker 1022 tripped open. This accrued during normal switching operation to place 1022 back in service after relay testing, switch 1072 a (SM5 fuse) B phase insulator broke allowing the hot line side of the fuse to make contact with ground causing the breaker to trip |  |  |  | Enid Service Center | FALSE |  | FALSE | PD Operations Services |  | Zachary Hamen | Dustin Kingcade |  | James Hutchison | I have reviewed this incident and support the mentioned corrective action. A corrective action that has already been completed was the replacing of the insulators on all three phases of the bypass switch. | James Hutchison |  | Low | [7 empty] | 8.1.2 Improper conduct that is condoned: Unintentional | [8 empty] | On Tuesday March 5 2019 breaker 1022 tripped open. This accrued during normal switching operation to place 1022 back in service after relay testing, switch 1072 a (SM5 fuse) B phase insulator broke allowing the hot line side of the fuse to make contact with ground causing the breaker to trip | 23. Defective Tools, Equipment or Materials | 9. Abnormal Operation | [68 empty] | Insulator and SM5 fuse barrel broke. Replaced broken fuse barrel and insulator and all remaining old insulators on switch 1072. | 2000 | Zachary Hamen | Structural | [20 empty] | 9090303
8748 | Enid Service Center | 2019-03-05 13:30 | On Tuesday March 5 2019 breaker 1022 tripped open. This accrued during normal switching operation to place 1022 back in service after relay testing, switch 1072 a (SM5 fuse) B phase insulator broke allowing the hot line side of the fuse to make contact with ground causing the breaker to trip. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Delivery | Dustin Kingcade | 2019-03-19 10:12 | 2019-03-07 10:43 | 2019-03-07 10:43 | 2019-03-18 11:43 | 2019-03-19 13:30 | 2019-03-07 09:59 | 2019-03-18 13:51 |  |  | Medford Substation, Medford OK |  |  | Cody Magby | approve cm | T&D Ops |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | TRUE | FALSE | Dustin Kingcade |  | On Tuesday March 5 2019 breaker 1022 tripped open. This accrued during normal switching operation to place 1022 back in service after relay testing, switch 1072 a (SM5 fuse) B phase insulator broke allowing the hot line side of the fuse to make contact with ground causing the breaker to trip |  |  |  | Enid Service Center | FALSE |  | FALSE | PD Operations Services |  | Zachary Hamen | Dustin Kingcade |  | James Hutchison | I have reviewed this incident and support the mentioned corrective action. A corrective action that has already been completed was the replacing of the insulators on all three phases of the bypass switch. | James Hutchison |  | Low | [7 empty] | 8.1.2 Improper conduct that is condoned: Unintentional | [8 empty] | On Tuesday March 5 2019 breaker 1022 tripped open. This accrued during normal switching operation to place 1022 back in service after relay testing, switch 1072 a (SM5 fuse) B phase insulator broke allowing the hot line side of the fuse to make contact with ground causing the breaker to trip | 23. Defective Tools, Equipment or Materials | 9. Abnormal Operation | [68 empty] | Insulator and SM5 fuse barrel broke. Replaced broken fuse barrel and insulator and all remaining old insulators on switch 1072. | 2000 | Zachary Hamen | Structural | [20 empty] | 9090303
8749 | Horseshoe Lake Power Plant | 2019-03-07 09:30 | CUT FINGER WHILE CHANGING SCRAPER BLADE. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Wade Gabbert | 2019-04-19 10:20 | 2019-03-08 13:29 | 2019-03-08 13:29 | 2019-03-26 07:45 | 2019-03-21 09:30 | 2019-03-07 15:00 | 2019-03-26 18:38 |  |  | HLS TURBINE FLOOR |  |  | Guillermo Sarmiento | Agree with report and corrective actions. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Wade Gabbert |  | AT AROUND 0950 CONTRACT MEMBER ACCIDENTALLY CUT HIS FINGER WHILE CHANGING A SCRAPER BLADE. HE APPLIED A BANDAGE TO THE CUT THAT WAS APPROXIMATELY 1/2 INCH IN LENGTH JUST BELOW THE SKIN. HE REPORTED THE INCCIDENT TO HIS SUPPERVISOR WHO THEN REPORTED TO ME. CONTRACTOR WAS WEARING CUT RESISTANT GLOVES. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Maintenance |  | Wade Gabbert | Wade Gabbert |  | Daniel Perry | We need the EAI incident report added to this incident. 3/26/19. It was initially reported to OG&E that the contractor was wearing cut resistant gloves. It was discovered during additional talks that he was wearing leather gloves. I cannot edit the text at this point. I think the description or the incident needs to be corrected if possible. | Daniel Perry |  | Low |  |  |  |  | 5.01 Lack of experience | [11 empty] | HE PUSHED THE SCRAPER BLADE WITH HIS THUMB WHILE INSTALLING. | 17. Failure to Identify Hazard, Risk | 6. Caught On (Snagged, Hung) | [5 empty] | Injury / Illness |  | Wade Gabbert | [5 empty] | 6. Caught On (Snagged, Hung) | Wade Gabbert | EAI | RUBEN MARIN |  |  |  | Wade Gabbert | [71 empty] | 9581777
8750 | Muskogee Power Plant | 2019-03-08 12:00 | The HP fuel skid lost instrument air pressure. As a result the burner gas trip valve failed closed. When this happened the Enable pressure regulator continued to build pressure. The HP slam shut valve did not close when pressure reached 200 PSIG. | Level 2 |  | TRUE | Member Injury |  |  |  |  | OG&E Corp Services |  | 2019-04-23 07:02 | 2019-03-08 21:32 | 2019-03-08 21:32 | 2019-03-22 17:16 | 2019-03-22 18:00 | 2019-03-08 21:26 | 2019-04-06 15:55 |  | 2019-03-25 07:17 | Muskogee PP Unit 4 HP Fuel Skid |  |  | William Young | Reviewed and approved. WCY 4-23-19 | UTS |  | Level 2 | Member Injury |  | FALSE | TRUE | TRUE |  | FALSE | FALSE |  |  | Upon losing instrument air pressure both HP regulator valves lost the ability to remain open. Upon closing pressure continued to build from the fuel line on the Enable side to the HP skid. The slam shut valve did not close fully. As a result the high pressure skid continued to allow gas to enter the skid after the unit had already tripped. The gas was bled off and an adjustment was made to the slam shut valve that allowed it to close completely. Upon further investigation the sensing lines and seat of the valve had black powder present. This was the reason for the valve not being able to close completely. The valve and instrumentation was cleaned out. Multiple verification tests on the valve were performed to assure it would close completely. These tests were successful with the valve closing at the designed 188 psi. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | UTS - Capital Projects |  |  |  |  | Christopher Lelak | None - CBL 04/06/19 | Christopher Lelak |  | Medium | [9 empty] | 10.05 Inadequate assessment of operational readiness | 11.10 Inadequate identification of hazardous materials | [5 empty] | Black powder was found in the instrumentation sensing lines and the seat of the valve. Both needed to be cleaned out. Valve is functioning properly now. | 24. Congestion or Restricted Action | 9. Abnormal Operation |  | No additional items at this time. MLH 3/25/19 | [90 empty] | none
8750 | Muskogee Power Plant | 2019-03-08 12:00 | The HP fuel skid lost instrument air pressure. As a result the burner gas trip valve failed closed. When this happened the Enable pressure regulator continued to build pressure. The HP slam shut valve did not close when pressure reached 200 PSIG. | Level 2 |  | TRUE | Member Injury |  |  |  |  | OG&E Corp Services |  | 2019-04-23 07:02 | 2019-03-08 21:32 | 2019-03-08 21:32 | 2019-03-22 17:16 | 2019-03-22 18:00 | 2019-03-08 21:26 | 2019-04-06 15:55 |  | 2019-03-25 07:17 | Muskogee PP Unit 4 HP Fuel Skid |  |  | William Young | Reviewed and approved. WCY 4-23-19 | UTS |  | Level 2 | Member Injury |  | FALSE | TRUE | TRUE |  | FALSE | FALSE |  |  | Upon losing instrument air pressure both HP regulator valves lost the ability to remain open. Upon closing pressure continued to build from the fuel line on the Enable side to the HP skid. The slam shut valve did not close fully. As a result the high pressure skid continued to allow gas to enter the skid after the unit had already tripped. The gas was bled off and an adjustment was made to the slam shut valve that allowed it to close completely. Upon further investigation the sensing lines and seat of the valve had black powder present. This was the reason for the valve not being able to close completely. The valve and instrumentation was cleaned out. Multiple verification tests on the valve were performed to assure it would close completely. These tests were successful with the valve closing at the designed 188 psi. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | UTS - Capital Projects |  |  |  |  | Christopher Lelak | None - CBL 04/06/19 | Christopher Lelak |  | Medium | [9 empty] | 10.08 Inadequate evaluation of changes | 11.10 Inadequate identification of hazardous materials | [5 empty] | Black powder was found in the instrumentation sensing lines and the seat of the valve. Both needed to be cleaned out. Valve is functioning properly now. | 24. Congestion or Restricted Action | 9. Abnormal Operation |  | No additional items at this time. MLH 3/25/19 | [90 empty] | none
8750 | Muskogee Power Plant | 2019-03-08 12:00 | The HP fuel skid lost instrument air pressure. As a result the burner gas trip valve failed closed. When this happened the Enable pressure regulator continued to build pressure. The HP slam shut valve did not close when pressure reached 200 PSIG. | Level 2 |  | TRUE | Property Damage |  |  |  |  | OG&E Corp Services |  | 2019-04-23 07:02 | 2019-03-08 21:32 | 2019-03-08 21:32 | 2019-03-22 17:16 | 2019-03-22 18:00 | 2019-03-08 21:26 | 2019-04-06 15:55 |  | 2019-03-25 07:17 | Muskogee PP Unit 4 HP Fuel Skid |  |  | William Young | Reviewed and approved. WCY 4-23-19 | UTS |  | Level 2 | Property Damage |  | FALSE | TRUE | TRUE |  | FALSE | FALSE |  |  | Upon losing instrument air pressure both HP regulator valves lost the ability to remain open. Upon closing pressure continued to build from the fuel line on the Enable side to the HP skid. The slam shut valve did not close fully. As a result the high pressure skid continued to allow gas to enter the skid after the unit had already tripped. The gas was bled off and an adjustment was made to the slam shut valve that allowed it to close completely. Upon further investigation the sensing lines and seat of the valve had black powder present. This was the reason for the valve not being able to close completely. The valve and instrumentation was cleaned out. Multiple verification tests on the valve were performed to assure it would close completely. These tests were successful with the valve closing at the designed 188 psi. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | UTS - Capital Projects |  |  |  |  | Christopher Lelak | None - CBL 04/06/19 | Christopher Lelak |  | Medium | [9 empty] | 10.05 Inadequate assessment of operational readiness | 11.10 Inadequate identification of hazardous materials | [5 empty] | Black powder was found in the instrumentation sensing lines and the seat of the valve. Both needed to be cleaned out. Valve is functioning properly now. | 24. Congestion or Restricted Action | 9. Abnormal Operation |  | No additional items at this time. MLH 3/25/19 | [90 empty] | none
8750 | Muskogee Power Plant | 2019-03-08 12:00 | The HP fuel skid lost instrument air pressure. As a result the burner gas trip valve failed closed. When this happened the Enable pressure regulator continued to build pressure. The HP slam shut valve did not close when pressure reached 200 PSIG. | Level 2 |  | TRUE | Property Damage |  |  |  |  | OG&E Corp Services |  | 2019-04-23 07:02 | 2019-03-08 21:32 | 2019-03-08 21:32 | 2019-03-22 17:16 | 2019-03-22 18:00 | 2019-03-08 21:26 | 2019-04-06 15:55 |  | 2019-03-25 07:17 | Muskogee PP Unit 4 HP Fuel Skid |  |  | William Young | Reviewed and approved. WCY 4-23-19 | UTS |  | Level 2 | Property Damage |  | FALSE | TRUE | TRUE |  | FALSE | FALSE |  |  | Upon losing instrument air pressure both HP regulator valves lost the ability to remain open. Upon closing pressure continued to build from the fuel line on the Enable side to the HP skid. The slam shut valve did not close fully. As a result the high pressure skid continued to allow gas to enter the skid after the unit had already tripped. The gas was bled off and an adjustment was made to the slam shut valve that allowed it to close completely. Upon further investigation the sensing lines and seat of the valve had black powder present. This was the reason for the valve not being able to close completely. The valve and instrumentation was cleaned out. Multiple verification tests on the valve were performed to assure it would close completely. These tests were successful with the valve closing at the designed 188 psi. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | UTS - Capital Projects |  |  |  |  | Christopher Lelak | None - CBL 04/06/19 | Christopher Lelak |  | Medium | [9 empty] | 10.08 Inadequate evaluation of changes | 11.10 Inadequate identification of hazardous materials | [5 empty] | Black powder was found in the instrumentation sensing lines and the seat of the valve. Both needed to be cleaned out. Valve is functioning properly now. | 24. Congestion or Restricted Action | 9. Abnormal Operation |  | No additional items at this time. MLH 3/25/19 | [90 empty] | none
8751 | Sooner Power Plant | 2019-03-09 12:18 | Due to high winds, the power lines sparked a grass fire north of the coal pile. The Operating Authority (OA) was notified by a resident who lives near the area where the fire took place and also reported that she contacted Red Rock fire department. The Operating Authority followed up by calling Red Rock Fire Department to make sure they have been notified and they are on the way. OA also called T&D to inspect the wires. T&D showed up at 14:30 and reported that one of the insulators was found on the ground and that most likely contributed to the fire with the wires touching. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Allen Moore | 2019-04-13 14:16 | 2019-03-09 16:07 | 2019-03-09 16:07 | 2019-03-28 19:22 | 2019-03-23 12:18 | 2019-03-09 15:51 | 2019-04-02 09:09 |  | 2019-03-29 08:43 | 300 yards north of coal pile |  |  | Jesse Murray | I Approve. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Allen Moore |  | Due to high winds, the power lines sparked a grass fire north of the coal pile. The Operating Authority (OA) was notified by a resident who lives near the area where the fire took place and also reported that she contacted Red Rock fire department. The Operating Authority followed up by calling Red Rock Fire Department to make sure they have been notified and they are on the way. OA also called T&D to inspect the wires. T&D showed up at 14:30 and reported that one of the insulators was found on the ground and that most likely contributed to the fire with the wires touching |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Operations |  | Allen Moore | Allen Moore |  | Alexander Taybah | I added another corrective action to reach out to T&D to either tighten the lines or install spacers to prevent the lines from touching on windy days. | Alexander Taybah |  | Medium | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | High wind caused the power lines to touch sparking a grass fire. As a result, the Red Rock and Morrison Fire Departments were called to put the fire out. | 40. Weather Conditions | 12. Equipment Failure |  | Approved by Brady Sowell on 3/29/2019 | [90 empty] | 123456
8752 | Horseshoe Lake Power Plant | 2019-03-10 03:00 | Siemens site engineer reported to FPO that a Siemens worker had his finger hit by another employee using a hammer while he held a punch. The Siemens team was advised to give the employee an Ibuprofen and Tylenol, and to ice the finger. The worker returned to normal work within a few minutes. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Peter Nowakowski | 2019-04-19 07:51 | 2019-03-10 20:09 | 2019-03-10 20:09 | 2019-04-04 23:05 | 2019-03-24 01:00 | 2019-03-10 19:57 | 2019-04-10 19:58 |  | 2019-04-05 06:58 | Horseshoe Lake PP Unit 8 Turbine |  |  | Jesse Murray | I Approve. Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Peter Nowakowski |  | Millwrights were removing bolting form the lower half of #2 gland casing. While in the process of removing the bolt, millwright “A” was holding a large punch for millwright “B”. Millwright “B” swung the hammer and missed the punch thereby striking millwright “A’s” left hand fingertip. Both millwrights were wearing leather gloves during the incident. Immediately after the incident, millwright “A” washed his hands and cleaned finger with alcohol, applied antibacterial ointment, and placed a band aid. Siemens contacted “WorkCare” for additional guidance. Millwright “A” spoke with the “WorkCare” nurse and it was recommended that ice be applied to the finger in order to minimize swelling and to take some Tylenol for pain and swelling. The incident occurred on Sunday, March 10, 2019 at approximately 1:00a.m. but was not reported to OGE until Sundar, March 10, 2019 at approximately 3:15AM. Siemens Engineer came into the control room Sunday morning and asked operations for a cup of ice. After some discussion, the Siemens engineer reported that an employee had suffered and incident and that he his finger was struck with a hammer. Operations gave the Siemens engineer an ice pack as well in case the cup of ice was not sufficient. OGE leadership had a discussion with Siemens concerning the importance of reporting incidents immediately as soon as safely possible. The millwright returned to work with. No serious injuries were sustained |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Maintenance |  | Peter Nowakowski | Peter Nowakowski |  | Daniel Perry | I have reviewed this report and I approve. | Daniel Perry |  | Medium |  |  |  | 4.04 Routine, monotony, demand for uneventful vigilance | 5.06 Lack of situational awareness | [8 empty] | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | Siemens millwright sustained a smashed finger while holding a punch for another as they tried to loosen a turbine bolt. | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) |  | Reviewed report. Everything looks good. The report contractor report did not include any corrective actions. Reached out to the contractor responsible and they explained that they are looking at other option in performing this job task but its not yet finalized. |  |  |  | Injury / Illness |  | Peter Nowakowski |  | Left middle finger struck by hammer brui | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Peter Nowakowski | Siemens | Mike Waqua | Crush/Smash |  | Finger | Peter Nowakowski | Left | FALSE | [69 empty] | 9572198
8753 | Mustang Power Plant | 2019-03-08 15:00 | Contractor requested LOTO on lightning circuit breaker to install new lights. LOTO was hung on wrong breaker by Mustang members. No injuries or property damage occurred. | Level 3 |  | TRUE | Member Injury | Donnie Jones | Jesse Murray | Jesse, Please assign Steve Sanders, Dale Richardson, and myself for the investigation team. | 2019-03-12 07:58 | Power Supply | William Sanders | 2019-03-21 11:39 | 2019-03-11 07:56 | 2019-03-11 07:56 | 2019-03-12 15:18 | 2019-03-22 15:00 | 2019-03-08 15:00 | 2019-03-12 15:24 | 2019-03-21 08:54 | 2019-03-12 15:21 | Mustang Unit 6 ISI Enclosure |  |  | Donnie Jones | Approved | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | William Sanders |  | Investigation: On the morning of March 7th a LOTO was requested by All-N-One to remove power from the 110v receptacles in the ISI enclosure on unit 6. They needed power removed to tie in a neutral wire for a new lighting circuit for the enclosure. The Operating Authority had a member go out to the enclosure and verify which breaker in electrical panel 06ELP-PNL-0001 was needed to remove the power. The member (A) and contractor plugged a drop light into the receptacle that was needing to be power down, and started cycling molded case breakers in panel 06ELP-PNL-0001 until the light went out. It was determined by this test method that breaker 10 was feeding the receptacles in the enclosure. The Operating Authority then created a LOTO that had breaker 10 in 06ELP-PNL-0001 panel on the tagging list. He asked the same member (A) to verify the LOTO due to the fact that it was not a template in WCM. The member (A) and Operating Authority agreed that the LOTO was correct, and the OA printed the tagging list. Another member (B) was asked to go hang the LOTO on unit 6, as he went the first member (B) followed him. Both members (A&B) were at panel 06ELP-PNL-0001, when the second member (B) hung the lock and tag on what was believed to be breaker 10 in the panel. The first member (A) verified the lock and tag and they both went back to the control room. Later that morning the first member (A) took the LOTO as PAE and the contract workers signed on. The contract workers began work in the new lighting circuit. On March 8th, the contractors signed off of the LOTO and ask for circuit 10 in panel 06ELP-PNL-0001 to be re-energized to test the new lights. The PAE was not on-site so the OA called him and asked for his LOTO return over the phone. The PAE approved and the un-tagging list was printed by the OA and a third member(C) was sent to un-tag the LOTO. When the third member(C) arrived at panel 06ELP-PNL-0001, he noticed the lock was on breaker 8, not breaker 10 like the un-tagging list stated. The lock and tag were hung on the wrong breaker in panel 06ELP-PNL-0001. The correct breaker was open and de-energized but had no LOTO installed. Findings: Both members went at the same time to hang and 2nd verify the LOTO tagging. This proved to not be the correct amount of rigor in verifying the LOTO was correctly hung. The first member(A) said he paid more attention to verifying that the tag and tagging list matched than he did verifying which breaker the lock was hung on. The first member (A) that verified the LOTO tagging, also became the PAE for the WCA. This led to the LOTO not being looked at for a 3rd time. The member had already looked at it during the first verification process. The 2nd member (B) says he knew it went on breaker 10, but accidentally hung it on the wrong breaker. | Dale Richardson | William Sanders |  | Mustang Power Plant | FALSE |  | TRUE | Operations |  | Michael Moffitt | William Sanders |  | William Sanders | Corrected actions have been completed for the incident. | William Sanders | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness | [10 empty] | 16.01 Inadequate horizontal communication between peers | Both members went at the same time to hang and 2nd verify the LOTO tagging. This proved to not be the correct amount of rigor in verifying the LOTO was correctly hung. | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation | I Approve. Jesse Murray | [91 empty] | none
8753 | Mustang Power Plant | 2019-03-08 15:00 | Contractor requested LOTO on lightning circuit breaker to install new lights. LOTO was hung on wrong breaker by Mustang members. No injuries or property damage occurred. | Level 3 |  | TRUE | Member Injury | Donnie Jones | Jesse Murray | Jesse, Please assign Steve Sanders, Dale Richardson, and myself for the investigation team. | 2019-03-12 07:58 | Power Supply | William Sanders | 2019-03-21 11:39 | 2019-03-11 07:56 | 2019-03-11 07:56 | 2019-03-12 15:18 | 2019-03-22 15:00 | 2019-03-08 15:00 | 2019-03-12 15:24 | 2019-03-21 08:54 | 2019-03-12 15:21 | Mustang Unit 6 ISI Enclosure |  |  | Donnie Jones | Approved | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | William Sanders |  | Investigation: On the morning of March 7th a LOTO was requested by All-N-One to remove power from the 110v receptacles in the ISI enclosure on unit 6. They needed power removed to tie in a neutral wire for a new lighting circuit for the enclosure. The Operating Authority had a member go out to the enclosure and verify which breaker in electrical panel 06ELP-PNL-0001 was needed to remove the power. The member (A) and contractor plugged a drop light into the receptacle that was needing to be power down, and started cycling molded case breakers in panel 06ELP-PNL-0001 until the light went out. It was determined by this test method that breaker 10 was feeding the receptacles in the enclosure. The Operating Authority then created a LOTO that had breaker 10 in 06ELP-PNL-0001 panel on the tagging list. He asked the same member (A) to verify the LOTO due to the fact that it was not a template in WCM. The member (A) and Operating Authority agreed that the LOTO was correct, and the OA printed the tagging list. Another member (B) was asked to go hang the LOTO on unit 6, as he went the first member (B) followed him. Both members (A&B) were at panel 06ELP-PNL-0001, when the second member (B) hung the lock and tag on what was believed to be breaker 10 in the panel. The first member (A) verified the lock and tag and they both went back to the control room. Later that morning the first member (A) took the LOTO as PAE and the contract workers signed on. The contract workers began work in the new lighting circuit. On March 8th, the contractors signed off of the LOTO and ask for circuit 10 in panel 06ELP-PNL-0001 to be re-energized to test the new lights. The PAE was not on-site so the OA called him and asked for his LOTO return over the phone. The PAE approved and the un-tagging list was printed by the OA and a third member(C) was sent to un-tag the LOTO. When the third member(C) arrived at panel 06ELP-PNL-0001, he noticed the lock was on breaker 8, not breaker 10 like the un-tagging list stated. The lock and tag were hung on the wrong breaker in panel 06ELP-PNL-0001. The correct breaker was open and de-energized but had no LOTO installed. Findings: Both members went at the same time to hang and 2nd verify the LOTO tagging. This proved to not be the correct amount of rigor in verifying the LOTO was correctly hung. The first member(A) said he paid more attention to verifying that the tag and tagging list matched than he did verifying which breaker the lock was hung on. The first member (A) that verified the LOTO tagging, also became the PAE for the WCA. This led to the LOTO not being looked at for a 3rd time. The member had already looked at it during the first verification process. The 2nd member (B) says he knew it went on breaker 10, but accidentally hung it on the wrong breaker. | Tanner Brady | William Sanders |  | Mustang Power Plant | FALSE |  | TRUE | Operations |  | Michael Moffitt | William Sanders |  | William Sanders | Corrected actions have been completed for the incident. | William Sanders | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness | [10 empty] | 16.01 Inadequate horizontal communication between peers | Both members went at the same time to hang and 2nd verify the LOTO tagging. This proved to not be the correct amount of rigor in verifying the LOTO was correctly hung. | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation | I Approve. Jesse Murray | [91 empty] | none
8754 | Metro Service Center | 2019-03-08 14:30 | After re-staking a portion of job I returned hammer to toolbox, I reached up to close lid on toolbox, with a downward motion. As tool box closed, I felt a pop in right armpit area. | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | John Legg | 2019-06-03 16:47 | 2019-03-11 10:49 | 2019-03-11 10:49 | 2019-05-02 11:05 | 2019-03-22 14:30 | 2019-03-11 10:37 | 2019-06-03 16:35 |  |  | Meadows @ MacArthur NW178 and Macarthur 3/10 north. |  |  | Marcus Huddleston | No additional comments. MLH 6/3/9 | T&D Ops |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | John Legg |  | After Mr. Wolfe re-staked a job he was returning tools to his tool box when he heard/felt a pop in his right arm. |  |  | FALSE | Metro Service Center | FALSE |  | FALSE | Resource Planning & Coord |  | Darrel Wolfe | John Legg |  | Nicole Rhodes | Reviewed. | Nicole Rhodes |  | Low | [5 empty] | 6.03 Infrequent performance |  |  |  | 10.02 Inadequate consideration of human factors/ergonomics | [6 empty] | Returning tool to toolbox. | 35. Inadequate Information, Data | 11. Overstress, Overpressure, Overexertion, Ergonomic | [26 empty] | FALSE |  | Job Transfer or Restriction (I) | 1989-04-10 | 1960-11-22 |  | 2019-03-08 06:00 | 0 | 28 |  | FALSE | Male | closeing lid on toolbox, with a downward motion. |  | FALSE | Darrel Wolfe |  | Recordable | Darrel Wolfe |  |  |  |  | Sprain/Strain | No lost time per F. Davis 4/9/19 | TRUE |  | Sr Contractor Resource Coordinator | Arm | Injury | Right | TRUE | John Legg | TRUE | 2019 | 3/8/2019 6:00:00 AM | 5+ | FALSE |  |  | Toolbox lid | re-staking a job and returned hammer to tool box | [24 empty] | 7376836
8755 | Enid Service Center | 2019-03-12 08:30 | Crew finished unloading material at job site, truck was travelling back to service center when lightning struck line truck. Foreman was approx. 50 yards ahead of line truck unloading material from a pickup when strike occurred. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Delivery | Brian Kaiser | 2019-04-10 11:09 | 2019-03-12 13:36 | 2019-03-12 13:36 | 2019-04-02 14:03 | 2019-03-26 07:30 | 2019-03-12 09:00 | 2019-04-09 07:30 |  | 2019-04-09 06:19 | 1/4 mile north of Enid service center on Enterprise Blvd |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Brian Kaiser |  | Crew was laying off material for new construction job. All poles had been removed from line truck, boom was stowed and truck was in transit. Foreman was at the last work location, approx. 50 yards in front of line truck laying out material from a pickup when lightning struck. Crew was temporarily blinded by the flash. When vision was restored, line truck was still running, but the instrument cluster showed electrical fault, and the truck would not drive. Summit mechanic determined all the electrical modules had been damaged. |  |  |  | Enid Service Center | FALSE |  | TRUE | Construction Services |  | Brian Kaiser | Christopher Bristol |  | Christopher Bristol | I approve of this corrective action. | Christopher Bristol |  | Medium | [12 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | Isolated thunderstorm moved through area. | 40. Weather Conditions | 2. Struck By (Hit By Moving Object) |  | I believe the corrective actions will help mitigate the risks of this incident and raise awareness in regards to better monitoring of weather events. | [90 empty] | none
8756 | Horseshoe Lake Power Plant | 2019-03-13 02:00 | The broderson crane was running poorly and was shut off. Then an odor of something burning was noticed. A rubber mount for the muffler was found to be involved in an incipient stage fire. It was extinguished with a fire extinguisher without further incident. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Jon Harriet | 2019-04-17 08:29 | 2019-03-13 02:59 | 2019-03-13 02:59 | 2019-04-10 21:34 | 2019-03-27 01:00 | 2019-03-13 02:06 | 2019-04-14 11:48 |  |  | In the basement of Unit 8 |  |  | Guillermo Sarmiento | Discussed it with Dan and agree with the report and its findings. | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Jon Harriet |  | Currently we have a third party company looking into the cause of the fire. Parts need to be acquired before we can proceed with the investigation as the crane is not currently running. More to come as information is available. The muffler was obstructed not allowing for proper exhaust flow. A new muffler was installed and the machine is now operating properly. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Maintenance |  | Terry Creed | Jon Harriet |  | Daniel Perry | I think we should add a corrective action to have the HL safety coordinator send out a safety alert on this to make the other plants aware of the hazard. There are several other cranes like this in the fleet. There should also be a corrective action to reach out to fleet services to see if there is anything they can do to check for restrictions on a PM. 4/14/19 I have reviewed the updated corrective actions and I approve the investigation. | Daniel Perry |  | Low | [11 empty] | 12.01.1 Inadequate preventative assessment of needs |  |  | 15.05 Inadequate maintenance |  | The Broderson was operated with an obstructed exhaust system. | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure | [68 empty] | We are still not sure what has caused the exhaust system to get this hot, but the damage from the fire appears to be limited to the mount for the muffler. | 200 | Terry Creed | Fire |  | F28-273 | [18 empty] | TBD
8757 | Sooner Power Plant | 2019-03-12 16:00 | While connecting filter skid to Unit #1 APH Guide Bearing oil system, the grating the member was standing on collapsed and the member fell approximately 2 feet. Member received minor scratches to his knee and back. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Assigned per Wilson | 2019-03-19 08:23 | Power Supply | Michael Dowell | 2019-04-22 08:15 | 2019-03-13 14:09 | 2019-03-13 14:09 | 2019-03-25 14:18 | 2019-03-26 16:00 | 2019-03-13 13:59 | 2019-04-01 15:20 | 2019-04-19 07:47 | 2019-03-28 15:27 | Sooner PP Unit 1B Air Preheated Guide Bearing. |  |  | Donnie Jones | Approved | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Frank Brixey |  | 2 members were assigned the task of filtering 1B APH support bearing. They went to move the filter skid from 1A to 1B guide bearing. While in the process of assessing how to hook the filter skid up, one of the members stepped on a piece of grating approximately 11" wide in the middle by 69" long. As the member placed weight on the grating, the grating gave way and the member fell through 18" to the structural beams above the air heater lagging. Distance to lagging is 36". This piece of grating is cut around the guide bearing so the grating is 11" wide at the point of failure. The grating had been cut lengthwise in previous years and cut above structural beams. They were never welded back together. We believe it was cut to gain access below grating to vacuum up economizer ash. This grating is traveled on often by operations on rounds. OGE does no have a standard on modifying grating we go back to the original manufacture drawings. Unit 1 grating was done by Allied Industries and Unit 2 grating was done by Bordean Metal Products. Unit 1 and Unit 2 grating was lay outs are different. The load rating for the grating is 150 p.s.f. Upon discussion members were given task to filter support bearing, but misread the order and went to guide bearing. No LOTO required to hook up filter. System must keep running to filter due to high viscosity of the oil. | Michael Dowell | Frank Brixey | FALSE | Sooner Power Plant | FALSE |  | FALSE | Maintenance |  | Jeffrey Ingmire | Michael Dowell |  | Frank Brixey | Approve - Brixey 4/1/2019 | Frank Brixey | Jesse Murray | High | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | Grating had unapproved modified and modification did not meet specifications. | 23. Defective Tools, Equipment or Materials | 3. Fall from Elevation to Lower Level | I Approve. Jesse Murray | approved by Brady Sowell on 3/28/2019 | [24 empty] | FALSE |  |  | 2017-09-06 | 1983-06-30 |  | 2019-03-12 07:00 | 0 | 0 |  | FALSE | Male | The grating that the member was standing on had been welded together previously. The grating broke at the welds. |  | FALSE | Jeffrey Ingmire |  | First Aid | Jeffrey Ingmire |  |  |  |  | Abrasion |  | FALSE |  | Plant Mechanic II | Knee |  | Lower |  | Michael Dowell |  |  | 3/12/2019 7:00:00 AM | 1.5 | FALSE |  |  | Grating support. | Installing filter skid on 1B APH guide bearing lube oil system | [24 empty] | 324188
8757 | Sooner Power Plant | 2019-03-12 16:00 | While connecting filter skid to Unit #1 APH Guide Bearing oil system, the grating the member was standing on collapsed and the member fell approximately 2 feet. Member received minor scratches to his knee and back. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Assigned per Wilson | 2019-03-19 08:23 | Power Supply | Michael Dowell | 2019-04-22 08:15 | 2019-03-13 14:09 | 2019-03-13 14:09 | 2019-03-25 14:18 | 2019-03-26 16:00 | 2019-03-13 13:59 | 2019-04-01 15:20 | 2019-04-19 07:47 | 2019-03-28 15:27 | Sooner PP Unit 1B Air Preheated Guide Bearing. |  |  | Donnie Jones | Approved | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Frank Brixey |  | 2 members were assigned the task of filtering 1B APH support bearing. They went to move the filter skid from 1A to 1B guide bearing. While in the process of assessing how to hook the filter skid up, one of the members stepped on a piece of grating approximately 11" wide in the middle by 69" long. As the member placed weight on the grating, the grating gave way and the member fell through 18" to the structural beams above the air heater lagging. Distance to lagging is 36". This piece of grating is cut around the guide bearing so the grating is 11" wide at the point of failure. The grating had been cut lengthwise in previous years and cut above structural beams. They were never welded back together. We believe it was cut to gain access below grating to vacuum up economizer ash. This grating is traveled on often by operations on rounds. OGE does no have a standard on modifying grating we go back to the original manufacture drawings. Unit 1 grating was done by Allied Industries and Unit 2 grating was done by Bordean Metal Products. Unit 1 and Unit 2 grating was lay outs are different. The load rating for the grating is 150 p.s.f. Upon discussion members were given task to filter support bearing, but misread the order and went to guide bearing. No LOTO required to hook up filter. System must keep running to filter due to high viscosity of the oil. | Brady Sowell | Frank Brixey | FALSE | Sooner Power Plant | FALSE |  | FALSE | Maintenance |  | Jeffrey Ingmire | Michael Dowell |  | Frank Brixey | Approve - Brixey 4/1/2019 | Frank Brixey | Jesse Murray | High | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | Grating had unapproved modified and modification did not meet specifications. | 23. Defective Tools, Equipment or Materials | 3. Fall from Elevation to Lower Level | I Approve. Jesse Murray | approved by Brady Sowell on 3/28/2019 | [24 empty] | FALSE |  |  | 2017-09-06 | 1983-06-30 |  | 2019-03-12 07:00 | 0 | 0 |  | FALSE | Male | The grating that the member was standing on had been welded together previously. The grating broke at the welds. |  | FALSE | Jeffrey Ingmire |  | First Aid | Jeffrey Ingmire |  |  |  |  | Abrasion |  | FALSE |  | Plant Mechanic II | Knee |  | Lower |  | Michael Dowell |  |  | 3/12/2019 7:00:00 AM | 1.5 | FALSE |  |  | Grating support. | Installing filter skid on 1B APH guide bearing lube oil system | [24 empty] | 324188
8758 | Muskogee Power Plant | 2019-03-12 15:00 | Operations member stepped into alley to investigate noise. Temporary drain (red hose) on Auxiliary Boiler steam line during steam blows contacted member. Member sustain burns. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Assigning per Jon S. | 2019-03-25 11:31 | Power Supply | Joel Leavell | 2019-06-10 13:51 | 2019-03-13 14:13 | 2019-03-13 14:13 | 2019-04-08 10:48 | 2019-03-26 20:00 | 2019-03-13 13:19 | 2019-04-30 07:45 | 2019-05-15 12:30 | 2019-04-10 14:40 | Muskogee 5 alley between turbine basement and boiler structure |  |  | Donnie Jones | Appreciate the investigation detail and action items. Please quickly move to closing all action items. | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | Member (general operator) is conducting normal rounds at Muskogee Power Plant when he hears something that sounds like thumping while traveling down staircase against alley. Member walks through door and see’s red hose hanging down over door spitting out hot water, looks up to trace pipe, reaches to open door to return inside when hose receives sudden pressure and pops member in legs and on back, burning member. |  |  | FALSE | Muskogee Power Plant | FALSE |  | FALSE | Operations |  | Floyd Lancaster | Joel Leavell |  |  | Reviewed. SPC |  | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.06 Inadequate communication methods | High traffic area, raises risk. Drain valve (point of hazardous energy) is located directly above door way. | 02. Failure to Warn | 2. Struck By (Hit By Moving Object) | I Approve. Jesse Murray | Solid investigation / Bob Wright | [24 empty] | FALSE |  | Days away from Work (H) | 2004-11-01 | 1965-11-07 |  | 2019-03-12 05:30 | 8 | 8 |  | FALSE | Male | Member heard an unusual noise and stepped in the alleyway to investigate. He was standing near a red hose running from a steam supply line when the hose pressurized. The steam contacted the member. |  | FALSE | Floyd Lancaster |  | Recordable | Floyd Lancaster | TRUE |  | Hillcrest Medical Center | ER Staff | Burn: Heat/Sun |  | TRUE |  | Plant Operator III | Groin | Injury | Front | TRUE | Joel Leavell | TRUE | 2019 | 3/12/2019 5:30:00 AM | 15yrs | TRUE | FALSE | TRUE | Steam | Member was walking the basement area when he heard an unusual noise out in the alleyway. | [24 empty] | None
8758 | Muskogee Power Plant | 2019-03-12 15:00 | Operations member stepped into alley to investigate noise. Temporary drain (red hose) on Auxiliary Boiler steam line during steam blows contacted member. Member sustain burns. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Assigning per Jon S. | 2019-03-25 11:31 | Power Supply | Joel Leavell | 2019-06-10 13:51 | 2019-03-13 14:13 | 2019-03-13 14:13 | 2019-04-08 10:48 | 2019-03-26 20:00 | 2019-03-13 13:19 | 2019-04-30 07:45 | 2019-05-15 12:30 | 2019-04-10 14:40 | Muskogee 5 alley between turbine basement and boiler structure |  |  | Donnie Jones | Appreciate the investigation detail and action items. Please quickly move to closing all action items. | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | Member (general operator) is conducting normal rounds at Muskogee Power Plant when he hears something that sounds like thumping while traveling down staircase against alley. Member walks through door and see’s red hose hanging down over door spitting out hot water, looks up to trace pipe, reaches to open door to return inside when hose receives sudden pressure and pops member in legs and on back, burning member. |  |  | FALSE | Muskogee Power Plant | FALSE |  | FALSE | Operations |  | Floyd Lancaster | Joel Leavell |  |  | Reviewed. SPC |  | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.06 Inadequate communication methods | No way to have visual of drip legs when operating chain valve for steam pressure. | 02. Failure to Warn | 2. Struck By (Hit By Moving Object) | I Approve. Jesse Murray | Solid investigation / Bob Wright | [24 empty] | FALSE |  | Days away from Work (H) | 2004-11-01 | 1965-11-07 |  | 2019-03-12 05:30 | 8 | 8 |  | FALSE | Male | Member heard an unusual noise and stepped in the alleyway to investigate. He was standing near a red hose running from a steam supply line when the hose pressurized. The steam contacted the member. |  | FALSE | Floyd Lancaster |  | Recordable | Floyd Lancaster | TRUE |  | Hillcrest Medical Center | ER Staff | Burn: Heat/Sun |  | TRUE |  | Plant Operator III | Groin | Injury | Front | TRUE | Joel Leavell | TRUE | 2019 | 3/12/2019 5:30:00 AM | 15yrs | TRUE | FALSE | TRUE | Steam | Member was walking the basement area when he heard an unusual noise out in the alleyway. | [24 empty] | None
8758 | Muskogee Power Plant | 2019-03-12 15:00 | Operations member stepped into alley to investigate noise. Temporary drain (red hose) on Auxiliary Boiler steam line during steam blows contacted member. Member sustain burns. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Assigning per Jon S. | 2019-03-25 11:31 | Power Supply | Joel Leavell | 2019-06-10 13:51 | 2019-03-13 14:13 | 2019-03-13 14:13 | 2019-04-08 10:48 | 2019-03-26 20:00 | 2019-03-13 13:19 | 2019-04-30 07:45 | 2019-05-15 12:30 | 2019-04-10 14:40 | Muskogee 5 alley between turbine basement and boiler structure |  |  | Donnie Jones | Appreciate the investigation detail and action items. Please quickly move to closing all action items. | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | Member (general operator) is conducting normal rounds at Muskogee Power Plant when he hears something that sounds like thumping while traveling down staircase against alley. Member walks through door and see’s red hose hanging down over door spitting out hot water, looks up to trace pipe, reaches to open door to return inside when hose receives sudden pressure and pops member in legs and on back, burning member. |  |  | FALSE | Muskogee Power Plant | FALSE |  | FALSE | Operations |  | Floyd Lancaster | Joel Leavell |  |  | Reviewed. SPC |  | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.06 Inadequate communication methods | Condensate drain for aux boiler is in a deceiving area due to it’s distance from the aux boiler (injured employee heard the all call but assumed the hazards were at the aux boiler. Didn’t realize this pipe could have any relation to steam blows). | 02. Failure to Warn | 2. Struck By (Hit By Moving Object) | I Approve. Jesse Murray | Solid investigation / Bob Wright | [24 empty] | FALSE |  | Days away from Work (H) | 2004-11-01 | 1965-11-07 |  | 2019-03-12 05:30 | 8 | 8 |  | FALSE | Male | Member heard an unusual noise and stepped in the alleyway to investigate. He was standing near a red hose running from a steam supply line when the hose pressurized. The steam contacted the member. |  | FALSE | Floyd Lancaster |  | Recordable | Floyd Lancaster | TRUE |  | Hillcrest Medical Center | ER Staff | Burn: Heat/Sun |  | TRUE |  | Plant Operator III | Groin | Injury | Front | TRUE | Joel Leavell | TRUE | 2019 | 3/12/2019 5:30:00 AM | 15yrs | TRUE | FALSE | TRUE | Steam | Member was walking the basement area when he heard an unusual noise out in the alleyway. | [24 empty] | None
8758 | Muskogee Power Plant | 2019-03-12 15:00 | Operations member stepped into alley to investigate noise. Temporary drain (red hose) on Auxiliary Boiler steam line during steam blows contacted member. Member sustain burns. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Assigning per Jon S. | 2019-03-25 11:31 | Power Supply | Joel Leavell | 2019-06-10 13:51 | 2019-03-13 14:13 | 2019-03-13 14:13 | 2019-04-08 10:48 | 2019-03-26 20:00 | 2019-03-13 13:19 | 2019-04-30 07:45 | 2019-05-15 12:30 | 2019-04-10 14:40 | Muskogee 5 alley between turbine basement and boiler structure |  |  | Donnie Jones | Appreciate the investigation detail and action items. Please quickly move to closing all action items. | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | Member (general operator) is conducting normal rounds at Muskogee Power Plant when he hears something that sounds like thumping while traveling down staircase against alley. Member walks through door and see’s red hose hanging down over door spitting out hot water, looks up to trace pipe, reaches to open door to return inside when hose receives sudden pressure and pops member in legs and on back, burning member. |  |  | FALSE | Muskogee Power Plant | FALSE |  | FALSE | Operations |  | Floyd Lancaster | Joel Leavell |  |  | Reviewed. SPC |  | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.06 Inadequate communication methods | No formal risk recognition and documentation completed-i.e. no pre-job berifing per site safety program completed, no plan of day documentation for specific member assignments, and no safe work permit completed. | 02. Failure to Warn | 2. Struck By (Hit By Moving Object) | I Approve. Jesse Murray | Solid investigation / Bob Wright | [24 empty] | FALSE |  | Days away from Work (H) | 2004-11-01 | 1965-11-07 |  | 2019-03-12 05:30 | 8 | 8 |  | FALSE | Male | Member heard an unusual noise and stepped in the alleyway to investigate. He was standing near a red hose running from a steam supply line when the hose pressurized. The steam contacted the member. |  | FALSE | Floyd Lancaster |  | Recordable | Floyd Lancaster | TRUE |  | Hillcrest Medical Center | ER Staff | Burn: Heat/Sun |  | TRUE |  | Plant Operator III | Groin | Injury | Front | TRUE | Joel Leavell | TRUE | 2019 | 3/12/2019 5:30:00 AM | 15yrs | TRUE | FALSE | TRUE | Steam | Member was walking the basement area when he heard an unusual noise out in the alleyway. | [24 empty] | None
8758 | Muskogee Power Plant | 2019-03-12 15:00 | Operations member stepped into alley to investigate noise. Temporary drain (red hose) on Auxiliary Boiler steam line during steam blows contacted member. Member sustain burns. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Assigning per Jon S. | 2019-03-25 11:31 | Power Supply | Joel Leavell | 2019-06-10 13:51 | 2019-03-13 14:13 | 2019-03-13 14:13 | 2019-04-08 10:48 | 2019-03-26 20:00 | 2019-03-13 13:19 | 2019-04-30 07:45 | 2019-05-15 12:30 | 2019-04-10 14:40 | Muskogee 5 alley between turbine basement and boiler structure |  |  | Donnie Jones | Appreciate the investigation detail and action items. Please quickly move to closing all action items. | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | Member (general operator) is conducting normal rounds at Muskogee Power Plant when he hears something that sounds like thumping while traveling down staircase against alley. Member walks through door and see’s red hose hanging down over door spitting out hot water, looks up to trace pipe, reaches to open door to return inside when hose receives sudden pressure and pops member in legs and on back, burning member. |  |  | FALSE | Muskogee Power Plant | FALSE |  | FALSE | Operations |  | Floyd Lancaster | Joel Leavell |  |  | Reviewed. SPC |  | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.06 Inadequate communication methods | Failure to follow policies- Contract specific steam blow procedure not followed precisely (procedure calls for visual of all hoses to recognize hammer potential and immediate clearance, hoses were not individually manned for visuals), barricading and signage policy company violation | 02. Failure to Warn | 2. Struck By (Hit By Moving Object) | I Approve. Jesse Murray | Solid investigation / Bob Wright | [24 empty] | FALSE |  | Days away from Work (H) | 2004-11-01 | 1965-11-07 |  | 2019-03-12 05:30 | 8 | 8 |  | FALSE | Male | Member heard an unusual noise and stepped in the alleyway to investigate. He was standing near a red hose running from a steam supply line when the hose pressurized. The steam contacted the member. |  | FALSE | Floyd Lancaster |  | Recordable | Floyd Lancaster | TRUE |  | Hillcrest Medical Center | ER Staff | Burn: Heat/Sun |  | TRUE |  | Plant Operator III | Groin | Injury | Front | TRUE | Joel Leavell | TRUE | 2019 | 3/12/2019 5:30:00 AM | 15yrs | TRUE | FALSE | TRUE | Steam | Member was walking the basement area when he heard an unusual noise out in the alleyway. | [24 empty] | None
8758 | Muskogee Power Plant | 2019-03-12 15:00 | Operations member stepped into alley to investigate noise. Temporary drain (red hose) on Auxiliary Boiler steam line during steam blows contacted member. Member sustain burns. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Assigning per Jon S. | 2019-03-25 11:31 | Power Supply | Joel Leavell | 2019-06-10 13:51 | 2019-03-13 14:13 | 2019-03-13 14:13 | 2019-04-08 10:48 | 2019-03-26 20:00 | 2019-03-13 13:19 | 2019-04-30 07:45 | 2019-05-15 12:30 | 2019-04-10 14:40 | Muskogee 5 alley between turbine basement and boiler structure |  |  | Donnie Jones | Appreciate the investigation detail and action items. Please quickly move to closing all action items. | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | Member (general operator) is conducting normal rounds at Muskogee Power Plant when he hears something that sounds like thumping while traveling down staircase against alley. Member walks through door and see’s red hose hanging down over door spitting out hot water, looks up to trace pipe, reaches to open door to return inside when hose receives sudden pressure and pops member in legs and on back, burning member. | Elizabeth Gough |  | FALSE | Muskogee Power Plant | FALSE |  | FALSE | Operations |  | Floyd Lancaster | Joel Leavell |  |  | Reviewed. SPC |  | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.06 Inadequate communication methods | High traffic area, raises risk. Drain valve (point of hazardous energy) is located directly above door way. | 02. Failure to Warn | 2. Struck By (Hit By Moving Object) | I Approve. Jesse Murray | Solid investigation / Bob Wright | [24 empty] | FALSE |  | Days away from Work (H) | 2004-11-01 | 1965-11-07 |  | 2019-03-12 05:30 | 8 | 8 |  | FALSE | Male | Member heard an unusual noise and stepped in the alleyway to investigate. He was standing near a red hose running from a steam supply line when the hose pressurized. The steam contacted the member. |  | FALSE | Floyd Lancaster |  | Recordable | Floyd Lancaster | TRUE |  | Hillcrest Medical Center | ER Staff | Burn: Heat/Sun |  | TRUE |  | Plant Operator III | Groin | Injury | Front | TRUE | Joel Leavell | TRUE | 2019 | 3/12/2019 5:30:00 AM | 15yrs | TRUE | FALSE | TRUE | Steam | Member was walking the basement area when he heard an unusual noise out in the alleyway. | [24 empty] | None
8758 | Muskogee Power Plant | 2019-03-12 15:00 | Operations member stepped into alley to investigate noise. Temporary drain (red hose) on Auxiliary Boiler steam line during steam blows contacted member. Member sustain burns. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Assigning per Jon S. | 2019-03-25 11:31 | Power Supply | Joel Leavell | 2019-06-10 13:51 | 2019-03-13 14:13 | 2019-03-13 14:13 | 2019-04-08 10:48 | 2019-03-26 20:00 | 2019-03-13 13:19 | 2019-04-30 07:45 | 2019-05-15 12:30 | 2019-04-10 14:40 | Muskogee 5 alley between turbine basement and boiler structure |  |  | Donnie Jones | Appreciate the investigation detail and action items. Please quickly move to closing all action items. | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | Member (general operator) is conducting normal rounds at Muskogee Power Plant when he hears something that sounds like thumping while traveling down staircase against alley. Member walks through door and see’s red hose hanging down over door spitting out hot water, looks up to trace pipe, reaches to open door to return inside when hose receives sudden pressure and pops member in legs and on back, burning member. | Elizabeth Gough |  | FALSE | Muskogee Power Plant | FALSE |  | FALSE | Operations |  | Floyd Lancaster | Joel Leavell |  |  | Reviewed. SPC |  | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.06 Inadequate communication methods | No way to have visual of drip legs when operating chain valve for steam pressure. | 02. Failure to Warn | 2. Struck By (Hit By Moving Object) | I Approve. Jesse Murray | Solid investigation / Bob Wright | [24 empty] | FALSE |  | Days away from Work (H) | 2004-11-01 | 1965-11-07 |  | 2019-03-12 05:30 | 8 | 8 |  | FALSE | Male | Member heard an unusual noise and stepped in the alleyway to investigate. He was standing near a red hose running from a steam supply line when the hose pressurized. The steam contacted the member. |  | FALSE | Floyd Lancaster |  | Recordable | Floyd Lancaster | TRUE |  | Hillcrest Medical Center | ER Staff | Burn: Heat/Sun |  | TRUE |  | Plant Operator III | Groin | Injury | Front | TRUE | Joel Leavell | TRUE | 2019 | 3/12/2019 5:30:00 AM | 15yrs | TRUE | FALSE | TRUE | Steam | Member was walking the basement area when he heard an unusual noise out in the alleyway. | [24 empty] | None
8758 | Muskogee Power Plant | 2019-03-12 15:00 | Operations member stepped into alley to investigate noise. Temporary drain (red hose) on Auxiliary Boiler steam line during steam blows contacted member. Member sustain burns. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Assigning per Jon S. | 2019-03-25 11:31 | Power Supply | Joel Leavell | 2019-06-10 13:51 | 2019-03-13 14:13 | 2019-03-13 14:13 | 2019-04-08 10:48 | 2019-03-26 20:00 | 2019-03-13 13:19 | 2019-04-30 07:45 | 2019-05-15 12:30 | 2019-04-10 14:40 | Muskogee 5 alley between turbine basement and boiler structure |  |  | Donnie Jones | Appreciate the investigation detail and action items. Please quickly move to closing all action items. | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | Member (general operator) is conducting normal rounds at Muskogee Power Plant when he hears something that sounds like thumping while traveling down staircase against alley. Member walks through door and see’s red hose hanging down over door spitting out hot water, looks up to trace pipe, reaches to open door to return inside when hose receives sudden pressure and pops member in legs and on back, burning member. | Elizabeth Gough |  | FALSE | Muskogee Power Plant | FALSE |  | FALSE | Operations |  | Floyd Lancaster | Joel Leavell |  |  | Reviewed. SPC |  | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.06 Inadequate communication methods | Condensate drain for aux boiler is in a deceiving area due to it’s distance from the aux boiler (injured employee heard the all call but assumed the hazards were at the aux boiler. Didn’t realize this pipe could have any relation to steam blows). | 02. Failure to Warn | 2. Struck By (Hit By Moving Object) | I Approve. Jesse Murray | Solid investigation / Bob Wright | [24 empty] | FALSE |  | Days away from Work (H) | 2004-11-01 | 1965-11-07 |  | 2019-03-12 05:30 | 8 | 8 |  | FALSE | Male | Member heard an unusual noise and stepped in the alleyway to investigate. He was standing near a red hose running from a steam supply line when the hose pressurized. The steam contacted the member. |  | FALSE | Floyd Lancaster |  | Recordable | Floyd Lancaster | TRUE |  | Hillcrest Medical Center | ER Staff | Burn: Heat/Sun |  | TRUE |  | Plant Operator III | Groin | Injury | Front | TRUE | Joel Leavell | TRUE | 2019 | 3/12/2019 5:30:00 AM | 15yrs | TRUE | FALSE | TRUE | Steam | Member was walking the basement area when he heard an unusual noise out in the alleyway. | [24 empty] | None
8758 | Muskogee Power Plant | 2019-03-12 15:00 | Operations member stepped into alley to investigate noise. Temporary drain (red hose) on Auxiliary Boiler steam line during steam blows contacted member. Member sustain burns. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Assigning per Jon S. | 2019-03-25 11:31 | Power Supply | Joel Leavell | 2019-06-10 13:51 | 2019-03-13 14:13 | 2019-03-13 14:13 | 2019-04-08 10:48 | 2019-03-26 20:00 | 2019-03-13 13:19 | 2019-04-30 07:45 | 2019-05-15 12:30 | 2019-04-10 14:40 | Muskogee 5 alley between turbine basement and boiler structure |  |  | Donnie Jones | Appreciate the investigation detail and action items. Please quickly move to closing all action items. | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | Member (general operator) is conducting normal rounds at Muskogee Power Plant when he hears something that sounds like thumping while traveling down staircase against alley. Member walks through door and see’s red hose hanging down over door spitting out hot water, looks up to trace pipe, reaches to open door to return inside when hose receives sudden pressure and pops member in legs and on back, burning member. | Elizabeth Gough |  | FALSE | Muskogee Power Plant | FALSE |  | FALSE | Operations |  | Floyd Lancaster | Joel Leavell |  |  | Reviewed. SPC |  | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.06 Inadequate communication methods | No formal risk recognition and documentation completed-i.e. no pre-job berifing per site safety program completed, no plan of day documentation for specific member assignments, and no safe work permit completed. | 02. Failure to Warn | 2. Struck By (Hit By Moving Object) | I Approve. Jesse Murray | Solid investigation / Bob Wright | [24 empty] | FALSE |  | Days away from Work (H) | 2004-11-01 | 1965-11-07 |  | 2019-03-12 05:30 | 8 | 8 |  | FALSE | Male | Member heard an unusual noise and stepped in the alleyway to investigate. He was standing near a red hose running from a steam supply line when the hose pressurized. The steam contacted the member. |  | FALSE | Floyd Lancaster |  | Recordable | Floyd Lancaster | TRUE |  | Hillcrest Medical Center | ER Staff | Burn: Heat/Sun |  | TRUE |  | Plant Operator III | Groin | Injury | Front | TRUE | Joel Leavell | TRUE | 2019 | 3/12/2019 5:30:00 AM | 15yrs | TRUE | FALSE | TRUE | Steam | Member was walking the basement area when he heard an unusual noise out in the alleyway. | [24 empty] | None
8758 | Muskogee Power Plant | 2019-03-12 15:00 | Operations member stepped into alley to investigate noise. Temporary drain (red hose) on Auxiliary Boiler steam line during steam blows contacted member. Member sustain burns. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Assigning per Jon S. | 2019-03-25 11:31 | Power Supply | Joel Leavell | 2019-06-10 13:51 | 2019-03-13 14:13 | 2019-03-13 14:13 | 2019-04-08 10:48 | 2019-03-26 20:00 | 2019-03-13 13:19 | 2019-04-30 07:45 | 2019-05-15 12:30 | 2019-04-10 14:40 | Muskogee 5 alley between turbine basement and boiler structure |  |  | Donnie Jones | Appreciate the investigation detail and action items. Please quickly move to closing all action items. | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | Member (general operator) is conducting normal rounds at Muskogee Power Plant when he hears something that sounds like thumping while traveling down staircase against alley. Member walks through door and see’s red hose hanging down over door spitting out hot water, looks up to trace pipe, reaches to open door to return inside when hose receives sudden pressure and pops member in legs and on back, burning member. | Elizabeth Gough |  | FALSE | Muskogee Power Plant | FALSE |  | FALSE | Operations |  | Floyd Lancaster | Joel Leavell |  |  | Reviewed. SPC |  | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.06 Inadequate communication methods | Failure to follow policies- Contract specific steam blow procedure not followed precisely (procedure calls for visual of all hoses to recognize hammer potential and immediate clearance, hoses were not individually manned for visuals), barricading and signage policy company violation | 02. Failure to Warn | 2. Struck By (Hit By Moving Object) | I Approve. Jesse Murray | Solid investigation / Bob Wright | [24 empty] | FALSE |  | Days away from Work (H) | 2004-11-01 | 1965-11-07 |  | 2019-03-12 05:30 | 8 | 8 |  | FALSE | Male | Member heard an unusual noise and stepped in the alleyway to investigate. He was standing near a red hose running from a steam supply line when the hose pressurized. The steam contacted the member. |  | FALSE | Floyd Lancaster |  | Recordable | Floyd Lancaster | TRUE |  | Hillcrest Medical Center | ER Staff | Burn: Heat/Sun |  | TRUE |  | Plant Operator III | Groin | Injury | Front | TRUE | Joel Leavell | TRUE | 2019 | 3/12/2019 5:30:00 AM | 15yrs | TRUE | FALSE | TRUE | Steam | Member was walking the basement area when he heard an unusual noise out in the alleyway. | [24 empty] | None
8758 | Muskogee Power Plant | 2019-03-12 15:00 | Operations member stepped into alley to investigate noise. Temporary drain (red hose) on Auxiliary Boiler steam line during steam blows contacted member. Member sustain burns. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Assigning per Jon S. | 2019-03-25 11:31 | Power Supply | Joel Leavell | 2019-06-10 13:51 | 2019-03-13 14:13 | 2019-03-13 14:13 | 2019-04-08 10:48 | 2019-03-26 20:00 | 2019-03-13 13:19 | 2019-04-30 07:45 | 2019-05-15 12:30 | 2019-04-10 14:40 | Muskogee 5 alley between turbine basement and boiler structure |  |  | Donnie Jones | Appreciate the investigation detail and action items. Please quickly move to closing all action items. | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | Member (general operator) is conducting normal rounds at Muskogee Power Plant when he hears something that sounds like thumping while traveling down staircase against alley. Member walks through door and see’s red hose hanging down over door spitting out hot water, looks up to trace pipe, reaches to open door to return inside when hose receives sudden pressure and pops member in legs and on back, burning member. | Marcus Huddleston |  | FALSE | Muskogee Power Plant | FALSE |  | FALSE | Operations |  | Floyd Lancaster | Joel Leavell |  |  | Reviewed. SPC |  | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.06 Inadequate communication methods | High traffic area, raises risk. Drain valve (point of hazardous energy) is located directly above door way. | 02. Failure to Warn | 2. Struck By (Hit By Moving Object) | I Approve. Jesse Murray | Solid investigation / Bob Wright | [24 empty] | FALSE |  | Days away from Work (H) | 2004-11-01 | 1965-11-07 |  | 2019-03-12 05:30 | 8 | 8 |  | FALSE | Male | Member heard an unusual noise and stepped in the alleyway to investigate. He was standing near a red hose running from a steam supply line when the hose pressurized. The steam contacted the member. |  | FALSE | Floyd Lancaster |  | Recordable | Floyd Lancaster | TRUE |  | Hillcrest Medical Center | ER Staff | Burn: Heat/Sun |  | TRUE |  | Plant Operator III | Groin | Injury | Front | TRUE | Joel Leavell | TRUE | 2019 | 3/12/2019 5:30:00 AM | 15yrs | TRUE | FALSE | TRUE | Steam | Member was walking the basement area when he heard an unusual noise out in the alleyway. | [24 empty] | None
8758 | Muskogee Power Plant | 2019-03-12 15:00 | Operations member stepped into alley to investigate noise. Temporary drain (red hose) on Auxiliary Boiler steam line during steam blows contacted member. Member sustain burns. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Assigning per Jon S. | 2019-03-25 11:31 | Power Supply | Joel Leavell | 2019-06-10 13:51 | 2019-03-13 14:13 | 2019-03-13 14:13 | 2019-04-08 10:48 | 2019-03-26 20:00 | 2019-03-13 13:19 | 2019-04-30 07:45 | 2019-05-15 12:30 | 2019-04-10 14:40 | Muskogee 5 alley between turbine basement and boiler structure |  |  | Donnie Jones | Appreciate the investigation detail and action items. Please quickly move to closing all action items. | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | Member (general operator) is conducting normal rounds at Muskogee Power Plant when he hears something that sounds like thumping while traveling down staircase against alley. Member walks through door and see’s red hose hanging down over door spitting out hot water, looks up to trace pipe, reaches to open door to return inside when hose receives sudden pressure and pops member in legs and on back, burning member. | Marcus Huddleston |  | FALSE | Muskogee Power Plant | FALSE |  | FALSE | Operations |  | Floyd Lancaster | Joel Leavell |  |  | Reviewed. SPC |  | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.06 Inadequate communication methods | No way to have visual of drip legs when operating chain valve for steam pressure. | 02. Failure to Warn | 2. Struck By (Hit By Moving Object) | I Approve. Jesse Murray | Solid investigation / Bob Wright | [24 empty] | FALSE |  | Days away from Work (H) | 2004-11-01 | 1965-11-07 |  | 2019-03-12 05:30 | 8 | 8 |  | FALSE | Male | Member heard an unusual noise and stepped in the alleyway to investigate. He was standing near a red hose running from a steam supply line when the hose pressurized. The steam contacted the member. |  | FALSE | Floyd Lancaster |  | Recordable | Floyd Lancaster | TRUE |  | Hillcrest Medical Center | ER Staff | Burn: Heat/Sun |  | TRUE |  | Plant Operator III | Groin | Injury | Front | TRUE | Joel Leavell | TRUE | 2019 | 3/12/2019 5:30:00 AM | 15yrs | TRUE | FALSE | TRUE | Steam | Member was walking the basement area when he heard an unusual noise out in the alleyway. | [24 empty] | None
8758 | Muskogee Power Plant | 2019-03-12 15:00 | Operations member stepped into alley to investigate noise. Temporary drain (red hose) on Auxiliary Boiler steam line during steam blows contacted member. Member sustain burns. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Assigning per Jon S. | 2019-03-25 11:31 | Power Supply | Joel Leavell | 2019-06-10 13:51 | 2019-03-13 14:13 | 2019-03-13 14:13 | 2019-04-08 10:48 | 2019-03-26 20:00 | 2019-03-13 13:19 | 2019-04-30 07:45 | 2019-05-15 12:30 | 2019-04-10 14:40 | Muskogee 5 alley between turbine basement and boiler structure |  |  | Donnie Jones | Appreciate the investigation detail and action items. Please quickly move to closing all action items. | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | Member (general operator) is conducting normal rounds at Muskogee Power Plant when he hears something that sounds like thumping while traveling down staircase against alley. Member walks through door and see’s red hose hanging down over door spitting out hot water, looks up to trace pipe, reaches to open door to return inside when hose receives sudden pressure and pops member in legs and on back, burning member. | Marcus Huddleston |  | FALSE | Muskogee Power Plant | FALSE |  | FALSE | Operations |  | Floyd Lancaster | Joel Leavell |  |  | Reviewed. SPC |  | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.06 Inadequate communication methods | Condensate drain for aux boiler is in a deceiving area due to it’s distance from the aux boiler (injured employee heard the all call but assumed the hazards were at the aux boiler. Didn’t realize this pipe could have any relation to steam blows). | 02. Failure to Warn | 2. Struck By (Hit By Moving Object) | I Approve. Jesse Murray | Solid investigation / Bob Wright | [24 empty] | FALSE |  | Days away from Work (H) | 2004-11-01 | 1965-11-07 |  | 2019-03-12 05:30 | 8 | 8 |  | FALSE | Male | Member heard an unusual noise and stepped in the alleyway to investigate. He was standing near a red hose running from a steam supply line when the hose pressurized. The steam contacted the member. |  | FALSE | Floyd Lancaster |  | Recordable | Floyd Lancaster | TRUE |  | Hillcrest Medical Center | ER Staff | Burn: Heat/Sun |  | TRUE |  | Plant Operator III | Groin | Injury | Front | TRUE | Joel Leavell | TRUE | 2019 | 3/12/2019 5:30:00 AM | 15yrs | TRUE | FALSE | TRUE | Steam | Member was walking the basement area when he heard an unusual noise out in the alleyway. | [24 empty] | None
8758 | Muskogee Power Plant | 2019-03-12 15:00 | Operations member stepped into alley to investigate noise. Temporary drain (red hose) on Auxiliary Boiler steam line during steam blows contacted member. Member sustain burns. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Assigning per Jon S. | 2019-03-25 11:31 | Power Supply | Joel Leavell | 2019-06-10 13:51 | 2019-03-13 14:13 | 2019-03-13 14:13 | 2019-04-08 10:48 | 2019-03-26 20:00 | 2019-03-13 13:19 | 2019-04-30 07:45 | 2019-05-15 12:30 | 2019-04-10 14:40 | Muskogee 5 alley between turbine basement and boiler structure |  |  | Donnie Jones | Appreciate the investigation detail and action items. Please quickly move to closing all action items. | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | Member (general operator) is conducting normal rounds at Muskogee Power Plant when he hears something that sounds like thumping while traveling down staircase against alley. Member walks through door and see’s red hose hanging down over door spitting out hot water, looks up to trace pipe, reaches to open door to return inside when hose receives sudden pressure and pops member in legs and on back, burning member. | Marcus Huddleston |  | FALSE | Muskogee Power Plant | FALSE |  | FALSE | Operations |  | Floyd Lancaster | Joel Leavell |  |  | Reviewed. SPC |  | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.06 Inadequate communication methods | No formal risk recognition and documentation completed-i.e. no pre-job berifing per site safety program completed, no plan of day documentation for specific member assignments, and no safe work permit completed. | 02. Failure to Warn | 2. Struck By (Hit By Moving Object) | I Approve. Jesse Murray | Solid investigation / Bob Wright | [24 empty] | FALSE |  | Days away from Work (H) | 2004-11-01 | 1965-11-07 |  | 2019-03-12 05:30 | 8 | 8 |  | FALSE | Male | Member heard an unusual noise and stepped in the alleyway to investigate. He was standing near a red hose running from a steam supply line when the hose pressurized. The steam contacted the member. |  | FALSE | Floyd Lancaster |  | Recordable | Floyd Lancaster | TRUE |  | Hillcrest Medical Center | ER Staff | Burn: Heat/Sun |  | TRUE |  | Plant Operator III | Groin | Injury | Front | TRUE | Joel Leavell | TRUE | 2019 | 3/12/2019 5:30:00 AM | 15yrs | TRUE | FALSE | TRUE | Steam | Member was walking the basement area when he heard an unusual noise out in the alleyway. | [24 empty] | None
8758 | Muskogee Power Plant | 2019-03-12 15:00 | Operations member stepped into alley to investigate noise. Temporary drain (red hose) on Auxiliary Boiler steam line during steam blows contacted member. Member sustain burns. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Assigning per Jon S. | 2019-03-25 11:31 | Power Supply | Joel Leavell | 2019-06-10 13:51 | 2019-03-13 14:13 | 2019-03-13 14:13 | 2019-04-08 10:48 | 2019-03-26 20:00 | 2019-03-13 13:19 | 2019-04-30 07:45 | 2019-05-15 12:30 | 2019-04-10 14:40 | Muskogee 5 alley between turbine basement and boiler structure |  |  | Donnie Jones | Appreciate the investigation detail and action items. Please quickly move to closing all action items. | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | Member (general operator) is conducting normal rounds at Muskogee Power Plant when he hears something that sounds like thumping while traveling down staircase against alley. Member walks through door and see’s red hose hanging down over door spitting out hot water, looks up to trace pipe, reaches to open door to return inside when hose receives sudden pressure and pops member in legs and on back, burning member. | Marcus Huddleston |  | FALSE | Muskogee Power Plant | FALSE |  | FALSE | Operations |  | Floyd Lancaster | Joel Leavell |  |  | Reviewed. SPC |  | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.06 Inadequate communication methods | Failure to follow policies- Contract specific steam blow procedure not followed precisely (procedure calls for visual of all hoses to recognize hammer potential and immediate clearance, hoses were not individually manned for visuals), barricading and signage policy company violation | 02. Failure to Warn | 2. Struck By (Hit By Moving Object) | I Approve. Jesse Murray | Solid investigation / Bob Wright | [24 empty] | FALSE |  | Days away from Work (H) | 2004-11-01 | 1965-11-07 |  | 2019-03-12 05:30 | 8 | 8 |  | FALSE | Male | Member heard an unusual noise and stepped in the alleyway to investigate. He was standing near a red hose running from a steam supply line when the hose pressurized. The steam contacted the member. |  | FALSE | Floyd Lancaster |  | Recordable | Floyd Lancaster | TRUE |  | Hillcrest Medical Center | ER Staff | Burn: Heat/Sun |  | TRUE |  | Plant Operator III | Groin | Injury | Front | TRUE | Joel Leavell | TRUE | 2019 | 3/12/2019 5:30:00 AM | 15yrs | TRUE | FALSE | TRUE | Steam | Member was walking the basement area when he heard an unusual noise out in the alleyway. | [24 empty] | None
8759 | Muskogee Power Plant | 2019-03-11 09:00 | A puncture hole was found in the flex metallic fuel hose on the boiler burner F2. There was no witness to the hole being placed in the hose. | Level 2 |  | FALSE | Property Damage |  |  |  |  | OG&E Corp Services |  | 2019-05-10 10:41 | 2019-03-13 16:02 | 2019-03-13 16:02 | 2019-04-02 10:02 | 2019-03-25 14:00 | 2019-03-13 15:55 | 2019-04-14 05:30 |  | 2019-04-10 10:07 | Muskogee PP Unit 5 Boiler Burner F2 |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE |  |  | During the start up and testing of Unit 5 following the gas conversion outage burner F2 was cycling in and out of service. After multiple iterations of firing and failing to maintain flame, operations went to have a visual on the burner. Upon inspection a hole was found to have been punctured in the flex metallic fuel pipe. The piece of equipment was tagged and removed from service. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | UTS - Capital Projects |  |  |  |  | Christopher Lelak | No comments - CBL 04/14/19 | Christopher Lelak |  | Medium |  | 2.02 Emotional disturbance |  | 4.10 Frustration |  |  |  | 8.2.1 Improper conduct that is not condoned: Intentional | [8 empty] | The believed cause of the incident is an impact force was received to the fuel pipe. It is unclear if this was an accident or intentional. | 15. Using Equipment Improperly | 9. Abnormal Operation |  | Without determining if the damage was intentional or not, i believe the corrective action is adequate. No additional comments. MLH 4/10/19 | [66 empty] | A puncture hole is currently in the flex hose fuel pipe from the block and bleed skid to the burner. | 7600 | Unknown | Fixed Equipment | [20 empty] | none
8759 | Muskogee Power Plant | 2019-03-11 09:00 | A puncture hole was found in the flex metallic fuel hose on the boiler burner F2. There was no witness to the hole being placed in the hose. | Level 2 |  | FALSE | Property Damage |  |  |  |  | OG&E Corp Services |  | 2019-05-10 10:41 | 2019-03-13 16:02 | 2019-03-13 16:02 | 2019-04-02 10:02 | 2019-03-25 14:00 | 2019-03-13 15:55 | 2019-04-14 05:30 |  | 2019-04-10 10:07 | Muskogee PP Unit 5 Boiler Burner F2 |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE |  |  | During the start up and testing of Unit 5 following the gas conversion outage burner F2 was cycling in and out of service. After multiple iterations of firing and failing to maintain flame, operations went to have a visual on the burner. Upon inspection a hole was found to have been punctured in the flex metallic fuel pipe. The piece of equipment was tagged and removed from service. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | UTS - Capital Projects |  |  |  |  | Christopher Lelak | No comments - CBL 04/14/19 | Christopher Lelak |  | Medium |  | 2.02 Emotional disturbance |  | 4.10 Frustration |  |  |  | 8.2.2 Improper conduct that is not condoned: Unintentional | [8 empty] | The believed cause of the incident is an impact force was received to the fuel pipe. It is unclear if this was an accident or intentional. | 15. Using Equipment Improperly | 9. Abnormal Operation |  | Without determining if the damage was intentional or not, i believe the corrective action is adequate. No additional comments. MLH 4/10/19 | [66 empty] | A puncture hole is currently in the flex hose fuel pipe from the block and bleed skid to the burner. | 7600 | Unknown | Fixed Equipment | [20 empty] | none
8759 | Muskogee Power Plant | 2019-03-11 09:00 | A puncture hole was found in the flex metallic fuel hose on the boiler burner F2. There was no witness to the hole being placed in the hose. | Level 2 |  | FALSE | Property Damage |  |  |  |  | OG&E Corp Services |  | 2019-05-10 10:41 | 2019-03-13 16:02 | 2019-03-13 16:02 | 2019-04-02 10:02 | 2019-03-25 14:00 | 2019-03-13 15:55 | 2019-04-14 05:30 |  | 2019-04-10 10:07 | Muskogee PP Unit 5 Boiler Burner F2 |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE |  |  | During the start up and testing of Unit 5 following the gas conversion outage burner F2 was cycling in and out of service. After multiple iterations of firing and failing to maintain flame, operations went to have a visual on the burner. Upon inspection a hole was found to have been punctured in the flex metallic fuel pipe. The piece of equipment was tagged and removed from service. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | UTS - Capital Projects |  |  |  |  | Christopher Lelak | No comments - CBL 04/14/19 | Christopher Lelak |  | Medium |  | 2.06 Poor coordination |  | 4.10 Frustration |  |  |  | 8.2.1 Improper conduct that is not condoned: Intentional | [8 empty] | The believed cause of the incident is an impact force was received to the fuel pipe. It is unclear if this was an accident or intentional. | 15. Using Equipment Improperly | 9. Abnormal Operation |  | Without determining if the damage was intentional or not, i believe the corrective action is adequate. No additional comments. MLH 4/10/19 | [66 empty] | A puncture hole is currently in the flex hose fuel pipe from the block and bleed skid to the burner. | 7600 | Unknown | Fixed Equipment | [20 empty] | none
8759 | Muskogee Power Plant | 2019-03-11 09:00 | A puncture hole was found in the flex metallic fuel hose on the boiler burner F2. There was no witness to the hole being placed in the hose. | Level 2 |  | FALSE | Property Damage |  |  |  |  | OG&E Corp Services |  | 2019-05-10 10:41 | 2019-03-13 16:02 | 2019-03-13 16:02 | 2019-04-02 10:02 | 2019-03-25 14:00 | 2019-03-13 15:55 | 2019-04-14 05:30 |  | 2019-04-10 10:07 | Muskogee PP Unit 5 Boiler Burner F2 |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE |  |  | During the start up and testing of Unit 5 following the gas conversion outage burner F2 was cycling in and out of service. After multiple iterations of firing and failing to maintain flame, operations went to have a visual on the burner. Upon inspection a hole was found to have been punctured in the flex metallic fuel pipe. The piece of equipment was tagged and removed from service. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | UTS - Capital Projects |  |  |  |  | Christopher Lelak | No comments - CBL 04/14/19 | Christopher Lelak |  | Medium |  | 2.06 Poor coordination |  | 4.10 Frustration |  |  |  | 8.2.2 Improper conduct that is not condoned: Unintentional | [8 empty] | The believed cause of the incident is an impact force was received to the fuel pipe. It is unclear if this was an accident or intentional. | 15. Using Equipment Improperly | 9. Abnormal Operation |  | Without determining if the damage was intentional or not, i believe the corrective action is adequate. No additional comments. MLH 4/10/19 | [66 empty] | A puncture hole is currently in the flex hose fuel pipe from the block and bleed skid to the burner. | 7600 | Unknown | Fixed Equipment | [20 empty] | none
8759 | Muskogee Power Plant | 2019-03-11 09:00 | A puncture hole was found in the flex metallic fuel hose on the boiler burner F2. There was no witness to the hole being placed in the hose. | Level 2 |  | FALSE | Property Damage |  |  |  |  | OG&E Corp Services |  | 2019-05-10 10:41 | 2019-03-13 16:02 | 2019-03-13 16:02 | 2019-04-02 10:02 | 2019-03-25 14:00 | 2019-03-13 15:55 | 2019-04-14 05:30 |  | 2019-04-10 10:07 | Muskogee PP Unit 5 Boiler Burner F2 |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE |  |  | During the start up and testing of Unit 5 following the gas conversion outage burner F2 was cycling in and out of service. After multiple iterations of firing and failing to maintain flame, operations went to have a visual on the burner. Upon inspection a hole was found to have been punctured in the flex metallic fuel pipe. The piece of equipment was tagged and removed from service. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | UTS - Capital Projects |  |  |  |  | Christopher Lelak | No comments - CBL 04/14/19 | Christopher Lelak |  | Medium |  | 2.04 Intelligence level |  | 4.10 Frustration |  |  |  | 8.2.1 Improper conduct that is not condoned: Intentional | [8 empty] | The believed cause of the incident is an impact force was received to the fuel pipe. It is unclear if this was an accident or intentional. | 15. Using Equipment Improperly | 9. Abnormal Operation |  | Without determining if the damage was intentional or not, i believe the corrective action is adequate. No additional comments. MLH 4/10/19 | [66 empty] | A puncture hole is currently in the flex hose fuel pipe from the block and bleed skid to the burner. | 7600 | Unknown | Fixed Equipment | [20 empty] | none
8759 | Muskogee Power Plant | 2019-03-11 09:00 | A puncture hole was found in the flex metallic fuel hose on the boiler burner F2. There was no witness to the hole being placed in the hose. | Level 2 |  | FALSE | Property Damage |  |  |  |  | OG&E Corp Services |  | 2019-05-10 10:41 | 2019-03-13 16:02 | 2019-03-13 16:02 | 2019-04-02 10:02 | 2019-03-25 14:00 | 2019-03-13 15:55 | 2019-04-14 05:30 |  | 2019-04-10 10:07 | Muskogee PP Unit 5 Boiler Burner F2 |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE |  |  | During the start up and testing of Unit 5 following the gas conversion outage burner F2 was cycling in and out of service. After multiple iterations of firing and failing to maintain flame, operations went to have a visual on the burner. Upon inspection a hole was found to have been punctured in the flex metallic fuel pipe. The piece of equipment was tagged and removed from service. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | UTS - Capital Projects |  |  |  |  | Christopher Lelak | No comments - CBL 04/14/19 | Christopher Lelak |  | Medium |  | 2.04 Intelligence level |  | 4.10 Frustration |  |  |  | 8.2.2 Improper conduct that is not condoned: Unintentional | [8 empty] | The believed cause of the incident is an impact force was received to the fuel pipe. It is unclear if this was an accident or intentional. | 15. Using Equipment Improperly | 9. Abnormal Operation |  | Without determining if the damage was intentional or not, i believe the corrective action is adequate. No additional comments. MLH 4/10/19 | [66 empty] | A puncture hole is currently in the flex hose fuel pipe from the block and bleed skid to the burner. | 7600 | Unknown | Fixed Equipment | [20 empty] | none
8761 | Muskogee Power Plant | 2019-03-13 14:00 | Witnessed insulators transporting sheet metal on small cart. Wind gust picked 3 pieces up and sent them flying down the road approximately 50-60 yards. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Samuel Spencer | 2019-08-06 11:06 | 2019-03-13 16:46 | 2019-03-13 16:46 | 2019-07-11 09:29 | 2019-03-27 14:00 | 2019-03-13 16:28 | 2019-07-22 13:02 |  | 2019-07-14 03:20 | Road going under 6 & 7 belts. |  |  | Jesse Murray | Please attach Brock Investigation. - Jesse Approved. Jesse 8-6-19 | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | TRUE |  | FALSE | FALSE | Samuel Spencer |  | Members were moving insulation material with a four wheeled cart. The wind was blowing 25-30 MPH with gust up to 40 MPH. A gust picked up two pieces of insulation material and blew it about 50 yards. Investigation findings found that the load wasn't tied down. The contractors procedures do not require their members to tie down loads on a push cart. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Maintenance |  | Samuel Spencer | Robert Wright |  | Andy Hedge | Sent back for editing 7/11/19 - Andy Hedge Reviewed and approved 7/22/19 - Andy Hedge | Andy Hedge |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [5 empty] | 11.08 Improper storage of materials | [5 empty] | Wind gust picked up insulation material and blew about 50 yards | 08. Improper Loading | 2. Struck By (Hit By Moving Object) |  | Reviewed Bob Wright |  |  |  | Property Damage |  | Samuel Spencer | Sheet metal insulation cover |  |  |  |  | 2. Struck By (Hit By Moving Object) | Samuel Spencer | Brock | James Matthews |  | 3rd Party Property/Equipment |  | Samuel Spencer |  |  |  |  | FALSE
8761 | Muskogee Power Plant | 2019-03-13 14:00 | Witnessed insulators transporting sheet metal on small cart. Wind gust picked 3 pieces up and sent them flying down the road approximately 50-60 yards. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Samuel Spencer | 2019-08-06 11:06 | 2019-03-13 16:46 | 2019-03-13 16:46 | 2019-07-11 09:29 | 2019-03-27 14:00 | 2019-03-13 16:28 | 2019-07-22 13:02 |  | 2019-07-14 03:20 | Road going under 6 & 7 belts. |  |  | Jesse Murray | Please attach Brock Investigation. - Jesse Approved. Jesse 8-6-19 | Power Supply |  | Level 2 | Property Damage |  | TRUE | FALSE | TRUE |  | FALSE | FALSE | Samuel Spencer |  | Members were moving insulation material with a four wheeled cart. The wind was blowing 25-30 MPH with gust up to 40 MPH. A gust picked up two pieces of insulation material and blew it about 50 yards. Investigation findings found that the load wasn't tied down. The contractors procedures do not require their members to tie down loads on a push cart. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Maintenance |  | Samuel Spencer | Robert Wright |  | Andy Hedge | Sent back for editing 7/11/19 - Andy Hedge Reviewed and approved 7/22/19 - Andy Hedge | Andy Hedge |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [5 empty] | 11.08 Improper storage of materials | [5 empty] | Wind gust picked up insulation material and blew about 50 yards | 08. Improper Loading | 2. Struck By (Hit By Moving Object) |  | Reviewed Bob Wright |  |  |  | Property Damage |  | Samuel Spencer | Sheet metal insulation cover |  |  |  |  | 2. Struck By (Hit By Moving Object) | Samuel Spencer | Brock | James Matthews |  | 3rd Party Property/Equipment |  | Samuel Spencer |  |  |  |  | FALSE
8762 | Muskogee Power Plant | 2019-03-11 11:00 | A contracting member was dismantling scaffolding that was very tight and in an awkward position. When he was applying force to remove the piece he felt a pull in his lower back. The pull in his back was accompanied by a feeling of pain. | Level 1 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services |  | 2019-04-10 10:12 | 2019-03-13 16:47 | 2019-03-13 16:47 | 2019-04-02 10:35 | 2019-03-25 11:00 | 2019-03-13 16:07 | 2019-04-06 15:54 |  |  | Muskogee PP Main Fuel Piperack |  |  | Marcus Huddleston | First aid only? Please contact me about any possible corrective actions that were taken (i.e. safety stand down or safety meeting). No additional comments. MLH 4/10/19 | UTS |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | A contracting member from Brock was working on tearing down a scaffold. The member was working in an awkward position. When he bent down to loosen a beam clamp he felt a pull in his back. The member reported to his supervisor. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | UTS - Capital Projects |  |  |  |  | Christopher Lelak | None - CBL 04/06/19 | Christopher Lelak |  | Low | 1.03 Limited ability to sustain body positions |  | 3.09 Constrained movement | [9 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | A contracting member was working in an awkward position. The member pulled a muscle in his back upon bending over to loosen a piece of scaffolding. | 11. Improper Position for Task | 11. Overstress, Overpressure, Overexertion, Ergonomic | [5 empty] | Injury / Illness |  |  |  | Lower back strain | FALSE |  |  | 11. Overstress, Overpressure, Overexertion, Ergonomic |  | TEIC - Brock | Enrique Dones | Sprain/Strain |  | Back |  | Lower | FALSE | [69 empty] | none
8762 | Muskogee Power Plant | 2019-03-11 11:00 | A contracting member was dismantling scaffolding that was very tight and in an awkward position. When he was applying force to remove the piece he felt a pull in his lower back. The pull in his back was accompanied by a feeling of pain. | Level 1 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services |  | 2019-04-10 10:12 | 2019-03-13 16:47 | 2019-03-13 16:47 | 2019-04-02 10:35 | 2019-03-25 11:00 | 2019-03-13 16:07 | 2019-04-06 15:54 |  |  | Muskogee PP Main Fuel Piperack |  |  | Marcus Huddleston | First aid only? Please contact me about any possible corrective actions that were taken (i.e. safety stand down or safety meeting). No additional comments. MLH 4/10/19 | UTS |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | A contracting member from Brock was working on tearing down a scaffold. The member was working in an awkward position. When he bent down to loosen a beam clamp he felt a pull in his back. The member reported to his supervisor. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | UTS - Capital Projects |  |  |  |  | Christopher Lelak | None - CBL 04/06/19 | Christopher Lelak |  | Low | 1.03 Limited ability to sustain body positions |  | 3.09 Constrained movement | [9 empty] | 13.02 Inadequate human factors/ergonomics considerations |  |  |  | A contracting member was working in an awkward position. The member pulled a muscle in his back upon bending over to loosen a piece of scaffolding. | 11. Improper Position for Task | 11. Overstress, Overpressure, Overexertion, Ergonomic | [5 empty] | Injury / Illness |  |  |  | Lower back strain | FALSE |  |  | 11. Overstress, Overpressure, Overexertion, Ergonomic |  | TEIC - Brock | Enrique Dones | Sprain/Strain |  | Back |  | Lower | FALSE | [69 empty] | none
8762 | Muskogee Power Plant | 2019-03-11 11:00 | A contracting member was dismantling scaffolding that was very tight and in an awkward position. When he was applying force to remove the piece he felt a pull in his lower back. The pull in his back was accompanied by a feeling of pain. | Level 1 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services |  | 2019-04-10 10:12 | 2019-03-13 16:47 | 2019-03-13 16:47 | 2019-04-02 10:35 | 2019-03-25 11:00 | 2019-03-13 16:07 | 2019-04-06 15:54 |  |  | Muskogee PP Main Fuel Piperack |  |  | Marcus Huddleston | First aid only? Please contact me about any possible corrective actions that were taken (i.e. safety stand down or safety meeting). No additional comments. MLH 4/10/19 | UTS |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | A contracting member from Brock was working on tearing down a scaffold. The member was working in an awkward position. When he bent down to loosen a beam clamp he felt a pull in his back. The member reported to his supervisor. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | UTS - Capital Projects |  |  |  |  | Christopher Lelak | None - CBL 04/06/19 | Christopher Lelak |  | Low | 1.02 Restricted range of body movement |  | 3.09 Constrained movement | [9 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | A contracting member was working in an awkward position. The member pulled a muscle in his back upon bending over to loosen a piece of scaffolding. | 11. Improper Position for Task | 11. Overstress, Overpressure, Overexertion, Ergonomic | [5 empty] | Injury / Illness |  |  |  | Lower back strain | FALSE |  |  | 11. Overstress, Overpressure, Overexertion, Ergonomic |  | TEIC - Brock | Enrique Dones | Sprain/Strain |  | Back |  | Lower | FALSE | [69 empty] | none
8762 | Muskogee Power Plant | 2019-03-11 11:00 | A contracting member was dismantling scaffolding that was very tight and in an awkward position. When he was applying force to remove the piece he felt a pull in his lower back. The pull in his back was accompanied by a feeling of pain. | Level 1 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services |  | 2019-04-10 10:12 | 2019-03-13 16:47 | 2019-03-13 16:47 | 2019-04-02 10:35 | 2019-03-25 11:00 | 2019-03-13 16:07 | 2019-04-06 15:54 |  |  | Muskogee PP Main Fuel Piperack |  |  | Marcus Huddleston | First aid only? Please contact me about any possible corrective actions that were taken (i.e. safety stand down or safety meeting). No additional comments. MLH 4/10/19 | UTS |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | A contracting member from Brock was working on tearing down a scaffold. The member was working in an awkward position. When he bent down to loosen a beam clamp he felt a pull in his back. The member reported to his supervisor. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | UTS - Capital Projects |  |  |  |  | Christopher Lelak | None - CBL 04/06/19 | Christopher Lelak |  | Low | 1.02 Restricted range of body movement |  | 3.09 Constrained movement | [9 empty] | 13.02 Inadequate human factors/ergonomics considerations |  |  |  | A contracting member was working in an awkward position. The member pulled a muscle in his back upon bending over to loosen a piece of scaffolding. | 11. Improper Position for Task | 11. Overstress, Overpressure, Overexertion, Ergonomic | [5 empty] | Injury / Illness |  |  |  | Lower back strain | FALSE |  |  | 11. Overstress, Overpressure, Overexertion, Ergonomic |  | TEIC - Brock | Enrique Dones | Sprain/Strain |  | Back |  | Lower | FALSE | [69 empty] | none
8763 | Enid Service Center | 2019-03-13 22:30 | Member fell during switching operations. In the process of opening switch 133 muddy boots and the wooden switch handle breaking caused member's knee to come in contact with platform. Member has bruising on knee no medical treatment needed. | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Dustin Kingcade | 2019-03-15 08:34 | 2019-03-14 12:06 | 2019-03-14 12:09 | 2019-03-14 13:11 | 2019-03-27 22:30 | 2019-03-13 23:00 |  |  |  | Fountain Road Tap |  |  | Cody Magby | Good job reporting this. FRO at this time. | T&D Ops |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | [5 empty] | FALSE | Enid Service Center | FALSE |  | FALSE | PD Operations Services |  | Dustin Kingcade | Dustin Kingcade |  |  |  | James Hutchison |  | Low | [45 empty] | FALSE |  |  | 2010-05-24 | 1983-11-03 |  | 2019-03-13 07:00 | 0 | 0 |  | FALSE | Male | Switch handle broke, muddy boots caused Member to loose balance and then slip while trying to recover. |  | FALSE | Mathew Weingartner |  | First Aid | Mathew Weingartner |  |  |  |  | Abrasion |  | FALSE |  |  | Knee |  | Front | FALSE | Dustin Kingcade | FALSE |  | 3/13/2019 7:00:00 AM | 5 | FALSE |  |  | Switching platform of a tap switch. | Preparing to preform switching
8764 | Seminole PP; EGX Gath/Trans | 2019-03-14 15:30 | Member had a hearing shift. | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Supply | Paul Schoelen | 2019-04-09 16:58 | 2019-03-14 16:07 | 2019-03-14 16:07 | 2019-03-27 08:22 | 2019-03-28 15:30 | 2019-03-14 15:55 | 2019-03-27 10:11 |  |  | SMPP |  |  | Chrysty Dorsey | Approved | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Paul Schoelen |  | Hearing Loss. Member has current ear fit validation. Member stated that he plays in a band and does not use hearing protection when playing. |  |  | FALSE | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | Operations |  | Paul Schoelen | Paul Schoelen |  | Paul Schoelen | Review Complete | Paul Schoelen |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Hearing shift | 28. Noise Exposure | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [26 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2003-08-19 | 1972-07-29 |  | 2019-03-14 06:00 | 0 | 0 |  | FALSE | Male | Hearing loss |  |  | Chance Wade |  | Recordable | Chance Wade |  |  |  |  | Hearing Loss |  | TRUE |  | Foreman Plant Operations | Ear | Hearing Loss |  | FALSE | Paul Schoelen | FALSE |  | 3/14/2019 6:00:00 AM |  | FALSE |  |  | Noise | [25 empty] | N/A
8765 | Muskogee Power Plant | 2019-03-12 10:30 | Contractor was running street sweeper to remove sand from parking lot area and plant roads. Street sweeper brush contacted rail damaging the flashing. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Joel Leavell | 2019-04-10 14:33 | 2019-03-14 16:38 | 2019-03-14 16:38 | 2019-03-27 14:07 | 2019-03-26 10:30 | 2019-03-14 16:25 | 2019-03-27 15:05 |  |  | Muskogee PP East Side of Unit 6. On Rail Road track entering crane well on Muskogee 6. |  |  | Robert Wright | Approved Bob Wright | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE |  |  | As part of the ash pond removal project we have been running a street sweeper to mitigate dust from the main travel route of the ash removal trucks. In this instance when the sweeper driver crossed the rail he noticed that he had pulled up a piece of flashing. Recognizing the hazard, he stopped work and contacted plant personnel to report the incident and mark the hazard until it could be eliminated. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | Other |  | Joel Leavell | Joel Leavell |  | Carol Rollins | Reviewed and approved | Carol Rollins |  | Low | [14 empty] | 15.03 Inadequate inspection and/or monitoring |  | Street sweeper brush caught edge of railroad flashing that had degraded over time pulling up a section of the flashing. | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure | [68 empty] | The flashing was pulled up by the street sweeper brush | 10 | Liles Land service | Industrial/Heavy Equipment | [20 empty] | N/A
8767 | Seminole PP; EGX Gath/Trans | 2019-03-15 06:30 | Started 1A CCW pump. Closed coil failed to open. This resulted in coil burning up. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Wayland Todd | 2019-06-11 08:51 | 2019-03-15 10:15 | 2019-03-15 10:15 | 2019-05-12 15:01 | 2019-03-29 06:30 | 2019-03-15 10:02 | 2019-05-16 12:18 |  | 2019-05-13 16:03 | Seminole Unit #1 4160 volt switch gear breaker 505. |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Wayland Todd |  | 0630 AO Member went to 1A CCW pump to check for starting. Pump was started from control room. Every thing looked good at CCW pump. No alarms or indication of problems in control room. 0642 SSG member reported smoke in switchgear. Electricians and operators reported to switchgear and started to open doors and start fans to clear smoke. Found smoke coming from 1A CCW Pump breaker 505. Notified control room to shut off 1A CCW pump. Electricians racked out breaker and discovered the closed coil was burnt up. 0935 placed LOTO on 1A 4160v switchgear to clean and repair. The investigation discovered that when the breaker closed, the x relay in Breaker 505 (Equipment No. 10849020) faulted not opening the circuit to the 125V DC closed coil. This caused the 50 lb. copper wound closed coil to burn up. We believe the x relay faulted due to age. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | Operations |  | Kelly Casey | Wayland Todd |  | Paul Schoelen | Review Complete | Paul Schoelen |  | Medium | [14 empty] | 15.02 Improper extension of service life |  | Equipment malfunction. | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure |  | Returning investigation. Please see workflow comments for reason for returning. Updates added. Review complete. | [66 empty] | Burnt coil | 1000 |  | Fire | [20 empty] | none
8768 | Muskogee Power Plant | 2019-03-15 12:00 | Muskogee Plant, Aerotek member working on 6B ID Fan using wire wheel on grinder. Wire went through glove into knuckle. First aid given. | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Supply | Gary Ridley | 2019-03-27 13:46 | 2019-03-16 08:31 | 2019-03-16 08:31 | 2019-03-27 13:43 | 2019-03-29 12:00 | 2019-03-16 08:15 |  |  |  | 6B ID Fan |  |  | Robert Wright | Discussed on call investigation complete | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | [5 empty] | FALSE | Muskogee Power Plant | FALSE |  | FALSE | Maintenance |  | Jason Moses | Gary Ridley |  |  |  | Andy Hedge |  | Low | [45 empty] | FALSE | [5 empty] | 2019-03-15 07:00 | 0 | 0 | Member pulled wire out and put band aid on it. | FALSE | Male | While using the grinder with a wire wheel, one of the wire came out and struck member in hand. |  | TRUE | Jason Lewis |  | First Aid | Jason Lewis |  |  |  |  | Puncture |  | FALSE |  |  | Hand |  | Left |  | Gary Ridley |  |  | 3/15/2019 7:00:00 AM | 3 years | FALSE |  |  | Wire came out of wire wheel while member was using it and stuck in his hand. | Getting ready to clean fan parts with grinder and wire wheel.
8769 | Enid Service Center | 2019-03-06 11:00 | Contractor was stacking logs and hurt himself. He was taken to a clinic and was diagnosed with a pulled muscle. No prescription was given and he returned to work with no restrictions. This is not a reportable incident it is just for record keeping. | Level 1 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services | Christopher Martin | 2019-03-20 17:36 | 2019-03-18 14:14 | 2019-03-18 14:14 | 2019-03-20 16:00 | 2019-03-20 11:00 | 2019-03-15 14:49 | 2019-03-20 16:13 |  |  | 2731 Midway St, Enid Oklahoma |  |  | Jerrie Looney | Approved. J. :Looney, 3.20.19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Christopher Martin |  | Jerriod Reuscher said that he was stacking logs and firewood on 03-06-19 midmorning. And he said the next day he was hurting, he did not report it to his Foreman he reported to his General Foreman 5:59PM 03-08-19. Jerriod requested medical treatment and was taken to the clinic by General ForemanAnthony Brown where he was drug screened, was diagnosed with a pulled muscle, there were no prescription given, was released to return to work without any restrictions. |  |  |  | Enid Service Center | FALSE |  | TRUE | PD - Resource Planning & Coord |  | Grant Ehlen | Christopher Martin |  |  | Example of vendor reporting all incidents. As this was not recordable, they could have kept it to themselves. I asked the forester to report for record keeping because it may help with a trend and to show the vendor has been forthright in reporting and preventing injuries, which is very much appreciated. No further action anticipated. cassada |  |  | Low | [6 empty] | 7.06 Improper attempt to save time or effort | [9 empty] | Jerriod Reuscher said that he was stacking logs and firewood on 03-06-19 midmorning. And he said the next day he was hurting, he did not report it to his Foreman he reported to his General Foreman 5:59PM 03-08-19. Jerriod requested medical treatment and was taken to the clinic by General ForemanAnthony Brown where he was drug screened, was diagnosed with a pulled muscle, there were no prescription given, was released to return to work without any restrictions. | 10. Improper Lifting | 11. Overstress, Overpressure, Overexertion, Ergonomic | [5 empty] | Injury / Illness |  | Christopher Martin | [5 empty] | 3. Fall from Elevation to Lower Level | Grant Ehlen | Wright Tree Service | Wright Tree Service tree trimmer |  |  |  | Christopher Martin | [71 empty] | none
8770 | Metro Service Center | 2019-03-19 09:00 | While setting a 300 kva transformer lifting chain rolled off lifting eye. dropping transformer 3-4 feet | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Delivery | John Legg | 2019-05-10 10:52 | 2019-03-19 09:29 | 2019-03-19 09:29 | 2019-05-01 09:17 | 2019-04-02 09:00 | 2019-03-19 09:24 | 2019-05-01 14:24 |  | 2019-05-01 14:16 | NW 164 and Portland ave. |  |  | William Young | Reviewed and approved. WCY | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | TRUE |  | FALSE | FALSE | John Legg |  | We were unloading a 300 KVA transformer off of a trailer at OnCue at 164th & Portland OGE job #7382041. The lifting strap had slipped from the back lifting hook that is mounted on the transformer. Also the 4x6 board underneath the transformer had broken and got caught on the ground. Both of these things happening at the same time resulted in the transformer falling on its back. There is no oil leaking from the transformer, and it seems like there is only cosmetic damage. We have contacted the project manager Tony Loughmiller and John Legg with OGE. We are returning the transformer to the North yard. In the future we are going to use clevises through the holes on the lifting ears so that this will not happen again. No one was injured. We had a verbal lifting plan in place. Individuals involved are listed below. We will conduct refresher with anyone lifting transformers to make sure everyone knows to utilize the eyes and clevises. |  |  |  | Metro Service Center | FALSE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  | Nicole Rhodes | Reviewed...no further comments. | Nicole Rhodes |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | The lifting strap had slipped from the back lifting hook that is mounted on the transformer. | 03. Failure to Secure | 3. Fall from Elevation to Lower Level |  | No additional comments. MLH 5/1/19 |  |  |  | Property Damage |  | John Legg | Dropped transformer |  |  |  |  | 3. Fall from Elevation to Lower Level | John Legg | Pathfinder | Dakota Greeson |  | Structural |  | John Legg |  |  |  |  | FALSE | [42 empty] | structural damage to outside of transformer no oil escaped. | 3000 | John Legg | Structural | [20 empty] | na
8770 | Metro Service Center | 2019-03-19 09:00 | While setting a 300 kva transformer lifting chain rolled off lifting eye. dropping transformer 3-4 feet | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Delivery | John Legg | 2019-05-10 10:52 | 2019-03-19 09:29 | 2019-03-19 09:29 | 2019-05-01 09:17 | 2019-04-02 09:00 | 2019-03-19 09:24 | 2019-05-01 14:24 |  | 2019-05-01 14:16 | NW 164 and Portland ave. |  |  | William Young | Reviewed and approved. WCY | T&D Ops |  | Level 2 | Property Damage |  | TRUE | FALSE | TRUE |  | FALSE | FALSE | John Legg |  | We were unloading a 300 KVA transformer off of a trailer at OnCue at 164th & Portland OGE job #7382041. The lifting strap had slipped from the back lifting hook that is mounted on the transformer. Also the 4x6 board underneath the transformer had broken and got caught on the ground. Both of these things happening at the same time resulted in the transformer falling on its back. There is no oil leaking from the transformer, and it seems like there is only cosmetic damage. We have contacted the project manager Tony Loughmiller and John Legg with OGE. We are returning the transformer to the North yard. In the future we are going to use clevises through the holes on the lifting ears so that this will not happen again. No one was injured. We had a verbal lifting plan in place. Individuals involved are listed below. We will conduct refresher with anyone lifting transformers to make sure everyone knows to utilize the eyes and clevises. |  |  |  | Metro Service Center | FALSE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  | Nicole Rhodes | Reviewed...no further comments. | Nicole Rhodes |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | The lifting strap had slipped from the back lifting hook that is mounted on the transformer. | 03. Failure to Secure | 3. Fall from Elevation to Lower Level |  | No additional comments. MLH 5/1/19 |  |  |  | Property Damage |  | John Legg | Dropped transformer |  |  |  |  | 3. Fall from Elevation to Lower Level | John Legg | Pathfinder | Dakota Greeson |  | Structural |  | John Legg |  |  |  |  | FALSE | [42 empty] | structural damage to outside of transformer no oil escaped. | 3000 | John Legg | Structural | [20 empty] | na
8771 | West Service Center | 2019-03-19 08:00 | On March 19 Dakota was loading the truck for the work to be performed that day. As he was using the ladder to get off the dock he missed the last step and twisted his ankle. At this time he alerted his field supervisor to the first aid and was taken to McBride clinic. It was determined that it was only a sprained ankle and the member returned to work. | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Joshua Robertson | 2019-03-29 12:46 | 2019-03-19 09:30 | 2019-03-19 09:30 | 2019-03-29 10:40 | 2019-04-02 08:00 | 2019-03-19 09:16 |  |  |  | loading dock West Service Center |  |  | Luke Kennedy | I have personally followed up with the member and he has had no set backs with his ankle. | T&D Ops |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | [5 empty] | FALSE | West Service Center | FALSE |  | FALSE | Construction Services |  | Dakota Neether | Joshua Robertson |  |  |  | Terry Garrett |  | Low |  |  |  |  | 5.01 Lack of experience | [11 empty] | member did not properly utilize steps to exit dock | 11. Improper Position for Task | 4. Fall on Same Level (Slip and Fall, Trip Over) | [26 empty] | FALSE |  |  | 2018-07-30 | 1995-11-12 |  | 2019-03-19 07:00 | 0 | 0 |  | FALSE | Male | member twisted ankle while stepping off dock |  |  | Dakota Neether |  | First Aid | Dakota Neether |  |  |  |  | Sprain/Strain |  | FALSE |  | Lineman Appr | Ankle |  |  |  | Lance Halvorson |  |  | 3/19/2019 7:00:00 AM |  | FALSE |  |  | Concrete floor
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Ryan Musgrove | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.06 Inadequate or improper controls |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.07 Inadequate monitoring of initial operation |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.3 Inadequate reparative examination of units | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.4 Inadequate reparative part substitution | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.3 Inadequate preventative adjustment/assembly | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.2 Inadequate preventative lubrication and servicing | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.02.2 Inadequate reparative scheduling of work | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.03 Inadequate inspection and/or monitoring | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.02 Improper extension of service life | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.04 Inadequate communication between work groups | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8772 | Shawnee Service Center | 2019-03-19 13:30 | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. | Level 3 |  | TRUE | Property Damage |  | Lindle Coleman | reviewed with operations | 2019-04-03 14:07 | Power Delivery | Bradley Kosemund | 2019-06-20 09:55 | 2019-03-19 17:13 | 2019-03-19 17:13 | 2019-05-03 13:22 | 2019-04-02 13:30 | 2019-03-19 17:06 | 2019-06-17 06:26 | 2019-06-18 10:43 | 2019-05-03 13:26 | McElroy substation in Stillwater Oklahoma |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Myers |  | While installing 4/0 protective ground on A phase 138kv 4 inch tubing, one side of 138kv V switch fell along with 4 inch diameter tubing section. The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. This must have broken when the switch was in the full open position since it did open all the way. Immediate & Basic Cause The broken insulator is the immediate and basic source for the loss of one phase of the 138kV “V” type switch and its connected tubing. Factors affecting the integrity of the insulator are: 1. Force applied to the top/bottom when opening (seized in jaws or at pivot point) 2. Physical degradation of the insulator based on environmental exposure. This includes weather, uv rays, sunlight, chemicals, etc. 3. Structural condition of the insulator from repeated stress that reveal as cracks or deformities. 4. Type and age of insulator on rotating pivot. 5. Manufacturer’s defect or second-class quality when compared to peer products. Powerdyne brand switches were installed from the mid 1950’s to the mid 1970’s on the OG&E system. There are 195 Powerdyne 138kV switches currently listed in Cascade out of total population of 295 of the same type from the same era. They have been identified as lower quality units that reached end of life earlier than peer products. Some have been replaced as they failed over time. But, at present, a 50 to 60 year old switch should be considered nearing the end of its useful life depending on the factors listed above. SEE ATTACHMENT FOR FULL REVIEW | Cody Magby | Steven Myers |  | Shawnee Service Center | FALSE |  | TRUE | PD Operations Services |  | Dean Beaudoin | Bradley Kosemund |  | James Hutchison | .I have reviewed this incident report and corrective actions and concur with these findings and assignments to complete the corrective actions. | James Hutchison | Lindle Coleman | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.1 Inadequate preventative assessment of needs | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.01 Inadequate planning of use | 16.10 Inadequate communication of safety and health data, regulations or guidelines | The top of the 138kv insulator on the V switch apparently broke during the opening of the switch. | 06. Using Defective Equipment | 12. Equipment Failure | approved | approve this investigation and corrective actions cm | [90 empty] | xxxx
8773 | Mustang Power Plant | 2019-03-20 09:00 | Hanging pipe support turnbuckle and rod fell from ceiling and land on RO Skid B. No injuries or equipment damage occurred. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | William Sanders | 2019-04-13 14:24 | 2019-03-20 11:57 | 2019-03-20 11:57 | 2019-03-20 12:19 | 2019-04-03 09:00 | 2019-03-20 09:00 | 2019-04-03 08:26 |  | 2019-03-21 21:06 | Mustang Water Treatment Building |  |  | Jesse Murray | I Approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | William Sanders |  | A pipe support hanger rod and turnbuckle were found lodged in the RO B Skid in the Water Treatment building. The rod came from a pipe support just above the skid. The retaining bolt and nut that secures the support rod to the ceiling joist had came loose allowing the rod to fall. While investigation it was noticed the the second support rod for the pipe support also has the nut and bolts loose as well. The area was barricaded until a repair can be made. It is unknown exactly when the support rod fell from the ceiling, it was discovered this morning at the start of the shift. |  |  |  | Mustang Power Plant | FALSE |  | TRUE | Other |  | Jermy Blodgett | William Sanders |  | Tony Shook | I have taken a look at this hazard and agree with the corrective actions. | Tony Shook |  | Medium | [8 empty] | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Bolts were not tightened correctly during construction. It is believed that the movement of the pipe from the process flow was able to shake the nut loose from the bolt. | 16. Failure to Follow Procedure, Policy, Practice | 12. Equipment Failure | [92 empty] | none
8773 | Mustang Power Plant | 2019-03-20 09:00 | Hanging pipe support turnbuckle and rod fell from ceiling and land on RO Skid B. No injuries or equipment damage occurred. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Supply | William Sanders | 2019-04-13 14:24 | 2019-03-20 11:57 | 2019-03-20 11:57 | 2019-03-20 12:19 | 2019-04-03 09:00 | 2019-03-20 09:00 | 2019-04-03 08:26 |  | 2019-03-21 21:06 | Mustang Water Treatment Building |  |  | Jesse Murray | I Approve. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | William Sanders |  | A pipe support hanger rod and turnbuckle were found lodged in the RO B Skid in the Water Treatment building. The rod came from a pipe support just above the skid. The retaining bolt and nut that secures the support rod to the ceiling joist had came loose allowing the rod to fall. While investigation it was noticed the the second support rod for the pipe support also has the nut and bolts loose as well. The area was barricaded until a repair can be made. It is unknown exactly when the support rod fell from the ceiling, it was discovered this morning at the start of the shift. |  |  |  | Mustang Power Plant | FALSE |  | TRUE | Other |  | Jermy Blodgett | William Sanders |  | Tony Shook | I have taken a look at this hazard and agree with the corrective actions. | Tony Shook |  | Medium | [8 empty] | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Bolts were not tightened correctly during construction. It is believed that the movement of the pipe from the process flow was able to shake the nut loose from the bolt. | 16. Failure to Follow Procedure, Policy, Practice | 12. Equipment Failure | [92 empty] | none
8774 | Seminole PP; EGX Gath/Trans | 2019-03-15 12:00 | Member has experienced an OSHSA recordable Standard Threshold Shift of the left ear. | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Supply | Justin Stahl | 2019-04-09 17:00 | 2019-03-20 14:19 | 2019-03-20 14:19 | 2019-03-29 11:24 | 2019-03-29 12:00 | 2019-03-15 12:00 | 2019-04-03 12:57 |  |  | Seminole Power Plant Engineering and Planning |  |  | Chrysty Dorsey | Approved. | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Justin Stahl |  | Member has experienced an OSHSA recordable Standard Threshold Shift of the left ear. |  |  | FALSE | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | Other |  | Bonnie Nevels | Justin Stahl |  | Scott Lee | I approve. | Scott Lee |  | Low | [9 empty] | 10.02 Inadequate consideration of human factors/ergonomics | [6 empty] | Exposure to power plant noise levels as well as farm equipment at home. | 28. Noise Exposure | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [26 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2002-02-28 | 1969-06-24 |  | 2019-03-15 06:30 | 0 | 0 |  | FALSE | Male | Noise exposure. |  | FALSE | Willie Shandy |  | Recordable | Willie Shandy |  |  |  |  | Hearing Loss |  | TRUE |  | System Planner | Ear | Hearing Loss |  | FALSE | Justin Stahl | FALSE |  | 3/15/2019 6:30:00 AM |  | FALSE |  |  | Noise. | [25 empty] | none
8775 | Shawnee Service Center | 2019-03-20 17:00 | While performing tripping tests on transformer bank 2 the relay crew was unable to reset the lock out relay. Relay tech went behind panel board to see if there was a problem on the lock out switch trip latch. He mistakenly got on the lock out relay for transformer bank 1 which is on the same panel. He tripped transformer bank 1 off line including all three circuits. | Level 1 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Bradley Kosemund | 2019-05-08 07:12 | 2019-03-20 17:58 |  | 2019-05-06 16:51 | 2019-05-01 17:00 | 2019-03-20 17:52 | 2019-05-07 07:00 |  |  | McElroy substation, Stillwater Oklahoma |  |  | Cody Magby | I have reviewed the investigation and approve of CAs. cm | T&D Ops |  | Level 1 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Bradley Kosemund |  | Operational Incident Summary On Wednesday; March 20th, 2019 while performing tripping tests on Transformer 2 at McElroy substation a relay technician inadvertently tripped Transformer 1. While conducting tripping test on the differential lockout relay he experienced problems with the relay resetting. The relay technician went behind the panel to determine if there was an issue on the lockout switch trip latch. The relay technician went to manually operate the trip latch, but mistakenly operated the lockout relay for Transformer 1. This resulted in the tripping of FIS 121 causing an outage to the associated 12.5kv circuits 3321, 3323, and 3325. Chain of Events: • Shawnee sub ops crews were on site to perform relay and maintenance testing of equipment during the week of spring breaker for OSU. • Transformer 3 at McElroy substation was removed from service on Monday to allow maintenance and relay crews to perform routine testing of the power equipment and the relays. o The crews experienced several unforeseen problems while this equipment was out of service that extended the scheduled outage time.  The 138kv bus tubing broke while protective grounds were being placed on the high side of the transformer. o The handle for safety switch 1BM3 broke as it was operated during switching. • Switching was re-written to leave the 3329 circuit out of service when transformer 3 was switched back in service to allow repairs to be made to the damaged safety switch. • Transformer 2 was switched out of service after transformer 3 was placed back in service. • A relay technician and a maintenance technician worked on replacing the damaged safety switch on the 3329 circuit. • The relay foreman began testing of the relays associated with transformer 2. o While conducting tripping test on the differential lockout relay the relay foreman experienced problems with the relay. The lockout relay was not operating correctly so the foreman went to the rear of the panel to manually trip the latch switch. • As the relay foreman walked to the rear of the panel he mistakenly went up to the lockout relay for transformer 1 and operated the trip latch. o As a result FIS 121 opened. o The relay foreman contacted the DCC and OSU personnel informing them of the event. He also informed the crew on site making them aware that transformer 1 had tripped open and switching would be conducted to place it back in service. o Once it was determined to be safe and everyone in the clear switching was performed to put transformer 1 back in service. • The relay foreman replaced the defective lockout relay and testing was completed. Incident Facts Ascertained: • At the time of the incident the relay foreman was working in the control house conducting the tripping test of the transformer relays while another relay technician on site worked out in the substation yard replacing the safety switch. o Caution Tags were placed on the front of the panel on the adjacent FIS handles above the differential lockouts. These tags provided a visual marker for the relay foreman indicating these two devices were in service and were not to be operated. • The lockout relay for transformer 1 and 2 were located on the same panel. o There were no labels or markings on the rear of the panel at these devices. o The relay foreman did not place any tags or markings on the rear of the panel as a visual indicator as to what was in service and what was out of service. |  |  |  | Shawnee Service Center | FALSE |  | FALSE | PD Operations Services |  | Marcus Parks | Bradley Kosemund |  | James Hutchison | I have reviewed this incident report and approve the corrective action as well. | James Hutchison |  | Low | [111 empty] | 7861492
8776 | Sooner Power Plant | 2019-03-21 09:00 | #1BLR MAN REPORTED FIRE AT B-APH GUIDE BRG. AT 0900 HRS, FELLOW WORKERS RESPONDED WITH FIRE EXTINGUISHERS AND PUT FIRE OUT BY 0909 HRS. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Allen Moore | 2019-06-27 07:54 | 2019-03-21 11:33 | 2019-03-21 11:33 | 2019-06-18 12:15 | 2019-04-04 09:00 | 2019-03-21 11:24 | 2019-06-21 11:03 |  |  | 1B AIR PREHEATER GUIDE BEARING |  |  | Brady Sowell | Alex, I have a few comments on Incident 8776. Detailed Description and Investigation Findings: At the end of your second paragraph it appears that you cut a sentence off. Is there more information that needs to be there? If so, please add. Also the “Detailed Description of Incident” doesn’t mention the second fire that occurred. We agreed that we would not create another intellex incident as long as we covered the 2nd fire in this intellex incident report. Please add the details and corrective actions for that incident as well. Please remove Kenny Glass’s name from the “Statements and Facts” portion due to HIPAA concerns. I would replace with “Lead Mechanic on Job” or something similar. Immediate and Basic Cause Section: For this section we need to create another entry for the second fire. I believe the cause of the second fire was the amount of time it took to run the LOTO and change the filter allowed the bearing to get hot and reignite the oil saturated insulation. Corrective Actions: In this section, you’ll need to add the Corrective Actions from the second fire. Please discuss with maintenance whether the best action is to install local disconnects or to use simple lotos for the filter changes. Please input a corrective action for whatever choice is made. Also, I believe we need to have a corrective action to communicate with the rest of the fleet what we found on our fire extinguishers. 2 of the extinguishers did not function properly. Please give me an action item to communicate with the other plants the findings from Johnson Controls. Document Attachment: We need to upload some pictures of the Guide Bearing as well as some of the damage observed. | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Alexander Taybah |  | Sooner’s Preventative/Predictive maintenance program calls for oil samples to be taken periodically on certain assets and have them sent out for analysis to check the health of the equipment. 1B APH guide bearing results came back with high Silica. The remedial process is to have Maintenance hook up an external filter skid and run it for a couple of days and then re-sample. The filter skid ran for about a week due to issues encountered with losing suction on the skid. Further investigation, with the help of Sooner’s Maintenance Engineer, revealed that the suction line was gummed up interrupting the flow and eventually cleared. The Maintenance Foreman whose crew had the order reached out to Operations for support to monitor the skid while running until the oil quality has been restored. On March 18th, boiler AO logged minor smoke coming out of the bearing due possible oil on the hot. On March 21st, the same AO called out for help after discovering fire bellowing from 1B APH guide bearing. Many operators responded with fire extinguishers and put the fire out. Once the Operating Authority was notified, unit load was dropped immediately at 20 MW/min to minimize heat on that side of the furnace while keeping the APH running to avoid distortion. The investigation revealed the following contributing factors to the fire: 1) Worn seals allowing ash in and oil out (Requires a major outage to inspect and repair) 2) Overfilling with oil: Misunderstanding of where the oil level should be due to multiple marks (over the years) on the dip stick. It was thought the guide bearing capacity was 22 gals versus design of 16 gal (11 gal for the bearing and 5 for the associated piping). 3) Time it takes to have a LOTO hung, verified, and taken on the circulating oil pump resulting in higher oil temperature without the circulating pump being on while the filters are being changed. 4) Oil leaking from one support stud onto the hot duct and saturating the insulation. 5) Breather: Plugged, its placement, and harsh environment it sits in. 6) Other minor contributing factors: Exhaust fans were added to the boiler enclosure and this resulted in higher ambient temperature The fire took place while the oil filter skid was on and the most plausible scenario was that the oil got very hot with the skid being on due to low level. Another fire broke out on April 12th when Maintenance members were in the process of changing filters on the same guide bearing. Investigation revealed that the oil might’ve gotten hot without the circulating oil pump being on. The filter skid was not hooked up at this time and the unit had the proper oil level. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Operations |  | Neal Alexander | Allen Moore |  | Alexander Taybah | This investigation is not complete until the next major outage when a thorough inspection of the guide bearing will be disassembled and looked into the root cause. For the time being and until then, the corrective actions implemented should prevent such an incident from occurring. I approve. | Alexander Taybah |  | Low | [8 empty] | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  | 12.02.3 Inadequate reparative examination of units |  |  |  |  | Oil leaking from around base of bearing housing and saturated insulation.Excessive heat from cracks in the duct work. | 23. Defective Tools, Equipment or Materials | 9. Abnormal Operation | [68 empty] | INSULATION AND LAGGING | 200 |  | Fire | [20 empty] | none
8776 | Sooner Power Plant | 2019-03-21 09:00 | #1BLR MAN REPORTED FIRE AT B-APH GUIDE BRG. AT 0900 HRS, FELLOW WORKERS RESPONDED WITH FIRE EXTINGUISHERS AND PUT FIRE OUT BY 0909 HRS. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Allen Moore | 2019-06-27 07:54 | 2019-03-21 11:33 | 2019-03-21 11:33 | 2019-06-18 12:15 | 2019-04-04 09:00 | 2019-03-21 11:24 | 2019-06-21 11:03 |  |  | 1B AIR PREHEATER GUIDE BEARING |  |  | Brady Sowell | Alex, I have a few comments on Incident 8776. Detailed Description and Investigation Findings: At the end of your second paragraph it appears that you cut a sentence off. Is there more information that needs to be there? If so, please add. Also the “Detailed Description of Incident” doesn’t mention the second fire that occurred. We agreed that we would not create another intellex incident as long as we covered the 2nd fire in this intellex incident report. Please add the details and corrective actions for that incident as well. Please remove Kenny Glass’s name from the “Statements and Facts” portion due to HIPAA concerns. I would replace with “Lead Mechanic on Job” or something similar. Immediate and Basic Cause Section: For this section we need to create another entry for the second fire. I believe the cause of the second fire was the amount of time it took to run the LOTO and change the filter allowed the bearing to get hot and reignite the oil saturated insulation. Corrective Actions: In this section, you’ll need to add the Corrective Actions from the second fire. Please discuss with maintenance whether the best action is to install local disconnects or to use simple lotos for the filter changes. Please input a corrective action for whatever choice is made. Also, I believe we need to have a corrective action to communicate with the rest of the fleet what we found on our fire extinguishers. 2 of the extinguishers did not function properly. Please give me an action item to communicate with the other plants the findings from Johnson Controls. Document Attachment: We need to upload some pictures of the Guide Bearing as well as some of the damage observed. | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Alexander Taybah |  | Sooner’s Preventative/Predictive maintenance program calls for oil samples to be taken periodically on certain assets and have them sent out for analysis to check the health of the equipment. 1B APH guide bearing results came back with high Silica. The remedial process is to have Maintenance hook up an external filter skid and run it for a couple of days and then re-sample. The filter skid ran for about a week due to issues encountered with losing suction on the skid. Further investigation, with the help of Sooner’s Maintenance Engineer, revealed that the suction line was gummed up interrupting the flow and eventually cleared. The Maintenance Foreman whose crew had the order reached out to Operations for support to monitor the skid while running until the oil quality has been restored. On March 18th, boiler AO logged minor smoke coming out of the bearing due possible oil on the hot. On March 21st, the same AO called out for help after discovering fire bellowing from 1B APH guide bearing. Many operators responded with fire extinguishers and put the fire out. Once the Operating Authority was notified, unit load was dropped immediately at 20 MW/min to minimize heat on that side of the furnace while keeping the APH running to avoid distortion. The investigation revealed the following contributing factors to the fire: 1) Worn seals allowing ash in and oil out (Requires a major outage to inspect and repair) 2) Overfilling with oil: Misunderstanding of where the oil level should be due to multiple marks (over the years) on the dip stick. It was thought the guide bearing capacity was 22 gals versus design of 16 gal (11 gal for the bearing and 5 for the associated piping). 3) Time it takes to have a LOTO hung, verified, and taken on the circulating oil pump resulting in higher oil temperature without the circulating pump being on while the filters are being changed. 4) Oil leaking from one support stud onto the hot duct and saturating the insulation. 5) Breather: Plugged, its placement, and harsh environment it sits in. 6) Other minor contributing factors: Exhaust fans were added to the boiler enclosure and this resulted in higher ambient temperature The fire took place while the oil filter skid was on and the most plausible scenario was that the oil got very hot with the skid being on due to low level. Another fire broke out on April 12th when Maintenance members were in the process of changing filters on the same guide bearing. Investigation revealed that the oil might’ve gotten hot without the circulating oil pump being on. The filter skid was not hooked up at this time and the unit had the proper oil level. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Operations |  | Neal Alexander | Allen Moore |  | Alexander Taybah | This investigation is not complete until the next major outage when a thorough inspection of the guide bearing will be disassembled and looked into the root cause. For the time being and until then, the corrective actions implemented should prevent such an incident from occurring. I approve. | Alexander Taybah |  | Low | [13 empty] | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | The length of time it took to have the LOTO hung and the work to begin contributed to the second fire. | 34. Inadequate Instructions, Procedures | 9. Abnormal Operation | [68 empty] | INSULATION AND LAGGING | 200 |  | Fire | [20 empty] | none
8777 | Seminole PP; EGX Gath/Trans | 2019-03-22 09:00 | Contractor was onsite to evaluate excessive noise from pump. Contractor wanted pump off to remove cooling fan blade to see if that was the source of the noise. Inspector informed contractor that a clearance would have to be issued and no one could work on pump until that point. Another fan contractor went to sight and removed fan guard and fan before issue of LOTO. | Level 3 |  | TRUE | Contractor | Jean Leger | William Young | Investigate incident, identify causal factors and identify corrective actions. | 2019-04-04 15:23 | OG&E Corp Services | Kelly Casey | 2019-07-27 14:19 | 2019-03-22 10:30 | 2019-03-22 10:30 | 2019-06-17 07:07 | 2019-04-05 09:00 | 2019-03-22 09:00 | 2019-07-15 04:52 | 2019-07-16 17:57 | 2019-06-17 07:08 | Seminole Unit 1 B Forced Draft Fan Lube oil pump. |  |  | Jean Leger | Huddleston please ensure this incident is included in the Contractor's performance file both in Supply Chain Supplier Corrective Action Report and ISNet. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | Contractor was onsite to evaluate excessive noise from pump. Contractor wanted pump off to remove cooling fan blade to see if that was the source of the noise. Inspector informed contractor that a clearance would have to be issued and no one could work on pump until that point. Another fan contractor went to sight and removed fan guard and fan before issue of LOTO. | Diana Edwards | Marcus Huddleston |  | Seminole PP; EGX Gath/Trans | FALSE |  | TRUE | UTS - Capital Projects |  | Matthew Cox | Kelly Casey |  | Christopher Lelak | No comments - CBL 07/15/19 |  | William Young | High |  |  |  |  | 5.05 Misunderstood directions |  | 7.06 Improper attempt to save time or effort | [8 empty] | 16.03. Inadequate communication between different organizations | Contractor violated OGE LOTO policy. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed finding and corrective actions. Approved. WCY 7/16/2019 | No additional comments. MLH 6/17/19 |  |  |  | Clearance / LOTO |  | Kelly Casey | [5 empty] | 5. Caught In (Pinch and Nip Points) | Matthew Cox | Howard Marten / Clarage | Rudy Schafranek / Mike Lowe |  |  |  | Kelly Casey | [71 empty] | none
8777 | Seminole PP; EGX Gath/Trans | 2019-03-22 09:00 | Contractor was onsite to evaluate excessive noise from pump. Contractor wanted pump off to remove cooling fan blade to see if that was the source of the noise. Inspector informed contractor that a clearance would have to be issued and no one could work on pump until that point. Another fan contractor went to sight and removed fan guard and fan before issue of LOTO. | Level 3 |  | TRUE | Contractor | Jean Leger | William Young | Investigate incident, identify causal factors and identify corrective actions. | 2019-04-04 15:23 | OG&E Corp Services | Kelly Casey | 2019-07-27 14:19 | 2019-03-22 10:30 | 2019-03-22 10:30 | 2019-06-17 07:07 | 2019-04-05 09:00 | 2019-03-22 09:00 | 2019-07-15 04:52 | 2019-07-16 17:57 | 2019-06-17 07:08 | Seminole Unit 1 B Forced Draft Fan Lube oil pump. |  |  | Jean Leger | Huddleston please ensure this incident is included in the Contractor's performance file both in Supply Chain Supplier Corrective Action Report and ISNet. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | Contractor was onsite to evaluate excessive noise from pump. Contractor wanted pump off to remove cooling fan blade to see if that was the source of the noise. Inspector informed contractor that a clearance would have to be issued and no one could work on pump until that point. Another fan contractor went to sight and removed fan guard and fan before issue of LOTO. | Diana Edwards | Marcus Huddleston |  | Seminole PP; EGX Gath/Trans | FALSE |  | TRUE | UTS - Capital Projects |  | Matthew Cox | Kelly Casey |  | Christopher Lelak | No comments - CBL 07/15/19 |  | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  | 7.06 Improper attempt to save time or effort | [8 empty] | 16.03. Inadequate communication between different organizations | Contractor violated OGE LOTO policy. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed finding and corrective actions. Approved. WCY 7/16/2019 | No additional comments. MLH 6/17/19 |  |  |  | Clearance / LOTO |  | Kelly Casey | [5 empty] | 5. Caught In (Pinch and Nip Points) | Matthew Cox | Howard Marten / Clarage | Rudy Schafranek / Mike Lowe |  |  |  | Kelly Casey | [71 empty] | none
8777 | Seminole PP; EGX Gath/Trans | 2019-03-22 09:00 | Contractor was onsite to evaluate excessive noise from pump. Contractor wanted pump off to remove cooling fan blade to see if that was the source of the noise. Inspector informed contractor that a clearance would have to be issued and no one could work on pump until that point. Another fan contractor went to sight and removed fan guard and fan before issue of LOTO. | Level 3 |  | TRUE | Contractor | Jean Leger | William Young | Investigate incident, identify causal factors and identify corrective actions. | 2019-04-04 15:23 | OG&E Corp Services | Kelly Casey | 2019-07-27 14:19 | 2019-03-22 10:30 | 2019-03-22 10:30 | 2019-06-17 07:07 | 2019-04-05 09:00 | 2019-03-22 09:00 | 2019-07-15 04:52 | 2019-07-16 17:57 | 2019-06-17 07:08 | Seminole Unit 1 B Forced Draft Fan Lube oil pump. |  |  | Jean Leger | Huddleston please ensure this incident is included in the Contractor's performance file both in Supply Chain Supplier Corrective Action Report and ISNet. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | Contractor was onsite to evaluate excessive noise from pump. Contractor wanted pump off to remove cooling fan blade to see if that was the source of the noise. Inspector informed contractor that a clearance would have to be issued and no one could work on pump until that point. Another fan contractor went to sight and removed fan guard and fan before issue of LOTO. | Diana Edwards | Marcus Huddleston |  | Seminole PP; EGX Gath/Trans | FALSE |  | TRUE | UTS - Capital Projects |  | Matthew Cox | Kelly Casey |  | Christopher Lelak | No comments - CBL 07/15/19 |  | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  | 7.06 Improper attempt to save time or effort | [8 empty] | 16.03. Inadequate communication between different organizations | Contractor violated OGE LOTO policy. | 20. Failure to Communicate, Coordinate | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed finding and corrective actions. Approved. WCY 7/16/2019 | No additional comments. MLH 6/17/19 |  |  |  | Clearance / LOTO |  | Kelly Casey | [5 empty] | 5. Caught In (Pinch and Nip Points) | Matthew Cox | Howard Marten / Clarage | Rudy Schafranek / Mike Lowe |  |  |  | Kelly Casey | [71 empty] | none
8778 | Seminole PP; EGX Gath/Trans | 2019-03-20 16:00 | Contractor cut through unidentified insulation when removing 3A FDF inlet housing. Insulation sample came back negative for asbestos. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, conduct causal analysis and establish corrective actions. | 2019-04-04 15:39 | OG&E Corp Services | Paul Schoelen | 2019-05-20 08:26 | 2019-03-22 15:33 | 2019-03-22 15:33 | 2019-05-06 09:42 | 2019-04-03 16:00 | 2019-03-22 15:21 | 2019-05-06 12:37 | 2019-05-10 10:57 | 2019-05-06 09:59 | SM 3A FDF |  |  | Jean Leger | No additional comments. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | Unit 3 during demolition, the contractor had an oxy lance and they were cutting the 3A housing. After cutting the housing they noticed insulation between the layers. The jobsite was barricaded off and the material was pulled for sampling and it was determined not asbestos. | Kelly Casey | William Young |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Paul Schoelen |  | Christopher Lelak | No further comments - CBL 05/06/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications | 10.03 Inadequate standards, specifications and/or design criteria | [6 empty] | Lack of engineering details on the drawings. | 35. Inadequate Information, Data | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Investigation complete. Approved CA's. WCY | No additional comments. MLH 5/6/19 |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Paul Schoelen | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Danny Pogue | Air Tek | Danny Bales |  |  |  | Danny Pogue | [71 empty] | 9580663
8778 | Seminole PP; EGX Gath/Trans | 2019-03-20 16:00 | Contractor cut through unidentified insulation when removing 3A FDF inlet housing. Insulation sample came back negative for asbestos. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, conduct causal analysis and establish corrective actions. | 2019-04-04 15:39 | OG&E Corp Services | Paul Schoelen | 2019-05-20 08:26 | 2019-03-22 15:33 | 2019-03-22 15:33 | 2019-05-06 09:42 | 2019-04-03 16:00 | 2019-03-22 15:21 | 2019-05-06 12:37 | 2019-05-10 10:57 | 2019-05-06 09:59 | SM 3A FDF |  |  | Jean Leger | No additional comments. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | Unit 3 during demolition, the contractor had an oxy lance and they were cutting the 3A housing. After cutting the housing they noticed insulation between the layers. The jobsite was barricaded off and the material was pulled for sampling and it was determined not asbestos. | Marcus Huddleston | William Young |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Paul Schoelen |  | Christopher Lelak | No further comments - CBL 05/06/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications | 10.03 Inadequate standards, specifications and/or design criteria | [6 empty] | Lack of engineering details on the drawings. | 35. Inadequate Information, Data | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Investigation complete. Approved CA's. WCY | No additional comments. MLH 5/6/19 |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Paul Schoelen | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Danny Pogue | Air Tek | Danny Bales |  |  |  | Danny Pogue | [71 empty] | 9580663
8779 | Muskogee Power Plant | 2019-03-22 22:00 | PVC pipe in demin building ruptured over the weekend. Upon walk down of the area Monday morning pieces of plastic were found several yards away. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Zackary Thompson | 2019-06-01 12:45 | 2019-03-25 11:23 | 2019-03-25 11:23 | 2019-05-02 22:06 | 2019-04-05 22:00 | 2019-03-25 11:10 | 2019-05-13 10:49 |  | 2019-05-06 12:16 | Unit 6 Demin building. |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Zackary Thompson |  | On 3/22/19 after the shift meeting, the crew returned the LOTO on 6 Cooling Tower Make- Up WCD 8139434. Shortly after returning the LOTO the crew started working on isolating a Fire Water leak by the FD Fans on 6. The outside operator was making rounds while the rest of the crew worked on the leak isolation. The outside operator notified the Shift Supervisor that the 6 RO/Demin building was flooded. The crew isolated the source of flooding by shutting the isolation valve in 4 Cooling Tower Make Up house that supplies service water to the UF system. The crew disconnected heaters in the building to remove additional hazards in the building. Multiple sections of PVC piping failed on the Orival Pre-Filter for the UF system. The job schedule associated with the 6 Cooling Tower Make-Up LOTO had changed before the execution of job and LOTO return. The Chemist had isolated the service water to UF system to support the job. Sometime before LOTO establishment the job was rescheduled and the service water to the UF was opened. The LOTO was established without the service water to the UF being isolated. When the LOTO was returned there was large pressure transient on the UF system. The UF system has control valves on the effluent of Orival Pre-Filters that feed the water to UF. The control valves opened/cycled in response due to error signal to maintain pressure to the UF system. The first gap is that we need to add the isolation of service water to UF system to all LOTO templates that would isolate water upstream to prevent water hammering. We were relying on communication and we dropped the ball. We also need to explore possible engineering solution to mitigate the control valve swinging by adding logic to PLC. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | Operations |  | Mark Graham | Zackary Thompson |  |  | Reviewed SPC |  |  | Medium | [8 empty] | 9.04 Giving inadequate policy, procedure, practices or guidelines | [6 empty] | 16.04 Inadequate communication between work groups | The water to UF system should have been isolated to prevent pressure surging/swinging | 16. Failure to Follow Procedure, Policy, Practice | 12. Equipment Failure |  | Reviewed Bob Wright | [66 empty] | Multiple sections of PVC piping on the Orival UF Pre-Filter System failed/busted. | 17713 |  | Process Interruption | [20 empty] | 9582611
8780 | Muskogee Power Plant | 2019-03-20 12:00 | Contractor slipped on loose tile on turbine deck. Contract had no injury | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Wileda Logan | 2019-04-09 16:59 | 2019-03-25 12:44 | 2019-03-25 12:44 | 2019-03-30 11:20 | 2019-04-03 12:00 | 2019-03-25 12:37 | 2019-03-30 15:17 |  |  | Muskogee Power Plant turbine deck between units 5 and 6. |  |  | Chrysty Dorsey | Approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Wileda Logan |  | On March 20th, 2019 a contractor from Turbine Generator Consulting was walking on the Muskogee Plant turbine deck between units 5 and 6 and slid approximately 4” on broken/loose floor tile pieces. Areas of floor tiles in this area have deteriorated and migrated out of the damaged areas of the floor creating a slip hazard. The contractor informed area contractor workers (Siemens) of the hazard and reported the hazard to OGE personnel. PSS Engineering was notified on 3-21-2019 of the incident. On 3-26-2019, the safety incident was entered into Intelex. Initially, the responsible PSS Engineer did not have access to Intelex. On 3-27-2019, the area was reviewed to document that the hazard had been temporarily removed. It was originally communicated that plywood had been thought to be laid in the damaged floor incident area. An area on the northeast side of Unit 6 was found with significant floor damage with broken tile pieces. It was assumed to be the incident location as it was in a heavy walkway path where the Unit 6 turbine outage work was occurring. This was communicated to Plant Operations prior to leaving the plant on 3-27-2019 and plans were made to lay plywood down over the area during the night shift. On 3/28/2019, the plant followed up and said that the identified damaged tile areas had been covered with plywood and sent pictures confirming the installation. Safety and Plant Operations walked down the area in the morning and made sure everything was in place. On 3-28-2019, PSS realized that the incorrect location had been communicated to Plant Operations when the original incident picture was compared to the repaired area. It was confirmed that plywood had not been installed at the area where the incident occurred between Units 5 and 6. Plant Operations was contacted and the correct area that required coverage was identified. The plant immediately installed plywood over the incident area and sent confirmation photos when the work was complete. The Muskogee Engineering department and UTS Design Engineering have been working together on an engineering assessment of the turbine deck floor and have plans to submit project proposals to return the floor to an acceptable or like new condition. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Power Supply Services |  | Wileda Logan | Wileda Logan |  | Patrick Coleman | Patrick please comment | Patrick Coleman |  | Low | [11 empty] | 12.01.4 Inadequate preventative cleaning or resurfacing |  |  |  |  | Muskogee Power Plant turbine deck has loose and broken tiles. | 27. Poor Housekeeping, Disorder | 4. Fall on Same Level (Slip and Fall, Trip Over) | [5 empty] | Injury / Illness |  | Wileda Logan | [5 empty] | 4. Fall on Same Level (Slip and Fall, Trip Over) | Wileda Logan | Turbine Generator Consultants | Dan Buckhiester |  |  |  | Wileda Logan | [71 empty] | 9581205
8781 | Durant Service Center | 2019-03-23 20:30 | While backing power dolly out of job site, the left track came off of the mud matts. This resulted in the power dolly laying over on a fence. | Level 3 |  | FALSE | Property Damage |  | Lindle Coleman | team picked in collaboration with operational leadership | 2019-03-26 15:49 | Power Delivery | Lyle Just | 2019-04-10 13:57 | 2019-03-25 15:59 | 2019-03-25 15:59 | 2019-04-05 14:28 | 2019-04-06 20:30 | 2019-03-25 15:52 | 2019-04-08 12:50 | 2019-04-09 11:41 | 2019-04-08 09:55 | 3044 Kande Lane Durant |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Chad Inman |  | While getting power dolly to job sight members retracted tracks in to maneuver between secondary ped, phone ped, and sewer cleanouts and transformers in middle of easements. Pulled to the south side of transformer to replace B/O pad mount transformer, machine got stuck. Crew then proceeded to put outriggers down to lift machine and install matts under tracks to stabilize machine while replacing transformer. By this time it had become dark when work was completed. Crew attempted to take machine out the way we came in and found it was unsafe to do so, because of slick conditions and being afraid of sliding into energized transformer. While exiting the work location, crew laid matts out for machine in a single file end to end arrangement (see pictures). While backing machine off first set of matts, left track of machine came off mat and came in contact with saturated ground and machine turned over onto stockade fence coming to rest on it's left side. Facts Ascertained: Tracks were sucked in while maneuvering through Telephone, Secondary pedestal, and sewer cleanout. After tracks were sucked in, they were left in Maneuvering was not confined where rollover occurred Warning label visible from operator controls states "For optimum safety and stability both tracks should be extended fully unless required for confined maneuvering" see picture Matts were laid out in a single file end to end arrangement (allowing for minimal maneuvering) User manual is on the power dolly trailer and readily accessible. Has 3 work lights on the equipment Machine has 44 service hours since 2016 when it was placed in service at Durant Machine has audible alarm and light to show tracks are retracted. Light is not working and you cannot hear audible alarm when machine is revved up. Foreman was not aware the equipment had any alarms indicating track position Crew stated remote was not working, fleet observation indicates it is. Unit was backed in (approximately 200') using the controls on the machine to the work location Foreman made decision to back in, due to the obstructions and in order for the operator to have more visibility Tailboard was conducted and the controls around bringing the power dolly in were covered verbally but not documented (track position and layout of mats was not included) | Paul Jefferson | Chad Inman |  | Durant Service Center | FALSE |  | FALSE | Construction Services |  | Jeremy Mullens | Lyle Just |  | Chad Inman | Reviewed and approved, thank you. | Chad Inman | Lindle Coleman | High |  |  |  |  | 5.03 Inadequate initial training | 6.05 Inadequate review instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | While getting power dolly to job sight members retracted tracks in to maneuver between secondary ped, phone ped, and sewer cleanouts and transformers in middle of easements. Pulled to the south side of transformer to replace B/O pad mount transformer, machine got stuck. Crew then proceeded to put outriggers down to lift machine and install matts under tracks to stabilize machine while replacing transformer. By this time it had become dark when work was completed. Crew attempted to take machine out the way we came in and found it was unsafe to do so, because of slick conditions and being afraid of sliding into energized transformer. While exiting the work location, crew laid matts out for machine in a single file end to end arrangement (see pictures). While backing machine off first set of matts, left track of machine came off mat and came in contact with saturated ground and machine turned over onto stockade fence coming to rest on it's left side. Facts Ascertained: Tracks were not extended while exiting the location. Maneuvering was not confined where rollover occurred Warning label visible from operator controls states "For optimum safety and stability both tracks should be extended fully unless required for confined maneuvering" see picture. Matts were laid out in a single file end to end arrangement (allowing for minimal maneuvering) 5.03: Training FPR and Derrick SOP does not cover when tracks should be extended/retracted 6.02: Crew feedback was that past leadership instructed them to use mats end to end (long ways) which requires the tracks to be retracted in order to fit on one mat. 6.05: Inadequate review of equipment labels and user manual. 9.04: Previous foreman instructed them to use mats end to end (long ways) which requires the tracks to be retracted in order to fit on one mat. | 15. Using Equipment Improperly | 9. Abnormal Operation | approved | Participated in the investigation team. Reviewed and approved TMH | [66 empty] | damaged fence panels and possibly a damaged power dolly. Waiting on fleet to inspect | 1000 | Jeremy Mullens | Industrial/Heavy Equipment | [20 empty] | 8588587
8781 | Durant Service Center | 2019-03-23 20:30 | While backing power dolly out of job site, the left track came off of the mud matts. This resulted in the power dolly laying over on a fence. | Level 3 |  | FALSE | Property Damage |  | Lindle Coleman | team picked in collaboration with operational leadership | 2019-03-26 15:49 | Power Delivery | Lyle Just | 2019-04-10 13:57 | 2019-03-25 15:59 | 2019-03-25 15:59 | 2019-04-05 14:28 | 2019-04-06 20:30 | 2019-03-25 15:52 | 2019-04-08 12:50 | 2019-04-09 11:41 | 2019-04-08 09:55 | 3044 Kande Lane Durant |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Chad Inman |  | While getting power dolly to job sight members retracted tracks in to maneuver between secondary ped, phone ped, and sewer cleanouts and transformers in middle of easements. Pulled to the south side of transformer to replace B/O pad mount transformer, machine got stuck. Crew then proceeded to put outriggers down to lift machine and install matts under tracks to stabilize machine while replacing transformer. By this time it had become dark when work was completed. Crew attempted to take machine out the way we came in and found it was unsafe to do so, because of slick conditions and being afraid of sliding into energized transformer. While exiting the work location, crew laid matts out for machine in a single file end to end arrangement (see pictures). While backing machine off first set of matts, left track of machine came off mat and came in contact with saturated ground and machine turned over onto stockade fence coming to rest on it's left side. Facts Ascertained: Tracks were sucked in while maneuvering through Telephone, Secondary pedestal, and sewer cleanout. After tracks were sucked in, they were left in Maneuvering was not confined where rollover occurred Warning label visible from operator controls states "For optimum safety and stability both tracks should be extended fully unless required for confined maneuvering" see picture Matts were laid out in a single file end to end arrangement (allowing for minimal maneuvering) User manual is on the power dolly trailer and readily accessible. Has 3 work lights on the equipment Machine has 44 service hours since 2016 when it was placed in service at Durant Machine has audible alarm and light to show tracks are retracted. Light is not working and you cannot hear audible alarm when machine is revved up. Foreman was not aware the equipment had any alarms indicating track position Crew stated remote was not working, fleet observation indicates it is. Unit was backed in (approximately 200') using the controls on the machine to the work location Foreman made decision to back in, due to the obstructions and in order for the operator to have more visibility Tailboard was conducted and the controls around bringing the power dolly in were covered verbally but not documented (track position and layout of mats was not included) | Paul Jefferson | Chad Inman |  | Durant Service Center | FALSE |  | FALSE | Construction Services |  | Jeremy Mullens | Lyle Just |  | Chad Inman | Reviewed and approved, thank you. | Chad Inman | Lindle Coleman | High |  |  |  |  | 5.03 Inadequate initial training | 6.05 Inadequate review instruction |  |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | While getting power dolly to job sight members retracted tracks in to maneuver between secondary ped, phone ped, and sewer cleanouts and transformers in middle of easements. Pulled to the south side of transformer to replace B/O pad mount transformer, machine got stuck. Crew then proceeded to put outriggers down to lift machine and install matts under tracks to stabilize machine while replacing transformer. By this time it had become dark when work was completed. Crew attempted to take machine out the way we came in and found it was unsafe to do so, because of slick conditions and being afraid of sliding into energized transformer. While exiting the work location, crew laid matts out for machine in a single file end to end arrangement (see pictures). While backing machine off first set of matts, left track of machine came off mat and came in contact with saturated ground and machine turned over onto stockade fence coming to rest on it's left side. Facts Ascertained: Tracks were not extended while exiting the location. Maneuvering was not confined where rollover occurred Warning label visible from operator controls states "For optimum safety and stability both tracks should be extended fully unless required for confined maneuvering" see picture. Matts were laid out in a single file end to end arrangement (allowing for minimal maneuvering) 5.03: Training FPR and Derrick SOP does not cover when tracks should be extended/retracted 6.02: Crew feedback was that past leadership instructed them to use mats end to end (long ways) which requires the tracks to be retracted in order to fit on one mat. 6.05: Inadequate review of equipment labels and user manual. 9.04: Previous foreman instructed them to use mats end to end (long ways) which requires the tracks to be retracted in order to fit on one mat. | 15. Using Equipment Improperly | 9. Abnormal Operation | approved | Participated in the investigation team. Reviewed and approved TMH | [66 empty] | damaged fence panels and possibly a damaged power dolly. Waiting on fleet to inspect | 1000 | Jeremy Mullens | Industrial/Heavy Equipment | [20 empty] | 8588587
8781 | Durant Service Center | 2019-03-23 20:30 | While backing power dolly out of job site, the left track came off of the mud matts. This resulted in the power dolly laying over on a fence. | Level 3 |  | FALSE | Property Damage |  | Lindle Coleman | team picked in collaboration with operational leadership | 2019-03-26 15:49 | Power Delivery | Lyle Just | 2019-04-10 13:57 | 2019-03-25 15:59 | 2019-03-25 15:59 | 2019-04-05 14:28 | 2019-04-06 20:30 | 2019-03-25 15:52 | 2019-04-08 12:50 | 2019-04-09 11:41 | 2019-04-08 09:55 | 3044 Kande Lane Durant |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Chad Inman |  | While getting power dolly to job sight members retracted tracks in to maneuver between secondary ped, phone ped, and sewer cleanouts and transformers in middle of easements. Pulled to the south side of transformer to replace B/O pad mount transformer, machine got stuck. Crew then proceeded to put outriggers down to lift machine and install matts under tracks to stabilize machine while replacing transformer. By this time it had become dark when work was completed. Crew attempted to take machine out the way we came in and found it was unsafe to do so, because of slick conditions and being afraid of sliding into energized transformer. While exiting the work location, crew laid matts out for machine in a single file end to end arrangement (see pictures). While backing machine off first set of matts, left track of machine came off mat and came in contact with saturated ground and machine turned over onto stockade fence coming to rest on it's left side. Facts Ascertained: Tracks were sucked in while maneuvering through Telephone, Secondary pedestal, and sewer cleanout. After tracks were sucked in, they were left in Maneuvering was not confined where rollover occurred Warning label visible from operator controls states "For optimum safety and stability both tracks should be extended fully unless required for confined maneuvering" see picture Matts were laid out in a single file end to end arrangement (allowing for minimal maneuvering) User manual is on the power dolly trailer and readily accessible. Has 3 work lights on the equipment Machine has 44 service hours since 2016 when it was placed in service at Durant Machine has audible alarm and light to show tracks are retracted. Light is not working and you cannot hear audible alarm when machine is revved up. Foreman was not aware the equipment had any alarms indicating track position Crew stated remote was not working, fleet observation indicates it is. Unit was backed in (approximately 200') using the controls on the machine to the work location Foreman made decision to back in, due to the obstructions and in order for the operator to have more visibility Tailboard was conducted and the controls around bringing the power dolly in were covered verbally but not documented (track position and layout of mats was not included) | Paul Jefferson | Chad Inman |  | Durant Service Center | FALSE |  | FALSE | Construction Services |  | Jeremy Mullens | Lyle Just |  | Chad Inman | Reviewed and approved, thank you. | Chad Inman | Lindle Coleman | High |  |  |  |  | 5.03 Inadequate initial training | 6.02 Inadequate practice |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | While getting power dolly to job sight members retracted tracks in to maneuver between secondary ped, phone ped, and sewer cleanouts and transformers in middle of easements. Pulled to the south side of transformer to replace B/O pad mount transformer, machine got stuck. Crew then proceeded to put outriggers down to lift machine and install matts under tracks to stabilize machine while replacing transformer. By this time it had become dark when work was completed. Crew attempted to take machine out the way we came in and found it was unsafe to do so, because of slick conditions and being afraid of sliding into energized transformer. While exiting the work location, crew laid matts out for machine in a single file end to end arrangement (see pictures). While backing machine off first set of matts, left track of machine came off mat and came in contact with saturated ground and machine turned over onto stockade fence coming to rest on it's left side. Facts Ascertained: Tracks were not extended while exiting the location. Maneuvering was not confined where rollover occurred Warning label visible from operator controls states "For optimum safety and stability both tracks should be extended fully unless required for confined maneuvering" see picture. Matts were laid out in a single file end to end arrangement (allowing for minimal maneuvering) 5.03: Training FPR and Derrick SOP does not cover when tracks should be extended/retracted 6.02: Crew feedback was that past leadership instructed them to use mats end to end (long ways) which requires the tracks to be retracted in order to fit on one mat. 6.05: Inadequate review of equipment labels and user manual. 9.04: Previous foreman instructed them to use mats end to end (long ways) which requires the tracks to be retracted in order to fit on one mat. | 15. Using Equipment Improperly | 9. Abnormal Operation | approved | Participated in the investigation team. Reviewed and approved TMH | [66 empty] | damaged fence panels and possibly a damaged power dolly. Waiting on fleet to inspect | 1000 | Jeremy Mullens | Industrial/Heavy Equipment | [20 empty] | 8588587
8781 | Durant Service Center | 2019-03-23 20:30 | While backing power dolly out of job site, the left track came off of the mud matts. This resulted in the power dolly laying over on a fence. | Level 3 |  | FALSE | Property Damage |  | Lindle Coleman | team picked in collaboration with operational leadership | 2019-03-26 15:49 | Power Delivery | Lyle Just | 2019-04-10 13:57 | 2019-03-25 15:59 | 2019-03-25 15:59 | 2019-04-05 14:28 | 2019-04-06 20:30 | 2019-03-25 15:52 | 2019-04-08 12:50 | 2019-04-09 11:41 | 2019-04-08 09:55 | 3044 Kande Lane Durant |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Chad Inman |  | While getting power dolly to job sight members retracted tracks in to maneuver between secondary ped, phone ped, and sewer cleanouts and transformers in middle of easements. Pulled to the south side of transformer to replace B/O pad mount transformer, machine got stuck. Crew then proceeded to put outriggers down to lift machine and install matts under tracks to stabilize machine while replacing transformer. By this time it had become dark when work was completed. Crew attempted to take machine out the way we came in and found it was unsafe to do so, because of slick conditions and being afraid of sliding into energized transformer. While exiting the work location, crew laid matts out for machine in a single file end to end arrangement (see pictures). While backing machine off first set of matts, left track of machine came off mat and came in contact with saturated ground and machine turned over onto stockade fence coming to rest on it's left side. Facts Ascertained: Tracks were sucked in while maneuvering through Telephone, Secondary pedestal, and sewer cleanout. After tracks were sucked in, they were left in Maneuvering was not confined where rollover occurred Warning label visible from operator controls states "For optimum safety and stability both tracks should be extended fully unless required for confined maneuvering" see picture Matts were laid out in a single file end to end arrangement (allowing for minimal maneuvering) User manual is on the power dolly trailer and readily accessible. Has 3 work lights on the equipment Machine has 44 service hours since 2016 when it was placed in service at Durant Machine has audible alarm and light to show tracks are retracted. Light is not working and you cannot hear audible alarm when machine is revved up. Foreman was not aware the equipment had any alarms indicating track position Crew stated remote was not working, fleet observation indicates it is. Unit was backed in (approximately 200') using the controls on the machine to the work location Foreman made decision to back in, due to the obstructions and in order for the operator to have more visibility Tailboard was conducted and the controls around bringing the power dolly in were covered verbally but not documented (track position and layout of mats was not included) | Paul Jefferson | Chad Inman |  | Durant Service Center | FALSE |  | FALSE | Construction Services |  | Jeremy Mullens | Lyle Just |  | Chad Inman | Reviewed and approved, thank you. | Chad Inman | Lindle Coleman | High |  |  |  |  | 5.03 Inadequate initial training | 6.02 Inadequate practice |  |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | While getting power dolly to job sight members retracted tracks in to maneuver between secondary ped, phone ped, and sewer cleanouts and transformers in middle of easements. Pulled to the south side of transformer to replace B/O pad mount transformer, machine got stuck. Crew then proceeded to put outriggers down to lift machine and install matts under tracks to stabilize machine while replacing transformer. By this time it had become dark when work was completed. Crew attempted to take machine out the way we came in and found it was unsafe to do so, because of slick conditions and being afraid of sliding into energized transformer. While exiting the work location, crew laid matts out for machine in a single file end to end arrangement (see pictures). While backing machine off first set of matts, left track of machine came off mat and came in contact with saturated ground and machine turned over onto stockade fence coming to rest on it's left side. Facts Ascertained: Tracks were not extended while exiting the location. Maneuvering was not confined where rollover occurred Warning label visible from operator controls states "For optimum safety and stability both tracks should be extended fully unless required for confined maneuvering" see picture. Matts were laid out in a single file end to end arrangement (allowing for minimal maneuvering) 5.03: Training FPR and Derrick SOP does not cover when tracks should be extended/retracted 6.02: Crew feedback was that past leadership instructed them to use mats end to end (long ways) which requires the tracks to be retracted in order to fit on one mat. 6.05: Inadequate review of equipment labels and user manual. 9.04: Previous foreman instructed them to use mats end to end (long ways) which requires the tracks to be retracted in order to fit on one mat. | 15. Using Equipment Improperly | 9. Abnormal Operation | approved | Participated in the investigation team. Reviewed and approved TMH | [66 empty] | damaged fence panels and possibly a damaged power dolly. Waiting on fleet to inspect | 1000 | Jeremy Mullens | Industrial/Heavy Equipment | [20 empty] | 8588587
8781 | Durant Service Center | 2019-03-23 20:30 | While backing power dolly out of job site, the left track came off of the mud matts. This resulted in the power dolly laying over on a fence. | Level 3 |  | FALSE | Property Damage |  | Lindle Coleman | team picked in collaboration with operational leadership | 2019-03-26 15:49 | Power Delivery | Lyle Just | 2019-04-10 13:57 | 2019-03-25 15:59 | 2019-03-25 15:59 | 2019-04-05 14:28 | 2019-04-06 20:30 | 2019-03-25 15:52 | 2019-04-08 12:50 | 2019-04-09 11:41 | 2019-04-08 09:55 | 3044 Kande Lane Durant |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Chad Inman |  | While getting power dolly to job sight members retracted tracks in to maneuver between secondary ped, phone ped, and sewer cleanouts and transformers in middle of easements. Pulled to the south side of transformer to replace B/O pad mount transformer, machine got stuck. Crew then proceeded to put outriggers down to lift machine and install matts under tracks to stabilize machine while replacing transformer. By this time it had become dark when work was completed. Crew attempted to take machine out the way we came in and found it was unsafe to do so, because of slick conditions and being afraid of sliding into energized transformer. While exiting the work location, crew laid matts out for machine in a single file end to end arrangement (see pictures). While backing machine off first set of matts, left track of machine came off mat and came in contact with saturated ground and machine turned over onto stockade fence coming to rest on it's left side. Facts Ascertained: Tracks were sucked in while maneuvering through Telephone, Secondary pedestal, and sewer cleanout. After tracks were sucked in, they were left in Maneuvering was not confined where rollover occurred Warning label visible from operator controls states "For optimum safety and stability both tracks should be extended fully unless required for confined maneuvering" see picture Matts were laid out in a single file end to end arrangement (allowing for minimal maneuvering) User manual is on the power dolly trailer and readily accessible. Has 3 work lights on the equipment Machine has 44 service hours since 2016 when it was placed in service at Durant Machine has audible alarm and light to show tracks are retracted. Light is not working and you cannot hear audible alarm when machine is revved up. Foreman was not aware the equipment had any alarms indicating track position Crew stated remote was not working, fleet observation indicates it is. Unit was backed in (approximately 200') using the controls on the machine to the work location Foreman made decision to back in, due to the obstructions and in order for the operator to have more visibility Tailboard was conducted and the controls around bringing the power dolly in were covered verbally but not documented (track position and layout of mats was not included) | Paul Jefferson | Chad Inman |  | Durant Service Center | FALSE |  | FALSE | Construction Services |  | Jeremy Mullens | Lyle Just |  | Chad Inman | Reviewed and approved, thank you. | Chad Inman | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | While getting power dolly to job sight members retracted tracks in to maneuver between secondary ped, phone ped, and sewer cleanouts and transformers in middle of easements. Pulled to the south side of transformer to replace B/O pad mount transformer, machine got stuck. Crew then proceeded to put outriggers down to lift machine and install matts under tracks to stabilize machine while replacing transformer. By this time it had become dark when work was completed. Crew attempted to take machine out the way we came in and found it was unsafe to do so, because of slick conditions and being afraid of sliding into energized transformer. While exiting the work location, crew laid matts out for machine in a single file end to end arrangement (see pictures). While backing machine off first set of matts, left track of machine came off mat and came in contact with saturated ground and machine turned over onto stockade fence coming to rest on it's left side. Facts Ascertained: Tracks were not extended while exiting the location. Maneuvering was not confined where rollover occurred Warning label visible from operator controls states "For optimum safety and stability both tracks should be extended fully unless required for confined maneuvering" see picture. Matts were laid out in a single file end to end arrangement (allowing for minimal maneuvering) 5.03: Training FPR and Derrick SOP does not cover when tracks should be extended/retracted 6.02: Crew feedback was that past leadership instructed them to use mats end to end (long ways) which requires the tracks to be retracted in order to fit on one mat. 6.05: Inadequate review of equipment labels and user manual. 9.04: Previous foreman instructed them to use mats end to end (long ways) which requires the tracks to be retracted in order to fit on one mat. | 15. Using Equipment Improperly | 9. Abnormal Operation | approved | Participated in the investigation team. Reviewed and approved TMH | [66 empty] | damaged fence panels and possibly a damaged power dolly. Waiting on fleet to inspect | 1000 | Jeremy Mullens | Industrial/Heavy Equipment | [20 empty] | 8588587
8781 | Durant Service Center | 2019-03-23 20:30 | While backing power dolly out of job site, the left track came off of the mud matts. This resulted in the power dolly laying over on a fence. | Level 3 |  | FALSE | Property Damage |  | Lindle Coleman | team picked in collaboration with operational leadership | 2019-03-26 15:49 | Power Delivery | Lyle Just | 2019-04-10 13:57 | 2019-03-25 15:59 | 2019-03-25 15:59 | 2019-04-05 14:28 | 2019-04-06 20:30 | 2019-03-25 15:52 | 2019-04-08 12:50 | 2019-04-09 11:41 | 2019-04-08 09:55 | 3044 Kande Lane Durant |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Chad Inman |  | While getting power dolly to job sight members retracted tracks in to maneuver between secondary ped, phone ped, and sewer cleanouts and transformers in middle of easements. Pulled to the south side of transformer to replace B/O pad mount transformer, machine got stuck. Crew then proceeded to put outriggers down to lift machine and install matts under tracks to stabilize machine while replacing transformer. By this time it had become dark when work was completed. Crew attempted to take machine out the way we came in and found it was unsafe to do so, because of slick conditions and being afraid of sliding into energized transformer. While exiting the work location, crew laid matts out for machine in a single file end to end arrangement (see pictures). While backing machine off first set of matts, left track of machine came off mat and came in contact with saturated ground and machine turned over onto stockade fence coming to rest on it's left side. Facts Ascertained: Tracks were sucked in while maneuvering through Telephone, Secondary pedestal, and sewer cleanout. After tracks were sucked in, they were left in Maneuvering was not confined where rollover occurred Warning label visible from operator controls states "For optimum safety and stability both tracks should be extended fully unless required for confined maneuvering" see picture Matts were laid out in a single file end to end arrangement (allowing for minimal maneuvering) User manual is on the power dolly trailer and readily accessible. Has 3 work lights on the equipment Machine has 44 service hours since 2016 when it was placed in service at Durant Machine has audible alarm and light to show tracks are retracted. Light is not working and you cannot hear audible alarm when machine is revved up. Foreman was not aware the equipment had any alarms indicating track position Crew stated remote was not working, fleet observation indicates it is. Unit was backed in (approximately 200') using the controls on the machine to the work location Foreman made decision to back in, due to the obstructions and in order for the operator to have more visibility Tailboard was conducted and the controls around bringing the power dolly in were covered verbally but not documented (track position and layout of mats was not included) | Paul Jefferson | Chad Inman |  | Durant Service Center | FALSE |  | FALSE | Construction Services |  | Jeremy Mullens | Lyle Just |  | Chad Inman | Reviewed and approved, thank you. | Chad Inman | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction |  |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | While getting power dolly to job sight members retracted tracks in to maneuver between secondary ped, phone ped, and sewer cleanouts and transformers in middle of easements. Pulled to the south side of transformer to replace B/O pad mount transformer, machine got stuck. Crew then proceeded to put outriggers down to lift machine and install matts under tracks to stabilize machine while replacing transformer. By this time it had become dark when work was completed. Crew attempted to take machine out the way we came in and found it was unsafe to do so, because of slick conditions and being afraid of sliding into energized transformer. While exiting the work location, crew laid matts out for machine in a single file end to end arrangement (see pictures). While backing machine off first set of matts, left track of machine came off mat and came in contact with saturated ground and machine turned over onto stockade fence coming to rest on it's left side. Facts Ascertained: Tracks were not extended while exiting the location. Maneuvering was not confined where rollover occurred Warning label visible from operator controls states "For optimum safety and stability both tracks should be extended fully unless required for confined maneuvering" see picture. Matts were laid out in a single file end to end arrangement (allowing for minimal maneuvering) 5.03: Training FPR and Derrick SOP does not cover when tracks should be extended/retracted 6.02: Crew feedback was that past leadership instructed them to use mats end to end (long ways) which requires the tracks to be retracted in order to fit on one mat. 6.05: Inadequate review of equipment labels and user manual. 9.04: Previous foreman instructed them to use mats end to end (long ways) which requires the tracks to be retracted in order to fit on one mat. | 15. Using Equipment Improperly | 9. Abnormal Operation | approved | Participated in the investigation team. Reviewed and approved TMH | [66 empty] | damaged fence panels and possibly a damaged power dolly. Waiting on fleet to inspect | 1000 | Jeremy Mullens | Industrial/Heavy Equipment | [20 empty] | 8588587
8781 | Durant Service Center | 2019-03-23 20:30 | While backing power dolly out of job site, the left track came off of the mud matts. This resulted in the power dolly laying over on a fence. | Level 3 |  | FALSE | Property Damage |  | Lindle Coleman | team picked in collaboration with operational leadership | 2019-03-26 15:49 | Power Delivery | Lyle Just | 2019-04-10 13:57 | 2019-03-25 15:59 | 2019-03-25 15:59 | 2019-04-05 14:28 | 2019-04-06 20:30 | 2019-03-25 15:52 | 2019-04-08 12:50 | 2019-04-09 11:41 | 2019-04-08 09:55 | 3044 Kande Lane Durant |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Chad Inman |  | While getting power dolly to job sight members retracted tracks in to maneuver between secondary ped, phone ped, and sewer cleanouts and transformers in middle of easements. Pulled to the south side of transformer to replace B/O pad mount transformer, machine got stuck. Crew then proceeded to put outriggers down to lift machine and install matts under tracks to stabilize machine while replacing transformer. By this time it had become dark when work was completed. Crew attempted to take machine out the way we came in and found it was unsafe to do so, because of slick conditions and being afraid of sliding into energized transformer. While exiting the work location, crew laid matts out for machine in a single file end to end arrangement (see pictures). While backing machine off first set of matts, left track of machine came off mat and came in contact with saturated ground and machine turned over onto stockade fence coming to rest on it's left side. Facts Ascertained: Tracks were sucked in while maneuvering through Telephone, Secondary pedestal, and sewer cleanout. After tracks were sucked in, they were left in Maneuvering was not confined where rollover occurred Warning label visible from operator controls states "For optimum safety and stability both tracks should be extended fully unless required for confined maneuvering" see picture Matts were laid out in a single file end to end arrangement (allowing for minimal maneuvering) User manual is on the power dolly trailer and readily accessible. Has 3 work lights on the equipment Machine has 44 service hours since 2016 when it was placed in service at Durant Machine has audible alarm and light to show tracks are retracted. Light is not working and you cannot hear audible alarm when machine is revved up. Foreman was not aware the equipment had any alarms indicating track position Crew stated remote was not working, fleet observation indicates it is. Unit was backed in (approximately 200') using the controls on the machine to the work location Foreman made decision to back in, due to the obstructions and in order for the operator to have more visibility Tailboard was conducted and the controls around bringing the power dolly in were covered verbally but not documented (track position and layout of mats was not included) | Paul Jefferson | Chad Inman |  | Durant Service Center | FALSE |  | FALSE | Construction Services |  | Jeremy Mullens | Lyle Just |  | Chad Inman | Reviewed and approved, thank you. | Chad Inman | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.02 Inadequate practice |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | While getting power dolly to job sight members retracted tracks in to maneuver between secondary ped, phone ped, and sewer cleanouts and transformers in middle of easements. Pulled to the south side of transformer to replace B/O pad mount transformer, machine got stuck. Crew then proceeded to put outriggers down to lift machine and install matts under tracks to stabilize machine while replacing transformer. By this time it had become dark when work was completed. Crew attempted to take machine out the way we came in and found it was unsafe to do so, because of slick conditions and being afraid of sliding into energized transformer. While exiting the work location, crew laid matts out for machine in a single file end to end arrangement (see pictures). While backing machine off first set of matts, left track of machine came off mat and came in contact with saturated ground and machine turned over onto stockade fence coming to rest on it's left side. Facts Ascertained: Tracks were not extended while exiting the location. Maneuvering was not confined where rollover occurred Warning label visible from operator controls states "For optimum safety and stability both tracks should be extended fully unless required for confined maneuvering" see picture. Matts were laid out in a single file end to end arrangement (allowing for minimal maneuvering) 5.03: Training FPR and Derrick SOP does not cover when tracks should be extended/retracted 6.02: Crew feedback was that past leadership instructed them to use mats end to end (long ways) which requires the tracks to be retracted in order to fit on one mat. 6.05: Inadequate review of equipment labels and user manual. 9.04: Previous foreman instructed them to use mats end to end (long ways) which requires the tracks to be retracted in order to fit on one mat. | 15. Using Equipment Improperly | 9. Abnormal Operation | approved | Participated in the investigation team. Reviewed and approved TMH | [66 empty] | damaged fence panels and possibly a damaged power dolly. Waiting on fleet to inspect | 1000 | Jeremy Mullens | Industrial/Heavy Equipment | [20 empty] | 8588587
8781 | Durant Service Center | 2019-03-23 20:30 | While backing power dolly out of job site, the left track came off of the mud matts. This resulted in the power dolly laying over on a fence. | Level 3 |  | FALSE | Property Damage |  | Lindle Coleman | team picked in collaboration with operational leadership | 2019-03-26 15:49 | Power Delivery | Lyle Just | 2019-04-10 13:57 | 2019-03-25 15:59 | 2019-03-25 15:59 | 2019-04-05 14:28 | 2019-04-06 20:30 | 2019-03-25 15:52 | 2019-04-08 12:50 | 2019-04-09 11:41 | 2019-04-08 09:55 | 3044 Kande Lane Durant |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Chad Inman |  | While getting power dolly to job sight members retracted tracks in to maneuver between secondary ped, phone ped, and sewer cleanouts and transformers in middle of easements. Pulled to the south side of transformer to replace B/O pad mount transformer, machine got stuck. Crew then proceeded to put outriggers down to lift machine and install matts under tracks to stabilize machine while replacing transformer. By this time it had become dark when work was completed. Crew attempted to take machine out the way we came in and found it was unsafe to do so, because of slick conditions and being afraid of sliding into energized transformer. While exiting the work location, crew laid matts out for machine in a single file end to end arrangement (see pictures). While backing machine off first set of matts, left track of machine came off mat and came in contact with saturated ground and machine turned over onto stockade fence coming to rest on it's left side. Facts Ascertained: Tracks were sucked in while maneuvering through Telephone, Secondary pedestal, and sewer cleanout. After tracks were sucked in, they were left in Maneuvering was not confined where rollover occurred Warning label visible from operator controls states "For optimum safety and stability both tracks should be extended fully unless required for confined maneuvering" see picture Matts were laid out in a single file end to end arrangement (allowing for minimal maneuvering) User manual is on the power dolly trailer and readily accessible. Has 3 work lights on the equipment Machine has 44 service hours since 2016 when it was placed in service at Durant Machine has audible alarm and light to show tracks are retracted. Light is not working and you cannot hear audible alarm when machine is revved up. Foreman was not aware the equipment had any alarms indicating track position Crew stated remote was not working, fleet observation indicates it is. Unit was backed in (approximately 200') using the controls on the machine to the work location Foreman made decision to back in, due to the obstructions and in order for the operator to have more visibility Tailboard was conducted and the controls around bringing the power dolly in were covered verbally but not documented (track position and layout of mats was not included) | Paul Jefferson | Chad Inman |  | Durant Service Center | FALSE |  | FALSE | Construction Services |  | Jeremy Mullens | Lyle Just |  | Chad Inman | Reviewed and approved, thank you. | Chad Inman | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.02 Inadequate practice |  |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | While getting power dolly to job sight members retracted tracks in to maneuver between secondary ped, phone ped, and sewer cleanouts and transformers in middle of easements. Pulled to the south side of transformer to replace B/O pad mount transformer, machine got stuck. Crew then proceeded to put outriggers down to lift machine and install matts under tracks to stabilize machine while replacing transformer. By this time it had become dark when work was completed. Crew attempted to take machine out the way we came in and found it was unsafe to do so, because of slick conditions and being afraid of sliding into energized transformer. While exiting the work location, crew laid matts out for machine in a single file end to end arrangement (see pictures). While backing machine off first set of matts, left track of machine came off mat and came in contact with saturated ground and machine turned over onto stockade fence coming to rest on it's left side. Facts Ascertained: Tracks were not extended while exiting the location. Maneuvering was not confined where rollover occurred Warning label visible from operator controls states "For optimum safety and stability both tracks should be extended fully unless required for confined maneuvering" see picture. Matts were laid out in a single file end to end arrangement (allowing for minimal maneuvering) 5.03: Training FPR and Derrick SOP does not cover when tracks should be extended/retracted 6.02: Crew feedback was that past leadership instructed them to use mats end to end (long ways) which requires the tracks to be retracted in order to fit on one mat. 6.05: Inadequate review of equipment labels and user manual. 9.04: Previous foreman instructed them to use mats end to end (long ways) which requires the tracks to be retracted in order to fit on one mat. | 15. Using Equipment Improperly | 9. Abnormal Operation | approved | Participated in the investigation team. Reviewed and approved TMH | [66 empty] | damaged fence panels and possibly a damaged power dolly. Waiting on fleet to inspect | 1000 | Jeremy Mullens | Industrial/Heavy Equipment | [20 empty] | 8588587
8781 | Durant Service Center | 2019-03-23 20:30 | While backing power dolly out of job site, the left track came off of the mud matts. This resulted in the power dolly laying over on a fence. | Level 3 |  | FALSE | Property Damage |  | Lindle Coleman | team picked in collaboration with operational leadership | 2019-03-26 15:49 | Power Delivery | Lyle Just | 2019-04-10 13:57 | 2019-03-25 15:59 | 2019-03-25 15:59 | 2019-04-05 14:28 | 2019-04-06 20:30 | 2019-03-25 15:52 | 2019-04-08 12:50 | 2019-04-09 11:41 | 2019-04-08 09:55 | 3044 Kande Lane Durant |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Chad Inman |  | While getting power dolly to job sight members retracted tracks in to maneuver between secondary ped, phone ped, and sewer cleanouts and transformers in middle of easements. Pulled to the south side of transformer to replace B/O pad mount transformer, machine got stuck. Crew then proceeded to put outriggers down to lift machine and install matts under tracks to stabilize machine while replacing transformer. By this time it had become dark when work was completed. Crew attempted to take machine out the way we came in and found it was unsafe to do so, because of slick conditions and being afraid of sliding into energized transformer. While exiting the work location, crew laid matts out for machine in a single file end to end arrangement (see pictures). While backing machine off first set of matts, left track of machine came off mat and came in contact with saturated ground and machine turned over onto stockade fence coming to rest on it's left side. Facts Ascertained: Tracks were sucked in while maneuvering through Telephone, Secondary pedestal, and sewer cleanout. After tracks were sucked in, they were left in Maneuvering was not confined where rollover occurred Warning label visible from operator controls states "For optimum safety and stability both tracks should be extended fully unless required for confined maneuvering" see picture Matts were laid out in a single file end to end arrangement (allowing for minimal maneuvering) User manual is on the power dolly trailer and readily accessible. Has 3 work lights on the equipment Machine has 44 service hours since 2016 when it was placed in service at Durant Machine has audible alarm and light to show tracks are retracted. Light is not working and you cannot hear audible alarm when machine is revved up. Foreman was not aware the equipment had any alarms indicating track position Crew stated remote was not working, fleet observation indicates it is. Unit was backed in (approximately 200') using the controls on the machine to the work location Foreman made decision to back in, due to the obstructions and in order for the operator to have more visibility Tailboard was conducted and the controls around bringing the power dolly in were covered verbally but not documented (track position and layout of mats was not included) | Hannah Everett | Chad Inman |  | Durant Service Center | FALSE |  | FALSE | Construction Services |  | Jeremy Mullens | Lyle Just |  | Chad Inman | Reviewed and approved, thank you. | Chad Inman | Lindle Coleman | High |  |  |  |  | 5.03 Inadequate initial training | 6.05 Inadequate review instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | While getting power dolly to job sight members retracted tracks in to maneuver between secondary ped, phone ped, and sewer cleanouts and transformers in middle of easements. Pulled to the south side of transformer to replace B/O pad mount transformer, machine got stuck. Crew then proceeded to put outriggers down to lift machine and install matts under tracks to stabilize machine while replacing transformer. By this time it had become dark when work was completed. Crew attempted to take machine out the way we came in and found it was unsafe to do so, because of slick conditions and being afraid of sliding into energized transformer. While exiting the work location, crew laid matts out for machine in a single file end to end arrangement (see pictures). While backing machine off first set of matts, left track of machine came off mat and came in contact with saturated ground and machine turned over onto stockade fence coming to rest on it's left side. Facts Ascertained: Tracks were not extended while exiting the location. Maneuvering was not confined where rollover occurred Warning label visible from operator controls states "For optimum safety and stability both tracks should be extended fully unless required for confined maneuvering" see picture. Matts were laid out in a single file end to end arrangement (allowing for minimal maneuvering) 5.03: Training FPR and Derrick SOP does not cover when tracks should be extended/retracted 6.02: Crew feedback was that past leadership instructed them to use mats end to end (long ways) which requires the tracks to be retracted in order to fit on one mat. 6.05: Inadequate review of equipment labels and user manual. 9.04: Previous foreman instructed them to use mats end to end (long ways) which requires the tracks to be retracted in order to fit on one mat. | 15. Using Equipment Improperly | 9. Abnormal Operation | approved | Participated in the investigation team. Reviewed and approved TMH | [66 empty] | damaged fence panels and possibly a damaged power dolly. Waiting on fleet to inspect | 1000 | Jeremy Mullens | Industrial/Heavy Equipment | [20 empty] | 8588587
8781 | Durant Service Center | 2019-03-23 20:30 | While backing power dolly out of job site, the left track came off of the mud matts. This resulted in the power dolly laying over on a fence. | Level 3 |  | FALSE | Property Damage |  | Lindle Coleman | team picked in collaboration with operational leadership | 2019-03-26 15:49 | Power Delivery | Lyle Just | 2019-04-10 13:57 | 2019-03-25 15:59 | 2019-03-25 15:59 | 2019-04-05 14:28 | 2019-04-06 20:30 | 2019-03-25 15:52 | 2019-04-08 12:50 | 2019-04-09 11:41 | 2019-04-08 09:55 | 3044 Kande Lane Durant |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Chad Inman |  | While getting power dolly to job sight members retracted tracks in to maneuver between secondary ped, phone ped, and sewer cleanouts and transformers in middle of easements. Pulled to the south side of transformer to replace B/O pad mount transformer, machine got stuck. Crew then proceeded to put outriggers down to lift machine and install matts under tracks to stabilize machine while replacing transformer. By this time it had become dark when work was completed. Crew attempted to take machine out the way we came in and found it was unsafe to do so, because of slick conditions and being afraid of sliding into energized transformer. While exiting the work location, crew laid matts out for machine in a single file end to end arrangement (see pictures). While backing machine off first set of matts, left track of machine came off mat and came in contact with saturated ground and machine turned over onto stockade fence coming to rest on it's left side. Facts Ascertained: Tracks were sucked in while maneuvering through Telephone, Secondary pedestal, and sewer cleanout. After tracks were sucked in, they were left in Maneuvering was not confined where rollover occurred Warning label visible from operator controls states "For optimum safety and stability both tracks should be extended fully unless required for confined maneuvering" see picture Matts were laid out in a single file end to end arrangement (allowing for minimal maneuvering) User manual is on the power dolly trailer and readily accessible. Has 3 work lights on the equipment Machine has 44 service hours since 2016 when it was placed in service at Durant Machine has audible alarm and light to show tracks are retracted. Light is not working and you cannot hear audible alarm when machine is revved up. Foreman was not aware the equipment had any alarms indicating track position Crew stated remote was not working, fleet observation indicates it is. Unit was backed in (approximately 200') using the controls on the machine to the work location Foreman made decision to back in, due to the obstructions and in order for the operator to have more visibility Tailboard was conducted and the controls around bringing the power dolly in were covered verbally but not documented (track position and layout of mats was not included) | Hannah Everett | Chad Inman |  | Durant Service Center | FALSE |  | FALSE | Construction Services |  | Jeremy Mullens | Lyle Just |  | Chad Inman | Reviewed and approved, thank you. | Chad Inman | Lindle Coleman | High |  |  |  |  | 5.03 Inadequate initial training | 6.05 Inadequate review instruction |  |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | While getting power dolly to job sight members retracted tracks in to maneuver between secondary ped, phone ped, and sewer cleanouts and transformers in middle of easements. Pulled to the south side of transformer to replace B/O pad mount transformer, machine got stuck. Crew then proceeded to put outriggers down to lift machine and install matts under tracks to stabilize machine while replacing transformer. By this time it had become dark when work was completed. Crew attempted to take machine out the way we came in and found it was unsafe to do so, because of slick conditions and being afraid of sliding into energized transformer. While exiting the work location, crew laid matts out for machine in a single file end to end arrangement (see pictures). While backing machine off first set of matts, left track of machine came off mat and came in contact with saturated ground and machine turned over onto stockade fence coming to rest on it's left side. Facts Ascertained: Tracks were not extended while exiting the location. Maneuvering was not confined where rollover occurred Warning label visible from operator controls states "For optimum safety and stability both tracks should be extended fully unless required for confined maneuvering" see picture. Matts were laid out in a single file end to end arrangement (allowing for minimal maneuvering) 5.03: Training FPR and Derrick SOP does not cover when tracks should be extended/retracted 6.02: Crew feedback was that past leadership instructed them to use mats end to end (long ways) which requires the tracks to be retracted in order to fit on one mat. 6.05: Inadequate review of equipment labels and user manual. 9.04: Previous foreman instructed them to use mats end to end (long ways) which requires the tracks to be retracted in order to fit on one mat. | 15. Using Equipment Improperly | 9. Abnormal Operation | approved | Participated in the investigation team. Reviewed and approved TMH | [66 empty] | damaged fence panels and possibly a damaged power dolly. Waiting on fleet to inspect | 1000 | Jeremy Mullens | Industrial/Heavy Equipment | [20 empty] | 8588587
8781 | Durant Service Center | 2019-03-23 20:30 | While backing power dolly out of job site, the left track came off of the mud matts. This resulted in the power dolly laying over on a fence. | Level 3 |  | FALSE | Property Damage |  | Lindle Coleman | team picked in collaboration with operational leadership | 2019-03-26 15:49 | Power Delivery | Lyle Just | 2019-04-10 13:57 | 2019-03-25 15:59 | 2019-03-25 15:59 | 2019-04-05 14:28 | 2019-04-06 20:30 | 2019-03-25 15:52 | 2019-04-08 12:50 | 2019-04-09 11:41 | 2019-04-08 09:55 | 3044 Kande Lane Durant |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Chad Inman |  | While getting power dolly to job sight members retracted tracks in to maneuver between secondary ped, phone ped, and sewer cleanouts and transformers in middle of easements. Pulled to the south side of transformer to replace B/O pad mount transformer, machine got stuck. Crew then proceeded to put outriggers down to lift machine and install matts under tracks to stabilize machine while replacing transformer. By this time it had become dark when work was completed. Crew attempted to take machine out the way we came in and found it was unsafe to do so, because of slick conditions and being afraid of sliding into energized transformer. While exiting the work location, crew laid matts out for machine in a single file end to end arrangement (see pictures). While backing machine off first set of matts, left track of machine came off mat and came in contact with saturated ground and machine turned over onto stockade fence coming to rest on it's left side. Facts Ascertained: Tracks were sucked in while maneuvering through Telephone, Secondary pedestal, and sewer cleanout. After tracks were sucked in, they were left in Maneuvering was not confined where rollover occurred Warning label visible from operator controls states "For optimum safety and stability both tracks should be extended fully unless required for confined maneuvering" see picture Matts were laid out in a single file end to end arrangement (allowing for minimal maneuvering) User manual is on the power dolly trailer and readily accessible. Has 3 work lights on the equipment Machine has 44 service hours since 2016 when it was placed in service at Durant Machine has audible alarm and light to show tracks are retracted. Light is not working and you cannot hear audible alarm when machine is revved up. Foreman was not aware the equipment had any alarms indicating track position Crew stated remote was not working, fleet observation indicates it is. Unit was backed in (approximately 200') using the controls on the machine to the work location Foreman made decision to back in, due to the obstructions and in order for the operator to have more visibility Tailboard was conducted and the controls around bringing the power dolly in were covered verbally but not documented (track position and layout of mats was not included) | Hannah Everett | Chad Inman |  | Durant Service Center | FALSE |  | FALSE | Construction Services |  | Jeremy Mullens | Lyle Just |  | Chad Inman | Reviewed and approved, thank you. | Chad Inman | Lindle Coleman | High |  |  |  |  | 5.03 Inadequate initial training | 6.02 Inadequate practice |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | While getting power dolly to job sight members retracted tracks in to maneuver between secondary ped, phone ped, and sewer cleanouts and transformers in middle of easements. Pulled to the south side of transformer to replace B/O pad mount transformer, machine got stuck. Crew then proceeded to put outriggers down to lift machine and install matts under tracks to stabilize machine while replacing transformer. By this time it had become dark when work was completed. Crew attempted to take machine out the way we came in and found it was unsafe to do so, because of slick conditions and being afraid of sliding into energized transformer. While exiting the work location, crew laid matts out for machine in a single file end to end arrangement (see pictures). While backing machine off first set of matts, left track of machine came off mat and came in contact with saturated ground and machine turned over onto stockade fence coming to rest on it's left side. Facts Ascertained: Tracks were not extended while exiting the location. Maneuvering was not confined where rollover occurred Warning label visible from operator controls states "For optimum safety and stability both tracks should be extended fully unless required for confined maneuvering" see picture. Matts were laid out in a single file end to end arrangement (allowing for minimal maneuvering) 5.03: Training FPR and Derrick SOP does not cover when tracks should be extended/retracted 6.02: Crew feedback was that past leadership instructed them to use mats end to end (long ways) which requires the tracks to be retracted in order to fit on one mat. 6.05: Inadequate review of equipment labels and user manual. 9.04: Previous foreman instructed them to use mats end to end (long ways) which requires the tracks to be retracted in order to fit on one mat. | 15. Using Equipment Improperly | 9. Abnormal Operation | approved | Participated in the investigation team. Reviewed and approved TMH | [66 empty] | damaged fence panels and possibly a damaged power dolly. Waiting on fleet to inspect | 1000 | Jeremy Mullens | Industrial/Heavy Equipment | [20 empty] | 8588587
8781 | Durant Service Center | 2019-03-23 20:30 | While backing power dolly out of job site, the left track came off of the mud matts. This resulted in the power dolly laying over on a fence. | Level 3 |  | FALSE | Property Damage |  | Lindle Coleman | team picked in collaboration with operational leadership | 2019-03-26 15:49 | Power Delivery | Lyle Just | 2019-04-10 13:57 | 2019-03-25 15:59 | 2019-03-25 15:59 | 2019-04-05 14:28 | 2019-04-06 20:30 | 2019-03-25 15:52 | 2019-04-08 12:50 | 2019-04-09 11:41 | 2019-04-08 09:55 | 3044 Kande Lane Durant |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Chad Inman |  | While getting power dolly to job sight members retracted tracks in to maneuver between secondary ped, phone ped, and sewer cleanouts and transformers in middle of easements. Pulled to the south side of transformer to replace B/O pad mount transformer, machine got stuck. Crew then proceeded to put outriggers down to lift machine and install matts under tracks to stabilize machine while replacing transformer. By this time it had become dark when work was completed. Crew attempted to take machine out the way we came in and found it was unsafe to do so, because of slick conditions and being afraid of sliding into energized transformer. While exiting the work location, crew laid matts out for machine in a single file end to end arrangement (see pictures). While backing machine off first set of matts, left track of machine came off mat and came in contact with saturated ground and machine turned over onto stockade fence coming to rest on it's left side. Facts Ascertained: Tracks were sucked in while maneuvering through Telephone, Secondary pedestal, and sewer cleanout. After tracks were sucked in, they were left in Maneuvering was not confined where rollover occurred Warning label visible from operator controls states "For optimum safety and stability both tracks should be extended fully unless required for confined maneuvering" see picture Matts were laid out in a single file end to end arrangement (allowing for minimal maneuvering) User manual is on the power dolly trailer and readily accessible. Has 3 work lights on the equipment Machine has 44 service hours since 2016 when it was placed in service at Durant Machine has audible alarm and light to show tracks are retracted. Light is not working and you cannot hear audible alarm when machine is revved up. Foreman was not aware the equipment had any alarms indicating track position Crew stated remote was not working, fleet observation indicates it is. Unit was backed in (approximately 200') using the controls on the machine to the work location Foreman made decision to back in, due to the obstructions and in order for the operator to have more visibility Tailboard was conducted and the controls around bringing the power dolly in were covered verbally but not documented (track position and layout of mats was not included) | Hannah Everett | Chad Inman |  | Durant Service Center | FALSE |  | FALSE | Construction Services |  | Jeremy Mullens | Lyle Just |  | Chad Inman | Reviewed and approved, thank you. | Chad Inman | Lindle Coleman | High |  |  |  |  | 5.03 Inadequate initial training | 6.02 Inadequate practice |  |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | While getting power dolly to job sight members retracted tracks in to maneuver between secondary ped, phone ped, and sewer cleanouts and transformers in middle of easements. Pulled to the south side of transformer to replace B/O pad mount transformer, machine got stuck. Crew then proceeded to put outriggers down to lift machine and install matts under tracks to stabilize machine while replacing transformer. By this time it had become dark when work was completed. Crew attempted to take machine out the way we came in and found it was unsafe to do so, because of slick conditions and being afraid of sliding into energized transformer. While exiting the work location, crew laid matts out for machine in a single file end to end arrangement (see pictures). While backing machine off first set of matts, left track of machine came off mat and came in contact with saturated ground and machine turned over onto stockade fence coming to rest on it's left side. Facts Ascertained: Tracks were not extended while exiting the location. Maneuvering was not confined where rollover occurred Warning label visible from operator controls states "For optimum safety and stability both tracks should be extended fully unless required for confined maneuvering" see picture. Matts were laid out in a single file end to end arrangement (allowing for minimal maneuvering) 5.03: Training FPR and Derrick SOP does not cover when tracks should be extended/retracted 6.02: Crew feedback was that past leadership instructed them to use mats end to end (long ways) which requires the tracks to be retracted in order to fit on one mat. 6.05: Inadequate review of equipment labels and user manual. 9.04: Previous foreman instructed them to use mats end to end (long ways) which requires the tracks to be retracted in order to fit on one mat. | 15. Using Equipment Improperly | 9. Abnormal Operation | approved | Participated in the investigation team. Reviewed and approved TMH | [66 empty] | damaged fence panels and possibly a damaged power dolly. Waiting on fleet to inspect | 1000 | Jeremy Mullens | Industrial/Heavy Equipment | [20 empty] | 8588587
8781 | Durant Service Center | 2019-03-23 20:30 | While backing power dolly out of job site, the left track came off of the mud matts. This resulted in the power dolly laying over on a fence. | Level 3 |  | FALSE | Property Damage |  | Lindle Coleman | team picked in collaboration with operational leadership | 2019-03-26 15:49 | Power Delivery | Lyle Just | 2019-04-10 13:57 | 2019-03-25 15:59 | 2019-03-25 15:59 | 2019-04-05 14:28 | 2019-04-06 20:30 | 2019-03-25 15:52 | 2019-04-08 12:50 | 2019-04-09 11:41 | 2019-04-08 09:55 | 3044 Kande Lane Durant |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Chad Inman |  | While getting power dolly to job sight members retracted tracks in to maneuver between secondary ped, phone ped, and sewer cleanouts and transformers in middle of easements. Pulled to the south side of transformer to replace B/O pad mount transformer, machine got stuck. Crew then proceeded to put outriggers down to lift machine and install matts under tracks to stabilize machine while replacing transformer. By this time it had become dark when work was completed. Crew attempted to take machine out the way we came in and found it was unsafe to do so, because of slick conditions and being afraid of sliding into energized transformer. While exiting the work location, crew laid matts out for machine in a single file end to end arrangement (see pictures). While backing machine off first set of matts, left track of machine came off mat and came in contact with saturated ground and machine turned over onto stockade fence coming to rest on it's left side. Facts Ascertained: Tracks were sucked in while maneuvering through Telephone, Secondary pedestal, and sewer cleanout. After tracks were sucked in, they were left in Maneuvering was not confined where rollover occurred Warning label visible from operator controls states "For optimum safety and stability both tracks should be extended fully unless required for confined maneuvering" see picture Matts were laid out in a single file end to end arrangement (allowing for minimal maneuvering) User manual is on the power dolly trailer and readily accessible. Has 3 work lights on the equipment Machine has 44 service hours since 2016 when it was placed in service at Durant Machine has audible alarm and light to show tracks are retracted. Light is not working and you cannot hear audible alarm when machine is revved up. Foreman was not aware the equipment had any alarms indicating track position Crew stated remote was not working, fleet observation indicates it is. Unit was backed in (approximately 200') using the controls on the machine to the work location Foreman made decision to back in, due to the obstructions and in order for the operator to have more visibility Tailboard was conducted and the controls around bringing the power dolly in were covered verbally but not documented (track position and layout of mats was not included) | Hannah Everett | Chad Inman |  | Durant Service Center | FALSE |  | FALSE | Construction Services |  | Jeremy Mullens | Lyle Just |  | Chad Inman | Reviewed and approved, thank you. | Chad Inman | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | While getting power dolly to job sight members retracted tracks in to maneuver between secondary ped, phone ped, and sewer cleanouts and transformers in middle of easements. Pulled to the south side of transformer to replace B/O pad mount transformer, machine got stuck. Crew then proceeded to put outriggers down to lift machine and install matts under tracks to stabilize machine while replacing transformer. By this time it had become dark when work was completed. Crew attempted to take machine out the way we came in and found it was unsafe to do so, because of slick conditions and being afraid of sliding into energized transformer. While exiting the work location, crew laid matts out for machine in a single file end to end arrangement (see pictures). While backing machine off first set of matts, left track of machine came off mat and came in contact with saturated ground and machine turned over onto stockade fence coming to rest on it's left side. Facts Ascertained: Tracks were not extended while exiting the location. Maneuvering was not confined where rollover occurred Warning label visible from operator controls states "For optimum safety and stability both tracks should be extended fully unless required for confined maneuvering" see picture. Matts were laid out in a single file end to end arrangement (allowing for minimal maneuvering) 5.03: Training FPR and Derrick SOP does not cover when tracks should be extended/retracted 6.02: Crew feedback was that past leadership instructed them to use mats end to end (long ways) which requires the tracks to be retracted in order to fit on one mat. 6.05: Inadequate review of equipment labels and user manual. 9.04: Previous foreman instructed them to use mats end to end (long ways) which requires the tracks to be retracted in order to fit on one mat. | 15. Using Equipment Improperly | 9. Abnormal Operation | approved | Participated in the investigation team. Reviewed and approved TMH | [66 empty] | damaged fence panels and possibly a damaged power dolly. Waiting on fleet to inspect | 1000 | Jeremy Mullens | Industrial/Heavy Equipment | [20 empty] | 8588587
8781 | Durant Service Center | 2019-03-23 20:30 | While backing power dolly out of job site, the left track came off of the mud matts. This resulted in the power dolly laying over on a fence. | Level 3 |  | FALSE | Property Damage |  | Lindle Coleman | team picked in collaboration with operational leadership | 2019-03-26 15:49 | Power Delivery | Lyle Just | 2019-04-10 13:57 | 2019-03-25 15:59 | 2019-03-25 15:59 | 2019-04-05 14:28 | 2019-04-06 20:30 | 2019-03-25 15:52 | 2019-04-08 12:50 | 2019-04-09 11:41 | 2019-04-08 09:55 | 3044 Kande Lane Durant |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Chad Inman |  | While getting power dolly to job sight members retracted tracks in to maneuver between secondary ped, phone ped, and sewer cleanouts and transformers in middle of easements. Pulled to the south side of transformer to replace B/O pad mount transformer, machine got stuck. Crew then proceeded to put outriggers down to lift machine and install matts under tracks to stabilize machine while replacing transformer. By this time it had become dark when work was completed. Crew attempted to take machine out the way we came in and found it was unsafe to do so, because of slick conditions and being afraid of sliding into energized transformer. While exiting the work location, crew laid matts out for machine in a single file end to end arrangement (see pictures). While backing machine off first set of matts, left track of machine came off mat and came in contact with saturated ground and machine turned over onto stockade fence coming to rest on it's left side. Facts Ascertained: Tracks were sucked in while maneuvering through Telephone, Secondary pedestal, and sewer cleanout. After tracks were sucked in, they were left in Maneuvering was not confined where rollover occurred Warning label visible from operator controls states "For optimum safety and stability both tracks should be extended fully unless required for confined maneuvering" see picture Matts were laid out in a single file end to end arrangement (allowing for minimal maneuvering) User manual is on the power dolly trailer and readily accessible. Has 3 work lights on the equipment Machine has 44 service hours since 2016 when it was placed in service at Durant Machine has audible alarm and light to show tracks are retracted. Light is not working and you cannot hear audible alarm when machine is revved up. Foreman was not aware the equipment had any alarms indicating track position Crew stated remote was not working, fleet observation indicates it is. Unit was backed in (approximately 200') using the controls on the machine to the work location Foreman made decision to back in, due to the obstructions and in order for the operator to have more visibility Tailboard was conducted and the controls around bringing the power dolly in were covered verbally but not documented (track position and layout of mats was not included) | Hannah Everett | Chad Inman |  | Durant Service Center | FALSE |  | FALSE | Construction Services |  | Jeremy Mullens | Lyle Just |  | Chad Inman | Reviewed and approved, thank you. | Chad Inman | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction |  |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | While getting power dolly to job sight members retracted tracks in to maneuver between secondary ped, phone ped, and sewer cleanouts and transformers in middle of easements. Pulled to the south side of transformer to replace B/O pad mount transformer, machine got stuck. Crew then proceeded to put outriggers down to lift machine and install matts under tracks to stabilize machine while replacing transformer. By this time it had become dark when work was completed. Crew attempted to take machine out the way we came in and found it was unsafe to do so, because of slick conditions and being afraid of sliding into energized transformer. While exiting the work location, crew laid matts out for machine in a single file end to end arrangement (see pictures). While backing machine off first set of matts, left track of machine came off mat and came in contact with saturated ground and machine turned over onto stockade fence coming to rest on it's left side. Facts Ascertained: Tracks were not extended while exiting the location. Maneuvering was not confined where rollover occurred Warning label visible from operator controls states "For optimum safety and stability both tracks should be extended fully unless required for confined maneuvering" see picture. Matts were laid out in a single file end to end arrangement (allowing for minimal maneuvering) 5.03: Training FPR and Derrick SOP does not cover when tracks should be extended/retracted 6.02: Crew feedback was that past leadership instructed them to use mats end to end (long ways) which requires the tracks to be retracted in order to fit on one mat. 6.05: Inadequate review of equipment labels and user manual. 9.04: Previous foreman instructed them to use mats end to end (long ways) which requires the tracks to be retracted in order to fit on one mat. | 15. Using Equipment Improperly | 9. Abnormal Operation | approved | Participated in the investigation team. Reviewed and approved TMH | [66 empty] | damaged fence panels and possibly a damaged power dolly. Waiting on fleet to inspect | 1000 | Jeremy Mullens | Industrial/Heavy Equipment | [20 empty] | 8588587
8781 | Durant Service Center | 2019-03-23 20:30 | While backing power dolly out of job site, the left track came off of the mud matts. This resulted in the power dolly laying over on a fence. | Level 3 |  | FALSE | Property Damage |  | Lindle Coleman | team picked in collaboration with operational leadership | 2019-03-26 15:49 | Power Delivery | Lyle Just | 2019-04-10 13:57 | 2019-03-25 15:59 | 2019-03-25 15:59 | 2019-04-05 14:28 | 2019-04-06 20:30 | 2019-03-25 15:52 | 2019-04-08 12:50 | 2019-04-09 11:41 | 2019-04-08 09:55 | 3044 Kande Lane Durant |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Chad Inman |  | While getting power dolly to job sight members retracted tracks in to maneuver between secondary ped, phone ped, and sewer cleanouts and transformers in middle of easements. Pulled to the south side of transformer to replace B/O pad mount transformer, machine got stuck. Crew then proceeded to put outriggers down to lift machine and install matts under tracks to stabilize machine while replacing transformer. By this time it had become dark when work was completed. Crew attempted to take machine out the way we came in and found it was unsafe to do so, because of slick conditions and being afraid of sliding into energized transformer. While exiting the work location, crew laid matts out for machine in a single file end to end arrangement (see pictures). While backing machine off first set of matts, left track of machine came off mat and came in contact with saturated ground and machine turned over onto stockade fence coming to rest on it's left side. Facts Ascertained: Tracks were sucked in while maneuvering through Telephone, Secondary pedestal, and sewer cleanout. After tracks were sucked in, they were left in Maneuvering was not confined where rollover occurred Warning label visible from operator controls states "For optimum safety and stability both tracks should be extended fully unless required for confined maneuvering" see picture Matts were laid out in a single file end to end arrangement (allowing for minimal maneuvering) User manual is on the power dolly trailer and readily accessible. Has 3 work lights on the equipment Machine has 44 service hours since 2016 when it was placed in service at Durant Machine has audible alarm and light to show tracks are retracted. Light is not working and you cannot hear audible alarm when machine is revved up. Foreman was not aware the equipment had any alarms indicating track position Crew stated remote was not working, fleet observation indicates it is. Unit was backed in (approximately 200') using the controls on the machine to the work location Foreman made decision to back in, due to the obstructions and in order for the operator to have more visibility Tailboard was conducted and the controls around bringing the power dolly in were covered verbally but not documented (track position and layout of mats was not included) | Hannah Everett | Chad Inman |  | Durant Service Center | FALSE |  | FALSE | Construction Services |  | Jeremy Mullens | Lyle Just |  | Chad Inman | Reviewed and approved, thank you. | Chad Inman | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.02 Inadequate practice |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | While getting power dolly to job sight members retracted tracks in to maneuver between secondary ped, phone ped, and sewer cleanouts and transformers in middle of easements. Pulled to the south side of transformer to replace B/O pad mount transformer, machine got stuck. Crew then proceeded to put outriggers down to lift machine and install matts under tracks to stabilize machine while replacing transformer. By this time it had become dark when work was completed. Crew attempted to take machine out the way we came in and found it was unsafe to do so, because of slick conditions and being afraid of sliding into energized transformer. While exiting the work location, crew laid matts out for machine in a single file end to end arrangement (see pictures). While backing machine off first set of matts, left track of machine came off mat and came in contact with saturated ground and machine turned over onto stockade fence coming to rest on it's left side. Facts Ascertained: Tracks were not extended while exiting the location. Maneuvering was not confined where rollover occurred Warning label visible from operator controls states "For optimum safety and stability both tracks should be extended fully unless required for confined maneuvering" see picture. Matts were laid out in a single file end to end arrangement (allowing for minimal maneuvering) 5.03: Training FPR and Derrick SOP does not cover when tracks should be extended/retracted 6.02: Crew feedback was that past leadership instructed them to use mats end to end (long ways) which requires the tracks to be retracted in order to fit on one mat. 6.05: Inadequate review of equipment labels and user manual. 9.04: Previous foreman instructed them to use mats end to end (long ways) which requires the tracks to be retracted in order to fit on one mat. | 15. Using Equipment Improperly | 9. Abnormal Operation | approved | Participated in the investigation team. Reviewed and approved TMH | [66 empty] | damaged fence panels and possibly a damaged power dolly. Waiting on fleet to inspect | 1000 | Jeremy Mullens | Industrial/Heavy Equipment | [20 empty] | 8588587
8781 | Durant Service Center | 2019-03-23 20:30 | While backing power dolly out of job site, the left track came off of the mud matts. This resulted in the power dolly laying over on a fence. | Level 3 |  | FALSE | Property Damage |  | Lindle Coleman | team picked in collaboration with operational leadership | 2019-03-26 15:49 | Power Delivery | Lyle Just | 2019-04-10 13:57 | 2019-03-25 15:59 | 2019-03-25 15:59 | 2019-04-05 14:28 | 2019-04-06 20:30 | 2019-03-25 15:52 | 2019-04-08 12:50 | 2019-04-09 11:41 | 2019-04-08 09:55 | 3044 Kande Lane Durant |  |  |  | Approve | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Chad Inman |  | While getting power dolly to job sight members retracted tracks in to maneuver between secondary ped, phone ped, and sewer cleanouts and transformers in middle of easements. Pulled to the south side of transformer to replace B/O pad mount transformer, machine got stuck. Crew then proceeded to put outriggers down to lift machine and install matts under tracks to stabilize machine while replacing transformer. By this time it had become dark when work was completed. Crew attempted to take machine out the way we came in and found it was unsafe to do so, because of slick conditions and being afraid of sliding into energized transformer. While exiting the work location, crew laid matts out for machine in a single file end to end arrangement (see pictures). While backing machine off first set of matts, left track of machine came off mat and came in contact with saturated ground and machine turned over onto stockade fence coming to rest on it's left side. Facts Ascertained: Tracks were sucked in while maneuvering through Telephone, Secondary pedestal, and sewer cleanout. After tracks were sucked in, they were left in Maneuvering was not confined where rollover occurred Warning label visible from operator controls states "For optimum safety and stability both tracks should be extended fully unless required for confined maneuvering" see picture Matts were laid out in a single file end to end arrangement (allowing for minimal maneuvering) User manual is on the power dolly trailer and readily accessible. Has 3 work lights on the equipment Machine has 44 service hours since 2016 when it was placed in service at Durant Machine has audible alarm and light to show tracks are retracted. Light is not working and you cannot hear audible alarm when machine is revved up. Foreman was not aware the equipment had any alarms indicating track position Crew stated remote was not working, fleet observation indicates it is. Unit was backed in (approximately 200') using the controls on the machine to the work location Foreman made decision to back in, due to the obstructions and in order for the operator to have more visibility Tailboard was conducted and the controls around bringing the power dolly in were covered verbally but not documented (track position and layout of mats was not included) | Hannah Everett | Chad Inman |  | Durant Service Center | FALSE |  | FALSE | Construction Services |  | Jeremy Mullens | Lyle Just |  | Chad Inman | Reviewed and approved, thank you. | Chad Inman | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.02 Inadequate practice |  |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | While getting power dolly to job sight members retracted tracks in to maneuver between secondary ped, phone ped, and sewer cleanouts and transformers in middle of easements. Pulled to the south side of transformer to replace B/O pad mount transformer, machine got stuck. Crew then proceeded to put outriggers down to lift machine and install matts under tracks to stabilize machine while replacing transformer. By this time it had become dark when work was completed. Crew attempted to take machine out the way we came in and found it was unsafe to do so, because of slick conditions and being afraid of sliding into energized transformer. While exiting the work location, crew laid matts out for machine in a single file end to end arrangement (see pictures). While backing machine off first set of matts, left track of machine came off mat and came in contact with saturated ground and machine turned over onto stockade fence coming to rest on it's left side. Facts Ascertained: Tracks were not extended while exiting the location. Maneuvering was not confined where rollover occurred Warning label visible from operator controls states "For optimum safety and stability both tracks should be extended fully unless required for confined maneuvering" see picture. Matts were laid out in a single file end to end arrangement (allowing for minimal maneuvering) 5.03: Training FPR and Derrick SOP does not cover when tracks should be extended/retracted 6.02: Crew feedback was that past leadership instructed them to use mats end to end (long ways) which requires the tracks to be retracted in order to fit on one mat. 6.05: Inadequate review of equipment labels and user manual. 9.04: Previous foreman instructed them to use mats end to end (long ways) which requires the tracks to be retracted in order to fit on one mat. | 15. Using Equipment Improperly | 9. Abnormal Operation | approved | Participated in the investigation team. Reviewed and approved TMH | [66 empty] | damaged fence panels and possibly a damaged power dolly. Waiting on fleet to inspect | 1000 | Jeremy Mullens | Industrial/Heavy Equipment | [20 empty] | 8588587
8782 | Sooner Power Plant | 2019-03-25 11:30 | Member was radioed by Control Operator and told that the BB hydrated lime weigh bin was plugged. Member then went to the scrubber area to unplug bin. Upon getting to location member proceeded to unplug AB bin which was not the correct bin. Hydrated lime was discharged from clean out port. No injuries occurred. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Jesse, Sooner would like to have the following members assigned to the investigation team for incident 8782. Alex Taybah Marc Hodgson Brady Sowell Jim Griffith | 2019-05-02 15:02 | Power Supply | Marc Hodgson | 2019-05-24 14:20 | 2019-03-26 12:01 | 2019-04-23 16:57 | 2019-05-06 12:14 | 2019-04-08 11:30 | 2019-03-26 11:14 | 2019-05-12 23:25 | 2019-05-22 10:19 | 2019-05-07 07:20 | Sooner Plant Unit 2 Scrubber Hydrated Lime Feeders area 1000 foot elevation of scrubber |  |  | Donnie Jones | I approve | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Alexander Taybah |  | On March 25, 2019 at about 1145 hours, Control Operator contacted Scrubber operator stating that on unit 2 B train, B hydrated lime feeder was plugged. Scrubber operator responded letting the Control operator know that he would head that way to unplug the feeder. Control operator than stated that he had placed the fill valve (2-li-fv-5000bb) in manual so it would not open. When the scrubber operator approached the weigh bin area he began to rod out what he assumed was the correct feeder. He did not communicate back to the Control operator that he was on the correct feeder. After about 20 minutes the Control Operator asked Scrubber operator if he was done cleaning the feeder comminuted back to Control Operator that he was done and the feeder should be feeding. At approximately, 1400 hours on this day OPC contacted Rick Wood (OGE) about a hydrate lime spill/leak. Rick then contacted the operations integration members to investigate. They went up to the hydrated lime feeder level and found lime on the flashing above the bottom clean out port on AB feeder (which was the incorrect feeder). They also discovered abnormal amounts of hydrated lime on the hand rails, grating, beams, cable trays, cement approximately 20 feet from the feeder. It is estimated that about 200-400 pounds of hydrated lime was discharged from the feeder. They also inspected the ground level and noted that there was approximately ¼ to ½ inch of hydrated lime on the floor. Next, Integration members contacted Mark Trammel and let him know what they had discovered. They decided that the Shift Supervisor should be made aware of the situation if he had not been made aware yet. At approximately 1530 hours, Integration members and Mark Trammel contacted the Shift Supervisor on duty. The Shift Supervisor was unware of any spill or leaks that had taken place in the scrubber area that day. | Marc Hodgson | Alexander Taybah | FALSE | Sooner Power Plant | FALSE |  | FALSE | Operations |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah | Jesse Murray | High |  |  |  |  | 5.01 Lack of experience | [8 empty] | 14.02.4 Inadequate communication of standards: training |  |  | Member got on the 2B Train "B" weigh bin instead of 2B Train "A" weigh bin and tried to unplug the blockage. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | I Approve. Jesse Murray | Approved by Brady Sowell on 5/7/2019 | [24 empty] | TRUE |  |  | 2018-07-16 | 1978-10-06 |  | 2019-03-25 06:00 | 0 | 0 | Member did not suffer any injury, although he dusted lime off of clothing and rinsed hands and face. | FALSE | Male |  |  | TRUE | Shawn Richardson |  | Uninjured | Shawn Richardson | [6 empty] | FALSE | Shawn Richardson | Plant Operator I |  |  |  |  | Marc Hodgson |  |  | 3/25/2019 6:00:00 AM | 8 months | FALSE | [28 empty] | NA
8782 | Sooner Power Plant | 2019-03-25 11:30 | Member was radioed by Control Operator and told that the BB hydrated lime weigh bin was plugged. Member then went to the scrubber area to unplug bin. Upon getting to location member proceeded to unplug AB bin which was not the correct bin. Hydrated lime was discharged from clean out port. No injuries occurred. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Jesse, Sooner would like to have the following members assigned to the investigation team for incident 8782. Alex Taybah Marc Hodgson Brady Sowell Jim Griffith | 2019-05-02 15:02 | Power Supply | Marc Hodgson | 2019-05-24 14:20 | 2019-03-26 12:01 | 2019-04-23 16:57 | 2019-05-06 12:14 | 2019-04-08 11:30 | 2019-03-26 11:14 | 2019-05-12 23:25 | 2019-05-22 10:19 | 2019-05-07 07:20 | Sooner Plant Unit 2 Scrubber Hydrated Lime Feeders area 1000 foot elevation of scrubber |  |  | Donnie Jones | I approve | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Alexander Taybah |  | On March 25, 2019 at about 1145 hours, Control Operator contacted Scrubber operator stating that on unit 2 B train, B hydrated lime feeder was plugged. Scrubber operator responded letting the Control operator know that he would head that way to unplug the feeder. Control operator than stated that he had placed the fill valve (2-li-fv-5000bb) in manual so it would not open. When the scrubber operator approached the weigh bin area he began to rod out what he assumed was the correct feeder. He did not communicate back to the Control operator that he was on the correct feeder. After about 20 minutes the Control Operator asked Scrubber operator if he was done cleaning the feeder comminuted back to Control Operator that he was done and the feeder should be feeding. At approximately, 1400 hours on this day OPC contacted Rick Wood (OGE) about a hydrate lime spill/leak. Rick then contacted the operations integration members to investigate. They went up to the hydrated lime feeder level and found lime on the flashing above the bottom clean out port on AB feeder (which was the incorrect feeder). They also discovered abnormal amounts of hydrated lime on the hand rails, grating, beams, cable trays, cement approximately 20 feet from the feeder. It is estimated that about 200-400 pounds of hydrated lime was discharged from the feeder. They also inspected the ground level and noted that there was approximately ¼ to ½ inch of hydrated lime on the floor. Next, Integration members contacted Mark Trammel and let him know what they had discovered. They decided that the Shift Supervisor should be made aware of the situation if he had not been made aware yet. At approximately 1530 hours, Integration members and Mark Trammel contacted the Shift Supervisor on duty. The Shift Supervisor was unware of any spill or leaks that had taken place in the scrubber area that day. | Marc Hodgson | Alexander Taybah | FALSE | Sooner Power Plant | FALSE |  | FALSE | Operations |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah | Jesse Murray | High |  |  |  |  | 5.01 Lack of experience | [8 empty] | 14.02.5 Inadequate communication of standards: reinforcing with signs, color codes |  |  | Member got on the 2B Train "B" weigh bin instead of 2B Train "A" weigh bin and tried to unplug the blockage. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | I Approve. Jesse Murray | Approved by Brady Sowell on 5/7/2019 | [24 empty] | TRUE |  |  | 2018-07-16 | 1978-10-06 |  | 2019-03-25 06:00 | 0 | 0 | Member did not suffer any injury, although he dusted lime off of clothing and rinsed hands and face. | FALSE | Male |  |  | TRUE | Shawn Richardson |  | Uninjured | Shawn Richardson | [6 empty] | FALSE | Shawn Richardson | Plant Operator I |  |  |  |  | Marc Hodgson |  |  | 3/25/2019 6:00:00 AM | 8 months | FALSE | [28 empty] | NA
8782 | Sooner Power Plant | 2019-03-25 11:30 | Member was radioed by Control Operator and told that the BB hydrated lime weigh bin was plugged. Member then went to the scrubber area to unplug bin. Upon getting to location member proceeded to unplug AB bin which was not the correct bin. Hydrated lime was discharged from clean out port. No injuries occurred. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Jesse, Sooner would like to have the following members assigned to the investigation team for incident 8782. Alex Taybah Marc Hodgson Brady Sowell Jim Griffith | 2019-05-02 15:02 | Power Supply | Marc Hodgson | 2019-05-24 14:20 | 2019-03-26 12:01 | 2019-04-23 16:57 | 2019-05-06 12:14 | 2019-04-08 11:30 | 2019-03-26 11:14 | 2019-05-12 23:25 | 2019-05-22 10:19 | 2019-05-07 07:20 | Sooner Plant Unit 2 Scrubber Hydrated Lime Feeders area 1000 foot elevation of scrubber |  |  | Donnie Jones | I approve | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Alexander Taybah |  | On March 25, 2019 at about 1145 hours, Control Operator contacted Scrubber operator stating that on unit 2 B train, B hydrated lime feeder was plugged. Scrubber operator responded letting the Control operator know that he would head that way to unplug the feeder. Control operator than stated that he had placed the fill valve (2-li-fv-5000bb) in manual so it would not open. When the scrubber operator approached the weigh bin area he began to rod out what he assumed was the correct feeder. He did not communicate back to the Control operator that he was on the correct feeder. After about 20 minutes the Control Operator asked Scrubber operator if he was done cleaning the feeder comminuted back to Control Operator that he was done and the feeder should be feeding. At approximately, 1400 hours on this day OPC contacted Rick Wood (OGE) about a hydrate lime spill/leak. Rick then contacted the operations integration members to investigate. They went up to the hydrated lime feeder level and found lime on the flashing above the bottom clean out port on AB feeder (which was the incorrect feeder). They also discovered abnormal amounts of hydrated lime on the hand rails, grating, beams, cable trays, cement approximately 20 feet from the feeder. It is estimated that about 200-400 pounds of hydrated lime was discharged from the feeder. They also inspected the ground level and noted that there was approximately ¼ to ½ inch of hydrated lime on the floor. Next, Integration members contacted Mark Trammel and let him know what they had discovered. They decided that the Shift Supervisor should be made aware of the situation if he had not been made aware yet. At approximately 1530 hours, Integration members and Mark Trammel contacted the Shift Supervisor on duty. The Shift Supervisor was unware of any spill or leaks that had taken place in the scrubber area that day. | Marc Hodgson | Alexander Taybah | FALSE | Sooner Power Plant | FALSE |  | FALSE | Operations |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah | Jesse Murray | High |  |  |  |  | 5.05 Misunderstood directions | [8 empty] | 14.02.4 Inadequate communication of standards: training |  |  | Member got on the 2B Train "B" weigh bin instead of 2B Train "A" weigh bin and tried to unplug the blockage. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | I Approve. Jesse Murray | Approved by Brady Sowell on 5/7/2019 | [24 empty] | TRUE |  |  | 2018-07-16 | 1978-10-06 |  | 2019-03-25 06:00 | 0 | 0 | Member did not suffer any injury, although he dusted lime off of clothing and rinsed hands and face. | FALSE | Male |  |  | TRUE | Shawn Richardson |  | Uninjured | Shawn Richardson | [6 empty] | FALSE | Shawn Richardson | Plant Operator I |  |  |  |  | Marc Hodgson |  |  | 3/25/2019 6:00:00 AM | 8 months | FALSE | [28 empty] | NA
8782 | Sooner Power Plant | 2019-03-25 11:30 | Member was radioed by Control Operator and told that the BB hydrated lime weigh bin was plugged. Member then went to the scrubber area to unplug bin. Upon getting to location member proceeded to unplug AB bin which was not the correct bin. Hydrated lime was discharged from clean out port. No injuries occurred. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Jesse, Sooner would like to have the following members assigned to the investigation team for incident 8782. Alex Taybah Marc Hodgson Brady Sowell Jim Griffith | 2019-05-02 15:02 | Power Supply | Marc Hodgson | 2019-05-24 14:20 | 2019-03-26 12:01 | 2019-04-23 16:57 | 2019-05-06 12:14 | 2019-04-08 11:30 | 2019-03-26 11:14 | 2019-05-12 23:25 | 2019-05-22 10:19 | 2019-05-07 07:20 | Sooner Plant Unit 2 Scrubber Hydrated Lime Feeders area 1000 foot elevation of scrubber |  |  | Donnie Jones | I approve | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Alexander Taybah |  | On March 25, 2019 at about 1145 hours, Control Operator contacted Scrubber operator stating that on unit 2 B train, B hydrated lime feeder was plugged. Scrubber operator responded letting the Control operator know that he would head that way to unplug the feeder. Control operator than stated that he had placed the fill valve (2-li-fv-5000bb) in manual so it would not open. When the scrubber operator approached the weigh bin area he began to rod out what he assumed was the correct feeder. He did not communicate back to the Control operator that he was on the correct feeder. After about 20 minutes the Control Operator asked Scrubber operator if he was done cleaning the feeder comminuted back to Control Operator that he was done and the feeder should be feeding. At approximately, 1400 hours on this day OPC contacted Rick Wood (OGE) about a hydrate lime spill/leak. Rick then contacted the operations integration members to investigate. They went up to the hydrated lime feeder level and found lime on the flashing above the bottom clean out port on AB feeder (which was the incorrect feeder). They also discovered abnormal amounts of hydrated lime on the hand rails, grating, beams, cable trays, cement approximately 20 feet from the feeder. It is estimated that about 200-400 pounds of hydrated lime was discharged from the feeder. They also inspected the ground level and noted that there was approximately ¼ to ½ inch of hydrated lime on the floor. Next, Integration members contacted Mark Trammel and let him know what they had discovered. They decided that the Shift Supervisor should be made aware of the situation if he had not been made aware yet. At approximately 1530 hours, Integration members and Mark Trammel contacted the Shift Supervisor on duty. The Shift Supervisor was unware of any spill or leaks that had taken place in the scrubber area that day. | Marc Hodgson | Alexander Taybah | FALSE | Sooner Power Plant | FALSE |  | FALSE | Operations |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah | Jesse Murray | High |  |  |  |  | 5.05 Misunderstood directions | [8 empty] | 14.02.5 Inadequate communication of standards: reinforcing with signs, color codes |  |  | Member got on the 2B Train "B" weigh bin instead of 2B Train "A" weigh bin and tried to unplug the blockage. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | I Approve. Jesse Murray | Approved by Brady Sowell on 5/7/2019 | [24 empty] | TRUE |  |  | 2018-07-16 | 1978-10-06 |  | 2019-03-25 06:00 | 0 | 0 | Member did not suffer any injury, although he dusted lime off of clothing and rinsed hands and face. | FALSE | Male |  |  | TRUE | Shawn Richardson |  | Uninjured | Shawn Richardson | [6 empty] | FALSE | Shawn Richardson | Plant Operator I |  |  |  |  | Marc Hodgson |  |  | 3/25/2019 6:00:00 AM | 8 months | FALSE | [28 empty] | NA
8782 | Sooner Power Plant | 2019-03-25 11:30 | Member was radioed by Control Operator and told that the BB hydrated lime weigh bin was plugged. Member then went to the scrubber area to unplug bin. Upon getting to location member proceeded to unplug AB bin which was not the correct bin. Hydrated lime was discharged from clean out port. No injuries occurred. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Jesse, Sooner would like to have the following members assigned to the investigation team for incident 8782. Alex Taybah Marc Hodgson Brady Sowell Jim Griffith | 2019-05-02 15:02 | Power Supply | Marc Hodgson | 2019-05-24 14:20 | 2019-03-26 12:01 | 2019-04-23 16:57 | 2019-05-06 12:14 | 2019-04-08 11:30 | 2019-03-26 11:14 | 2019-05-12 23:25 | 2019-05-22 10:19 | 2019-05-07 07:20 | Sooner Plant Unit 2 Scrubber Hydrated Lime Feeders area 1000 foot elevation of scrubber |  |  | Donnie Jones | I approve | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Alexander Taybah |  | On March 25, 2019 at about 1145 hours, Control Operator contacted Scrubber operator stating that on unit 2 B train, B hydrated lime feeder was plugged. Scrubber operator responded letting the Control operator know that he would head that way to unplug the feeder. Control operator than stated that he had placed the fill valve (2-li-fv-5000bb) in manual so it would not open. When the scrubber operator approached the weigh bin area he began to rod out what he assumed was the correct feeder. He did not communicate back to the Control operator that he was on the correct feeder. After about 20 minutes the Control Operator asked Scrubber operator if he was done cleaning the feeder comminuted back to Control Operator that he was done and the feeder should be feeding. At approximately, 1400 hours on this day OPC contacted Rick Wood (OGE) about a hydrate lime spill/leak. Rick then contacted the operations integration members to investigate. They went up to the hydrated lime feeder level and found lime on the flashing above the bottom clean out port on AB feeder (which was the incorrect feeder). They also discovered abnormal amounts of hydrated lime on the hand rails, grating, beams, cable trays, cement approximately 20 feet from the feeder. It is estimated that about 200-400 pounds of hydrated lime was discharged from the feeder. They also inspected the ground level and noted that there was approximately ¼ to ½ inch of hydrated lime on the floor. Next, Integration members contacted Mark Trammel and let him know what they had discovered. They decided that the Shift Supervisor should be made aware of the situation if he had not been made aware yet. At approximately 1530 hours, Integration members and Mark Trammel contacted the Shift Supervisor on duty. The Shift Supervisor was unware of any spill or leaks that had taken place in the scrubber area that day. | Marc Hodgson | Alexander Taybah | FALSE | Sooner Power Plant | FALSE |  | FALSE | Operations |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness | [8 empty] | 14.02.4 Inadequate communication of standards: training |  |  | Member got on the 2B Train "B" weigh bin instead of 2B Train "A" weigh bin and tried to unplug the blockage. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | I Approve. Jesse Murray | Approved by Brady Sowell on 5/7/2019 | [24 empty] | TRUE |  |  | 2018-07-16 | 1978-10-06 |  | 2019-03-25 06:00 | 0 | 0 | Member did not suffer any injury, although he dusted lime off of clothing and rinsed hands and face. | FALSE | Male |  |  | TRUE | Shawn Richardson |  | Uninjured | Shawn Richardson | [6 empty] | FALSE | Shawn Richardson | Plant Operator I |  |  |  |  | Marc Hodgson |  |  | 3/25/2019 6:00:00 AM | 8 months | FALSE | [28 empty] | NA
8782 | Sooner Power Plant | 2019-03-25 11:30 | Member was radioed by Control Operator and told that the BB hydrated lime weigh bin was plugged. Member then went to the scrubber area to unplug bin. Upon getting to location member proceeded to unplug AB bin which was not the correct bin. Hydrated lime was discharged from clean out port. No injuries occurred. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Jesse, Sooner would like to have the following members assigned to the investigation team for incident 8782. Alex Taybah Marc Hodgson Brady Sowell Jim Griffith | 2019-05-02 15:02 | Power Supply | Marc Hodgson | 2019-05-24 14:20 | 2019-03-26 12:01 | 2019-04-23 16:57 | 2019-05-06 12:14 | 2019-04-08 11:30 | 2019-03-26 11:14 | 2019-05-12 23:25 | 2019-05-22 10:19 | 2019-05-07 07:20 | Sooner Plant Unit 2 Scrubber Hydrated Lime Feeders area 1000 foot elevation of scrubber |  |  | Donnie Jones | I approve | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Alexander Taybah |  | On March 25, 2019 at about 1145 hours, Control Operator contacted Scrubber operator stating that on unit 2 B train, B hydrated lime feeder was plugged. Scrubber operator responded letting the Control operator know that he would head that way to unplug the feeder. Control operator than stated that he had placed the fill valve (2-li-fv-5000bb) in manual so it would not open. When the scrubber operator approached the weigh bin area he began to rod out what he assumed was the correct feeder. He did not communicate back to the Control operator that he was on the correct feeder. After about 20 minutes the Control Operator asked Scrubber operator if he was done cleaning the feeder comminuted back to Control Operator that he was done and the feeder should be feeding. At approximately, 1400 hours on this day OPC contacted Rick Wood (OGE) about a hydrate lime spill/leak. Rick then contacted the operations integration members to investigate. They went up to the hydrated lime feeder level and found lime on the flashing above the bottom clean out port on AB feeder (which was the incorrect feeder). They also discovered abnormal amounts of hydrated lime on the hand rails, grating, beams, cable trays, cement approximately 20 feet from the feeder. It is estimated that about 200-400 pounds of hydrated lime was discharged from the feeder. They also inspected the ground level and noted that there was approximately ¼ to ½ inch of hydrated lime on the floor. Next, Integration members contacted Mark Trammel and let him know what they had discovered. They decided that the Shift Supervisor should be made aware of the situation if he had not been made aware yet. At approximately 1530 hours, Integration members and Mark Trammel contacted the Shift Supervisor on duty. The Shift Supervisor was unware of any spill or leaks that had taken place in the scrubber area that day. | Marc Hodgson | Alexander Taybah | FALSE | Sooner Power Plant | FALSE |  | FALSE | Operations |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness | [8 empty] | 14.02.5 Inadequate communication of standards: reinforcing with signs, color codes |  |  | Member got on the 2B Train "B" weigh bin instead of 2B Train "A" weigh bin and tried to unplug the blockage. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | I Approve. Jesse Murray | Approved by Brady Sowell on 5/7/2019 | [24 empty] | TRUE |  |  | 2018-07-16 | 1978-10-06 |  | 2019-03-25 06:00 | 0 | 0 | Member did not suffer any injury, although he dusted lime off of clothing and rinsed hands and face. | FALSE | Male |  |  | TRUE | Shawn Richardson |  | Uninjured | Shawn Richardson | [6 empty] | FALSE | Shawn Richardson | Plant Operator I |  |  |  |  | Marc Hodgson |  |  | 3/25/2019 6:00:00 AM | 8 months | FALSE | [28 empty] | NA
8782 | Sooner Power Plant | 2019-03-25 11:30 | Member was radioed by Control Operator and told that the BB hydrated lime weigh bin was plugged. Member then went to the scrubber area to unplug bin. Upon getting to location member proceeded to unplug AB bin which was not the correct bin. Hydrated lime was discharged from clean out port. No injuries occurred. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Jesse, Sooner would like to have the following members assigned to the investigation team for incident 8782. Alex Taybah Marc Hodgson Brady Sowell Jim Griffith | 2019-05-02 15:02 | Power Supply | Marc Hodgson | 2019-05-24 14:20 | 2019-03-26 12:01 | 2019-04-23 16:57 | 2019-05-06 12:14 | 2019-04-08 11:30 | 2019-03-26 11:14 | 2019-05-12 23:25 | 2019-05-22 10:19 | 2019-05-07 07:20 | Sooner Plant Unit 2 Scrubber Hydrated Lime Feeders area 1000 foot elevation of scrubber |  |  | Donnie Jones | I approve | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Alexander Taybah |  | On March 25, 2019 at about 1145 hours, Control Operator contacted Scrubber operator stating that on unit 2 B train, B hydrated lime feeder was plugged. Scrubber operator responded letting the Control operator know that he would head that way to unplug the feeder. Control operator than stated that he had placed the fill valve (2-li-fv-5000bb) in manual so it would not open. When the scrubber operator approached the weigh bin area he began to rod out what he assumed was the correct feeder. He did not communicate back to the Control operator that he was on the correct feeder. After about 20 minutes the Control Operator asked Scrubber operator if he was done cleaning the feeder comminuted back to Control Operator that he was done and the feeder should be feeding. At approximately, 1400 hours on this day OPC contacted Rick Wood (OGE) about a hydrate lime spill/leak. Rick then contacted the operations integration members to investigate. They went up to the hydrated lime feeder level and found lime on the flashing above the bottom clean out port on AB feeder (which was the incorrect feeder). They also discovered abnormal amounts of hydrated lime on the hand rails, grating, beams, cable trays, cement approximately 20 feet from the feeder. It is estimated that about 200-400 pounds of hydrated lime was discharged from the feeder. They also inspected the ground level and noted that there was approximately ¼ to ½ inch of hydrated lime on the floor. Next, Integration members contacted Mark Trammel and let him know what they had discovered. They decided that the Shift Supervisor should be made aware of the situation if he had not been made aware yet. At approximately 1530 hours, Integration members and Mark Trammel contacted the Shift Supervisor on duty. The Shift Supervisor was unware of any spill or leaks that had taken place in the scrubber area that day. | Brady Sowell | Alexander Taybah | FALSE | Sooner Power Plant | FALSE |  | FALSE | Operations |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah | Jesse Murray | High |  |  |  |  | 5.01 Lack of experience | [8 empty] | 14.02.4 Inadequate communication of standards: training |  |  | Member got on the 2B Train "B" weigh bin instead of 2B Train "A" weigh bin and tried to unplug the blockage. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | I Approve. Jesse Murray | Approved by Brady Sowell on 5/7/2019 | [24 empty] | TRUE |  |  | 2018-07-16 | 1978-10-06 |  | 2019-03-25 06:00 | 0 | 0 | Member did not suffer any injury, although he dusted lime off of clothing and rinsed hands and face. | FALSE | Male |  |  | TRUE | Shawn Richardson |  | Uninjured | Shawn Richardson | [6 empty] | FALSE | Shawn Richardson | Plant Operator I |  |  |  |  | Marc Hodgson |  |  | 3/25/2019 6:00:00 AM | 8 months | FALSE | [28 empty] | NA
8782 | Sooner Power Plant | 2019-03-25 11:30 | Member was radioed by Control Operator and told that the BB hydrated lime weigh bin was plugged. Member then went to the scrubber area to unplug bin. Upon getting to location member proceeded to unplug AB bin which was not the correct bin. Hydrated lime was discharged from clean out port. No injuries occurred. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Jesse, Sooner would like to have the following members assigned to the investigation team for incident 8782. Alex Taybah Marc Hodgson Brady Sowell Jim Griffith | 2019-05-02 15:02 | Power Supply | Marc Hodgson | 2019-05-24 14:20 | 2019-03-26 12:01 | 2019-04-23 16:57 | 2019-05-06 12:14 | 2019-04-08 11:30 | 2019-03-26 11:14 | 2019-05-12 23:25 | 2019-05-22 10:19 | 2019-05-07 07:20 | Sooner Plant Unit 2 Scrubber Hydrated Lime Feeders area 1000 foot elevation of scrubber |  |  | Donnie Jones | I approve | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Alexander Taybah |  | On March 25, 2019 at about 1145 hours, Control Operator contacted Scrubber operator stating that on unit 2 B train, B hydrated lime feeder was plugged. Scrubber operator responded letting the Control operator know that he would head that way to unplug the feeder. Control operator than stated that he had placed the fill valve (2-li-fv-5000bb) in manual so it would not open. When the scrubber operator approached the weigh bin area he began to rod out what he assumed was the correct feeder. He did not communicate back to the Control operator that he was on the correct feeder. After about 20 minutes the Control Operator asked Scrubber operator if he was done cleaning the feeder comminuted back to Control Operator that he was done and the feeder should be feeding. At approximately, 1400 hours on this day OPC contacted Rick Wood (OGE) about a hydrate lime spill/leak. Rick then contacted the operations integration members to investigate. They went up to the hydrated lime feeder level and found lime on the flashing above the bottom clean out port on AB feeder (which was the incorrect feeder). They also discovered abnormal amounts of hydrated lime on the hand rails, grating, beams, cable trays, cement approximately 20 feet from the feeder. It is estimated that about 200-400 pounds of hydrated lime was discharged from the feeder. They also inspected the ground level and noted that there was approximately ¼ to ½ inch of hydrated lime on the floor. Next, Integration members contacted Mark Trammel and let him know what they had discovered. They decided that the Shift Supervisor should be made aware of the situation if he had not been made aware yet. At approximately 1530 hours, Integration members and Mark Trammel contacted the Shift Supervisor on duty. The Shift Supervisor was unware of any spill or leaks that had taken place in the scrubber area that day. | Brady Sowell | Alexander Taybah | FALSE | Sooner Power Plant | FALSE |  | FALSE | Operations |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah | Jesse Murray | High |  |  |  |  | 5.01 Lack of experience | [8 empty] | 14.02.5 Inadequate communication of standards: reinforcing with signs, color codes |  |  | Member got on the 2B Train "B" weigh bin instead of 2B Train "A" weigh bin and tried to unplug the blockage. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | I Approve. Jesse Murray | Approved by Brady Sowell on 5/7/2019 | [24 empty] | TRUE |  |  | 2018-07-16 | 1978-10-06 |  | 2019-03-25 06:00 | 0 | 0 | Member did not suffer any injury, although he dusted lime off of clothing and rinsed hands and face. | FALSE | Male |  |  | TRUE | Shawn Richardson |  | Uninjured | Shawn Richardson | [6 empty] | FALSE | Shawn Richardson | Plant Operator I |  |  |  |  | Marc Hodgson |  |  | 3/25/2019 6:00:00 AM | 8 months | FALSE | [28 empty] | NA
8782 | Sooner Power Plant | 2019-03-25 11:30 | Member was radioed by Control Operator and told that the BB hydrated lime weigh bin was plugged. Member then went to the scrubber area to unplug bin. Upon getting to location member proceeded to unplug AB bin which was not the correct bin. Hydrated lime was discharged from clean out port. No injuries occurred. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Jesse, Sooner would like to have the following members assigned to the investigation team for incident 8782. Alex Taybah Marc Hodgson Brady Sowell Jim Griffith | 2019-05-02 15:02 | Power Supply | Marc Hodgson | 2019-05-24 14:20 | 2019-03-26 12:01 | 2019-04-23 16:57 | 2019-05-06 12:14 | 2019-04-08 11:30 | 2019-03-26 11:14 | 2019-05-12 23:25 | 2019-05-22 10:19 | 2019-05-07 07:20 | Sooner Plant Unit 2 Scrubber Hydrated Lime Feeders area 1000 foot elevation of scrubber |  |  | Donnie Jones | I approve | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Alexander Taybah |  | On March 25, 2019 at about 1145 hours, Control Operator contacted Scrubber operator stating that on unit 2 B train, B hydrated lime feeder was plugged. Scrubber operator responded letting the Control operator know that he would head that way to unplug the feeder. Control operator than stated that he had placed the fill valve (2-li-fv-5000bb) in manual so it would not open. When the scrubber operator approached the weigh bin area he began to rod out what he assumed was the correct feeder. He did not communicate back to the Control operator that he was on the correct feeder. After about 20 minutes the Control Operator asked Scrubber operator if he was done cleaning the feeder comminuted back to Control Operator that he was done and the feeder should be feeding. At approximately, 1400 hours on this day OPC contacted Rick Wood (OGE) about a hydrate lime spill/leak. Rick then contacted the operations integration members to investigate. They went up to the hydrated lime feeder level and found lime on the flashing above the bottom clean out port on AB feeder (which was the incorrect feeder). They also discovered abnormal amounts of hydrated lime on the hand rails, grating, beams, cable trays, cement approximately 20 feet from the feeder. It is estimated that about 200-400 pounds of hydrated lime was discharged from the feeder. They also inspected the ground level and noted that there was approximately ¼ to ½ inch of hydrated lime on the floor. Next, Integration members contacted Mark Trammel and let him know what they had discovered. They decided that the Shift Supervisor should be made aware of the situation if he had not been made aware yet. At approximately 1530 hours, Integration members and Mark Trammel contacted the Shift Supervisor on duty. The Shift Supervisor was unware of any spill or leaks that had taken place in the scrubber area that day. | Brady Sowell | Alexander Taybah | FALSE | Sooner Power Plant | FALSE |  | FALSE | Operations |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah | Jesse Murray | High |  |  |  |  | 5.05 Misunderstood directions | [8 empty] | 14.02.4 Inadequate communication of standards: training |  |  | Member got on the 2B Train "B" weigh bin instead of 2B Train "A" weigh bin and tried to unplug the blockage. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | I Approve. Jesse Murray | Approved by Brady Sowell on 5/7/2019 | [24 empty] | TRUE |  |  | 2018-07-16 | 1978-10-06 |  | 2019-03-25 06:00 | 0 | 0 | Member did not suffer any injury, although he dusted lime off of clothing and rinsed hands and face. | FALSE | Male |  |  | TRUE | Shawn Richardson |  | Uninjured | Shawn Richardson | [6 empty] | FALSE | Shawn Richardson | Plant Operator I |  |  |  |  | Marc Hodgson |  |  | 3/25/2019 6:00:00 AM | 8 months | FALSE | [28 empty] | NA
8782 | Sooner Power Plant | 2019-03-25 11:30 | Member was radioed by Control Operator and told that the BB hydrated lime weigh bin was plugged. Member then went to the scrubber area to unplug bin. Upon getting to location member proceeded to unplug AB bin which was not the correct bin. Hydrated lime was discharged from clean out port. No injuries occurred. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Jesse, Sooner would like to have the following members assigned to the investigation team for incident 8782. Alex Taybah Marc Hodgson Brady Sowell Jim Griffith | 2019-05-02 15:02 | Power Supply | Marc Hodgson | 2019-05-24 14:20 | 2019-03-26 12:01 | 2019-04-23 16:57 | 2019-05-06 12:14 | 2019-04-08 11:30 | 2019-03-26 11:14 | 2019-05-12 23:25 | 2019-05-22 10:19 | 2019-05-07 07:20 | Sooner Plant Unit 2 Scrubber Hydrated Lime Feeders area 1000 foot elevation of scrubber |  |  | Donnie Jones | I approve | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Alexander Taybah |  | On March 25, 2019 at about 1145 hours, Control Operator contacted Scrubber operator stating that on unit 2 B train, B hydrated lime feeder was plugged. Scrubber operator responded letting the Control operator know that he would head that way to unplug the feeder. Control operator than stated that he had placed the fill valve (2-li-fv-5000bb) in manual so it would not open. When the scrubber operator approached the weigh bin area he began to rod out what he assumed was the correct feeder. He did not communicate back to the Control operator that he was on the correct feeder. After about 20 minutes the Control Operator asked Scrubber operator if he was done cleaning the feeder comminuted back to Control Operator that he was done and the feeder should be feeding. At approximately, 1400 hours on this day OPC contacted Rick Wood (OGE) about a hydrate lime spill/leak. Rick then contacted the operations integration members to investigate. They went up to the hydrated lime feeder level and found lime on the flashing above the bottom clean out port on AB feeder (which was the incorrect feeder). They also discovered abnormal amounts of hydrated lime on the hand rails, grating, beams, cable trays, cement approximately 20 feet from the feeder. It is estimated that about 200-400 pounds of hydrated lime was discharged from the feeder. They also inspected the ground level and noted that there was approximately ¼ to ½ inch of hydrated lime on the floor. Next, Integration members contacted Mark Trammel and let him know what they had discovered. They decided that the Shift Supervisor should be made aware of the situation if he had not been made aware yet. At approximately 1530 hours, Integration members and Mark Trammel contacted the Shift Supervisor on duty. The Shift Supervisor was unware of any spill or leaks that had taken place in the scrubber area that day. | Brady Sowell | Alexander Taybah | FALSE | Sooner Power Plant | FALSE |  | FALSE | Operations |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah | Jesse Murray | High |  |  |  |  | 5.05 Misunderstood directions | [8 empty] | 14.02.5 Inadequate communication of standards: reinforcing with signs, color codes |  |  | Member got on the 2B Train "B" weigh bin instead of 2B Train "A" weigh bin and tried to unplug the blockage. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | I Approve. Jesse Murray | Approved by Brady Sowell on 5/7/2019 | [24 empty] | TRUE |  |  | 2018-07-16 | 1978-10-06 |  | 2019-03-25 06:00 | 0 | 0 | Member did not suffer any injury, although he dusted lime off of clothing and rinsed hands and face. | FALSE | Male |  |  | TRUE | Shawn Richardson |  | Uninjured | Shawn Richardson | [6 empty] | FALSE | Shawn Richardson | Plant Operator I |  |  |  |  | Marc Hodgson |  |  | 3/25/2019 6:00:00 AM | 8 months | FALSE | [28 empty] | NA
8782 | Sooner Power Plant | 2019-03-25 11:30 | Member was radioed by Control Operator and told that the BB hydrated lime weigh bin was plugged. Member then went to the scrubber area to unplug bin. Upon getting to location member proceeded to unplug AB bin which was not the correct bin. Hydrated lime was discharged from clean out port. No injuries occurred. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Jesse, Sooner would like to have the following members assigned to the investigation team for incident 8782. Alex Taybah Marc Hodgson Brady Sowell Jim Griffith | 2019-05-02 15:02 | Power Supply | Marc Hodgson | 2019-05-24 14:20 | 2019-03-26 12:01 | 2019-04-23 16:57 | 2019-05-06 12:14 | 2019-04-08 11:30 | 2019-03-26 11:14 | 2019-05-12 23:25 | 2019-05-22 10:19 | 2019-05-07 07:20 | Sooner Plant Unit 2 Scrubber Hydrated Lime Feeders area 1000 foot elevation of scrubber |  |  | Donnie Jones | I approve | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Alexander Taybah |  | On March 25, 2019 at about 1145 hours, Control Operator contacted Scrubber operator stating that on unit 2 B train, B hydrated lime feeder was plugged. Scrubber operator responded letting the Control operator know that he would head that way to unplug the feeder. Control operator than stated that he had placed the fill valve (2-li-fv-5000bb) in manual so it would not open. When the scrubber operator approached the weigh bin area he began to rod out what he assumed was the correct feeder. He did not communicate back to the Control operator that he was on the correct feeder. After about 20 minutes the Control Operator asked Scrubber operator if he was done cleaning the feeder comminuted back to Control Operator that he was done and the feeder should be feeding. At approximately, 1400 hours on this day OPC contacted Rick Wood (OGE) about a hydrate lime spill/leak. Rick then contacted the operations integration members to investigate. They went up to the hydrated lime feeder level and found lime on the flashing above the bottom clean out port on AB feeder (which was the incorrect feeder). They also discovered abnormal amounts of hydrated lime on the hand rails, grating, beams, cable trays, cement approximately 20 feet from the feeder. It is estimated that about 200-400 pounds of hydrated lime was discharged from the feeder. They also inspected the ground level and noted that there was approximately ¼ to ½ inch of hydrated lime on the floor. Next, Integration members contacted Mark Trammel and let him know what they had discovered. They decided that the Shift Supervisor should be made aware of the situation if he had not been made aware yet. At approximately 1530 hours, Integration members and Mark Trammel contacted the Shift Supervisor on duty. The Shift Supervisor was unware of any spill or leaks that had taken place in the scrubber area that day. | Brady Sowell | Alexander Taybah | FALSE | Sooner Power Plant | FALSE |  | FALSE | Operations |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness | [8 empty] | 14.02.4 Inadequate communication of standards: training |  |  | Member got on the 2B Train "B" weigh bin instead of 2B Train "A" weigh bin and tried to unplug the blockage. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | I Approve. Jesse Murray | Approved by Brady Sowell on 5/7/2019 | [24 empty] | TRUE |  |  | 2018-07-16 | 1978-10-06 |  | 2019-03-25 06:00 | 0 | 0 | Member did not suffer any injury, although he dusted lime off of clothing and rinsed hands and face. | FALSE | Male |  |  | TRUE | Shawn Richardson |  | Uninjured | Shawn Richardson | [6 empty] | FALSE | Shawn Richardson | Plant Operator I |  |  |  |  | Marc Hodgson |  |  | 3/25/2019 6:00:00 AM | 8 months | FALSE | [28 empty] | NA
8782 | Sooner Power Plant | 2019-03-25 11:30 | Member was radioed by Control Operator and told that the BB hydrated lime weigh bin was plugged. Member then went to the scrubber area to unplug bin. Upon getting to location member proceeded to unplug AB bin which was not the correct bin. Hydrated lime was discharged from clean out port. No injuries occurred. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Jesse, Sooner would like to have the following members assigned to the investigation team for incident 8782. Alex Taybah Marc Hodgson Brady Sowell Jim Griffith | 2019-05-02 15:02 | Power Supply | Marc Hodgson | 2019-05-24 14:20 | 2019-03-26 12:01 | 2019-04-23 16:57 | 2019-05-06 12:14 | 2019-04-08 11:30 | 2019-03-26 11:14 | 2019-05-12 23:25 | 2019-05-22 10:19 | 2019-05-07 07:20 | Sooner Plant Unit 2 Scrubber Hydrated Lime Feeders area 1000 foot elevation of scrubber |  |  | Donnie Jones | I approve | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Alexander Taybah |  | On March 25, 2019 at about 1145 hours, Control Operator contacted Scrubber operator stating that on unit 2 B train, B hydrated lime feeder was plugged. Scrubber operator responded letting the Control operator know that he would head that way to unplug the feeder. Control operator than stated that he had placed the fill valve (2-li-fv-5000bb) in manual so it would not open. When the scrubber operator approached the weigh bin area he began to rod out what he assumed was the correct feeder. He did not communicate back to the Control operator that he was on the correct feeder. After about 20 minutes the Control Operator asked Scrubber operator if he was done cleaning the feeder comminuted back to Control Operator that he was done and the feeder should be feeding. At approximately, 1400 hours on this day OPC contacted Rick Wood (OGE) about a hydrate lime spill/leak. Rick then contacted the operations integration members to investigate. They went up to the hydrated lime feeder level and found lime on the flashing above the bottom clean out port on AB feeder (which was the incorrect feeder). They also discovered abnormal amounts of hydrated lime on the hand rails, grating, beams, cable trays, cement approximately 20 feet from the feeder. It is estimated that about 200-400 pounds of hydrated lime was discharged from the feeder. They also inspected the ground level and noted that there was approximately ¼ to ½ inch of hydrated lime on the floor. Next, Integration members contacted Mark Trammel and let him know what they had discovered. They decided that the Shift Supervisor should be made aware of the situation if he had not been made aware yet. At approximately 1530 hours, Integration members and Mark Trammel contacted the Shift Supervisor on duty. The Shift Supervisor was unware of any spill or leaks that had taken place in the scrubber area that day. | Brady Sowell | Alexander Taybah | FALSE | Sooner Power Plant | FALSE |  | FALSE | Operations |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness | [8 empty] | 14.02.5 Inadequate communication of standards: reinforcing with signs, color codes |  |  | Member got on the 2B Train "B" weigh bin instead of 2B Train "A" weigh bin and tried to unplug the blockage. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | I Approve. Jesse Murray | Approved by Brady Sowell on 5/7/2019 | [24 empty] | TRUE |  |  | 2018-07-16 | 1978-10-06 |  | 2019-03-25 06:00 | 0 | 0 | Member did not suffer any injury, although he dusted lime off of clothing and rinsed hands and face. | FALSE | Male |  |  | TRUE | Shawn Richardson |  | Uninjured | Shawn Richardson | [6 empty] | FALSE | Shawn Richardson | Plant Operator I |  |  |  |  | Marc Hodgson |  |  | 3/25/2019 6:00:00 AM | 8 months | FALSE | [28 empty] | NA
8782 | Sooner Power Plant | 2019-03-25 11:30 | Member was radioed by Control Operator and told that the BB hydrated lime weigh bin was plugged. Member then went to the scrubber area to unplug bin. Upon getting to location member proceeded to unplug AB bin which was not the correct bin. Hydrated lime was discharged from clean out port. No injuries occurred. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Jesse, Sooner would like to have the following members assigned to the investigation team for incident 8782. Alex Taybah Marc Hodgson Brady Sowell Jim Griffith | 2019-05-02 15:02 | Power Supply | Marc Hodgson | 2019-05-24 14:20 | 2019-03-26 12:01 | 2019-04-23 16:57 | 2019-05-06 12:14 | 2019-04-08 11:30 | 2019-03-26 11:14 | 2019-05-12 23:25 | 2019-05-22 10:19 | 2019-05-07 07:20 | Sooner Plant Unit 2 Scrubber Hydrated Lime Feeders area 1000 foot elevation of scrubber |  |  | Donnie Jones | I approve | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Alexander Taybah |  | On March 25, 2019 at about 1145 hours, Control Operator contacted Scrubber operator stating that on unit 2 B train, B hydrated lime feeder was plugged. Scrubber operator responded letting the Control operator know that he would head that way to unplug the feeder. Control operator than stated that he had placed the fill valve (2-li-fv-5000bb) in manual so it would not open. When the scrubber operator approached the weigh bin area he began to rod out what he assumed was the correct feeder. He did not communicate back to the Control operator that he was on the correct feeder. After about 20 minutes the Control Operator asked Scrubber operator if he was done cleaning the feeder comminuted back to Control Operator that he was done and the feeder should be feeding. At approximately, 1400 hours on this day OPC contacted Rick Wood (OGE) about a hydrate lime spill/leak. Rick then contacted the operations integration members to investigate. They went up to the hydrated lime feeder level and found lime on the flashing above the bottom clean out port on AB feeder (which was the incorrect feeder). They also discovered abnormal amounts of hydrated lime on the hand rails, grating, beams, cable trays, cement approximately 20 feet from the feeder. It is estimated that about 200-400 pounds of hydrated lime was discharged from the feeder. They also inspected the ground level and noted that there was approximately ¼ to ½ inch of hydrated lime on the floor. Next, Integration members contacted Mark Trammel and let him know what they had discovered. They decided that the Shift Supervisor should be made aware of the situation if he had not been made aware yet. At approximately 1530 hours, Integration members and Mark Trammel contacted the Shift Supervisor on duty. The Shift Supervisor was unware of any spill or leaks that had taken place in the scrubber area that day. | James Griffith | Alexander Taybah | FALSE | Sooner Power Plant | FALSE |  | FALSE | Operations |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah | Jesse Murray | High |  |  |  |  | 5.01 Lack of experience | [8 empty] | 14.02.4 Inadequate communication of standards: training |  |  | Member got on the 2B Train "B" weigh bin instead of 2B Train "A" weigh bin and tried to unplug the blockage. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | I Approve. Jesse Murray | Approved by Brady Sowell on 5/7/2019 | [24 empty] | TRUE |  |  | 2018-07-16 | 1978-10-06 |  | 2019-03-25 06:00 | 0 | 0 | Member did not suffer any injury, although he dusted lime off of clothing and rinsed hands and face. | FALSE | Male |  |  | TRUE | Shawn Richardson |  | Uninjured | Shawn Richardson | [6 empty] | FALSE | Shawn Richardson | Plant Operator I |  |  |  |  | Marc Hodgson |  |  | 3/25/2019 6:00:00 AM | 8 months | FALSE | [28 empty] | NA
8782 | Sooner Power Plant | 2019-03-25 11:30 | Member was radioed by Control Operator and told that the BB hydrated lime weigh bin was plugged. Member then went to the scrubber area to unplug bin. Upon getting to location member proceeded to unplug AB bin which was not the correct bin. Hydrated lime was discharged from clean out port. No injuries occurred. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Jesse, Sooner would like to have the following members assigned to the investigation team for incident 8782. Alex Taybah Marc Hodgson Brady Sowell Jim Griffith | 2019-05-02 15:02 | Power Supply | Marc Hodgson | 2019-05-24 14:20 | 2019-03-26 12:01 | 2019-04-23 16:57 | 2019-05-06 12:14 | 2019-04-08 11:30 | 2019-03-26 11:14 | 2019-05-12 23:25 | 2019-05-22 10:19 | 2019-05-07 07:20 | Sooner Plant Unit 2 Scrubber Hydrated Lime Feeders area 1000 foot elevation of scrubber |  |  | Donnie Jones | I approve | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Alexander Taybah |  | On March 25, 2019 at about 1145 hours, Control Operator contacted Scrubber operator stating that on unit 2 B train, B hydrated lime feeder was plugged. Scrubber operator responded letting the Control operator know that he would head that way to unplug the feeder. Control operator than stated that he had placed the fill valve (2-li-fv-5000bb) in manual so it would not open. When the scrubber operator approached the weigh bin area he began to rod out what he assumed was the correct feeder. He did not communicate back to the Control operator that he was on the correct feeder. After about 20 minutes the Control Operator asked Scrubber operator if he was done cleaning the feeder comminuted back to Control Operator that he was done and the feeder should be feeding. At approximately, 1400 hours on this day OPC contacted Rick Wood (OGE) about a hydrate lime spill/leak. Rick then contacted the operations integration members to investigate. They went up to the hydrated lime feeder level and found lime on the flashing above the bottom clean out port on AB feeder (which was the incorrect feeder). They also discovered abnormal amounts of hydrated lime on the hand rails, grating, beams, cable trays, cement approximately 20 feet from the feeder. It is estimated that about 200-400 pounds of hydrated lime was discharged from the feeder. They also inspected the ground level and noted that there was approximately ¼ to ½ inch of hydrated lime on the floor. Next, Integration members contacted Mark Trammel and let him know what they had discovered. They decided that the Shift Supervisor should be made aware of the situation if he had not been made aware yet. At approximately 1530 hours, Integration members and Mark Trammel contacted the Shift Supervisor on duty. The Shift Supervisor was unware of any spill or leaks that had taken place in the scrubber area that day. | James Griffith | Alexander Taybah | FALSE | Sooner Power Plant | FALSE |  | FALSE | Operations |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah | Jesse Murray | High |  |  |  |  | 5.01 Lack of experience | [8 empty] | 14.02.5 Inadequate communication of standards: reinforcing with signs, color codes |  |  | Member got on the 2B Train "B" weigh bin instead of 2B Train "A" weigh bin and tried to unplug the blockage. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | I Approve. Jesse Murray | Approved by Brady Sowell on 5/7/2019 | [24 empty] | TRUE |  |  | 2018-07-16 | 1978-10-06 |  | 2019-03-25 06:00 | 0 | 0 | Member did not suffer any injury, although he dusted lime off of clothing and rinsed hands and face. | FALSE | Male |  |  | TRUE | Shawn Richardson |  | Uninjured | Shawn Richardson | [6 empty] | FALSE | Shawn Richardson | Plant Operator I |  |  |  |  | Marc Hodgson |  |  | 3/25/2019 6:00:00 AM | 8 months | FALSE | [28 empty] | NA
8782 | Sooner Power Plant | 2019-03-25 11:30 | Member was radioed by Control Operator and told that the BB hydrated lime weigh bin was plugged. Member then went to the scrubber area to unplug bin. Upon getting to location member proceeded to unplug AB bin which was not the correct bin. Hydrated lime was discharged from clean out port. No injuries occurred. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Jesse, Sooner would like to have the following members assigned to the investigation team for incident 8782. Alex Taybah Marc Hodgson Brady Sowell Jim Griffith | 2019-05-02 15:02 | Power Supply | Marc Hodgson | 2019-05-24 14:20 | 2019-03-26 12:01 | 2019-04-23 16:57 | 2019-05-06 12:14 | 2019-04-08 11:30 | 2019-03-26 11:14 | 2019-05-12 23:25 | 2019-05-22 10:19 | 2019-05-07 07:20 | Sooner Plant Unit 2 Scrubber Hydrated Lime Feeders area 1000 foot elevation of scrubber |  |  | Donnie Jones | I approve | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Alexander Taybah |  | On March 25, 2019 at about 1145 hours, Control Operator contacted Scrubber operator stating that on unit 2 B train, B hydrated lime feeder was plugged. Scrubber operator responded letting the Control operator know that he would head that way to unplug the feeder. Control operator than stated that he had placed the fill valve (2-li-fv-5000bb) in manual so it would not open. When the scrubber operator approached the weigh bin area he began to rod out what he assumed was the correct feeder. He did not communicate back to the Control operator that he was on the correct feeder. After about 20 minutes the Control Operator asked Scrubber operator if he was done cleaning the feeder comminuted back to Control Operator that he was done and the feeder should be feeding. At approximately, 1400 hours on this day OPC contacted Rick Wood (OGE) about a hydrate lime spill/leak. Rick then contacted the operations integration members to investigate. They went up to the hydrated lime feeder level and found lime on the flashing above the bottom clean out port on AB feeder (which was the incorrect feeder). They also discovered abnormal amounts of hydrated lime on the hand rails, grating, beams, cable trays, cement approximately 20 feet from the feeder. It is estimated that about 200-400 pounds of hydrated lime was discharged from the feeder. They also inspected the ground level and noted that there was approximately ¼ to ½ inch of hydrated lime on the floor. Next, Integration members contacted Mark Trammel and let him know what they had discovered. They decided that the Shift Supervisor should be made aware of the situation if he had not been made aware yet. At approximately 1530 hours, Integration members and Mark Trammel contacted the Shift Supervisor on duty. The Shift Supervisor was unware of any spill or leaks that had taken place in the scrubber area that day. | James Griffith | Alexander Taybah | FALSE | Sooner Power Plant | FALSE |  | FALSE | Operations |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah | Jesse Murray | High |  |  |  |  | 5.05 Misunderstood directions | [8 empty] | 14.02.4 Inadequate communication of standards: training |  |  | Member got on the 2B Train "B" weigh bin instead of 2B Train "A" weigh bin and tried to unplug the blockage. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | I Approve. Jesse Murray | Approved by Brady Sowell on 5/7/2019 | [24 empty] | TRUE |  |  | 2018-07-16 | 1978-10-06 |  | 2019-03-25 06:00 | 0 | 0 | Member did not suffer any injury, although he dusted lime off of clothing and rinsed hands and face. | FALSE | Male |  |  | TRUE | Shawn Richardson |  | Uninjured | Shawn Richardson | [6 empty] | FALSE | Shawn Richardson | Plant Operator I |  |  |  |  | Marc Hodgson |  |  | 3/25/2019 6:00:00 AM | 8 months | FALSE | [28 empty] | NA
8782 | Sooner Power Plant | 2019-03-25 11:30 | Member was radioed by Control Operator and told that the BB hydrated lime weigh bin was plugged. Member then went to the scrubber area to unplug bin. Upon getting to location member proceeded to unplug AB bin which was not the correct bin. Hydrated lime was discharged from clean out port. No injuries occurred. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Jesse, Sooner would like to have the following members assigned to the investigation team for incident 8782. Alex Taybah Marc Hodgson Brady Sowell Jim Griffith | 2019-05-02 15:02 | Power Supply | Marc Hodgson | 2019-05-24 14:20 | 2019-03-26 12:01 | 2019-04-23 16:57 | 2019-05-06 12:14 | 2019-04-08 11:30 | 2019-03-26 11:14 | 2019-05-12 23:25 | 2019-05-22 10:19 | 2019-05-07 07:20 | Sooner Plant Unit 2 Scrubber Hydrated Lime Feeders area 1000 foot elevation of scrubber |  |  | Donnie Jones | I approve | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Alexander Taybah |  | On March 25, 2019 at about 1145 hours, Control Operator contacted Scrubber operator stating that on unit 2 B train, B hydrated lime feeder was plugged. Scrubber operator responded letting the Control operator know that he would head that way to unplug the feeder. Control operator than stated that he had placed the fill valve (2-li-fv-5000bb) in manual so it would not open. When the scrubber operator approached the weigh bin area he began to rod out what he assumed was the correct feeder. He did not communicate back to the Control operator that he was on the correct feeder. After about 20 minutes the Control Operator asked Scrubber operator if he was done cleaning the feeder comminuted back to Control Operator that he was done and the feeder should be feeding. At approximately, 1400 hours on this day OPC contacted Rick Wood (OGE) about a hydrate lime spill/leak. Rick then contacted the operations integration members to investigate. They went up to the hydrated lime feeder level and found lime on the flashing above the bottom clean out port on AB feeder (which was the incorrect feeder). They also discovered abnormal amounts of hydrated lime on the hand rails, grating, beams, cable trays, cement approximately 20 feet from the feeder. It is estimated that about 200-400 pounds of hydrated lime was discharged from the feeder. They also inspected the ground level and noted that there was approximately ¼ to ½ inch of hydrated lime on the floor. Next, Integration members contacted Mark Trammel and let him know what they had discovered. They decided that the Shift Supervisor should be made aware of the situation if he had not been made aware yet. At approximately 1530 hours, Integration members and Mark Trammel contacted the Shift Supervisor on duty. The Shift Supervisor was unware of any spill or leaks that had taken place in the scrubber area that day. | James Griffith | Alexander Taybah | FALSE | Sooner Power Plant | FALSE |  | FALSE | Operations |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah | Jesse Murray | High |  |  |  |  | 5.05 Misunderstood directions | [8 empty] | 14.02.5 Inadequate communication of standards: reinforcing with signs, color codes |  |  | Member got on the 2B Train "B" weigh bin instead of 2B Train "A" weigh bin and tried to unplug the blockage. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | I Approve. Jesse Murray | Approved by Brady Sowell on 5/7/2019 | [24 empty] | TRUE |  |  | 2018-07-16 | 1978-10-06 |  | 2019-03-25 06:00 | 0 | 0 | Member did not suffer any injury, although he dusted lime off of clothing and rinsed hands and face. | FALSE | Male |  |  | TRUE | Shawn Richardson |  | Uninjured | Shawn Richardson | [6 empty] | FALSE | Shawn Richardson | Plant Operator I |  |  |  |  | Marc Hodgson |  |  | 3/25/2019 6:00:00 AM | 8 months | FALSE | [28 empty] | NA
8782 | Sooner Power Plant | 2019-03-25 11:30 | Member was radioed by Control Operator and told that the BB hydrated lime weigh bin was plugged. Member then went to the scrubber area to unplug bin. Upon getting to location member proceeded to unplug AB bin which was not the correct bin. Hydrated lime was discharged from clean out port. No injuries occurred. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Jesse, Sooner would like to have the following members assigned to the investigation team for incident 8782. Alex Taybah Marc Hodgson Brady Sowell Jim Griffith | 2019-05-02 15:02 | Power Supply | Marc Hodgson | 2019-05-24 14:20 | 2019-03-26 12:01 | 2019-04-23 16:57 | 2019-05-06 12:14 | 2019-04-08 11:30 | 2019-03-26 11:14 | 2019-05-12 23:25 | 2019-05-22 10:19 | 2019-05-07 07:20 | Sooner Plant Unit 2 Scrubber Hydrated Lime Feeders area 1000 foot elevation of scrubber |  |  | Donnie Jones | I approve | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Alexander Taybah |  | On March 25, 2019 at about 1145 hours, Control Operator contacted Scrubber operator stating that on unit 2 B train, B hydrated lime feeder was plugged. Scrubber operator responded letting the Control operator know that he would head that way to unplug the feeder. Control operator than stated that he had placed the fill valve (2-li-fv-5000bb) in manual so it would not open. When the scrubber operator approached the weigh bin area he began to rod out what he assumed was the correct feeder. He did not communicate back to the Control operator that he was on the correct feeder. After about 20 minutes the Control Operator asked Scrubber operator if he was done cleaning the feeder comminuted back to Control Operator that he was done and the feeder should be feeding. At approximately, 1400 hours on this day OPC contacted Rick Wood (OGE) about a hydrate lime spill/leak. Rick then contacted the operations integration members to investigate. They went up to the hydrated lime feeder level and found lime on the flashing above the bottom clean out port on AB feeder (which was the incorrect feeder). They also discovered abnormal amounts of hydrated lime on the hand rails, grating, beams, cable trays, cement approximately 20 feet from the feeder. It is estimated that about 200-400 pounds of hydrated lime was discharged from the feeder. They also inspected the ground level and noted that there was approximately ¼ to ½ inch of hydrated lime on the floor. Next, Integration members contacted Mark Trammel and let him know what they had discovered. They decided that the Shift Supervisor should be made aware of the situation if he had not been made aware yet. At approximately 1530 hours, Integration members and Mark Trammel contacted the Shift Supervisor on duty. The Shift Supervisor was unware of any spill or leaks that had taken place in the scrubber area that day. | James Griffith | Alexander Taybah | FALSE | Sooner Power Plant | FALSE |  | FALSE | Operations |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness | [8 empty] | 14.02.4 Inadequate communication of standards: training |  |  | Member got on the 2B Train "B" weigh bin instead of 2B Train "A" weigh bin and tried to unplug the blockage. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | I Approve. Jesse Murray | Approved by Brady Sowell on 5/7/2019 | [24 empty] | TRUE |  |  | 2018-07-16 | 1978-10-06 |  | 2019-03-25 06:00 | 0 | 0 | Member did not suffer any injury, although he dusted lime off of clothing and rinsed hands and face. | FALSE | Male |  |  | TRUE | Shawn Richardson |  | Uninjured | Shawn Richardson | [6 empty] | FALSE | Shawn Richardson | Plant Operator I |  |  |  |  | Marc Hodgson |  |  | 3/25/2019 6:00:00 AM | 8 months | FALSE | [28 empty] | NA
8782 | Sooner Power Plant | 2019-03-25 11:30 | Member was radioed by Control Operator and told that the BB hydrated lime weigh bin was plugged. Member then went to the scrubber area to unplug bin. Upon getting to location member proceeded to unplug AB bin which was not the correct bin. Hydrated lime was discharged from clean out port. No injuries occurred. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Jesse, Sooner would like to have the following members assigned to the investigation team for incident 8782. Alex Taybah Marc Hodgson Brady Sowell Jim Griffith | 2019-05-02 15:02 | Power Supply | Marc Hodgson | 2019-05-24 14:20 | 2019-03-26 12:01 | 2019-04-23 16:57 | 2019-05-06 12:14 | 2019-04-08 11:30 | 2019-03-26 11:14 | 2019-05-12 23:25 | 2019-05-22 10:19 | 2019-05-07 07:20 | Sooner Plant Unit 2 Scrubber Hydrated Lime Feeders area 1000 foot elevation of scrubber |  |  | Donnie Jones | I approve | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Alexander Taybah |  | On March 25, 2019 at about 1145 hours, Control Operator contacted Scrubber operator stating that on unit 2 B train, B hydrated lime feeder was plugged. Scrubber operator responded letting the Control operator know that he would head that way to unplug the feeder. Control operator than stated that he had placed the fill valve (2-li-fv-5000bb) in manual so it would not open. When the scrubber operator approached the weigh bin area he began to rod out what he assumed was the correct feeder. He did not communicate back to the Control operator that he was on the correct feeder. After about 20 minutes the Control Operator asked Scrubber operator if he was done cleaning the feeder comminuted back to Control Operator that he was done and the feeder should be feeding. At approximately, 1400 hours on this day OPC contacted Rick Wood (OGE) about a hydrate lime spill/leak. Rick then contacted the operations integration members to investigate. They went up to the hydrated lime feeder level and found lime on the flashing above the bottom clean out port on AB feeder (which was the incorrect feeder). They also discovered abnormal amounts of hydrated lime on the hand rails, grating, beams, cable trays, cement approximately 20 feet from the feeder. It is estimated that about 200-400 pounds of hydrated lime was discharged from the feeder. They also inspected the ground level and noted that there was approximately ¼ to ½ inch of hydrated lime on the floor. Next, Integration members contacted Mark Trammel and let him know what they had discovered. They decided that the Shift Supervisor should be made aware of the situation if he had not been made aware yet. At approximately 1530 hours, Integration members and Mark Trammel contacted the Shift Supervisor on duty. The Shift Supervisor was unware of any spill or leaks that had taken place in the scrubber area that day. | James Griffith | Alexander Taybah | FALSE | Sooner Power Plant | FALSE |  | FALSE | Operations |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness | [8 empty] | 14.02.5 Inadequate communication of standards: reinforcing with signs, color codes |  |  | Member got on the 2B Train "B" weigh bin instead of 2B Train "A" weigh bin and tried to unplug the blockage. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | I Approve. Jesse Murray | Approved by Brady Sowell on 5/7/2019 | [24 empty] | TRUE |  |  | 2018-07-16 | 1978-10-06 |  | 2019-03-25 06:00 | 0 | 0 | Member did not suffer any injury, although he dusted lime off of clothing and rinsed hands and face. | FALSE | Male |  |  | TRUE | Shawn Richardson |  | Uninjured | Shawn Richardson | [6 empty] | FALSE | Shawn Richardson | Plant Operator I |  |  |  |  | Marc Hodgson |  |  | 3/25/2019 6:00:00 AM | 8 months | FALSE | [28 empty] | NA
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.03 Infrequent performance | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  | 13.03 Inadequate standards or specifications | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules | 15.06 Use by unqualified or untrained people |  | Sensing line was unknowingly isolated Inconsistency in trailer design | 06. Using Defective Equipment | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.03 Infrequent performance | 7.11 Improper supervisory example |  | 9.12 Inadequate performance measurement and evaluation |  |  |  | 13.03 Inadequate standards or specifications | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules | 15.06 Use by unqualified or untrained people |  | Sensing line was unknowingly isolated Inconsistency in trailer design | 06. Using Defective Equipment | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  | 13.03 Inadequate standards or specifications | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules | 15.06 Use by unqualified or untrained people |  | Sensing line was unknowingly isolated Inconsistency in trailer design | 06. Using Defective Equipment | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.12 Inadequate performance measurement and evaluation |  |  |  | 13.03 Inadequate standards or specifications | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules | 15.06 Use by unqualified or untrained people |  | Sensing line was unknowingly isolated Inconsistency in trailer design | 06. Using Defective Equipment | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.02 Inadequate practice | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  | 13.03 Inadequate standards or specifications | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules | 15.06 Use by unqualified or untrained people |  | Sensing line was unknowingly isolated Inconsistency in trailer design | 06. Using Defective Equipment | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.02 Inadequate practice | 7.11 Improper supervisory example |  | 9.12 Inadequate performance measurement and evaluation |  |  |  | 13.03 Inadequate standards or specifications | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules | 15.06 Use by unqualified or untrained people |  | Sensing line was unknowingly isolated Inconsistency in trailer design | 06. Using Defective Equipment | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.03 Infrequent performance | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  | 13.03 Inadequate standards or specifications | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules | 15.06 Use by unqualified or untrained people |  | Sensing line was unknowingly isolated Inconsistency in trailer design | 06. Using Defective Equipment | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.03 Infrequent performance | 7.11 Improper supervisory example |  | 9.12 Inadequate performance measurement and evaluation |  |  |  | 13.03 Inadequate standards or specifications | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules | 15.06 Use by unqualified or untrained people |  | Sensing line was unknowingly isolated Inconsistency in trailer design | 06. Using Defective Equipment | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  | 13.03 Inadequate standards or specifications | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules | 15.06 Use by unqualified or untrained people |  | Sensing line was unknowingly isolated Inconsistency in trailer design | 06. Using Defective Equipment | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.12 Inadequate performance measurement and evaluation |  |  |  | 13.03 Inadequate standards or specifications | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules | 15.06 Use by unqualified or untrained people |  | Sensing line was unknowingly isolated Inconsistency in trailer design | 06. Using Defective Equipment | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.02 Inadequate practice | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  | 13.03 Inadequate standards or specifications | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules | 15.06 Use by unqualified or untrained people |  | Sensing line was unknowingly isolated Inconsistency in trailer design | 06. Using Defective Equipment | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.02 Inadequate practice | 7.11 Improper supervisory example |  | 9.12 Inadequate performance measurement and evaluation |  |  |  | 13.03 Inadequate standards or specifications | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules | 15.06 Use by unqualified or untrained people |  | Sensing line was unknowingly isolated Inconsistency in trailer design | 06. Using Defective Equipment | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  | 13.03 Inadequate standards or specifications | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules | 15.06 Use by unqualified or untrained people |  | Sensing line was unknowingly isolated Inconsistency in trailer design | 06. Using Defective Equipment | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance | 7.11 Improper supervisory example |  | 9.12 Inadequate performance measurement and evaluation |  |  |  | 13.03 Inadequate standards or specifications | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules | 15.06 Use by unqualified or untrained people |  | Sensing line was unknowingly isolated Inconsistency in trailer design | 06. Using Defective Equipment | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  | 13.03 Inadequate standards or specifications | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules | 15.06 Use by unqualified or untrained people |  | Sensing line was unknowingly isolated Inconsistency in trailer design | 06. Using Defective Equipment | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.12 Inadequate performance measurement and evaluation |  |  |  | 13.03 Inadequate standards or specifications | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules | 15.06 Use by unqualified or untrained people |  | Sensing line was unknowingly isolated Inconsistency in trailer design | 06. Using Defective Equipment | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.02 Inadequate practice | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  | 13.03 Inadequate standards or specifications | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules | 15.06 Use by unqualified or untrained people |  | Sensing line was unknowingly isolated Inconsistency in trailer design | 06. Using Defective Equipment | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.02 Inadequate practice | 7.11 Improper supervisory example |  | 9.12 Inadequate performance measurement and evaluation |  |  |  | 13.03 Inadequate standards or specifications | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules | 15.06 Use by unqualified or untrained people |  | Sensing line was unknowingly isolated Inconsistency in trailer design | 06. Using Defective Equipment | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching |  |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  | 16.03. Inadequate communication between different organizations | • Lack of adequate training • Contractor had only been on job 2 weeks | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching |  |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.03. Inadequate communication between different organizations | • Lack of adequate training • Contractor had only been on job 2 weeks | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching |  |  | 9.11 Inadequate matching of individual qualifications and job/task requirements |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  | 16.03. Inadequate communication between different organizations | • Lack of adequate training • Contractor had only been on job 2 weeks | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching |  |  | 9.11 Inadequate matching of individual qualifications and job/task requirements |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.03. Inadequate communication between different organizations | • Lack of adequate training • Contractor had only been on job 2 weeks | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  | 16.03. Inadequate communication between different organizations | • Lack of adequate training • Contractor had only been on job 2 weeks | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.03. Inadequate communication between different organizations | • Lack of adequate training • Contractor had only been on job 2 weeks | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.02 Inadequate practice |  |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  | 16.03. Inadequate communication between different organizations | • Lack of adequate training • Contractor had only been on job 2 weeks | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.02 Inadequate practice |  |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.03. Inadequate communication between different organizations | • Lack of adequate training • Contractor had only been on job 2 weeks | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.02 Inadequate practice |  |  | 9.11 Inadequate matching of individual qualifications and job/task requirements |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  | 16.03. Inadequate communication between different organizations | • Lack of adequate training • Contractor had only been on job 2 weeks | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.02 Inadequate practice |  |  | 9.11 Inadequate matching of individual qualifications and job/task requirements |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.03. Inadequate communication between different organizations | • Lack of adequate training • Contractor had only been on job 2 weeks | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.02 Inadequate practice |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  | 16.03. Inadequate communication between different organizations | • Lack of adequate training • Contractor had only been on job 2 weeks | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.02 Inadequate practice |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.03. Inadequate communication between different organizations | • Lack of adequate training • Contractor had only been on job 2 weeks | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.04 Lack of coaching |  |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  | 16.03. Inadequate communication between different organizations | • Lack of adequate training • Contractor had only been on job 2 weeks | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.04 Lack of coaching |  |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.03. Inadequate communication between different organizations | • Lack of adequate training • Contractor had only been on job 2 weeks | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.04 Lack of coaching |  |  | 9.11 Inadequate matching of individual qualifications and job/task requirements |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  | 16.03. Inadequate communication between different organizations | • Lack of adequate training • Contractor had only been on job 2 weeks | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.04 Lack of coaching |  |  | 9.11 Inadequate matching of individual qualifications and job/task requirements |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.03. Inadequate communication between different organizations | • Lack of adequate training • Contractor had only been on job 2 weeks | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.04 Lack of coaching |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  | 16.03. Inadequate communication between different organizations | • Lack of adequate training • Contractor had only been on job 2 weeks | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.04 Lack of coaching |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.03. Inadequate communication between different organizations | • Lack of adequate training • Contractor had only been on job 2 weeks | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.02 Inadequate practice |  |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  | 16.03. Inadequate communication between different organizations | • Lack of adequate training • Contractor had only been on job 2 weeks | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.02 Inadequate practice |  |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.03. Inadequate communication between different organizations | • Lack of adequate training • Contractor had only been on job 2 weeks | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.02 Inadequate practice |  |  | 9.11 Inadequate matching of individual qualifications and job/task requirements |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  | 16.03. Inadequate communication between different organizations | • Lack of adequate training • Contractor had only been on job 2 weeks | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.02 Inadequate practice |  |  | 9.11 Inadequate matching of individual qualifications and job/task requirements |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.03. Inadequate communication between different organizations | • Lack of adequate training • Contractor had only been on job 2 weeks | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.02 Inadequate practice |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  | 16.03. Inadequate communication between different organizations | • Lack of adequate training • Contractor had only been on job 2 weeks | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8783 | Sooner Power Plant | 2019-03-26 12:30 | JRT Pebble lime truck driver, unhooked from silo with line still pressurized. Pebble lime discharged from truck line coming into contact with JRT driver. Driver recieved minor burns around his wrists. Truck Driver was wearing his PPE. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Marc Hodgson | 2019-05-02 12:56 | 2019-03-26 15:20 | 2019-03-26 15:20 | 2019-04-08 14:18 | 2019-04-09 12:30 | 2019-03-26 14:55 | 2019-04-13 10:08 |  | 2019-04-09 16:00 | Sooner Plant Scrubber Pebble Lime silo, west FGD Byproduct silo. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | SEQUENCE OF EVENTS On March 25th of 2019, at approximately 1200 hours JRT Driver was exposed to pebble lime causing minor burns to his wrists. Driver came on site at approximately 0900 hours after checking in with operations to start off loading pebble lime. At approximately 1100 hours OGE operator contacted Integration team member as this driver had plugged his line several times in the previous two hours. OGE operator was able to help get the JRT truck line unplugged. Then about 1145 hours JRT driver contacted operations to notify them that he was finished off loading. Integration team member went to the pebble lime silo to verify that the driver had zero line pressure and then gave the go head to unhook his hose from the silo. Integration team member then left to continue his duties in the plant. About 5 minutes after Integration member left he was contacted by the Control Room Operator that the driver had contacted him stating that he had a lime spill. Integration team member then when back to the truck and discovered that while the gauges were reading zero, the driver had not completely finished blowing off all his pebble lime. After investigating the situation Integration Team Member verified that the lime spill indeed was from the line plugage from the truck as the silo was still holding a vacuum at this time. After looking over the pneumatic trailer in more detail, even though OGE operations has NO formal training in this area. Integration team member noted that the sensing line for the gauge was not in proper place and with the valving that was in place the gauge would always read ZERO. The sensing line was on the depressurized side of the valve (NOTE: See Attached Pictures for Detailed Explanation). Integration team member then contacted the OGE Safety Professional to have him come to the area to witness the situation. However, before Integration team left to go pick up Safety Professional he told the driver to stay put and not to touch anything. Upon their arrival back to the area they noticed that the driver had used the eye wash station. At this point Shift Supervisor was contacted asking him to notify a rescue team member to go to the area to check on the JRT driver. Rescue team members arrived at site to assess the driver, noting that he had minor burns to his wrists. They interviewed the patient and treated one wrist with burn cream, he then stated that the other wrist was starting to have some pain so they also treated it as well. They continued to monitor the patient and he stated that the pain and burning feeling was going away. After, a period of time the driver stated that he no longer had any pain and did not need any more assistance and was released by the rescue team members. FINDINGS • Sensing line was unknowingly isolated • Lack of adequate training • Inconsistency in trailer design • Contractor had only been on job 2 weeks • No Chemical training for pebble lime for contractors • Contractor was unware of issues that drivers were having at site, due to lack of commutation every time a line plugs. • Previous corrective actions were not being followed (Note: SWP was not filled out) • Not taking the time to properly situate trailer to off load |  |  |  | Sooner Power Plant | FALSE | Burn: Chemical | FALSE | Other |  | James Griffith | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.02 Inadequate practice |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.03. Inadequate communication between different organizations | • Lack of adequate training • Contractor had only been on job 2 weeks | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 4/9/2019 |  |  |  | Injury / Illness |  | Marc Hodgson |  | burn | TRUE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Griffith | JRT Trucking | tyler fitzgerald | Burn: Chemical |  | Wrist | Marc Trammell | Multiple | FALSE | [69 empty] | none
8784 | Ft Smith Service Center | 2019-03-22 15:00 | Public vehicle struck tree contractor crew member | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Elizabeth Mason-Reynolds | 2019-05-10 10:44 | 2019-03-27 10:53 | 2019-03-27 10:53 | 2019-04-07 15:01 | 2019-04-05 15:00 | 2019-03-27 10:43 | 2019-04-29 09:06 |  | 2019-04-12 13:10 | 3117 State Line Rd., Ft. Smith, AR 72916 |  |  | William Young | Reviewed and approved. WCY | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Elizabeth Mason-Reynolds |  | On Friday the 22nd day of March, 2019, at approximately 3:00pm, a crew was chipping brush alongside State Line road when a vehicle passing southbound through the work zone hit Bobby Marlette as he was pulling brush. Marlette's hire date is 2/20/2019 and had completed training in Aerial Rescue, First Aid, CPR/AED, Hardware Identification, JSA and PowerSafe Training. The crew was working on the downslope of a small hill, in which they successfully established their work zone with proper warning signage and cone placement, along with a flagger located on top of the hill directing traffic. Marlette was wearing hearing protection and the chipper was running. Marlette was pulling brush from roadside and was at the left edge of the work zone. After the driver of the vehicle failed to yield and reduce speed upon entering the work zone, the driver hit Marlette with her driver side mirror. This caused Marlette to spin and fall to the ground, where the vehicle’s rear tire then ran over his right foot. The crew contacted the appropriate authorities and waited for their arrival. Marlette was then taken to Mercy Hospital ER by West Tree’s Regional General Foreman, where he was diagnosed and treated for four broken bones in his right foot. Marlette was later referred to an Orthopedic Specialist and will remain off work until he is released for regular duty. As a result from this incident, the driver of the vehicle was cited for failure to yield and failure to reduce speed in a work zone |  |  |  | Ft Smith Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Elizabeth Mason-Reynolds | Elizabeth Mason-Reynolds |  |  | See comments in workflow. This event was a wake up call for crews working in Ft Smith area with narrow, winding roads and limited sight distances. Beth captured some great corrective actions and West Tree Management was very open to suggestions. West has definitely ramped up their safety effort in recent weeks as well as other training for their members. cassadjk |  |  | Medium |  |  |  |  | 5.01 Lack of experience | [7 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | Civilian vehicle failed to yield and reduce speed in properly marked work zone. | 04. Operating at Improper Speed | 2. Struck By (Hit By Moving Object) |  | 4/8/19: Supv. states worker had 4 hours intensive work zone training 1-month prior at time of hire so his experience was limited. Supv. considering a bull horn to signal worker when a car approaches at unsafe speed. Will also position buffer vehicles for control measure. Worker expected to be out 6-8 wks with 4 metatarsal breaks. West Safety Rep, Clint, to call back with description of footwear worn on day of accident. Steel/composite boots are a requirement per our Contractor Reference Guide. J. Looney 4/11/19: West, Eric Connor, confirmed that worker was wearing composite toe. Will consider metatarsal guards for work zones. |  |  |  | Injury / Illness |  | Elizabeth Mason-Reynolds |  | broken foot | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Elizabeth Mason-Reynolds | West Tree Service | Bobby Marlette | Fracture |  | Foot | Elizabeth Mason-Reynolds | Right | TRUE | Company Vehicle | [68 empty] | 9138024191- Arkoma cycle
8784 | Ft Smith Service Center | 2019-03-22 15:00 | Public vehicle struck tree contractor crew member | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Elizabeth Mason-Reynolds | 2019-05-10 10:44 | 2019-03-27 10:53 | 2019-03-27 10:53 | 2019-04-07 15:01 | 2019-04-05 15:00 | 2019-03-27 10:43 | 2019-04-29 09:06 |  | 2019-04-12 13:10 | 3117 State Line Rd., Ft. Smith, AR 72916 |  |  | William Young | Reviewed and approved. WCY | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Elizabeth Mason-Reynolds |  | On Friday the 22nd day of March, 2019, at approximately 3:00pm, a crew was chipping brush alongside State Line road when a vehicle passing southbound through the work zone hit Bobby Marlette as he was pulling brush. Marlette's hire date is 2/20/2019 and had completed training in Aerial Rescue, First Aid, CPR/AED, Hardware Identification, JSA and PowerSafe Training. The crew was working on the downslope of a small hill, in which they successfully established their work zone with proper warning signage and cone placement, along with a flagger located on top of the hill directing traffic. Marlette was wearing hearing protection and the chipper was running. Marlette was pulling brush from roadside and was at the left edge of the work zone. After the driver of the vehicle failed to yield and reduce speed upon entering the work zone, the driver hit Marlette with her driver side mirror. This caused Marlette to spin and fall to the ground, where the vehicle’s rear tire then ran over his right foot. The crew contacted the appropriate authorities and waited for their arrival. Marlette was then taken to Mercy Hospital ER by West Tree’s Regional General Foreman, where he was diagnosed and treated for four broken bones in his right foot. Marlette was later referred to an Orthopedic Specialist and will remain off work until he is released for regular duty. As a result from this incident, the driver of the vehicle was cited for failure to yield and failure to reduce speed in a work zone |  |  |  | Ft Smith Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Elizabeth Mason-Reynolds | Elizabeth Mason-Reynolds |  |  | See comments in workflow. This event was a wake up call for crews working in Ft Smith area with narrow, winding roads and limited sight distances. Beth captured some great corrective actions and West Tree Management was very open to suggestions. West has definitely ramped up their safety effort in recent weeks as well as other training for their members. cassadjk |  |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [7 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | Civilian vehicle failed to yield and reduce speed in properly marked work zone. | 04. Operating at Improper Speed | 2. Struck By (Hit By Moving Object) |  | 4/8/19: Supv. states worker had 4 hours intensive work zone training 1-month prior at time of hire so his experience was limited. Supv. considering a bull horn to signal worker when a car approaches at unsafe speed. Will also position buffer vehicles for control measure. Worker expected to be out 6-8 wks with 4 metatarsal breaks. West Safety Rep, Clint, to call back with description of footwear worn on day of accident. Steel/composite boots are a requirement per our Contractor Reference Guide. J. Looney 4/11/19: West, Eric Connor, confirmed that worker was wearing composite toe. Will consider metatarsal guards for work zones. |  |  |  | Injury / Illness |  | Elizabeth Mason-Reynolds |  | broken foot | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Elizabeth Mason-Reynolds | West Tree Service | Bobby Marlette | Fracture |  | Foot | Elizabeth Mason-Reynolds | Right | TRUE | Company Vehicle | [68 empty] | 9138024191- Arkoma cycle
8785 | Metro Service Center | 2019-03-26 14:30 | Member was operating an electrical pipe threading tool, threading 1 1/2 inch pipe. The tool caught hold of the pipe and the handle contacted member's knee and took him to the ground. Members knee was sore the next day, he does not wish to seek any medical attention at this time. OGE nurse was notified of the event. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Delivery | Kenny La Ferney | 2019-04-10 12:14 | 2019-03-27 13:19 | 2019-03-27 13:19 | 2019-04-05 10:50 | 2019-04-09 14:30 | 2019-03-27 11:00 | 2019-04-08 18:13 |  |  | Salt Creek Substation Construction site in Coalgate, OK |  |  | Cody Magby | Approve the investigation and corrective action. working with supervisor on new tool purchase to prevent future problems | T&D Ops |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Kenny La Ferney |  | Member was operating an electrical pipe threading tool, threading 1 1/2 inch pipe. The tool caught hold of the pipe and the handle contacted member's knee and took him to the ground. The incident was investigated onsite and determination was made to add a new threading device to tool inventory. New tool is a self contained unit that does not require person to try holding it against torque. It is operated with foot control while pipe is held in the threading unit instead of held on to. The piece of pipe being threaded can be purchased pre threaded but due to project deadline member decided to make the piece onsite instead of waiting on parts. There are some instances pipe will have to be threaded on site due to custom size. |  |  |  | Metro Service Center | FALSE |  | TRUE | Construction Services |  | David Rogers | Kenny La Ferney |  | Gary Lassley | The Supervisor and Foreman are looking for a newer/safer threader to replace threader on all three crews. This will be completed within 30 days. | Gary Lassley |  | Low | [9 empty] | 10.06 Inadequate or improper controls | 11.02 Inadequate research on materials/equipment |  | 13.01 Inadequate assessment of needs and risks |  |  |  | The tool does not have guards or barrier to prevent contact. No guards were removed, the tool was old and best technology at time of purchase. | 21. Inadequate Guards or Barriers | 6. Caught On (Snagged, Hung) | [92 empty] | 1646182
8786 | Central District Office | 2019-03-26 10:00 | While switching out bank 3 at Muskogee substation the center switch of 104M2 fell open due to a broken insulator. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Delivery | Joseph Manseau | 2019-07-23 10:59 | 2019-03-27 15:24 | 2019-03-27 15:24 | 2019-07-18 08:19 | 2019-04-09 10:00 | 2019-03-26 10:00 | 2019-07-23 09:27 |  | 2019-07-22 11:20 | 161KV yard of Muskogee substation |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Joseph Manseau |  | Operational Incident Summary On Tuesday; March 26th while performing switching at Muskogee substation an outage occurred on the 69Kv Bus 1 and 2 when the Transformer Bank 4 differential lockout relay operated tripping the 69kv breaker 4 and the 138kv breaker 104. Chain of Events: • A System maintenance crew arrived at Muskogee substation to switch out Transformer Bank 3 to allow for maintenance testing. o Maintenance foreman arrived on site and reviewed Switching Order S0472 in the control house. o The maintenance foreman then walked over to the crew located by transformer bank 3, conducted a tailboard and discussed the switching order with the crew members. • At the start of the tailboard two maintenance technician apprentices informed the maintenance foreman that they had noticed what appeared to be a broken switch when they arrived at the substation. . o The foreman informed them that it was probably just a normally open switch. • The foreman then contacted the TCC and let the operator know that he was ready to begin switching. o Step 1 of SWO S0472 “Open by SCADA Muskogee 3” was then executed by the TCC operator. • The 69kv PCB 4 and 138kv PCB 104 tripped open immediately after PCB 3 was opened by the TCC operator. o This caused an outage to both the 69kv Bus 1 and 2 • At this time the members of the maintenance crew went over to examine the reported switch. • Upon investigation it was discovered that one of the support insulators on A phase of Switch 104M2 had broken and that the blade was hanging down in an open position. o B and C Phase of the switch appeared to have no damage and were still in the closed position. o This switch was associated with Transformer Bank 4 and was not part of Switching Order S0472 which contained steps to switch out Transformer Bank 3 for maintenance. • It was determined that switching would be written and performed to isolate switch 104M2, leaving Transformer Bank 4 out of service, and to place Transformer Bank 3 back in service. Incident Facts Ascertained: • Substation Inspection performed on 3/8/2019 did not indicate there was a broken switch. • The two maintenance technician apprentice’s informed the foreman prior to performing any work or switching that there was what they perceived to be a broken switch within sight of their current location within the substation yard. o The foreman failed to investigate the suspected switch to determine its condition or the possible impact it could have on their switching or maintenance activities before executing SWO S0472. • The day after the incident while at the plant one of the maintenance technician apprentices’ had a discussion with a member of the plant. He informed the apprentice that the switch had been broken for a couple of weeks but was not reported. Causal Factors: • Switch 104M2 A phase support insulator broke which allowed the switch blade to fall open. An unbalance occurred on the current polarizing circuit on both Transformer 3 and 4 when the 69kv breaker 3 was opened by SCADA during switching. The opening of breaker 3 resulted in a greater unbalance on the Transformer 4 current circuit. This allowed the Tertiary Neutral Overcurrent tripping element 51N4T to time out which then operated the Primary and BU Lockout relays tripping Transformer 4. Opportunities for Improvement: • Improved communication between members working together to understand the impact and hazards associated with damaged equipment within the substation on their task. |  |  |  | Central District Office | FALSE |  | TRUE | PD Operations Services |  | Phillip Thomas | Joseph Manseau |  | James Hutchison | I have reviewed this incident, it's findings and corrective actions. I approve this report and the corrective action recommended. | James Hutchison |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Failure to identify the hazard of the broken switch. | 17. Failure to Identify Hazard, Risk | 9. Abnormal Operation |  | Approve the closure even though the report from vendor has not came back. cm
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.05 Inadequate review instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.05 Inadequate review instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.05 Inadequate review instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.05 Inadequate review instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.05 Inadequate review instruction |  |  | 9.03 Improper or insufficient delegation | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.05 Inadequate review instruction |  |  | 9.03 Improper or insufficient delegation | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.05 Inadequate review instruction |  |  | 9.03 Improper or insufficient delegation | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.05 Inadequate review instruction |  |  | 9.03 Improper or insufficient delegation | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.05 Inadequate review instruction |  |  | 9.07 Inadequate instructions, orientation and/or training | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.05 Inadequate review instruction |  |  | 9.07 Inadequate instructions, orientation and/or training | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.05 Inadequate review instruction |  |  | 9.07 Inadequate instructions, orientation and/or training | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.05 Inadequate review instruction |  |  | 9.07 Inadequate instructions, orientation and/or training | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.03 Infrequent performance |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.03 Infrequent performance |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.03 Infrequent performance |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.03 Infrequent performance |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.03 Infrequent performance |  |  | 9.03 Improper or insufficient delegation | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.03 Infrequent performance |  |  | 9.03 Improper or insufficient delegation | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.03 Infrequent performance |  |  | 9.03 Improper or insufficient delegation | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.03 Infrequent performance |  |  | 9.03 Improper or insufficient delegation | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.03 Infrequent performance |  |  | 9.07 Inadequate instructions, orientation and/or training | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.03 Infrequent performance |  |  | 9.07 Inadequate instructions, orientation and/or training | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.03 Infrequent performance |  |  | 9.07 Inadequate instructions, orientation and/or training | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.03 Infrequent performance |  |  | 9.07 Inadequate instructions, orientation and/or training | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.05 Inadequate review instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.05 Inadequate review instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.05 Inadequate review instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.05 Inadequate review instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.05 Inadequate review instruction |  |  | 9.03 Improper or insufficient delegation | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.05 Inadequate review instruction |  |  | 9.03 Improper or insufficient delegation | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.05 Inadequate review instruction |  |  | 9.03 Improper or insufficient delegation | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.05 Inadequate review instruction |  |  | 9.03 Improper or insufficient delegation | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.05 Inadequate review instruction |  |  | 9.07 Inadequate instructions, orientation and/or training | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.05 Inadequate review instruction |  |  | 9.07 Inadequate instructions, orientation and/or training | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.05 Inadequate review instruction |  |  | 9.07 Inadequate instructions, orientation and/or training | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.05 Inadequate review instruction |  |  | 9.07 Inadequate instructions, orientation and/or training | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.03 Infrequent performance |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.03 Infrequent performance |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.03 Infrequent performance |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.03 Infrequent performance |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.03 Infrequent performance |  |  | 9.03 Improper or insufficient delegation | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.03 Infrequent performance |  |  | 9.03 Improper or insufficient delegation | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.03 Infrequent performance |  |  | 9.03 Improper or insufficient delegation | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.03 Infrequent performance |  |  | 9.03 Improper or insufficient delegation | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.03 Infrequent performance |  |  | 9.07 Inadequate instructions, orientation and/or training | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.03 Infrequent performance |  |  | 9.07 Inadequate instructions, orientation and/or training | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.03 Infrequent performance |  |  | 9.07 Inadequate instructions, orientation and/or training | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.03 Infrequent performance |  |  | 9.07 Inadequate instructions, orientation and/or training | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction |  |  | 9.03 Improper or insufficient delegation | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction |  |  | 9.03 Improper or insufficient delegation | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction |  |  | 9.03 Improper or insufficient delegation | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction |  |  | 9.03 Improper or insufficient delegation | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction |  |  | 9.07 Inadequate instructions, orientation and/or training | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction |  |  | 9.07 Inadequate instructions, orientation and/or training | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction |  |  | 9.07 Inadequate instructions, orientation and/or training | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction |  |  | 9.07 Inadequate instructions, orientation and/or training | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance |  |  | 9.03 Improper or insufficient delegation | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance |  |  | 9.03 Improper or insufficient delegation | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance |  |  | 9.03 Improper or insufficient delegation | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance |  |  | 9.03 Improper or insufficient delegation | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance |  |  | 9.07 Inadequate instructions, orientation and/or training | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance |  |  | 9.07 Inadequate instructions, orientation and/or training | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance |  |  | 9.07 Inadequate instructions, orientation and/or training | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.4 Inadequate communication of standards: training |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8787 | Seminole PP; EGX Gath/Trans | 2019-03-27 11:30 | While installing FDF housing on Unit 3A, contractor was lifting intermediate housing portion and the rigging became unattached from one side causing load to shift. When load shifted it dropped approximately 12" and bounced striking contractors foot. Contractor was freed and foot was injured. Contract crew took member to seek treatment. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Kelly Casey | 2019-05-10 10:50 | 2019-03-28 08:58 | 2019-03-28 08:58 | 2019-04-24 11:58 | 2019-04-10 11:30 | 2019-03-27 11:30 | 2019-05-01 12:28 |  | 2019-04-29 07:32 | Seminole PP Unit 3A FDF |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | The incident happened installing the bottom section of the FD fan housing. During the installation the load shifted to the north causing the south choker eyelet to make contact with the chain fall throatlatch which resulted in the latch failing. Equipment was a 1 1/2 ton chain fall and 2- 8ft, 1/2 inch thick steel chokers. The chokers were basketed above the bottom housing piece, and they were orientated in a triangle manner at roughly a 45* angle. The employee went to grab the chain fall when the fan housing fell approximately 6 inches and strike the employees right foot. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue | Kelly Casey |  | Christopher Lelak | No additional comments CBL 05/01/19 | Christopher Lelak |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance |  |  | 9.07 Inadequate instructions, orientation and/or training | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.02.1 Inadequate communication of standards: publication |  |  | Workers assigned the task were not qualified. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 4/29/19 |  |  |  | Injury / Illness |  | Kelly Casey |  | stitches and 3 broken toes | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Danny Pogue | Clarage | Michael Sharp | Crush/Smash |  | Foot | Kelly Casey | Right | TRUE | Personal Vehicle | [68 empty] | 9580663
8788 | Metro Service Center | 2019-03-27 16:00 | This is a first aid. While cleaning up the deck of mobile crane member tripped over ratchet strap that secures outriggers. Member fell on the deck of the mobile crane landing on the right side. | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Hershel Goodson | 2019-04-01 07:44 | 2019-03-28 17:57 | 2019-03-28 17:57 | 2019-03-28 18:03 | 2019-04-10 16:00 | 2019-03-28 17:52 |  |  |  | Turnpike job. Luther and NE 23rd. |  |  | Terry Hackett | Fall occurred while conducting housekeeping. | T&D Ops |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE |  |  | While cleaning up the deck of mobile crane member tripped over ratchet strap that secures outrigger pads on the deck during transport. Member fell on the deck of the mobile crane landing on the right side. Ratchet strap was left laying on the deck of the crane. Corrective Action 6402 is tied to this incident "Require crews to store ratchet straps in a way that it does not pose a tripping hazard when not in use (i.e. bins, boxes, etc....)." |  |  | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | James Allred | Hershel Goodson |  |  |  | Gary Lassley |  | Low |  |  |  | 4.09 Preoccupation with problems |  |  |  | 8.1.2 Improper conduct that is condoned: Unintentional | [8 empty] | Ratchet straps left laying on the deck while not in use. | 09. Improper Placement | 4. Fall on Same Level (Slip and Fall, Trip Over) | [26 empty] | FALSE |  |  | 1993-11-15 | 1965-05-07 |  | 2019-03-20 07:00 | 0 | 0 | otc anti-inflammatory and advised to ice for first 3 days. | FALSE | Male | Tripped over ratchet strap |  | TRUE | James Allred |  | First Aid | James Allred |  |  |  |  | Inflammation |  | FALSE |  | Equipment Oper | Back |  | Right | FALSE | Hershel Goodson | FALSE |  | 3/20/2019 7:00:00 AM |  | FALSE |  |  | crane deck | cleaning back of crane off
8789 | South District Service Center | 2019-03-28 16:00 | Public vehicle rearend Company vehicle. | Level 1 |  | FALSE | Vehicle |  |  |  |  | OG&E Corp Services | Mike Jones | 2019-04-03 14:44 | 2019-03-29 09:43 | 2019-03-29 09:43 | 2019-04-03 14:39 | 2019-04-11 16:00 | 2019-03-29 09:35 |  |  |  | Corner of Southbound SE 29th and I-35 Service Road. |  |  | Cody Vinyard | Approved, Cody Vinyard | UTS |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | [6 empty] | South District Service Center | FALSE |  | FALSE | UTS - Asset & LC Mgmt |  | Gary Sanders | Mike Jones |  |  |  | Donald Ciupak |  | Low | [93 empty] | FALSE |  | Oklahoma Cityd | Public Vehicle Struck OGE | OGE Vehicle Stopped/Parked | 1981-11-15 18:00 |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Clear
8790 | Sooner Power Plant | 2019-03-30 14:00 | dropped object-member was washing out dewatering bin with 1-1/2 fire hose slung over shoulder, member went to move fire hose to other shoulder and fire hose lifted hard hat off his head and it fell into dewatering bin and ended up in coal yard scraper. hard hat tether was in use. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Daniel Dickinson | 2019-04-11 11:18 | 2019-03-30 16:48 | 2019-03-30 16:48 | 2019-03-30 18:04 | 2019-04-13 14:00 | 2019-03-30 16:41 | 2019-04-02 08:58 |  |  | Sooner PP-ash silo area- "B" bottom ash dewatering bin |  |  | Brady Sowell | Approved by Brady Sowell | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Daniel Dickinson |  | Bottom ash from the bottom of the boilers is removed every shift and transferred to the dewatering bins. The dewatering bins house the ash until it is ready to be dumped twice a week. In order to dump the dewatering bin, it is first dewatered, a coal yard scraper is parked under the bin and then the bin is unloaded into the scraper 10-12 times. Once empty, the operator goes on top of the bin and uses a 1-1/2 inch fire hose to wash any remaining ash from the sides of the bin and the dewatering screens while the coal yard scraper is still parked underneath. This requires the Operator to walk the fire hose around the platform in order to access all areas of the bin. The Operator was slightly bent over with the charged fire hose on his shoulder washing the sides and came to a light pole and lifted the charged fire hose up and over his head to get around the light pole and swap to his other shoulder. This caused the fire hose to push his hard hat off his head and the tether to come off his collar, the hard hat fell into the dewatering bin and ended up in the coal yard scraper. I rated the consequence of this as negligible because there was no way for anyone to have been beneath the falling object with the scraper parked under the bin, and unlikely because this job is performed in a windy environment and hard hats are tethered and cinched down tight before going on top of dewatering bins. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Operations |  | Curtis Tweedy | Daniel Dickinson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | dropped object-member was washing out dewatering bin with 1-1/2 fire hose slung over shoulder, member went to move fire hose to other shoulder and fire hose lifted hard hat off his head and it fell into dewatering bin and ended up in coal yard scraper. hard hat tether was in use. | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level | [92 empty] | NONE
8791 | Seminole PP; EGX Gath/Trans | 2019-04-01 11:15 | While working in the SM3 boiler basement, electrical contractor maneuvered manlift which contacted and dragged a water hose running through the basement. The hose was looped over a drain pipe exiting a house heat heater, and the act of pulling on the hose bent the drain line and damaged a fitting in the line. This caused a minor water drip/leak onto the floor of the basement. | Level 1 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services |  | 2019-05-01 14:19 | 2019-04-01 17:01 | 2019-04-01 17:01 | 2019-04-30 16:12 | 2019-04-15 11:15 | 2019-04-01 16:51 | 2019-05-01 12:48 |  |  | Seminole PP Unit 3 boiler basement, east side |  |  | Marcus Huddleston | No additional comments. MLH 5/1/19 | UTS |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | Manlift being operated by electrical contractor snagged and drug a water hose that was elevated and hanging on piping/heater equipment. Hose had been improperly situated by mechanical contractor and left in place Electrical contractor did not notice the hose when maneuvering manlift. Force imparted to hose broke an element of the heater equipment. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Project Mgmt |  | Danny Pogue |  |  | Christopher Lelak | No further comments - CBL 05/01/19 | Christopher Lelak |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Worker moved hanging water hose to reposition his manlift. Worker's manlift snagged hanging water hose which broke a condensate line. | 18. Failure to Check, Monitor | 6. Caught On (Snagged, Hung) | [5 empty] | Property Damage |  |  | Damaged fitting on heater drain line |  |  |  |  | 6. Caught On (Snagged, Hung) | Danny Pogue | Electrical Contractors of America | Unknown |  | Fixed Equipment | [6 empty] | FALSE | [66 empty] | 1646037
8792 | Muskogee Power Plant | 2019-04-02 07:00 | Handrails on the boiler side of the walkway have been removed and area was not barricaded. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Scott Stidham | 2019-05-02 13:07 | 2019-04-02 09:11 | 2019-04-02 09:11 | 2019-04-03 10:00 | 2019-04-16 07:00 | 2019-04-02 08:49 | 2019-04-25 11:14 |  | 2019-04-04 14:50 | Muskogee Boiler #5, level 5 north side corner 2 to corner 3. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Scott Stidham |  | Boiler operator was walking down the boiler and noticed that the boiler side handrails on level 5 were missing. He contacted me to check it out and we compared the handrail situation on Boiler 4 to verify that they should be there. After discovering that unit 4 did have these handrails I reviewed our grating and handrail log and found that a permit had been issued for this area back in October of last year. I had the boiler operator Barricade and log the areas with missing handrail and create a safety notification to get them replaced. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Other |  | Scott Stidham | Scott Stidham |  |  | Discussion was held with TEI site leadership, area walked down and coaching secession performed. SPC |  |  | Medium | [13 empty] | 14.04 Inadequate monitoring of compliance |  |  | TEI removed the Handrail and Grating for the Gas conversion project and didn't put the handrail back in place upon completion. | 16. Failure to Follow Procedure, Policy, Practice | 3. Fall from Elevation to Lower Level |  | TEI contract group did not follow the process. They had a handrail removal permit and failed to put the railing back when the job was finished. Reviewed Bob Wright |  |  | MK Gas Conversion | Property Damage |  | Scott Stidham | [5 empty] | 3. Fall from Elevation to Lower Level | Scott Stidham | TEI | Billy Anderson | [75 empty] | none
8792 | Muskogee Power Plant | 2019-04-02 07:00 | Handrails on the boiler side of the walkway have been removed and area was not barricaded. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Scott Stidham | 2019-05-02 13:07 | 2019-04-02 09:11 | 2019-04-02 09:11 | 2019-04-03 10:00 | 2019-04-16 07:00 | 2019-04-02 08:49 | 2019-04-25 11:14 |  | 2019-04-04 14:50 | Muskogee Boiler #5, level 5 north side corner 2 to corner 3. |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Scott Stidham |  | Boiler operator was walking down the boiler and noticed that the boiler side handrails on level 5 were missing. He contacted me to check it out and we compared the handrail situation on Boiler 4 to verify that they should be there. After discovering that unit 4 did have these handrails I reviewed our grating and handrail log and found that a permit had been issued for this area back in October of last year. I had the boiler operator Barricade and log the areas with missing handrail and create a safety notification to get them replaced. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Other |  | Scott Stidham | Scott Stidham |  |  | Discussion was held with TEI site leadership, area walked down and coaching secession performed. SPC |  |  | Medium | [13 empty] | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  |  | TEI removed the Handrail and Grating for the Gas conversion project and didn't put the handrail back in place upon completion. | 16. Failure to Follow Procedure, Policy, Practice | 3. Fall from Elevation to Lower Level |  | TEI contract group did not follow the process. They had a handrail removal permit and failed to put the railing back when the job was finished. Reviewed Bob Wright |  |  | MK Gas Conversion | Property Damage |  | Scott Stidham | [5 empty] | 3. Fall from Elevation to Lower Level | Scott Stidham | TEI | Billy Anderson | [75 empty] | none
8793 | Muskogee Power Plant | 2019-04-02 11:00 | Whittinghill Disposal driver struck card reader. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Scott Stidham | 2019-05-01 11:40 | 2019-04-02 14:28 | 2019-04-02 14:28 | 2019-04-29 08:01 | 2019-04-16 11:00 | 2019-04-02 14:16 | 2019-04-30 07:46 |  |  | Muskogee PP secondary perimeter entry gate South East of unit 6. |  |  | Robert Wright | Approved Bob Wright | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Scott Stidham |  | Whitinghill disposal driver caught the front of the card reader with the truck or trailer while pulling through the gate. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | Other |  | Scott Stidham | Scott Stidham |  |  | reviewed. SPC |  |  | Low |  | 2.06 Poor coordination | [14 empty] | Driver struck the card reader because they pulled up close to card in and were not aware of the position of part the vehicle or the trailer in relationship to the Card reader stand resulting in hitting it when they pulled forward. | 01. Operating Equipment Without Authority | 1. Struck Against (Running or Bumping Into) | [68 empty] | Front face of card reader was knocked off, reader is no longer working | 1000 |  | Fixed Equipment | [20 empty] | none
8794 | Seminole PP; EGX Gath/Trans | 2019-04-01 11:00 | While contractor was welding new fan housing in place, OG&E member noted that a flexible conduit serving a motor on the 3A FD fan guillotine damper was smoking. Immediate cause was unknown, but was assumed to be due to contractor's welding operations on the fan housing. | Level 1 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services |  | 2019-05-01 14:18 | 2019-04-02 17:20 | 2019-04-02 17:20 | 2019-04-30 15:52 | 2019-04-15 11:00 | 2019-04-01 11:30 | 2019-05-01 12:29 |  |  | Seminole PP Unit 3A FD fan |  |  | Marcus Huddleston | No additional comments. MLH 5/1/19 | UTS |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | OG&E contends that contractors were welding on fan housing without proper grounding - i.e., ground should have been attached to housing itself, which was somewhat isolated from the structure by the expansion joint above. However, the contractor was apparently grounded to the structure, not the housing. Contractor Clarage/AirTek, on the contrary, denied that their welders had improperly grounded. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | No further comments - CBL 05/01/19 | Christopher Lelak |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [8 empty] | 14.04 Inadequate monitoring of compliance |  |  | Apparently welders placed grounds improperly while welding. | 09. Improper Placement | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Property Damage |  |  | burned conduit and conductor |  |  |  |  | 9. Abnormal Operation | Danny Pogue | Clarage/AirTek | Unknown |  | Fixed Equipment | [6 empty] | FALSE | [66 empty] | 1646037
8795 | Ardmore Service Center | 2019-04-02 07:30 | contractor sitting at red light and public vehicle struck rear of company vehicle. | Level 1 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Richard Norton | 2019-04-12 13:14 | 2019-04-03 08:07 | 2019-04-03 08:07 | 2019-04-03 08:54 | 2019-04-16 07:30 | 2019-04-03 07:43 | 2019-04-08 16:48 |  |  | W. Main St & S 9th , Durant Ok |  |  | Jerrie Looney | Approved, J. Looney 4.12.19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Richard Norton |  | Contractor was sitting at red light at W Main & 9th St Durant Oklahoma when public vehicle struck his vehicle from behind by hitting his receiver device. |  |  |  | Ardmore Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Richard Norton | Richard Norton |  |  | ` |  |  | Low |  |  |  |  | 5.06 Lack of situational awareness |  |  |  |  | 10.07 Inadequate monitoring of initial operation | [6 empty] | Contractor was struck from behind by public vehicle, public vehicle driver stated he had bad breaks. | 05. Making Safety Devices Inoperative | 1. Struck Against (Running or Bumping Into) | [5 empty] | Vehicle |  | Richard Norton | [5 empty] | 1. Struck Against (Running or Bumping Into) | Richard Norton | Whitmier | Danny Chennault |  |  |  | Richard Norton | [71 empty] | None
8796 | McClain Power Plant | 2019-04-03 | BROCK EMPLOYEE WAS ERECTING SCAFFOLDING UP TO THE BOTTOM OF THE INTERCEPT AND REHEAT STOP VALVES, UNDER THE GRATING AT TURBINE LEVEL. HE REACHED OUT TO GRAB A GRATING STRUCTURE BRACE FOR A HAND HOLD. WHEN HE GRABBED THE BRACE, THE BOLT SECURING THE BRACE TO THE GRATING STRUCTURE FELL OUT, CAUSING THE BRACE TO SWING DOWN AND THE WORKER LOST BALANCE BUT WAS ABLE TO CATCH HIMSELF BEFORE FALLING. THE BOLT FELL TO THE UNDER FOUNDATION AREA OF THE TURBINE. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Ralph Evans | 2019-04-18 06:28 | 2019-04-03 12:53 | 2019-04-03 12:53 | 2019-04-15 09:26 | 2019-04-17 | 2019-04-03 12:40 | 2019-04-17 11:11 |  |  | MCCLAIN UNIT 3 (STG ) EAST SIDE TURBINE LEVEL AT #2 REHEAT STOP AND INTERCEPT VALVES, UNDER LAGGING AT HP/IP TURBINE |  |  | Tanner Brady | Brock employee reported correctly, area was assessed and determined maintenance would immediately secure all unknown loose bolts. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Ralph Evans |  | A Brock employee was erecting scaffolding up to the bottom of the intercept and reheat stop valves, under the grating at the turbine level. He reached out to grab a grating structure brace for a hand hold. While grabbing hold of the structure/brace, the bolt securing the brace to the grating structure fell out. This caused the brace to swing down and the contractor lost balance. He did not fall as he was able to catch himself, regaining balance. The Brock employee was wearing the proper PPE during the time of this occurrence. The bolt that was inserted fell to the under foundation area of the turbine. The area that this incident occurred in was barricaded off properly. The contractor reported this incident immediately. While reviewing the surrounding area that they would continue to work in it was determined that brace was not the only one that had loose bolts. The bolts in the area were either replaced or tightened so they could continue to build scaffold for the outage. |  |  |  | McClain Power Plant | FALSE |  | TRUE | Maintenance |  | Ralph Evans | Ralph Evans |  | Jimmy Green | No further comments | Jimmy Green |  | Low | [11 empty] | 12.01.1 Inadequate preventative assessment of needs |  |  |  |  | When Contractor grabbed the grating structure brace to hold onto, the bolt securing the brace to the structure fell out swinging and causing the contractor to lose his balance. | 37. Inadequate Support, Assistance | 12. Equipment Failure | [5 empty] | Property Damage |  | Ralph Evans | [5 empty] | 4. Fall on Same Level (Slip and Fall, Trip Over) | Ralph Evans | BROCK GROUP | JORGE ESCOBAR |  |  |  | Ralph Evans | [71 empty] | 483065
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Chrysty Dorsey | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Chrysty Dorsey | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Environmental | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Chrysty Dorsey | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.10 Lack of supervisory/management job knowledge |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Chrysty Dorsey | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.10 Lack of supervisory/management job knowledge |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Environmental | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Chrysty Dorsey | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Chrysty Dorsey | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Environmental | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Chrysty Dorsey | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.03 Inadequate initial training | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Chrysty Dorsey | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.03 Inadequate initial training | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Environmental | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Chrysty Dorsey | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.03 Inadequate initial training | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.10 Lack of supervisory/management job knowledge |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Chrysty Dorsey | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.03 Inadequate initial training | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.10 Lack of supervisory/management job knowledge |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Environmental | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Chrysty Dorsey | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.03 Inadequate initial training | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Chrysty Dorsey | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.03 Inadequate initial training | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Environmental | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Chrysty Dorsey | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.06 Lack of situational awareness | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Chrysty Dorsey | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.06 Lack of situational awareness | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Environmental | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Chrysty Dorsey | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.06 Lack of situational awareness | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.10 Lack of supervisory/management job knowledge |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Chrysty Dorsey | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.06 Lack of situational awareness | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.10 Lack of supervisory/management job knowledge |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Environmental | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Chrysty Dorsey | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.06 Lack of situational awareness | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Chrysty Dorsey | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.06 Lack of situational awareness | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Environmental | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Marcus Huddleston | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Marcus Huddleston | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Environmental | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Marcus Huddleston | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.10 Lack of supervisory/management job knowledge |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Marcus Huddleston | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.10 Lack of supervisory/management job knowledge |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Environmental | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Marcus Huddleston | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Marcus Huddleston | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Environmental | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Marcus Huddleston | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.03 Inadequate initial training | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Marcus Huddleston | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.03 Inadequate initial training | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Environmental | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Marcus Huddleston | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.03 Inadequate initial training | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.10 Lack of supervisory/management job knowledge |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Marcus Huddleston | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.03 Inadequate initial training | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.10 Lack of supervisory/management job knowledge |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Environmental | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Marcus Huddleston | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.03 Inadequate initial training | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Marcus Huddleston | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.03 Inadequate initial training | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Environmental | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Marcus Huddleston | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.06 Lack of situational awareness | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Marcus Huddleston | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.06 Lack of situational awareness | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Environmental | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Marcus Huddleston | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.06 Lack of situational awareness | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.10 Lack of supervisory/management job knowledge |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Marcus Huddleston | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.06 Lack of situational awareness | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.10 Lack of supervisory/management job knowledge |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Environmental | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Marcus Huddleston | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.06 Lack of situational awareness | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8797 | Seminole PP; EGX Gath/Trans | 2019-04-03 08:30 | Company members noticed suspect insulation material on floor of U2 breezeway upon entering the building. Contractor had apparently removed firestop material in a vertical cable tray rising from the cable tunnel below. Breezeway, storeroom and welding shop were immediately cordoned off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results returned late in the day and indicate the material is positive for asbestos. The area remains cordoned off pending further air monitoring to allow clearance for resuming occupancy of these areas. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate incident, establish causal factors and establish corrective actions. | 2019-04-05 07:53 | OG&E Corp Services |  | 2019-06-07 07:44 | 2019-04-03 18:55 | 2019-04-03 18:55 | 2019-05-14 13:47 | 2019-04-17 08:30 | 2019-04-03 18:33 | 2019-05-20 07:58 | 2019-05-23 08:51 | 2019-05-15 13:59 | Seminole PP Unit 2 breezeway at ground floor, just outside storeroom |  |  | Jean Leger | See Workflow comment. | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Diana Edwards |  | Incident Investigation: On April 3, 2019, member noticed suspect insulation material on the floor of Unit #2 breezeway upon entering the building at approximately 8:30 am. It appeared that ECA employees had removed firestop material from a vertical cable tray rising from the cable tunnel below. This work took place the day before on April 2, 2019. Member informed Danny Pogue of the material. Plant personnel and Asbestos Coordinator were contacted at this time. Breezeway, storeroom and welding shop were immediately barricaded off and all access restricted. EAI was dispatched to sample the material and remediate the area. Sample results were returned later that day and confirmed the material was positive for asbestos. EAI performed a thorough cleaning of the area and clearance samples were taken by Astech. EAI also abated the remaining firestop from the cable tray followed by another set of clearance samples. The Fastenal room remained barricaded throughout the completion of the abatement and completion of clearance samples. A stand down was held with ECA and all their employees to discuss the incident and go over asbestos concerns at Seminole PP. The stand down was held by Danny Pogue. The investigation team interviewed the individuals involved in the incident and the following sequence of events established: 1. Pre-construction meeting was held on January 23, 2019 with contractors working on the Seminole FD Fan Project. 2. Randy Smith and Devin Dooly were in attendance. 3. OGE Asbestos Coordinator addressed asbestos concerns within the plan including: where insulation is commonly located, labeling system, and clear instructions not to damage material that is not clearly labeled as “asbestos free”. Any material that is not labeled is to be presumed to be asbestos containing building material and not disturbed until proven otherwise. It was also discussed that an EAI asbestos crew is onsite to assist with the identification of material. 4. OGE Safety Professional, provided a contractor safety orientation during the preconstruction meeting that also covered asbestos concerns and pre-job briefings. 5. Bob Lawson and Jason Raska watched the contractor orientation (main and plant). 6. Danny Pogue covered asbestos hazards in his contractor orientation that he performed. 7. ECA completed a task risk assessment on April 2, 2019 prior to the start of the task. 8. Bob Lawson read the task risk assessment. He was aware that “asbestos” had been checked on the form. There was not a clear understanding of what was meant when the box was checked on the task risk assessment. 9. Bob Lawson was on the basement level and Jason Raska was in the cable vault. 10. Bob removed the cover panel and saw that there was firestop. He noted that the firestop had been previously disturbed and pieces of the material left behind. 11. Bob asked Jason to come up to the basement level to look at the material. They decided to go ahead with the wire pull and Bob widened the hole opening in preparation for the wire pull. 12. Assumption was made by ECA members involved to move forward with the wire pull. It was stated during the investigation interview that since the material appeared to have been disturbed previously that it was not asbestos and the continued without determining if the material contained asbestos. 13. The pull was completed in approximately 30 minutes and the two moved on to another job. The material was not cleaned up. 14. OGE member found the firestop debris and dust on the floor the following morning by and OGE member at approximately 8:30 am. The finding was immediately reported to Danny Pogue. 15. EAI was contacted, the breezeway, machine shop and storage room barricaded. 16. Samples of the material were sent to the lab and clean-up of the area initiated. 17. Bulk samples confirmed to be asbestos later that day. 18. A safety stand down was held with ECA. 19. Clearance air samples were completed prior to allowing re-entry into the spaces. 20. All ECA members received asbestos awareness training following the incident. During the interview process, the following deficiencies were identified: 1. ECA Field superintendent stated that he had not read the OGE Contractor Reference Guide. This document is required to be read and information provided downstream to contractor employees. 2. ECA does not have an asbestos program. 3. ECA had not provided asbestos awareness training to electricians. 4. ECA hires electricians from the local union hall on regular bases. Electricians indicated that they have not had asbestos awareness training. 5. ECA electricians did not know what it specifically meant if “asbestos” was checked on the task risk assessment and there was not any comments provided. 6. OGE orientation addresses asbestos in the plant, but does not go into much depth on location of material other than on piping. 7. Asbestos was not a program requirement for contractors in ISNet. Causal Factors: 1. ECA did not provide asbestos awareness training to electricians hired through the local union to work on the FD Fan Project. 2. ECA electricians assumed the suspect firestop material was not asbestos because it appeared to have been previously disturbed and proceeded with the cable pull. 3. OGE did not require an asbestos awareness program in ISNet for contractors working in facilities that are known to contain asbestos containing building material. | Marcus Huddleston | Diana Edwards |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | None - CBL 05/20/19 | Christopher Lelak | William Young | High |  |  |  |  | 5.06 Lack of situational awareness | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | ECA employees failed to communicate their concerns regarding suspect material to their supervisor. The pre-task job briefing did not provide specific information on what to do if suspect material is encountered. | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed incident investigation and corrective actions. Approved WCY 5/23/19 | Returning to add details. No additional comments. MLH 5/15/19 |  |  |  | Environmental | [7 empty] | 13. Environmental Release | Danny Pogue | Electrical Corporation of America | Jason Raska | [75 empty] | None
8798 | Sooner Power Plant | 2019-04-03 15:30 | Member was looking overhead to scope out a job. Member didn't realize he was close to the edge of the raised concrete and lost his footing. Member caught himself before falling. Member was not injured. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Supply |  | 2019-04-11 11:19 | 2019-04-04 09:56 | 2019-04-04 09:56 | 2019-04-04 10:26 | 2019-04-17 15:30 | 2019-04-03 16:30 | 2019-04-08 11:20 |  |  | Sooner Water Treatment Building |  |  | Brady Sowell | Approved by Brady Sowell | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE |  |  | Member was looking at piping in the Water Treatment Building. Member was focused on upper-level piping while walking. Member did not notice he was close to the edge of the raised concrete surface and stepped off the edge unexpectedly. Member was not hurt. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Engineering & Planning |  | Tony Mena |  |  | Donald Wyckoff | I have reviewed the incident investigation and approve of corrective action. Donald Wyckoff 4/8/19. | Donald Wyckoff |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Member didn't recognize he was close to the edge of a raised surface and stepped off. | 17. Failure to Identify Hazard, Risk | 4. Fall on Same Level (Slip and Fall, Trip Over) | [92 empty] | 9578616
8799 | Seminole PP; EGX Gath/Trans | 2019-04-04 12:00 | Member started to open door that had Danger Asbestos tape across it. Member did not see tape initially, but felt brush her hand when she opened the door 2-3 inches. When she saw that it was danger tape she immediately closed door, reattached the tape and notified a supervisor of what had happened. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Supply |  | 2019-05-22 08:32 | 2019-04-04 14:25 | 2019-04-04 14:25 | 2019-04-17 10:14 | 2019-04-18 17:00 | 2019-04-04 13:29 | 2019-05-13 08:35 |  |  | Seminole Plant welding shop at the door to the Fastenal area. |  |  | Chrysty Dorsey | Approved. | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE |  |  | Member was going into Fastenal area to check stock of kitchen supplies. The door to the Fastenal area is a secured location with badge access required and the entrance through the weld shop is on the North side. She entered the weld shop through the West walkthrough door coming from the basement. She was looking forward talking with a contractor. Being dominant left-handed and used to entering the door frequently, she swiped her badge to gain access to the secured area with her left hand and used her left hand to open the door without ever looking directly at the door. Therefore, she did not see the asbestos danger tape across the door. She badged, heard the beep, and opened the door 2-3 inches. The barricade tape brushed against her hand. It was then that she looked straight ahead and saw the barricade tape. She immediately closed the door and reattached the tape. Then she went to find a supervisor to report what had happened. Member was not onsite the day before and was unaware of the asbestos incident in the area. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | TRUE | Quality Assurance |  | Tiffany Hightower |  |  | Bryan Pool | I approve | Bryan Pool |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Member was going into Fastenal area to check stock of kitchen supplies. She had her head turned while talking with a contractor and was not looking at door. Therefore she did not see the asbestos danger tape across the door. She badged, heard the beep, and opened the door 2-3 inches. The barricade tape brushed against her hand. It was then that she looked straight ahead and saw the barricade tape. She immediately closed the door and reattached the tape. Then she went to find a supervisor to report what had happened. | 11. Improper Position for Task | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [92 empty] | none
8800 | West Service Center | 2019-04-04 05:00 | Member was pulling into service center at the end of his shift and noticed smoke coming from passenger side bin. When the member investigated he discovered the trigger from the torch had been pushed and a sling was burned. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Delivery | Joshua Robertson | 2019-04-30 12:53 | 2019-04-04 16:52 | 2019-04-04 16:52 | 2019-04-22 10:04 | 2019-04-18 05:00 | 2019-04-04 16:30 | 2019-04-29 14:10 |  | 2019-04-26 12:11 | West District Service Center |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Joshua Robertson |  | Date of occurrence: 4-4-2019 @ 5:00 AM Crew had worked a bad underground the night before. When finishing up the job it started raining / storming. The crew loaded up the underground tools in a bag and hung the bag in the bin of the Linetruck. The proceeded to work other trouble call throughout the night. When the crew pulled into West District yard the passenger of the truck noticed smoke coming from the bin of the truck, he stopped the driver of the truck opened the bin and found that the button of the small propane torch was pushed down by a grip hanging in the bin and was lit. The torch had burnt some slings that were in the bin and were smoldering. They extinguished the slings and removed them from the bin. Takeaways: proper storing and removing the torch head from the small propane bottle and bleeding it off after each use (this is common way of storing) should always be done. |  |  |  | West Service Center | FALSE |  | TRUE | Construction Services |  |  | Joshua Robertson |  | Terry Garrett | I approve....TG | Terry Garrett |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | failing to take the torch head off of the propane tank and bleed it down prior to storing it in the bin. | 17. Failure to Identify Hazard, Risk | 5. Caught In (Pinch and Nip Points) |  | I believe the corrective actions are the best form of mitigation at this time. Approved 4/26/19 | [90 empty] | none
8801 | Ft Smith Service Center | 2019-04-02 09:00 | While member was lowering Service basket to store in cradle, bucket tilted forward, without operator control (on its own),dumping some tools out of tool board. Member lowered basket by using leveling handle and lowering handle simultaneously. No injury occurred. | Level 3 |  | TRUE | Member Injury |  | Lindle Coleman | reviewed | 2019-04-05 11:33 | Power Delivery | Sean Spicer | 2019-05-06 07:58 | 2019-04-05 10:57 | 2019-04-05 10:57 | 2019-04-15 11:21 | 2019-04-16 09:00 | 2019-04-05 10:08 | 2019-04-17 11:00 | 2019-04-18 13:16 | 2019-04-15 13:13 | East Main St, Ozark, Ar. |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | TRUE | Charles Kolp |  | While member was descending in the bucket he felt a slight tilt without operator control. Member lowered bucket by using leveling handle and lowering handle simultaneously. Member was wearing fall protection and had his spot device on person. Fleet was notified and bucket truck F08-424, boom F12-424 was red tagged and pulled out of service that day 4/2/2019. Facts: -Truck was put in service at Ft Smith service center in July 16 2009. -DVIR was completed by the member the day of the incident. -Monthly tool & equipment inspection was completed 3/26/2019. -Bucket truck had hydraulic and dialectical tested by ETI on 3/21/2019 (approx 2 weeks prior), which passed all tests. -Fleet found cylinder internal piston seal failed. There was no way to visually identify failure of cylinder. -Fleet met with ETI on 4/12/2019 to communicate solutions or mitigation's, it was noted that this type of failure was uncommon. No recalls were found. -F08-424 is a 2008 International had 206,891 miles and 10,091 Engine hours. -Boom found to have 3,076 PTO hours, team estimating 50% actual boom usage. -Fleet replaced holding valve on cylinder and it did not correct the problem, fleet then replaced bucket leveling cylinder which corrected the problem. Bucket was then put back in service 4/9/2019. NOTE: Bill Hyatt was apart of this investigation. | Sean Spicer | Charles Kolp |  | Ft Smith Service Center | FALSE |  | TRUE | Construction Services |  | Billy White | Sean Spicer |  | Chad Inman | I approve the corrective actions. | Chad Inman | Lindle Coleman | High | [12 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | While member was descending in the bucket he felt a slight tilt without operator control. Member lowered bucket by using leveling handle and lowering handle simultaneously. Member was wearing fall protection and had his spot device on person. Fleet was notified and bucket truck F08-424, boom F12-424 was red tagged and pulled out of service that day 4/2/2019. Facts: -Truck was put in service at Ft Smith service center in July 16 2009. -DVIR was completed by the member the day of the incident. -Monthly tool & equipment inspection was completed 3/26/2019. -Bucket truck had hydraulic and dialectical tested by ETI on 3/21/2019 (approx 2 weeks prior), which passed all tests. -Fleet found cylinder internal piston seal failed. There was no way to visually identify failure of cylinder. -Fleet met with ETI on 4/12/2019 to communicate solutions or mitigation's, it was noted that this type of failure was uncommon. No recalls were found. -F08-424 is a 2008 International had 206,891 miles and 10,091 Engine hours. -Boom found to have 3,076 PTO hours, team estimating 50% actual boom usage. -Fleet replaced holding valve on cylinder and it did not correct the problem, fleet then replaced bucket leveling cylinder which corrected the problem. Bucket was then put back in service 4/9/2019. | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure | approved | Reviewed with investigation team. | [90 empty] | NA
8801 | Ft Smith Service Center | 2019-04-02 09:00 | While member was lowering Service basket to store in cradle, bucket tilted forward, without operator control (on its own),dumping some tools out of tool board. Member lowered basket by using leveling handle and lowering handle simultaneously. No injury occurred. | Level 3 |  | TRUE | Member Injury |  | Lindle Coleman | reviewed | 2019-04-05 11:33 | Power Delivery | Sean Spicer | 2019-05-06 07:58 | 2019-04-05 10:57 | 2019-04-05 10:57 | 2019-04-15 11:21 | 2019-04-16 09:00 | 2019-04-05 10:08 | 2019-04-17 11:00 | 2019-04-18 13:16 | 2019-04-15 13:13 | East Main St, Ozark, Ar. |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | TRUE | Charles Kolp |  | While member was descending in the bucket he felt a slight tilt without operator control. Member lowered bucket by using leveling handle and lowering handle simultaneously. Member was wearing fall protection and had his spot device on person. Fleet was notified and bucket truck F08-424, boom F12-424 was red tagged and pulled out of service that day 4/2/2019. Facts: -Truck was put in service at Ft Smith service center in July 16 2009. -DVIR was completed by the member the day of the incident. -Monthly tool & equipment inspection was completed 3/26/2019. -Bucket truck had hydraulic and dialectical tested by ETI on 3/21/2019 (approx 2 weeks prior), which passed all tests. -Fleet found cylinder internal piston seal failed. There was no way to visually identify failure of cylinder. -Fleet met with ETI on 4/12/2019 to communicate solutions or mitigation's, it was noted that this type of failure was uncommon. No recalls were found. -F08-424 is a 2008 International had 206,891 miles and 10,091 Engine hours. -Boom found to have 3,076 PTO hours, team estimating 50% actual boom usage. -Fleet replaced holding valve on cylinder and it did not correct the problem, fleet then replaced bucket leveling cylinder which corrected the problem. Bucket was then put back in service 4/9/2019. NOTE: Bill Hyatt was apart of this investigation. | Hannah Everett | Charles Kolp |  | Ft Smith Service Center | FALSE |  | TRUE | Construction Services |  | Billy White | Sean Spicer |  | Chad Inman | I approve the corrective actions. | Chad Inman | Lindle Coleman | High | [12 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | While member was descending in the bucket he felt a slight tilt without operator control. Member lowered bucket by using leveling handle and lowering handle simultaneously. Member was wearing fall protection and had his spot device on person. Fleet was notified and bucket truck F08-424, boom F12-424 was red tagged and pulled out of service that day 4/2/2019. Facts: -Truck was put in service at Ft Smith service center in July 16 2009. -DVIR was completed by the member the day of the incident. -Monthly tool & equipment inspection was completed 3/26/2019. -Bucket truck had hydraulic and dialectical tested by ETI on 3/21/2019 (approx 2 weeks prior), which passed all tests. -Fleet found cylinder internal piston seal failed. There was no way to visually identify failure of cylinder. -Fleet met with ETI on 4/12/2019 to communicate solutions or mitigation's, it was noted that this type of failure was uncommon. No recalls were found. -F08-424 is a 2008 International had 206,891 miles and 10,091 Engine hours. -Boom found to have 3,076 PTO hours, team estimating 50% actual boom usage. -Fleet replaced holding valve on cylinder and it did not correct the problem, fleet then replaced bucket leveling cylinder which corrected the problem. Bucket was then put back in service 4/9/2019. | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure | approved | Reviewed with investigation team. | [90 empty] | NA
8801 | Ft Smith Service Center | 2019-04-02 09:00 | While member was lowering Service basket to store in cradle, bucket tilted forward, without operator control (on its own),dumping some tools out of tool board. Member lowered basket by using leveling handle and lowering handle simultaneously. No injury occurred. | Level 3 |  | TRUE | Vehicle |  | Lindle Coleman | reviewed | 2019-04-05 11:33 | Power Delivery | Sean Spicer | 2019-05-06 07:58 | 2019-04-05 10:57 | 2019-04-05 10:57 | 2019-04-15 11:21 | 2019-04-16 09:00 | 2019-04-05 10:08 | 2019-04-17 11:00 | 2019-04-18 13:16 | 2019-04-15 13:13 | East Main St, Ozark, Ar. |  |  |  | Approve | T&D Ops |  | Level 3 | Vehicle |  | FALSE | TRUE | FALSE |  | FALSE | TRUE | Charles Kolp |  | While member was descending in the bucket he felt a slight tilt without operator control. Member lowered bucket by using leveling handle and lowering handle simultaneously. Member was wearing fall protection and had his spot device on person. Fleet was notified and bucket truck F08-424, boom F12-424 was red tagged and pulled out of service that day 4/2/2019. Facts: -Truck was put in service at Ft Smith service center in July 16 2009. -DVIR was completed by the member the day of the incident. -Monthly tool & equipment inspection was completed 3/26/2019. -Bucket truck had hydraulic and dialectical tested by ETI on 3/21/2019 (approx 2 weeks prior), which passed all tests. -Fleet found cylinder internal piston seal failed. There was no way to visually identify failure of cylinder. -Fleet met with ETI on 4/12/2019 to communicate solutions or mitigation's, it was noted that this type of failure was uncommon. No recalls were found. -F08-424 is a 2008 International had 206,891 miles and 10,091 Engine hours. -Boom found to have 3,076 PTO hours, team estimating 50% actual boom usage. -Fleet replaced holding valve on cylinder and it did not correct the problem, fleet then replaced bucket leveling cylinder which corrected the problem. Bucket was then put back in service 4/9/2019. NOTE: Bill Hyatt was apart of this investigation. | Sean Spicer | Charles Kolp |  | Ft Smith Service Center | FALSE |  | TRUE | Construction Services |  | Billy White | Sean Spicer |  | Chad Inman | I approve the corrective actions. | Chad Inman | Lindle Coleman | High | [12 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | While member was descending in the bucket he felt a slight tilt without operator control. Member lowered bucket by using leveling handle and lowering handle simultaneously. Member was wearing fall protection and had his spot device on person. Fleet was notified and bucket truck F08-424, boom F12-424 was red tagged and pulled out of service that day 4/2/2019. Facts: -Truck was put in service at Ft Smith service center in July 16 2009. -DVIR was completed by the member the day of the incident. -Monthly tool & equipment inspection was completed 3/26/2019. -Bucket truck had hydraulic and dialectical tested by ETI on 3/21/2019 (approx 2 weeks prior), which passed all tests. -Fleet found cylinder internal piston seal failed. There was no way to visually identify failure of cylinder. -Fleet met with ETI on 4/12/2019 to communicate solutions or mitigation's, it was noted that this type of failure was uncommon. No recalls were found. -F08-424 is a 2008 International had 206,891 miles and 10,091 Engine hours. -Boom found to have 3,076 PTO hours, team estimating 50% actual boom usage. -Fleet replaced holding valve on cylinder and it did not correct the problem, fleet then replaced bucket leveling cylinder which corrected the problem. Bucket was then put back in service 4/9/2019. | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure | approved | Reviewed with investigation team. | [90 empty] | NA
8801 | Ft Smith Service Center | 2019-04-02 09:00 | While member was lowering Service basket to store in cradle, bucket tilted forward, without operator control (on its own),dumping some tools out of tool board. Member lowered basket by using leveling handle and lowering handle simultaneously. No injury occurred. | Level 3 |  | TRUE | Vehicle |  | Lindle Coleman | reviewed | 2019-04-05 11:33 | Power Delivery | Sean Spicer | 2019-05-06 07:58 | 2019-04-05 10:57 | 2019-04-05 10:57 | 2019-04-15 11:21 | 2019-04-16 09:00 | 2019-04-05 10:08 | 2019-04-17 11:00 | 2019-04-18 13:16 | 2019-04-15 13:13 | East Main St, Ozark, Ar. |  |  |  | Approve | T&D Ops |  | Level 3 | Vehicle |  | FALSE | TRUE | FALSE |  | FALSE | TRUE | Charles Kolp |  | While member was descending in the bucket he felt a slight tilt without operator control. Member lowered bucket by using leveling handle and lowering handle simultaneously. Member was wearing fall protection and had his spot device on person. Fleet was notified and bucket truck F08-424, boom F12-424 was red tagged and pulled out of service that day 4/2/2019. Facts: -Truck was put in service at Ft Smith service center in July 16 2009. -DVIR was completed by the member the day of the incident. -Monthly tool & equipment inspection was completed 3/26/2019. -Bucket truck had hydraulic and dialectical tested by ETI on 3/21/2019 (approx 2 weeks prior), which passed all tests. -Fleet found cylinder internal piston seal failed. There was no way to visually identify failure of cylinder. -Fleet met with ETI on 4/12/2019 to communicate solutions or mitigation's, it was noted that this type of failure was uncommon. No recalls were found. -F08-424 is a 2008 International had 206,891 miles and 10,091 Engine hours. -Boom found to have 3,076 PTO hours, team estimating 50% actual boom usage. -Fleet replaced holding valve on cylinder and it did not correct the problem, fleet then replaced bucket leveling cylinder which corrected the problem. Bucket was then put back in service 4/9/2019. NOTE: Bill Hyatt was apart of this investigation. | Hannah Everett | Charles Kolp |  | Ft Smith Service Center | FALSE |  | TRUE | Construction Services |  | Billy White | Sean Spicer |  | Chad Inman | I approve the corrective actions. | Chad Inman | Lindle Coleman | High | [12 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | While member was descending in the bucket he felt a slight tilt without operator control. Member lowered bucket by using leveling handle and lowering handle simultaneously. Member was wearing fall protection and had his spot device on person. Fleet was notified and bucket truck F08-424, boom F12-424 was red tagged and pulled out of service that day 4/2/2019. Facts: -Truck was put in service at Ft Smith service center in July 16 2009. -DVIR was completed by the member the day of the incident. -Monthly tool & equipment inspection was completed 3/26/2019. -Bucket truck had hydraulic and dialectical tested by ETI on 3/21/2019 (approx 2 weeks prior), which passed all tests. -Fleet found cylinder internal piston seal failed. There was no way to visually identify failure of cylinder. -Fleet met with ETI on 4/12/2019 to communicate solutions or mitigation's, it was noted that this type of failure was uncommon. No recalls were found. -F08-424 is a 2008 International had 206,891 miles and 10,091 Engine hours. -Boom found to have 3,076 PTO hours, team estimating 50% actual boom usage. -Fleet replaced holding valve on cylinder and it did not correct the problem, fleet then replaced bucket leveling cylinder which corrected the problem. Bucket was then put back in service 4/9/2019. | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure | approved | Reviewed with investigation team. | [90 empty] | NA
8812 | Seminole PP; EGX Gath/Trans | 2019-04-05 | During demolition of 3B fan housing, telescopic handler driver maneuvered close to U3A FDF stairs going to motor level of fan. While maneuvering, his back right tire caught on the stairs and started to pick the stairs off the concrete. This was quickly noticed by another worker who stopped the driver, then remedied the issue. Stairs lifted off the concrete only a few inches, no one injured, no property damage. | Level 1 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services |  | 2019-05-06 15:41 | 2019-04-05 16:59 | 2019-04-05 16:59 | 2019-05-03 14:01 | 2019-04-19 | 2019-04-05 16:53 | 2019-05-06 12:34 |  |  | Seminole PP Unit 3B FD fan |  |  | Marcus Huddleston | This incident was investigated after the contractor left site. No additional comments. MLH 5/6/19. | UTS |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | Worker was operating a telescoping manlift near the U3 FD fans. While backing the unit, one of the back tires contacted the stairs going up to the 3A FD fan platform. Worker was caught in mid-action and he stopped the movement of the equipment. No spotter was being used for this operation. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | TRUE | UTS - Capital Projects |  |  |  |  | Christopher Lelak | No further comments - CBL 05/06/19 | Christopher Lelak |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Worker operating equipment in congested area was not aware of obstructions behind him | 02. Failure to Warn | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage | [7 empty] | 1. Struck Against (Running or Bumping Into) |  | Clarage/AirTek | Unknown | [75 empty] | 1646037
8813 | Muskogee Power Plant | 2019-04-08 12:00 | Contracting employee dropped a cable tray strap while he was performing finishing work on the tray. There was no barricade underneath. | Level 1 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services |  | 2019-04-29 07:31 | 2019-04-08 17:35 | 2019-04-08 17:35 | 2019-04-15 22:31 | 2019-04-22 17:00 | 2019-04-08 16:58 | 2019-04-19 05:22 |  |  | Muskogee PP Unit 4 and 5 Piperack |  |  | Marcus Huddleston | No additional comments. MLH 4/29/19 | UTS |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | Contracting members were performing work on a cable tray on the piperack between unit 4 and 5. The area below where they were working was not barricaded off. One of the members dropped a cable tray strap to the ground. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | UTS - Capital Projects |  |  |  |  | Christopher Lelak | NONE- CBL 04/19 | Christopher Lelak |  | Low |  |  |  | 4.06 "Meaningless" or "degrading" activities | 5.03 Inadequate initial training | [11 empty] | Members did not have tethers on the tool used. The area below was not barricaded. | 03. Failure to Secure | 3. Fall from Elevation to Lower Level |  |  |  |  | MK Gas Conversion | Injury / Illness | [7 empty] | 2. Struck By (Hit By Moving Object) |  | ECA | Nelson Sack | [75 empty] | none
8813 | Muskogee Power Plant | 2019-04-08 12:00 | Contracting employee dropped a cable tray strap while he was performing finishing work on the tray. There was no barricade underneath. | Level 1 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services |  | 2019-04-29 07:31 | 2019-04-08 17:35 | 2019-04-08 17:35 | 2019-04-15 22:31 | 2019-04-22 17:00 | 2019-04-08 16:58 | 2019-04-19 05:22 |  |  | Muskogee PP Unit 4 and 5 Piperack |  |  | Marcus Huddleston | No additional comments. MLH 4/29/19 | UTS |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | Contracting members were performing work on a cable tray on the piperack between unit 4 and 5. The area below where they were working was not barricaded off. One of the members dropped a cable tray strap to the ground. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | UTS - Capital Projects |  |  |  |  | Christopher Lelak | NONE- CBL 04/19 | Christopher Lelak |  | Low |  |  |  | 4.06 "Meaningless" or "degrading" activities | 5.06 Lack of situational awareness | [11 empty] | Members did not have tethers on the tool used. The area below was not barricaded. | 03. Failure to Secure | 3. Fall from Elevation to Lower Level |  |  |  |  | MK Gas Conversion | Injury / Illness | [7 empty] | 2. Struck By (Hit By Moving Object) |  | ECA | Nelson Sack | [75 empty] | none
8813 | Muskogee Power Plant | 2019-04-08 12:00 | Contracting employee dropped a cable tray strap while he was performing finishing work on the tray. There was no barricade underneath. | Level 1 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services |  | 2019-04-29 07:31 | 2019-04-08 17:35 | 2019-04-08 17:35 | 2019-04-15 22:31 | 2019-04-22 17:00 | 2019-04-08 16:58 | 2019-04-19 05:22 |  |  | Muskogee PP Unit 4 and 5 Piperack |  |  | Marcus Huddleston | No additional comments. MLH 4/29/19 | UTS |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | Contracting members were performing work on a cable tray on the piperack between unit 4 and 5. The area below where they were working was not barricaded off. One of the members dropped a cable tray strap to the ground. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | UTS - Capital Projects |  |  |  |  | Christopher Lelak | NONE- CBL 04/19 | Christopher Lelak |  | Low |  |  |  | 4.04 Routine, monotony, demand for uneventful vigilance | 5.03 Inadequate initial training | [11 empty] | Members did not have tethers on the tool used. The area below was not barricaded. | 03. Failure to Secure | 3. Fall from Elevation to Lower Level |  |  |  |  | MK Gas Conversion | Injury / Illness | [7 empty] | 2. Struck By (Hit By Moving Object) |  | ECA | Nelson Sack | [75 empty] | none
8813 | Muskogee Power Plant | 2019-04-08 12:00 | Contracting employee dropped a cable tray strap while he was performing finishing work on the tray. There was no barricade underneath. | Level 1 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services |  | 2019-04-29 07:31 | 2019-04-08 17:35 | 2019-04-08 17:35 | 2019-04-15 22:31 | 2019-04-22 17:00 | 2019-04-08 16:58 | 2019-04-19 05:22 |  |  | Muskogee PP Unit 4 and 5 Piperack |  |  | Marcus Huddleston | No additional comments. MLH 4/29/19 | UTS |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | Contracting members were performing work on a cable tray on the piperack between unit 4 and 5. The area below where they were working was not barricaded off. One of the members dropped a cable tray strap to the ground. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | UTS - Capital Projects |  |  |  |  | Christopher Lelak | NONE- CBL 04/19 | Christopher Lelak |  | Low |  |  |  | 4.04 Routine, monotony, demand for uneventful vigilance | 5.06 Lack of situational awareness | [11 empty] | Members did not have tethers on the tool used. The area below was not barricaded. | 03. Failure to Secure | 3. Fall from Elevation to Lower Level |  |  |  |  | MK Gas Conversion | Injury / Illness | [7 empty] | 2. Struck By (Hit By Moving Object) |  | ECA | Nelson Sack | [75 empty] | none
8814 | Seminole PP; EGX Gath/Trans | 2019-04-08 17:00 | Member was extending crane's boom and made contact with insulated piping. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Matthew Cox | 2019-05-03 09:03 | 2019-04-08 18:09 | 2019-04-08 18:09 | 2019-04-09 18:12 | 2019-04-22 17:00 | 2019-04-08 17:00 | 2019-04-18 12:34 |  |  | Seminole PP Unit 3 piping above gas trip valve |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Matthew Cox |  | While replacing #3 gas trip valve crane made contact with abandoned steam coil piping and damaged the insulation. Member was following signalman's instructions by booming the crane out. The signalman stopped giving the signal to boom out (did not give an all stop), but crane operator proceed to boom out making contact with piping. At that point job was stopped until we determine insulation type. Upon investigation of insulation it was found the crane hit on a transition of insulation from fiberglass to block type insulation. No damage or disturbance was found on block type insulation and only to the fiberglass. Sample was taken to see if it is ACM and damaged area was sealed. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | Special Services |  | David Holman | Matthew Cox |  | Kelly Casey | I agreed with Matt on corrective actions to retrain members on hand signals and operation of equipment unless someone is signaling. | Kelly Casey |  | Low |  |  |  |  | 5.01 Lack of experience | [11 empty] | Members did not follow the best hand signal practices. | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) | [68 empty] | Damage to flashing covering insulation. | 500 | David Holman | Industrial/Heavy Equipment | [20 empty] | 9579391
8814 | Seminole PP; EGX Gath/Trans | 2019-04-08 17:00 | Member was extending crane's boom and made contact with insulated piping. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Matthew Cox | 2019-05-03 09:03 | 2019-04-08 18:09 | 2019-04-08 18:09 | 2019-04-09 18:12 | 2019-04-22 17:00 | 2019-04-08 17:00 | 2019-04-18 12:34 |  |  | Seminole PP Unit 3 piping above gas trip valve |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Matthew Cox |  | While replacing #3 gas trip valve crane made contact with abandoned steam coil piping and damaged the insulation. Member was following signalman's instructions by booming the crane out. The signalman stopped giving the signal to boom out (did not give an all stop), but crane operator proceed to boom out making contact with piping. At that point job was stopped until we determine insulation type. Upon investigation of insulation it was found the crane hit on a transition of insulation from fiberglass to block type insulation. No damage or disturbance was found on block type insulation and only to the fiberglass. Sample was taken to see if it is ACM and damaged area was sealed. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | Special Services |  | David Holman | Matthew Cox |  | Kelly Casey | I agreed with Matt on corrective actions to retrain members on hand signals and operation of equipment unless someone is signaling. | Kelly Casey |  | Low |  |  |  |  | 5.05 Misunderstood directions | [11 empty] | Members did not follow the best hand signal practices. | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) | [68 empty] | Damage to flashing covering insulation. | 500 | David Holman | Industrial/Heavy Equipment | [20 empty] | 9579391
8815 | McClain Power Plant | 2019-04-09 05:00 | At approximately 05:00 member climbed down a ladder to access the top HRSG doors to test for confined space permit. The member thought he was stepping on a platform near the bottom of the ladder when he fell to the HRSG door area below. This was a fall of approximately 3 feet. As a result of the fall the member received some scrapes to his hands, arms, and legs. | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Supply | Michael Booher | 2019-04-12 07:35 | 2019-04-09 07:18 | 2019-04-09 07:18 | 2019-04-10 06:01 | 2019-04-23 05:00 | 2019-04-09 06:53 |  |  |  | McClain Power Plant top of HRSG 2. |  |  | Tanner Brady | The risk ranking should have been ranked as a Medium. I have went over the incident with the Foreman and Member. We have walked down the site as well. | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE |  |  | At approximately 5 AM on April 9, 2019, the Member was on top of #2 HRSG sniffing the drums for confined space entry. The Member was looking for the re heater section that had been opened up and went to the wrong confined space that was supposed to be sniffed. The operator then climbed down a ladder (see picture "inside View of Fall") on the east side between the HP and IP drums. Half way down the ladder there is a platform to the side that you can step off of. When climbing down, the operator thought that the platform extended all the way across from what was seen out of his peripherals. The result was stepping off and thinking that he was safe on a platform that was not there. The operator fell approximately 3 feet to the top of the HRSG resulting in scrapes on his hands , arms, and legs. The shirt he was wearing was also ripped. The operator immediately reported the incident to his foreman. The operator finished his shift. At 3PM of the same day the operator went to the McBride Clinic and saw Dr. Estep. There were no significant injuries and went into his night shift the same day. |  |  | FALSE | McClain Power Plant | FALSE |  | FALSE | Operations |  | Robert Bent | Michael Booher |  |  |  | Heath Biehl |  | Low | [5 empty] | 6.03 Infrequent performance | [10 empty] | Recognition of platform not extending across | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level | [26 empty] | FALSE |  |  | 2018-04-16 | 1976-08-20 |  | 2019-04-08 18:00 | 0 | 0 | Member came back into the Admin Building and took 800miligrams of Ibuprofen. | FALSE | Male | Member was climbing down a ladder with a platform to his left. The Member thought that the platform extended all the way over. When he let go, he fell approximately 3 ft. The result of the fall was scrapes down his left side, right knee, and bruising. |  | TRUE | Robert Bent |  | First Aid | Robert Bent |  |  |  |  | Laceration |  | FALSE |  | Plant Operator Senior | Arm |  | Left |  | Michael Booher |  |  | 4/8/2019 6:00:00 PM | 51 Weeks | FALSE |  |  | Side of the platform, and the ladder. | Walking HRSG down to perform confined space air testing.
8817 | Sooner Power Plant | 2019-04-09 14:00 | Found scaffold plank laying on top of duct work with one end of the plank being charred. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Lance Lantz | 2019-05-02 12:25 | 2019-04-09 16:41 | 2019-04-09 16:41 | 2019-04-17 16:19 | 2019-04-23 14:00 | 2019-04-09 16:34 | 2019-04-23 09:06 |  | 2019-04-19 13:52 | Sooner Unit 1 F Pulverizer Air Inlet Duct |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Lance Lantz |  | On Tuesday, April 9, 2019 at approximately 1400 an operator and safety coordinator were investigating a coal leak on 1F pulverizer. While looking for the leak they discovered a scaffolding plank laying on top of the air inlet duct to 1F pulverizer. The scaffold plank was covered in dust and appeared to have been burnt on one end. The scaffold board was removed from the top of the duct and cleaned off. The scaffold board was burnt on one end. Upon investigation it was found that scaffold boards are used to cover openings in the grating when journal doors are removed for repairs. These scaffold boards are provided by Brock, but are not tracked as a scaffold. Brock and other crews that have been working in this area were asked if they might have laid the scaffold board on the duct during the course of their work. It is believed the scaffold plank was used during the spring of 2018 outage on unit 1 mills and set on the duct when the doors and journals were being installed. The scaffold board appeared to have been laying in this location for a while. All the other scaffold planks that were used during the outage were picked up, but this board was missed since it was laying on the duct outside the grating. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Brady Sowell | Lance Lantz |  | Frank Brixey | Approve - Brixey | Frank Brixey |  | Medium | [11 empty] | 12.02.1 Inadequate reparative communication of needs | 13.07 Inadequate removal and replacement of unsuitable items |  |  |  | smoldering coal heated the board up enough to char. | 09. Improper Placement | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell |  |  |  | Property Damage |  | Lance Lantz | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Brady Sowell | N/A | N/A |  |  |  | Lance Lantz | [71 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | William Young | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | William Young | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | William Young | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | William Young | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | William Young | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.06 Inadequate work planning or programming | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | William Young | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.06 Inadequate work planning or programming | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | William Young | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.06 Inadequate work planning or programming | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | William Young | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.06 Inadequate work planning or programming | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | William Young | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | William Young | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | William Young | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | William Young | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | William Young | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | William Young | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | William Young | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | William Young | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | William Young | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | William Young | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | William Young | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | William Young | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | William Young | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | William Young | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | William Young | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | William Young | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Edward Mayberry | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Edward Mayberry | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Edward Mayberry | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Edward Mayberry | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Edward Mayberry | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.06 Inadequate work planning or programming | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Edward Mayberry | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.06 Inadequate work planning or programming | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Edward Mayberry | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.06 Inadequate work planning or programming | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Edward Mayberry | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.06 Inadequate work planning or programming | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Edward Mayberry | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Edward Mayberry | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Edward Mayberry | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Edward Mayberry | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Edward Mayberry | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Edward Mayberry | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Edward Mayberry | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Edward Mayberry | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Edward Mayberry | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Edward Mayberry | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Edward Mayberry | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Edward Mayberry | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Edward Mayberry | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Edward Mayberry | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Edward Mayberry | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Edward Mayberry | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Carol Rollins | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Carol Rollins | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Carol Rollins | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Carol Rollins | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Carol Rollins | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.06 Inadequate work planning or programming | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Carol Rollins | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.06 Inadequate work planning or programming | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Carol Rollins | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.06 Inadequate work planning or programming | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Carol Rollins | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.06 Inadequate work planning or programming | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Carol Rollins | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Carol Rollins | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Carol Rollins | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Carol Rollins | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Carol Rollins | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Carol Rollins | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Carol Rollins | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Carol Rollins | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Carol Rollins | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Carol Rollins | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Carol Rollins | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Carol Rollins | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Carol Rollins | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Carol Rollins | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Carol Rollins | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Carol Rollins | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Marcus Huddleston | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Marcus Huddleston | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Marcus Huddleston | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Marcus Huddleston | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Marcus Huddleston | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.06 Inadequate work planning or programming | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Marcus Huddleston | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.06 Inadequate work planning or programming | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Marcus Huddleston | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.06 Inadequate work planning or programming | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Marcus Huddleston | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.06 Inadequate work planning or programming | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Marcus Huddleston | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Marcus Huddleston | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Marcus Huddleston | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Marcus Huddleston | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Marcus Huddleston | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Marcus Huddleston | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Marcus Huddleston | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Marcus Huddleston | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Marcus Huddleston | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Marcus Huddleston | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Marcus Huddleston | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Marcus Huddleston | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Marcus Huddleston | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.06 Inadequate or improper controls |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Marcus Huddleston | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.06 Inadequate or improper controls |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Marcus Huddleston | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.01 Inadequate assessment of needs and risks | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8819 | Muskogee Power Plant | 2019-04-10 14:00 | While lowering the bucket, from Unit 6 chimney, the bucket hung up at the breaching level (approximately 40’ above the ground) tipping. A single brick struck contractor on hardhat. Contractor stated he was okay, but was taken to clinic for evaluation. | Level 3 |  | FALSE | Contractor | Robert Burch | William Young | The chimney contractor, HCI, is repairing and removing loose brick at the top of the MK6 Chimney brick-liner. They are lowering it with a bucket to the ground in the annulus space inside the chimney. At one time, while lowering the bucket, it got hung up at the breaching level about 40’ above the ground, and somehow, it got tumbled and partially spilled the brick (there might be a tagline). One of the falling brick hit an HCI employee, who is in-charge of retrieving the brick at the ground level, on his hard hat. He was feeling fine, but they send him to a local clinic, then St. Francis hospital at Tulsa for thorough review. | 2019-04-12 15:57 | OG&E Corp Services | Dadi Soemantri | 2019-06-12 11:50 | 2019-04-10 16:47 | 2019-04-10 16:47 | 2019-05-06 09:40 | 2019-04-24 14:00 | 2019-04-10 15:53 | 2019-05-08 21:51 | 2019-05-10 10:58 | 2019-05-06 09:55 | Muskogee PP Chimney 6 at ground level inside the chimney. |  |  | Robert Burch | No additional comments | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | During unit six stack repairs by contractor HCI, they were in the process of removing brick and lowering them to the ground in a debris barrel. As the barrel was being lowered it struck the baffle wall, tipping the barrel resulting in the loss of a brick that fell approximately 45 feet striking a worker directly on top of his hard hat. | Marcus Huddleston | William Young |  | Muskogee Power Plant | TRUE |  | FALSE | UTS - Project Mgmt |  | Dadi Soemantri | Carol Rollins |  | Carol Rollins | Reviewed. CDR 5/8/19 | Carol Rollins | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.03 Inadequate standards, specifications and/or design criteria |  |  | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Worker in line-of-fire, directly under suspended load. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | Incident investigation complete. Corrective actions implemented and complete. WCY | No additional comments. MLH 5/6/19 |  |  |  | Injury / Illness |  | Dadi Soemantri |  | Brick fell on head | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Dadi Soemantri | Hammon Custodis | Bill | Contusion |  | Head | Jerry Herriman | Top | TRUE | Company Vehicle | [68 empty] | None
8820 | Muskogee Power Plant | 2019-04-10 14:30 | Member was walking past "boiler alley way" south towards the U6 Motor rebuild shop when he felt debris enter the corner of his Right eye. Member had on all required PPE including Hard Hat Lanyard. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Supply | Daniel Moffett | 2019-07-09 07:44 | 2019-04-11 12:56 | 2019-04-11 12:56 | 2019-05-13 14:16 | 2019-04-24 14:30 | 2019-04-10 15:00 | 2019-06-24 07:42 |  | 2019-05-13 14:19 | Muskogee U6 East Side of Unit Structures Ground Level |  |  | Jesse Murray | Please add pictures of the glasses Trent was wearing and picture of how those glasses fit Trent's face. Jesse Murray Approved Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Daniel Moffett |  | JC Trent was walking from a work area to another work area, in his route he walk south of the boiler alley way. The wind was gusting close to 50mph, in the area it is known that the wind between the buildings can be amplified higher. while he was walking by he felt some dust enter his eye. JC had on all PPE and was aware of the wind as we discussed this in our morning meeting and he was wearing his hard hat lanyard attached to prevent his hard hat from blowing off of his person. He went to the Electric Shop Break room and called me and report what happened. When I came to the shop I called Bob Wright and asked for his assistance. We instructed JC not to rub his eye and we must try to wash any debris out. We first used a bottle of eye wash from the first aid cabinet and then took him to the nearby eye wash and tried flushing his eye again. He stated he felt like it was still in his eye so Bob called Med Now in Muskogee while I drove JC to the clinic. The on Staff Doctor attempted to remove the debris but felt unsuccessful so we then proceeded to the TRIAD Eye Center for a more through exam. The second exam did not show he had any debris and offered over the counter artificial tears to treat his eye and to follow up Friday 4/12 if his eye did not return to normal. The next day I noticed dirt and dust in the Alley way from outage activities and normal operation that could have become air bourn and entered his eye. The wind was blowing but not as hard as it was the day of the incident and I did not notice or feel any debris in the air. |  |  | FALSE | Muskogee Power Plant | FALSE |  | FALSE | Maintenance |  | James Trent | Daniel Moffett |  | Andy Hedge | Reviewed and approved. Andy Hedge 6/24/19 | Andy Hedge |  | Medium | [10 empty] | 11.03 Inadequate specifications to vendors |  | 13.03 Inadequate standards or specifications |  |  |  | Due to high wind and work activities dust became entrained in the wind causing dust to enter members eye | 22. Inadequate or Improper Protective Equipment | 2. Struck By (Hit By Moving Object) |  | good investigation Bob Wright | [24 empty] | FALSE |  |  | 2003-12-15 | 1966-03-16 |  | 2019-04-10 07:00 | 0 | 0 | We flushed eye with solution found in first aid kit and then went to safety eye wash and rinsed it for several minutes before transporting him to Med Now for medical treatment. The first Dr did not feel he had removed it all and directed us to Triad Eye Center. where he was given an exam to verify all debris was removed and recommended use of artificial tears for several days. | FALSE | Male | While walking past boiler alley way dust flew past his safety glasses and entered the corner of his right eye |  | TRUE | James Trent |  | First Aid | James Trent | FALSE |  | Med Now; TRIAD Eye Center | Staff Dr's @ Med Now in Muskogee and TRIAD Eye Center in Muskogee | Foreign Body |  | FALSE |  | Plant Electrician Senior | Eye |  | Right |  | Daniel Moffett |  |  | 4/10/2019 7:00:00 AM | 15 | TRUE | FALSE | FALSE | Dust, potentially Calcium Silicate insulation due to DR describing what he saw in his eye | Walking from job site to the motor rebuild shop | [24 empty] | none
8820 | Muskogee Power Plant | 2019-04-10 14:30 | Member was walking past "boiler alley way" south towards the U6 Motor rebuild shop when he felt debris enter the corner of his Right eye. Member had on all required PPE including Hard Hat Lanyard. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Supply | Daniel Moffett | 2019-07-09 07:44 | 2019-04-11 12:56 | 2019-04-11 12:56 | 2019-05-13 14:16 | 2019-04-24 14:30 | 2019-04-10 15:00 | 2019-06-24 07:42 |  | 2019-05-13 14:19 | Muskogee U6 East Side of Unit Structures Ground Level |  |  | Jesse Murray | Please add pictures of the glasses Trent was wearing and picture of how those glasses fit Trent's face. Jesse Murray Approved Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Daniel Moffett |  | JC Trent was walking from a work area to another work area, in his route he walk south of the boiler alley way. The wind was gusting close to 50mph, in the area it is known that the wind between the buildings can be amplified higher. while he was walking by he felt some dust enter his eye. JC had on all PPE and was aware of the wind as we discussed this in our morning meeting and he was wearing his hard hat lanyard attached to prevent his hard hat from blowing off of his person. He went to the Electric Shop Break room and called me and report what happened. When I came to the shop I called Bob Wright and asked for his assistance. We instructed JC not to rub his eye and we must try to wash any debris out. We first used a bottle of eye wash from the first aid cabinet and then took him to the nearby eye wash and tried flushing his eye again. He stated he felt like it was still in his eye so Bob called Med Now in Muskogee while I drove JC to the clinic. The on Staff Doctor attempted to remove the debris but felt unsuccessful so we then proceeded to the TRIAD Eye Center for a more through exam. The second exam did not show he had any debris and offered over the counter artificial tears to treat his eye and to follow up Friday 4/12 if his eye did not return to normal. The next day I noticed dirt and dust in the Alley way from outage activities and normal operation that could have become air bourn and entered his eye. The wind was blowing but not as hard as it was the day of the incident and I did not notice or feel any debris in the air. |  |  | FALSE | Muskogee Power Plant | FALSE |  | FALSE | Maintenance |  | James Trent | Daniel Moffett |  | Andy Hedge | Reviewed and approved. Andy Hedge 6/24/19 | Andy Hedge |  | Medium | [10 empty] | 11.03 Inadequate specifications to vendors |  | 13.02 Inadequate human factors/ergonomics considerations |  |  |  | Due to high wind and work activities dust became entrained in the wind causing dust to enter members eye | 22. Inadequate or Improper Protective Equipment | 2. Struck By (Hit By Moving Object) |  | good investigation Bob Wright | [24 empty] | FALSE |  |  | 2003-12-15 | 1966-03-16 |  | 2019-04-10 07:00 | 0 | 0 | We flushed eye with solution found in first aid kit and then went to safety eye wash and rinsed it for several minutes before transporting him to Med Now for medical treatment. The first Dr did not feel he had removed it all and directed us to Triad Eye Center. where he was given an exam to verify all debris was removed and recommended use of artificial tears for several days. | FALSE | Male | While walking past boiler alley way dust flew past his safety glasses and entered the corner of his right eye |  | TRUE | James Trent |  | First Aid | James Trent | FALSE |  | Med Now; TRIAD Eye Center | Staff Dr's @ Med Now in Muskogee and TRIAD Eye Center in Muskogee | Foreign Body |  | FALSE |  | Plant Electrician Senior | Eye |  | Right |  | Daniel Moffett |  |  | 4/10/2019 7:00:00 AM | 15 | TRUE | FALSE | FALSE | Dust, potentially Calcium Silicate insulation due to DR describing what he saw in his eye | Walking from job site to the motor rebuild shop | [24 empty] | none
8821 | Metro Service Center | 2019-03-19 | Distribution Operator noticed after returning a Hot Line Hold (HLHO) for a contractor on an intellirupter it appeared that the crew was issued a HLHO the morning of Tues, 3/19, but over the course of the day, switching was performed that changed the original source feed of the circuit, which ultimately led to the crew working on the circuit without having HLHO protection. | Level 3 |  | FALSE | System Operational Incident |  | Lindle Coleman | assigned with operations input | 2019-04-16 14:21 | Power Delivery | Douglas Mack | 2019-06-20 09:56 | 2019-04-12 15:05 |  | 2019-06-07 08:50 | 2019-04-30 | 2019-04-12 13:53 | 2019-06-11 09:00 | 2019-06-11 16:47 | 2019-06-07 16:10 | Distribution Control Center at Metro. |  |  |  | Approve | T&D Ops |  | Level 3 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Jeffrey Uhls |  | Operational Incident Summary On Tuesday, March 19th, 2019 a Hot Line Hold Order (HLHO) was issued by the DCC to a contractor working behind reclosing device 352900 on the Colony 4022 circuit at 0742 and was returned to the DCC at 18:21. A load transfer was conducted on the Colony 4022 circuit at 12:53 placing it on the Colony 4029 by closing the Normally Open (NO) reclosing device 35291 between the two circuits. This switching changed the direction of the feed on the Colony 4022 circuit and left the contractor crew working for approximately 4 ½ hours without proper arc flash protection. Chain of Events: • The contractor crew that was working near transformer 9942 on the Colony 4022 circuit was issued a HLHO from DCC Operator #1 at 07:42 on reclosing device 352900. o It was entered into the electronic HLHO Log which displayed the entry on the big screen located in the DCC. • At 12:53 DCC Operator #2 directed field members to execute Switching Order M0331. o This switching transferred the load on the Colony 4022 circuit to the Colony 4029 circuit by closing the NO 352910 intellirupter between the two circuits. • Upon completing their work the contractor crew called the DCC to return their HLHO on reclosing device 352900. o At 18:21 the HLHO was returned to DCC Operator #3 and the intellirupter was placed back in the Supv/Auto position. o DCC Operator #3 then entered the appropriate information into the HLHO log and closed the entry removing it from the log. • DCC Operator #3 noticed that the maps of the circuits indicated two circuits were tied together and determined that there was outstanding switching in place. o It was discovered that a load transfer conducted on SWO M0331 changed the direction of the feed on the Colony 4022 circuit that affected the returned HLHO.  The DCC Operator #3 determined that this change in direction of the feed left the contractor crew working without proper arc flash protection during part of the day. • DCC Operator #3 notified the shift supervisor on duty of the situation. Incident Facts Ascertained: • When an electronic Control Inhibit Tag is placed on an intellirupter a “C” is placed on the map at the device to indicate there is a HLHO issued on the device. o The “C” is difficult to see and can be overlooked by an operator. • The Colony 4022 circuit load transfer was scheduled for two days. • DCC Operator #2 did not review the HLHO log before directing SWO M0331. o Operator stated he does not normally look at the log; he only looks at the substation SCADA screen and at the device to be closed on the maps before directing switching. • When two circuits are tied together on the maps the circuits turn green. o This is what alerted DCC Operator #3 that there had been switching directed on these circuits. • Multiple operators conducted activities related to the Colony 4022 circuit that day. o One operator issued the HLHO in the morning, another operator directed the load transfer mid-day, while a third operator took the return of the HLHO in the late afternoon. • If recognized before directing switching order M0331, the HLHO on reclosing device 352900 could have been moved to reclosing device 352910. This would have provided the contractor crew with proper arc flash protection while working near transformer 9942. Causal Factors: • The DCC Operator did not check the HLHO log before directing SWO M0331 which transferred load on the Colony 4022 circuit onto the Colony 4029 circuit. This switching changed the direction of the feed on the Colony 4022 circuit and as a result left the contractor crew working for approximately 4 ½ hours without proper arc flash protection. Opportunities for Improvement: • Review and ensure the operator understands their specific job responsibility related to issuing HLHO or directing switching that could alter the protection being provided by the HLHO. • Improve the HLHO Log entry form to allow for information related to reclosing devices to be entered into the form by the operator. o Currently, the fields on the form relate to information related to substation breakers. o The operator’s HLHO log screen at the desk does not update until the operator exit the application and reenters the program. • Improve situational awareness for the operators relating to substation switching and the impact it may have on line devices for arc flash protection. o No indication on the substation SCADA screen alerting the operator that there is a HLHO on a reclosing device on a circuit. • Establish a process to ensure that any activities conducted on a circuit are identifiable and their impact from an operational perspective is understood before any switching is directed. | Michael Gaunder | Jeffrey Uhls |  | Metro Service Center | FALSE |  | FALSE | System Operations |  | Tyler Simpson | Douglas Mack |  | Dallas Rowley | I approve of the investigations and findings along with the associated corrective actions. I did change the priority of CA #6771 from a low to a medium. Also, CA #6500 somehow get mixed in to this incident. I believe this may be a CA for the PS group? I will discuss this with Safety. D. Rowley | Dallas Rowley | Lindle Coleman | High | [19 empty] | 6/11/19 review | I agree with Jeff's investigation findings and corrective actions. Follow up to assist with CAs. CM | [90 empty] | None
8821 | Metro Service Center | 2019-03-19 | Distribution Operator noticed after returning a Hot Line Hold (HLHO) for a contractor on an intellirupter it appeared that the crew was issued a HLHO the morning of Tues, 3/19, but over the course of the day, switching was performed that changed the original source feed of the circuit, which ultimately led to the crew working on the circuit without having HLHO protection. | Level 3 |  | FALSE | System Operational Incident |  | Lindle Coleman | assigned with operations input | 2019-04-16 14:21 | Power Delivery | Douglas Mack | 2019-06-20 09:56 | 2019-04-12 15:05 |  | 2019-06-07 08:50 | 2019-04-30 | 2019-04-12 13:53 | 2019-06-11 09:00 | 2019-06-11 16:47 | 2019-06-07 16:10 | Distribution Control Center at Metro. |  |  |  | Approve | T&D Ops |  | Level 3 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Jeffrey Uhls |  | Operational Incident Summary On Tuesday, March 19th, 2019 a Hot Line Hold Order (HLHO) was issued by the DCC to a contractor working behind reclosing device 352900 on the Colony 4022 circuit at 0742 and was returned to the DCC at 18:21. A load transfer was conducted on the Colony 4022 circuit at 12:53 placing it on the Colony 4029 by closing the Normally Open (NO) reclosing device 35291 between the two circuits. This switching changed the direction of the feed on the Colony 4022 circuit and left the contractor crew working for approximately 4 ½ hours without proper arc flash protection. Chain of Events: • The contractor crew that was working near transformer 9942 on the Colony 4022 circuit was issued a HLHO from DCC Operator #1 at 07:42 on reclosing device 352900. o It was entered into the electronic HLHO Log which displayed the entry on the big screen located in the DCC. • At 12:53 DCC Operator #2 directed field members to execute Switching Order M0331. o This switching transferred the load on the Colony 4022 circuit to the Colony 4029 circuit by closing the NO 352910 intellirupter between the two circuits. • Upon completing their work the contractor crew called the DCC to return their HLHO on reclosing device 352900. o At 18:21 the HLHO was returned to DCC Operator #3 and the intellirupter was placed back in the Supv/Auto position. o DCC Operator #3 then entered the appropriate information into the HLHO log and closed the entry removing it from the log. • DCC Operator #3 noticed that the maps of the circuits indicated two circuits were tied together and determined that there was outstanding switching in place. o It was discovered that a load transfer conducted on SWO M0331 changed the direction of the feed on the Colony 4022 circuit that affected the returned HLHO.  The DCC Operator #3 determined that this change in direction of the feed left the contractor crew working without proper arc flash protection during part of the day. • DCC Operator #3 notified the shift supervisor on duty of the situation. Incident Facts Ascertained: • When an electronic Control Inhibit Tag is placed on an intellirupter a “C” is placed on the map at the device to indicate there is a HLHO issued on the device. o The “C” is difficult to see and can be overlooked by an operator. • The Colony 4022 circuit load transfer was scheduled for two days. • DCC Operator #2 did not review the HLHO log before directing SWO M0331. o Operator stated he does not normally look at the log; he only looks at the substation SCADA screen and at the device to be closed on the maps before directing switching. • When two circuits are tied together on the maps the circuits turn green. o This is what alerted DCC Operator #3 that there had been switching directed on these circuits. • Multiple operators conducted activities related to the Colony 4022 circuit that day. o One operator issued the HLHO in the morning, another operator directed the load transfer mid-day, while a third operator took the return of the HLHO in the late afternoon. • If recognized before directing switching order M0331, the HLHO on reclosing device 352900 could have been moved to reclosing device 352910. This would have provided the contractor crew with proper arc flash protection while working near transformer 9942. Causal Factors: • The DCC Operator did not check the HLHO log before directing SWO M0331 which transferred load on the Colony 4022 circuit onto the Colony 4029 circuit. This switching changed the direction of the feed on the Colony 4022 circuit and as a result left the contractor crew working for approximately 4 ½ hours without proper arc flash protection. Opportunities for Improvement: • Review and ensure the operator understands their specific job responsibility related to issuing HLHO or directing switching that could alter the protection being provided by the HLHO. • Improve the HLHO Log entry form to allow for information related to reclosing devices to be entered into the form by the operator. o Currently, the fields on the form relate to information related to substation breakers. o The operator’s HLHO log screen at the desk does not update until the operator exit the application and reenters the program. • Improve situational awareness for the operators relating to substation switching and the impact it may have on line devices for arc flash protection. o No indication on the substation SCADA screen alerting the operator that there is a HLHO on a reclosing device on a circuit. • Establish a process to ensure that any activities conducted on a circuit are identifiable and their impact from an operational perspective is understood before any switching is directed. | Cody Magby | Jeffrey Uhls |  | Metro Service Center | FALSE |  | FALSE | System Operations |  | Tyler Simpson | Douglas Mack |  | Dallas Rowley | I approve of the investigations and findings along with the associated corrective actions. I did change the priority of CA #6771 from a low to a medium. Also, CA #6500 somehow get mixed in to this incident. I believe this may be a CA for the PS group? I will discuss this with Safety. D. Rowley | Dallas Rowley | Lindle Coleman | High | [19 empty] | 6/11/19 review | I agree with Jeff's investigation findings and corrective actions. Follow up to assist with CAs. CM | [90 empty] | None
8822 | Muskogee Power Plant | 2019-04-13 15:30 | A Contractor was using an arc gouger when one of the leads come in contact with the control power box for 6D1 ignitor causing damage to the top of the box. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Zackary Thompson | 2019-07-02 09:42 | 2019-04-14 12:42 | 2019-04-14 12:42 | 2019-06-13 15:58 | 2019-04-27 15:30 | 2019-04-14 12:32 | 2019-06-13 15:59 |  |  | Muskogee PP 6 boiler level 8 corner 1 |  |  | Robert Wright | Approved Bob Wright | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Jerry Knight |  | Welding lead separated and the live end struck and damaged 6D1 igniter control box. A welder had been gouging on the upper levels of the boiler when he lost his connection. As he traced his lead back to the source he noticed the welding lead had come loose from a connector. It fell to the level below striking and arcing out on top of a 6D1 igniter control box. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | Maintenance |  | David Englebretson | Zackary Thompson |  | Jerry Knight | Add notes and attachments of documents and pictures. | Jerry Knight |  | Low | [14 empty] | 15.03 Inadequate inspection and/or monitoring |  | Welding lead got hot,Causing the Welding lead to come apart and arc out on the igniter box. | 23. Defective Tools, Equipment or Materials | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [68 empty] | 6D1 ignitor control box was damaged beyond repair and will have to be replaced. | 1500 | Zachary | Fixed Equipment | [20 empty] | none
8823 | South District Service Center | 2019-04-15 11:30 | While releasing auger to dig the second hole of the day, bolt holding Kelly bar and auger in place, sheared off causing assembly to fall to the ground. Members had discussed staying out of the bit (pinch point) while releasing auger to the ground, in preparation of digging hole. The bolt was replaced and work continued without incident. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Delivery | Gary Parks | 2019-04-30 12:55 | 2019-04-16 07:41 | 2019-04-16 07:41 | 2019-04-25 12:29 | 2019-04-29 11:30 | 2019-04-16 07:30 | 2019-04-29 14:13 |  | 2019-04-26 12:19 | SE 86th and Sunnylane, Okc. Wild Mary Sub training facility |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Gary Parks |  | South construction crew was setting up on there second job of the day. Members had discussed staying out of the bite (pinch point) on their tailboard. At this time they began to position the auger in preparation of digging the hole. When they released the auger the bolt securing the Kelly bar assembly was sheered and the Completed assembly fell to the ground. At this time the crew stood down to analyze what happened and alert their supervisor. The foreman replaced the bolt and work was resumed. |  |  |  | South District Service Center | FALSE |  | TRUE | Construction Services |  | Dusty Stejskal | Gary Parks |  | Terry Garrett | I approve.....TG | Terry Garrett |  | Medium | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | the cause of the close call was the bolt sheering that connects the auger to the Kelly bar | 23. Defective Tools, Equipment or Materials | 2. Struck By (Hit By Moving Object) |  | in addition to discussing key learnings on the call and in the may T&D safety agenda, I believe it is important to have these bolts removed and inspected upon PM's. | [90 empty] | n/a
8825 | Metro Service Center | 2019-04-16 10:00 | Contractor did not follow appropriate procedure for entering facility or performing work. | Level 2 |  | FALSE | Contractor |  |  |  |  | OGE Energy Corp | Phillip Messer | 2019-05-23 08:42 | 2019-04-17 07:58 | 2019-04-17 07:58 | 2019-04-29 14:32 | 2019-04-30 10:00 | 2019-04-17 07:47 | 2019-05-15 13:01 |  | 2019-04-29 14:36 | Seminole Power Plant warehouse |  |  | William Young | Reviewed and approved. WCY | Enterprise Services |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Phillip Messer |  | Seminole PP contacted Facilities for repair to be performed on North crane bay OH door. Work was assigned to Facility Coordinator on 8/15/19. Prior to work day, coordinator notified both plant members and vendor via email for scheduled timelines (8/16/19) of proposed work. At 10:00 am contractor PDC reported to the guard shack and was allowed to proceed into Plant grounds, neither guard or vendor notified Plant contact prior to entrance. Investigation also revealed vendor did not check into control room and did not request LOTO prior to beginning work. At approximately 11:30 am, post repair, a PDC contractor went into the planner office requesting power to be turned on to the overhead door. Both SM Planners called the Shift Supervisor (SS) to request help for PDC in their troubleshooting efforts. Both Planners were unaware of PDC contractors being onsite prior to them coming to the planners’ office. The SS sent a plant operator down to assist. The plant operator engaged the breaker so PDC could operate the overhead door. Planner spoke to MPM/O during which a questions was raised about whether they had pulled a LOTO. The MPM/O and planner called the SS back and asked if PDC had been to the Control Room and asked for a LOTO prior to requesting power to operate the door. Once the SS confirmed that there was no LOTO on the overhead door, the planner went down to the basement area to talk to the PDC contractors. He asked them who they had contacted in the Control Room. The other contractor said he didn’t know who he spoke to, it was just somebody in the Control Room. The planner told them that they were not under a proper LOTO and he asked them to stop until Operations got with them. The PDC contractor informed the planner that he saw the tag, which was just a Caution Tag, on the door controls. (LOTO had not been taken for OH door after failure.) The PDC contractor stated he did not do anything electrical. All he did was adjust the motor drive and put the chain back on the sprocket. The SS then asked the MPM/O if we were going to let PDC finish adjusting the spring on the door. The MPM/O agreed if a proper LOTO was in place. A simple LOTO was hung and PDC was allowed to proceed. |  |  |  | Metro Service Center | FALSE |  | FALSE | Real Estate |  | Paul Schoelen | Phillip Messer |  | Vance Krebs | Proper plant contact will be obtained before any future work by contractors. | Vance Krebs |  | Medium | [5 empty] | 6.02 Inadequate practice | [10 empty] | Contractor did not follow appropriate procedure for entering facility or performing work. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved, Cody Vinyard |  |  |  | Clearance / LOTO |  | Phillip Messer | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Paul Schoelen | PDC | Gabe Wiyninger |  |  |  | Phillip Messer | [71 empty] | .
8826 | Sooner Power Plant | 2019-04-16 17:30 | It was discovered that an Emergency Stop button on bottom ash system was used as a boundary and part of LOTO to prevent a machine from starting. This is not recommended by OSHA | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Jimmie Allen | 2019-05-16 10:43 | 2019-04-17 15:16 | 2019-04-17 15:16 | 2019-04-30 15:44 | 2019-04-30 17:30 | 2019-04-16 17:30 | 2019-04-30 15:44 |  |  | Sooner Power Plant Bottom Ash Area |  |  | Brady Sowell | approved | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Alexander Taybah |  | A member was trying to sign onto a LOTO to get into the boiler and one of the boundaries was an Emergency Stop (E-Stop) push bottom. The member notified the Operating Authority that E-Stops are not considered boundaries per OSHA. Further follow up by the OA revealed that this equipment was specifically requested for the purpose of protecting the actual equipment, not as a boundary for potential safety of personnel. Emergency stop buttons or electronic red tags are not used for an actual boundary on a LOTO for protection of employees. This equipment was requested because of a prior incident that involved climber cables getting caught in the clinker grinder when the climber was used on a wall tube lower in the boiler and the cable slack was hanging lower than it would normally hang. The breakers for the clinker grinders are to be used instead of the E-Stop. In the past, the E-Stop was given an equipment number to make sure the system is off when changing out bottom ash rams. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Operations |  | Frank Brixey | Alexander Taybah |  | Alexander Taybah | I approve. | Alexander Taybah |  | Low | [5 empty] | 6.01 Inadequate initial instruction | [10 empty] | It was discovered that an Emergency Stop button on bottom ash system was used as a boundary and part of LOTO to prevent a machine from starting. This is not recommended by OSHA | 16. Failure to Follow Procedure, Policy, Practice | 5. Caught In (Pinch and Nip Points) | [92 empty] | 9582116
8826 | Sooner Power Plant | 2019-04-16 17:30 | It was discovered that an Emergency Stop button on bottom ash system was used as a boundary and part of LOTO to prevent a machine from starting. This is not recommended by OSHA | Level 1 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Jimmie Allen | 2019-05-16 10:43 | 2019-04-17 15:16 | 2019-04-17 15:16 | 2019-04-30 15:44 | 2019-04-30 17:30 | 2019-04-16 17:30 | 2019-04-30 15:44 |  |  | Sooner Power Plant Bottom Ash Area |  |  | Brady Sowell | approved | Power Supply |  | Level 1 | Property Damage |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Alexander Taybah |  | A member was trying to sign onto a LOTO to get into the boiler and one of the boundaries was an Emergency Stop (E-Stop) push bottom. The member notified the Operating Authority that E-Stops are not considered boundaries per OSHA. Further follow up by the OA revealed that this equipment was specifically requested for the purpose of protecting the actual equipment, not as a boundary for potential safety of personnel. Emergency stop buttons or electronic red tags are not used for an actual boundary on a LOTO for protection of employees. This equipment was requested because of a prior incident that involved climber cables getting caught in the clinker grinder when the climber was used on a wall tube lower in the boiler and the cable slack was hanging lower than it would normally hang. The breakers for the clinker grinders are to be used instead of the E-Stop. In the past, the E-Stop was given an equipment number to make sure the system is off when changing out bottom ash rams. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Operations |  | Frank Brixey | Alexander Taybah |  | Alexander Taybah | I approve. | Alexander Taybah |  | Low | [5 empty] | 6.01 Inadequate initial instruction | [10 empty] | It was discovered that an Emergency Stop button on bottom ash system was used as a boundary and part of LOTO to prevent a machine from starting. This is not recommended by OSHA | 16. Failure to Follow Procedure, Policy, Practice | 5. Caught In (Pinch and Nip Points) | [92 empty] | 9582116
8827 | Muskogee Power Plant | 2019-04-17 15:00 | Insufficient boundary for hot work overhead. Hot slag falling in area where members and contractors could be injured. I&C technician went up to the job and stopped it. Contractors increased the area of the boundary. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Randall Miller | 2019-07-14 12:53 | 2019-04-17 15:48 | 2019-04-17 15:48 | 2019-07-02 08:15 | 2019-05-01 15:00 | 2019-04-17 15:42 | 2019-07-03 15:15 |  | 2019-07-02 10:22 | North side of unit 6 boiler, ground level |  |  | Jesse Murray | Approve Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Randall Miller |  | Contractors had not sufficiently guarded against sparks coming from overhead. The wind had shifted and their barrier was no longer containing slag from cutting operations. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Maintenance |  | Randall Miller | Randall Miller |  | Andy Hedge | Reviewed and approved. Andy Hedge 7/3/19 | Andy Hedge |  | Medium |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming | [7 empty] | Insufficient guarding from overhead arc gouging | 21. Inadequate Guards or Barriers | 1. Struck Against (Running or Bumping Into) |  | Reviewed Bob Wright |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Randall Miller | [5 empty] | 2. Struck By (Hit By Moving Object) | Randall Miller | Zachary | Mann Self |  |  |  | Randall Miller | [71 empty] | 323802
8827 | Muskogee Power Plant | 2019-04-17 15:00 | Insufficient boundary for hot work overhead. Hot slag falling in area where members and contractors could be injured. I&C technician went up to the job and stopped it. Contractors increased the area of the boundary. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Randall Miller | 2019-07-14 12:53 | 2019-04-17 15:48 | 2019-04-17 15:48 | 2019-07-02 08:15 | 2019-05-01 15:00 | 2019-04-17 15:42 | 2019-07-03 15:15 |  | 2019-07-02 10:22 | North side of unit 6 boiler, ground level |  |  | Jesse Murray | Approve Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Randall Miller |  | Contractors had not sufficiently guarded against sparks coming from overhead. The wind had shifted and their barrier was no longer containing slag from cutting operations. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Maintenance |  | Randall Miller | Randall Miller |  | Andy Hedge | Reviewed and approved. Andy Hedge 7/3/19 | Andy Hedge |  | Medium |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Insufficient guarding from overhead arc gouging | 21. Inadequate Guards or Barriers | 1. Struck Against (Running or Bumping Into) |  | Reviewed Bob Wright |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Randall Miller | [5 empty] | 2. Struck By (Hit By Moving Object) | Randall Miller | Zachary | Mann Self |  |  |  | Randall Miller | [71 empty] | 323802
8828 | Metro Service Center | 2019-04-16 | Substation construction coordinator received call from TCC operator to place MOS 139 from manual to supervisor mode at the Degrasse substation. While performing the switching process the coordinator inadvertently hit the open button instead of the supervisor button. | Level 1 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Kenny La Ferney | 2019-05-13 11:36 | 2019-04-18 10:49 |  | 2019-04-30 14:21 | 2019-05-28 | 2019-04-17 14:00 | 2019-05-13 07:46 |  |  | Degrasse Substation |  |  | Cody Magby | approve these findings and CAs. The incident was a human error with little in the way of possible corrective actions. Member is well experienced and did not make the error out of confusion or misunderstanding. His finger accidentally hit the open button on the control panel. Buttons are in close proximity to one another and could very easily be pushed inadvertently. | T&D Ops |  | Level 1 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Kenny La Ferney |  | Substation construction coordinator received call from TCC operator to place MOS 139 from manual to supervisor mode at the Degrasse substation. Switching process was done via phone call (switching log). While going through switching process the coordinator received permission to place MOS 139 on supervisor mode. coordinator repeated the directions back to TCC operator. The coordinator inadvertently pressed open instead of supervisor button. The coordinators phone dropped the call after receiving the order. The coordinator immediately noticed the error and called TCC back to get further instructions. TCC operator asked if there was any damage to the switch, there was not, operator instructed him to proceed with placing in supervisor mode. Once in supervisor mode TCC operator closed the switch through SCADA. There was no injury, damage to equipment, or load loss. The substation had not been energized to the transformer because it is a newly built substation. After discussions with member it was determined there was no miscommunication, no misunderstanding, this was a human error. He inadvertently pressed the wrong button. |  |  |  | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Wayne Adams | Kenny La Ferney |  | Gary Lassley | Review switching SOP with member and discuss the extreme importance of performing error free switching, and the potential severity associated with switching errors. Also discuss the importance of checking and double checking before each step of switching. | Gary Lassley |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Member pressed the wrong button on relay during switching process. The open button was inadvertently hit while preparing to hit the supervisor button. | 19. Failure to React, Correct | 9. Abnormal Operation | [92 empty] | 1645462
8829 | Seminole PP; EGX Gath/Trans | 2019-04-18 10:00 | Contractor electrician got a foreign object in his eye due to blowing dust after a cart drove by and stirred up the dust. | Level 1 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services |  | 2019-05-06 15:42 | 2019-04-18 12:50 | 2019-04-18 12:50 | 2019-05-03 13:37 | 2019-05-02 10:00 | 2019-04-18 12:35 | 2019-05-06 12:35 |  |  | Seminole PP Unit 3B FD fan |  |  | Marcus Huddleston | No additional comments. MLH 5/6/19. | UTS |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | Later in the day of the incident, it was determined that this remained a first aid case. No further action was necessary. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | No further comments - CBL 05/06/19 | Christopher Lelak |  | Low | [9 empty] | 10.02 Inadequate consideration of human factors/ergonomics |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | Flying debris | 39. Road Conditions | 2. Struck By (Hit By Moving Object) | [5 empty] | Injury / Illness |  | Marcus Huddleston |  | Debris in eye. | FALSE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Danny Pogue | ECA | Dragan Grybisic | Foreign Body |  | Eye |  | Right | FALSE | [69 empty] | 1646037
8830 | Metro Service Center | 2019-04-18 10:00 | Substation construction coordinator was in route to deliver material to Red Corn substation. He had a 12'6" switching stick tied down in back of his pickup. The stick is too long to fit in the carrier tube, member had the stick leaned up in the bed against the head ache rack and tied in with pull rope. The stick came loose and flew out of the truck. Member heard a noise and noticed stick was gone, turned around to retrieve the stick. No vehicle damage to OGE or 3rd party, stick was damaged. | Level 2 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Kenny La Ferney | 2019-06-04 14:52 | 2019-04-18 16:35 | 2019-04-18 16:35 | 2019-05-29 13:49 | 2019-05-02 10:00 | 2019-04-18 15:30 | 2019-06-04 14:07 |  | 2019-06-01 17:55 | 59th and Interstate 240 |  |  | Lindle Coleman | Recommendation is to create a more irreversible corrective action item. for example. describe how to secure properly or can we discontinue using the material (white flat rope type) that failed? Or do we need to install a switch stick tube holder? FOLLOW UP TO CONCERNS COMPLETED 6/4/19 | T&D Ops |  | Level 2 | Vehicle |  | FALSE | FALSE | TRUE |  | FALSE | TRUE | Kenny La Ferney |  | Substation construction coordinator was in route to deliver material to Red Corn substation. He had a 12'6" switching stick tied down in back of his pickup. The stick is too long to fit in the carrier tube, member had the stick leaned up in the bed against the head ache rack and tied in with pull rope. The stick came loose and flew out of the truck. Member heard a noise and noticed stick was gone, turned around to retrieve the stick. No vehicle damage to OGE or 3rd party, stick was damaged. The member tied the stick on the headache rack but in transit the knot came untied. The wind caught the stick and flipped it up and over the truck rack landing on the edge of the roadway. Member turned around and returned to pick up the stick and proceeded to the work site. Member had loaded the stick on the truck the night before and did his 360 walk around before leaving that morning. Not able to determine what caused the rope to come untied other than high winds and being tied to the headache rack just above the cab of the pickup. The stick was too long to fit in the carrying tube and due to the flexibility of the fiberglass member was afraid of strapping it down too tightly with a ratchet strap. |  |  |  | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Roy Hoffman | Kenny La Ferney |  | Gary Lassley | Discuss current methods for transporting tools and materials. Go over any possibilities for safer transport methods. | Gary Lassley |  | Medium | [12 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | Switching stick came untied while travelling to worksite. Stick was tied with rope to the headache rack. | 03. Failure to Secure | 9. Abnormal Operation |  | Approved. Continue to push the importance of proper load securement and obtain temporary transport tubes for switching sticks | [66 empty] | Fiberglass Switching stick damaged | 400 | Roy Hoffman | Portable Tool |  | F04-516 | FALSE |  | Oklahoma City | Other | Loss of Cargo/Material | 1992-02-23 18:00 |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Clear |  |  | none
8830 | Metro Service Center | 2019-04-18 10:00 | Substation construction coordinator was in route to deliver material to Red Corn substation. He had a 12'6" switching stick tied down in back of his pickup. The stick is too long to fit in the carrier tube, member had the stick leaned up in the bed against the head ache rack and tied in with pull rope. The stick came loose and flew out of the truck. Member heard a noise and noticed stick was gone, turned around to retrieve the stick. No vehicle damage to OGE or 3rd party, stick was damaged. | Level 2 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Kenny La Ferney | 2019-06-04 14:52 | 2019-04-18 16:35 | 2019-04-18 16:35 | 2019-05-29 13:49 | 2019-05-02 10:00 | 2019-04-18 15:30 | 2019-06-04 14:07 |  | 2019-06-01 17:55 | 59th and Interstate 240 |  |  | Lindle Coleman | Recommendation is to create a more irreversible corrective action item. for example. describe how to secure properly or can we discontinue using the material (white flat rope type) that failed? Or do we need to install a switch stick tube holder? FOLLOW UP TO CONCERNS COMPLETED 6/4/19 | T&D Ops |  | Level 2 | Vehicle |  | FALSE | FALSE | TRUE |  | FALSE | TRUE | Kenny La Ferney |  | Substation construction coordinator was in route to deliver material to Red Corn substation. He had a 12'6" switching stick tied down in back of his pickup. The stick is too long to fit in the carrier tube, member had the stick leaned up in the bed against the head ache rack and tied in with pull rope. The stick came loose and flew out of the truck. Member heard a noise and noticed stick was gone, turned around to retrieve the stick. No vehicle damage to OGE or 3rd party, stick was damaged. The member tied the stick on the headache rack but in transit the knot came untied. The wind caught the stick and flipped it up and over the truck rack landing on the edge of the roadway. Member turned around and returned to pick up the stick and proceeded to the work site. Member had loaded the stick on the truck the night before and did his 360 walk around before leaving that morning. Not able to determine what caused the rope to come untied other than high winds and being tied to the headache rack just above the cab of the pickup. The stick was too long to fit in the carrying tube and due to the flexibility of the fiberglass member was afraid of strapping it down too tightly with a ratchet strap. |  |  |  | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Roy Hoffman | Kenny La Ferney |  | Gary Lassley | Discuss current methods for transporting tools and materials. Go over any possibilities for safer transport methods. | Gary Lassley |  | Medium | [12 empty] | 13.03 Inadequate standards or specifications |  |  |  | Switching stick came untied while travelling to worksite. Stick was tied with rope to the headache rack. | 03. Failure to Secure | 9. Abnormal Operation |  | Approved. Continue to push the importance of proper load securement and obtain temporary transport tubes for switching sticks | [66 empty] | Fiberglass Switching stick damaged | 400 | Roy Hoffman | Portable Tool |  | F04-516 | FALSE |  | Oklahoma City | Other | Loss of Cargo/Material | 1992-02-23 18:00 |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Clear |  |  | none
8830 | Metro Service Center | 2019-04-18 10:00 | Substation construction coordinator was in route to deliver material to Red Corn substation. He had a 12'6" switching stick tied down in back of his pickup. The stick is too long to fit in the carrier tube, member had the stick leaned up in the bed against the head ache rack and tied in with pull rope. The stick came loose and flew out of the truck. Member heard a noise and noticed stick was gone, turned around to retrieve the stick. No vehicle damage to OGE or 3rd party, stick was damaged. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Delivery | Kenny La Ferney | 2019-06-04 14:52 | 2019-04-18 16:35 | 2019-04-18 16:35 | 2019-05-29 13:49 | 2019-05-02 10:00 | 2019-04-18 15:30 | 2019-06-04 14:07 |  | 2019-06-01 17:55 | 59th and Interstate 240 |  |  | Lindle Coleman | Recommendation is to create a more irreversible corrective action item. for example. describe how to secure properly or can we discontinue using the material (white flat rope type) that failed? Or do we need to install a switch stick tube holder? FOLLOW UP TO CONCERNS COMPLETED 6/4/19 | T&D Ops |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | TRUE | Kenny La Ferney |  | Substation construction coordinator was in route to deliver material to Red Corn substation. He had a 12'6" switching stick tied down in back of his pickup. The stick is too long to fit in the carrier tube, member had the stick leaned up in the bed against the head ache rack and tied in with pull rope. The stick came loose and flew out of the truck. Member heard a noise and noticed stick was gone, turned around to retrieve the stick. No vehicle damage to OGE or 3rd party, stick was damaged. The member tied the stick on the headache rack but in transit the knot came untied. The wind caught the stick and flipped it up and over the truck rack landing on the edge of the roadway. Member turned around and returned to pick up the stick and proceeded to the work site. Member had loaded the stick on the truck the night before and did his 360 walk around before leaving that morning. Not able to determine what caused the rope to come untied other than high winds and being tied to the headache rack just above the cab of the pickup. The stick was too long to fit in the carrying tube and due to the flexibility of the fiberglass member was afraid of strapping it down too tightly with a ratchet strap. |  |  |  | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Roy Hoffman | Kenny La Ferney |  | Gary Lassley | Discuss current methods for transporting tools and materials. Go over any possibilities for safer transport methods. | Gary Lassley |  | Medium | [12 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | Switching stick came untied while travelling to worksite. Stick was tied with rope to the headache rack. | 03. Failure to Secure | 9. Abnormal Operation |  | Approved. Continue to push the importance of proper load securement and obtain temporary transport tubes for switching sticks | [66 empty] | Fiberglass Switching stick damaged | 400 | Roy Hoffman | Portable Tool |  | F04-516 | FALSE |  | Oklahoma City | Other | Loss of Cargo/Material | 1992-02-23 18:00 |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Clear |  |  | none
8830 | Metro Service Center | 2019-04-18 10:00 | Substation construction coordinator was in route to deliver material to Red Corn substation. He had a 12'6" switching stick tied down in back of his pickup. The stick is too long to fit in the carrier tube, member had the stick leaned up in the bed against the head ache rack and tied in with pull rope. The stick came loose and flew out of the truck. Member heard a noise and noticed stick was gone, turned around to retrieve the stick. No vehicle damage to OGE or 3rd party, stick was damaged. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Delivery | Kenny La Ferney | 2019-06-04 14:52 | 2019-04-18 16:35 | 2019-04-18 16:35 | 2019-05-29 13:49 | 2019-05-02 10:00 | 2019-04-18 15:30 | 2019-06-04 14:07 |  | 2019-06-01 17:55 | 59th and Interstate 240 |  |  | Lindle Coleman | Recommendation is to create a more irreversible corrective action item. for example. describe how to secure properly or can we discontinue using the material (white flat rope type) that failed? Or do we need to install a switch stick tube holder? FOLLOW UP TO CONCERNS COMPLETED 6/4/19 | T&D Ops |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | TRUE | Kenny La Ferney |  | Substation construction coordinator was in route to deliver material to Red Corn substation. He had a 12'6" switching stick tied down in back of his pickup. The stick is too long to fit in the carrier tube, member had the stick leaned up in the bed against the head ache rack and tied in with pull rope. The stick came loose and flew out of the truck. Member heard a noise and noticed stick was gone, turned around to retrieve the stick. No vehicle damage to OGE or 3rd party, stick was damaged. The member tied the stick on the headache rack but in transit the knot came untied. The wind caught the stick and flipped it up and over the truck rack landing on the edge of the roadway. Member turned around and returned to pick up the stick and proceeded to the work site. Member had loaded the stick on the truck the night before and did his 360 walk around before leaving that morning. Not able to determine what caused the rope to come untied other than high winds and being tied to the headache rack just above the cab of the pickup. The stick was too long to fit in the carrying tube and due to the flexibility of the fiberglass member was afraid of strapping it down too tightly with a ratchet strap. |  |  |  | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Roy Hoffman | Kenny La Ferney |  | Gary Lassley | Discuss current methods for transporting tools and materials. Go over any possibilities for safer transport methods. | Gary Lassley |  | Medium | [12 empty] | 13.03 Inadequate standards or specifications |  |  |  | Switching stick came untied while travelling to worksite. Stick was tied with rope to the headache rack. | 03. Failure to Secure | 9. Abnormal Operation |  | Approved. Continue to push the importance of proper load securement and obtain temporary transport tubes for switching sticks | [66 empty] | Fiberglass Switching stick damaged | 400 | Roy Hoffman | Portable Tool |  | F04-516 | FALSE |  | Oklahoma City | Other | Loss of Cargo/Material | 1992-02-23 18:00 |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Clear |  |  | none
8831 | Seminole PP; EGX Gath/Trans | 2019-04-15 12:00 | Overhead door fell approximately 10 feet in tracks during operation. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Paul Schoelen | 2019-05-02 12:34 | 2019-04-19 07:58 | 2019-04-19 07:58 | 2019-04-19 13:48 | 2019-04-29 12:00 | 2019-04-15 12:30 | 2019-04-22 09:53 |  | 2019-04-19 14:56 | SMPP crane bay basement |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Paul Schoelen |  | On Monday, 4/15 an OG&E member went to help a contractor move a trash dumpster from the crane bay. When they were finished the OG&E member began to close the overhead door. On the way down the dropped suddenly dropped the last 10 feet to ground. There were no injuries and the door was not damaged. PDS was called to check the door. They determined the drive chain had loosened up and slipped off the motor. They also found the door spring was out of adjustment. The spring being out of adjustment it was allowed the door to fall when the chain came off. PDC made the repairs and the door was placed back in to service. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | TRUE | Other |  | Michael Hammett | Paul Schoelen |  | Scott Lee | I have reviewed this incident report and I approve. | Scott Lee |  | Medium | [11 empty] | 12.01.3 Inadequate preventative adjustment/assembly |  |  |  |  | Door drive chain slipped off the motor and the door fell 10 feet | 23. Defective Tools, Equipment or Materials | 9. Abnormal Operation |  | Reviewed and approved. | [90 empty] | N/A
8831 | Seminole PP; EGX Gath/Trans | 2019-04-15 12:00 | Overhead door fell approximately 10 feet in tracks during operation. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Paul Schoelen | 2019-05-02 12:34 | 2019-04-19 07:58 | 2019-04-19 07:58 | 2019-04-19 13:48 | 2019-04-29 12:00 | 2019-04-15 12:30 | 2019-04-22 09:53 |  | 2019-04-19 14:56 | SMPP crane bay basement |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Paul Schoelen |  | On Monday, 4/15 an OG&E member went to help a contractor move a trash dumpster from the crane bay. When they were finished the OG&E member began to close the overhead door. On the way down the dropped suddenly dropped the last 10 feet to ground. There were no injuries and the door was not damaged. PDS was called to check the door. They determined the drive chain had loosened up and slipped off the motor. They also found the door spring was out of adjustment. The spring being out of adjustment it was allowed the door to fall when the chain came off. PDC made the repairs and the door was placed back in to service. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | TRUE | Other |  | Michael Hammett | Paul Schoelen |  | Scott Lee | I have reviewed this incident report and I approve. | Scott Lee |  | Medium | [11 empty] | 12.01.3 Inadequate preventative adjustment/assembly |  |  |  |  | Door drive chain slipped off the motor and the door fell 10 feet | 23. Defective Tools, Equipment or Materials | 9. Abnormal Operation |  | Reviewed and approved. | [90 empty] | N/A
8832 | Horseshoe Lake Power Plant | 2019-04-18 17:00 | On April 18, 2019 at approx. 17:00 Unit 6 Gas Recirc fan failed to start. When troubleshooting it was found to still have a Locked out Breaker with tag and lock and a tag on the control power. However, the LOTO had been returned on April 12, 2019 @ 17:47 by the shift about to go home. | Level 1 |  | FALSE | System Operational Incident |  |  |  |  | Power Supply | Michael Kennedy | 2019-07-19 14:43 | 2019-04-19 15:10 |  | 2019-06-27 22:36 | 2019-05-30 16:00 | 2019-04-19 14:42 | 2019-07-10 06:28 |  |  | Unit 6 Gas Recirc Fan |  |  | Guillermo Sarmiento | 07/15/16 - Still reviewing, have some additional questions. 07/17/2019 - added corrective action after the call. Approve of investigation and corrective action. | Power Supply |  | Level 1 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Peter Nowakowski |  | On 4/12/2019 Operations were lifting a LOTO on Unit 6 Gas Recirc Fan just prior to going off shift for the day. During this process one member went out early opened some breaker doors he knew was associated with the untagging list then suited up in a 100 cal suit while the other member was doing a couple of steps on the untagging list. Suited member closed all breakers on the doors that were opened while other member took off locks and tags from the breakers being racked in. Once breakers were racked in suited member went to take off the 100 cal suit while the other member completed the last few steps of the LOTO. Both members met back at the control room and initialed steps complete not realizing they had missed one piece of equipment because they didn't compare tags in hand verse untagging list. Findings: - The equipment was left in a safe state, members were not exposed to hazardous energy at any point in time. - The 100cal suit was utilized because it is the only suit HSL currently has available; will purchase 40cal suits. - Shifts try not to transfer returning LOTO's to oncoming shift "mid-flight;" a self sense of urgency was created due to it being near end of shift. - Un-tagging list was not initialed as completed after each step was completed; instead it was all done after the fact. - Potential damage to property and equipment was minor; potential delay in coming online may be result. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Operations |  | Billy Spinks | Kyle Thornton |  | Robert Doupe | RDD Approve | Robert Doupe |  | Low |  |  |  | 4.04 Routine, monotony, demand for uneventful vigilance |  |  |  |  | 9.06 Inadequate work planning or programming | [7 empty] | Operators omitted step(s) in return process of LOTO. LOTO was returned in WCM indicating all equipment was ready for service. | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation | [92 empty] | none
8833 | Sooner Power Plant | 2019-04-19 17:00 | *First Aid* Member experienced discomfort in eyes following a shift of assisting with boiler repairs | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Supply | Michael Dowell | 2019-04-30 15:40 | 2019-04-20 08:04 | 2019-04-20 08:04 | 2019-04-20 08:15 | 2019-05-03 17:00 | 2019-04-20 07:55 |  |  |  | Sooner PP Unit 2 Boiler Water Walls |  |  | Brady Sowell | approved by Brady Sowell | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | [5 empty] | FALSE | Sooner Power Plant | FALSE |  | FALSE | Maintenance |  | Brian St Andrews | Michael Dowell |  |  |  | Frank Brixey |  | Low | [45 empty] | FALSE |  |  | 2005-10-10 | 1978-02-15 |  | 2019-04-19 07:30 | 0 | 0 | Member applied an over the counter eye drop to his eye before returning to work the next day. | FALSE | Male | Member was on suspended scaffold with another member that was welding. |  | TRUE | Brian St Andrews |  | First Aid | Brian St Andrews |  |  |  |  | Burn: Welding/Flash |  | FALSE |  | Plant Mechanic Senior | Eye |  | Top |  | Michael Dowell |  |  | 4/19/2019 7:30:00 AM | 13 | FALSE |  |  | Welding Arc/Flash | Assisting with boiler tube repair. Cutting and prepping boiler tubes
8834 | Seminole PP; EGX Gath/Trans | 2019-04-22 11:00 | Plant was preparing for a bump test to determine rotation on the SM2 2A FD fan motor, which was uncoupled from the fan. The coupling halves were pulled back and secured by a strap and bolts. During the rotation of the motor, the nuts on the bolts securing the fan coupling half worked loose and the strap the was allowed to spin in the space between the shafts. Upon noticing this condition, the motor was shut down to eliminate this condition. | Level 2 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services |  | 2019-05-10 10:54 | 2019-04-22 17:08 | 2019-04-22 17:08 | 2019-05-03 14:59 | 2019-05-06 11:00 | 2019-04-22 16:57 | 2019-05-06 12:36 |  | 2019-05-06 09:54 | Seminole PP Unit 2A FD Fan |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | Coupling halves on 2A FD fan were inadequately restrained, causing the bolt and strap restraint to come loose when the fan was running. This could have resulted in an injury if a person was in close proximity to the coupling. The remedy for this situation was to restrain the coupling halves by wiring/turnbuckling them back to a fixed portion of the machinery and keep significant distance between the halves. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | TRUE | UTS - Capital Projects |  | Scott Lee |  |  | Christopher Lelak | No further comments - CBL 05/06/19 | Christopher Lelak |  | Medium | [8 empty] | 9.06 Inadequate work planning or programming | [7 empty] | Strap restraining coupling housing was not adequately tightened to prevent mechanism to come apart in operation. | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) |  | No additional comments. MLH 5/6/19. |  |  |  | Injury / Illness | [7 empty] | 2. Struck By (Hit By Moving Object) | Scott Lee | Clarage/AirTek | Unknown | [75 empty] | 1646031
8835 | Sooner Power Plant | 2019-04-23 00:30 | Member was using a post driver to drive sign posts into the ground. As member was driving the post down the driver hung up on the post and the driver hit the member on top of the head. Took to emergency room for concussion evaluation. Everything ok, released for work | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Supply | Trent Novotny | 2019-05-22 10:12 | 2019-04-23 05:09 | 2019-04-23 05:09 | 2019-05-06 16:28 | 2019-05-07 00:30 | 2019-04-23 04:56 | 2019-05-13 08:35 |  | 2019-05-07 07:31 | Sooner PP near the boat house |  |  | Jesse Murray | I Approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Frank Brixey |  | On April 23rd at approximately 23:30, member 1 and member 2 went out to the intake dikes to pull up 5' T-posts with signs and put in 8' sign posts for signage. The members stood on the flat platform of the Tommy Lift to drive the sign posts due to the 8' length of the posts. Member 1 drove in the first 2 posts with no incident. On the third post, member 2 asked to drive it in. Member 2 began to drive it in with the post driver. On the 3rd or 4th strike he accidentally pulled the driver up too far allowing it to catch the edge of the post kicking over subsequently striking member 2 in the head. The blow dazed him and put a small gash (~1/2") in the top of his head. He slumped backward into the bed of the truck. EMR team checked him out took vitals and cleaned up cut. Member 2 wasn’t answering questions about things that happened during the incident and couldn’t remember some things that happened in the previous days so the EMR member drove member 1 and member 2 to ER. A CAT scan was performed, cleaned up the wound, and gave him a Tetanus shot. Member returned to work that night with no restrictions. Upon the investigation it was found that on the drive to the work location the members took their hard hats off while in the vehicle. Once at the work location, member 2 did not put on his hard hat and was not wearing it at the time of the incident. Neither member could remember if member 1 was wearing hard hat or not. An SWP was not filled out for this job. T Post driver is a shop made driver that was looked at by engineering, but upon discussion with engineering they recommended purchasing a new one. |  |  | FALSE | Sooner Power Plant | FALSE | Laceration | FALSE | Maintenance |  | Trent Novotny | Trent Novotny |  | Frank Brixey | Approve - Brixey 5/9/2019 | Frank Brixey |  | Medium | [12 empty] | 13.07 Inadequate removal and replacement of unsuitable items |  |  |  | Member struck in head by T-post driver. | 06. Using Defective Equipment | 2. Struck By (Hit By Moving Object) |  | Approved by Brady Sowell on 5/7/2019 | [24 empty] | TRUE |  |  | 2018-10-08 | 1993-02-18 |  | 2019-04-22 19:00 | 0 | 0 | Stopped the bleeding and monitored patient. | TRUE |  | Member did not have a hard hat on and the t-post driver caught on the post and inadvertently hit himself in the head. |  | TRUE | Jess Locust |  | Non-Recordable | Jess Locust | TRUE |  | Stillwater Hospital |  | Laceration |  | FALSE | Scott Buchanan | Plant Mechanic I | Head |  | Upper |  | Trent Novotny | FALSE |  | 4/22/2019 7:00:00 PM | 1 | TRUE | FALSE | TRUE | T-post driver | Driving a t-post | [24 empty] | none
8835 | Sooner Power Plant | 2019-04-23 00:30 | Member was using a post driver to drive sign posts into the ground. As member was driving the post down the driver hung up on the post and the driver hit the member on top of the head. Took to emergency room for concussion evaluation. Everything ok, released for work | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Supply | Trent Novotny | 2019-05-22 10:12 | 2019-04-23 05:09 | 2019-04-23 05:09 | 2019-05-06 16:28 | 2019-05-07 00:30 | 2019-04-23 04:56 | 2019-05-13 08:35 |  | 2019-05-07 07:31 | Sooner PP near the boat house |  |  | Jesse Murray | I Approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Frank Brixey |  | On April 23rd at approximately 23:30, member 1 and member 2 went out to the intake dikes to pull up 5' T-posts with signs and put in 8' sign posts for signage. The members stood on the flat platform of the Tommy Lift to drive the sign posts due to the 8' length of the posts. Member 1 drove in the first 2 posts with no incident. On the third post, member 2 asked to drive it in. Member 2 began to drive it in with the post driver. On the 3rd or 4th strike he accidentally pulled the driver up too far allowing it to catch the edge of the post kicking over subsequently striking member 2 in the head. The blow dazed him and put a small gash (~1/2") in the top of his head. He slumped backward into the bed of the truck. EMR team checked him out took vitals and cleaned up cut. Member 2 wasn’t answering questions about things that happened during the incident and couldn’t remember some things that happened in the previous days so the EMR member drove member 1 and member 2 to ER. A CAT scan was performed, cleaned up the wound, and gave him a Tetanus shot. Member returned to work that night with no restrictions. Upon the investigation it was found that on the drive to the work location the members took their hard hats off while in the vehicle. Once at the work location, member 2 did not put on his hard hat and was not wearing it at the time of the incident. Neither member could remember if member 1 was wearing hard hat or not. An SWP was not filled out for this job. T Post driver is a shop made driver that was looked at by engineering, but upon discussion with engineering they recommended purchasing a new one. |  |  | FALSE | Sooner Power Plant | FALSE | Laceration | FALSE | Maintenance |  | Trent Novotny | Trent Novotny |  | Frank Brixey | Approve - Brixey 5/9/2019 | Frank Brixey |  | Medium | [8 empty] | 9.06 Inadequate work planning or programming | [7 empty] | Member struck in head with T-Post driver. | 07. Failing to Use PPE Properly | 2. Struck By (Hit By Moving Object) |  | Approved by Brady Sowell on 5/7/2019 | [24 empty] | TRUE |  |  | 2018-10-08 | 1993-02-18 |  | 2019-04-22 19:00 | 0 | 0 | Stopped the bleeding and monitored patient. | TRUE |  | Member did not have a hard hat on and the t-post driver caught on the post and inadvertently hit himself in the head. |  | TRUE | Jess Locust |  | Non-Recordable | Jess Locust | TRUE |  | Stillwater Hospital |  | Laceration |  | FALSE | Scott Buchanan | Plant Mechanic I | Head |  | Upper |  | Trent Novotny | FALSE |  | 4/22/2019 7:00:00 PM | 1 | TRUE | FALSE | TRUE | T-post driver | Driving a t-post | [24 empty] | none
8836 | Muskogee Power Plant | 2019-04-22 15:00 | Contractor was walking along the catwalk transporting tools. One of their tool bags reportedly struck a box of light bulbs sitting against the handrail causing it to become dislodged and fall from the catwalk to the turbine level. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Robert Martin | 2019-05-22 08:37 | 2019-04-23 11:30 | 2019-04-23 11:30 | 2019-05-06 16:20 | 2019-05-06 15:00 | 2019-04-22 16:00 | 2019-05-06 16:21 |  |  | Muskogee Unit 6 Catwalk above and along the north side of the turbine level. |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Robert Martin |  | Introduction A dropped object incident occurred at the Muskogee Power Plant on April 22, 2019 at approximately 3:00 p.m. Mr. Kyle Veon, Thielsch Inspection Technician, was removing equipment from the turbine building roof level after Thielsch finished inspections of the main steam and hot reheat lines. While being transported along the catwalk above the north side of the turbine deck, an equipment bag struck a box containing light bulbs knocking it from the catwalk. Conclusions 1. Advise all personnel and emphasis good housekeeping practices on a continual basis. 2. Include an emphasis on good housekeeping practices and reporting of unusual conditions during pre-outage/pre-project meetings to eliminate hazardous conditions. 3. Place strong emphasis on situational awareness on an on-going basis to ward off workplace complacency. 4. Raise awareness of proper disposal of potentially hazardous materials. Discussion Mr. Kyle Veon Interview Mr. Veon was interviewed on April 24, 2019. He said that Thielsch completed inspections of the high-energy piping systems located adjacent to the turbine building and were transporting their inspection equipment to ground level. Removing the equipment from the inspection area required transporting it along the catwalk above the turbine-building floor to reach the Unit 5 elevator. When asked, Mr. Veon said that the box was present several days prior when Thielsch entered the area to begin inspections. He said that the box was sitting on a scaffold deck board and the middle handrail of the catwalk and slightly wedged under the top rail. Mr. Veon said that while removing their equipment and carrying it along the catwalk, one of the bags struck the box causing it to fall. The box struck and lodged in some piping above the turbine deck spilling its contents onto the floor below. Mr. Veon said that he went down to clean up the debris and estimated that three bulbs had been broken and that there were two unbroken bulbs. Site Observations The incident occurred near the west face of column 23-K at approximately the boundary line between Units 5 and 6 (Photograph 1). The broken bulbs were unavailable for inspection as they had been cleaned up and dumped for disposal. Two unbroken bulbs that appeared to be contained within the original packaging were located on an adjacent shelving unit (Photograph 2). The box originally containing the bulbs was lodged in some piping approximately 10 feet above the turbine deck (Photographs 1 and 3). The catwalk was located approximately 30 feet above the turbine deck level (Photograph 1). The walkway surface was approximately 32 inches wide. At the incident location, an aluminum, scaffold section was against the north handrail, and it was secured to the handrail by a wire tie. The presence of the deck board encroached approximately 6 inches into the walking surface increasing the difficulty of passing with equipment (Photographs 4A and 4B). The box was reportedly wedged between the top of the scaffold deck section/middle handrail and the top handrail (Photographs 5 and 6). The general area has a significant accumulation of dust. The box, which had contained the light bulbs, also appeared to have some dust accumulation. The box’s appearance was consistent with having been on the catwalk for extended period. Mercury Vapor Bulbs Mercury vapor bulbs comprise an inner bulb/arc chamber containing low pressure mercury vapor and an outer bulb/encasement that often have a phosphor coating on the internal surface. Due to the mercury content, disposal of old or broken bulb require additional precautions. Because the external bulb/encasement absorbs a significant amount of the impact energy, the much smaller and durable internal bulb/arc chamber likely survived the impact intact. Therefore, the likelihood of fugitive mercury was low. However, where and how the debris was ultimately disposed of was unknown. Analysis It was indeterminate when the bulbs were originally taken to the catwalk. Good housekeeping practices after any bulb replacements may have been performed were not followed, and the box was left in an inappropriate location. The box and bulbs should have been removed from the catwalk to eliminate any possibility of this type of incident. More awareness while transporting equipment to and from the work area would likely have prevented the incident. In addition, given the original circumstances, the box should have been reported to the proper personnel and removed from the area. To prevent future incidents of this type, it is crucial to communicate adherence OGE housekeeping requirements. Briefing of employees and contractors prior to outage and projects should include an emphasis on housekeeping and the reporting of unusual condition or poor housekeeping practices. SEE ATTACHMENT |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | Power Supply Services |  | Brent Case | Robert Martin |  | Patrick Coleman | Add write up to investigation field. | Patrick Coleman |  | Low | [6 empty] | 7.06 Improper attempt to save time or effort | [9 empty] | A box containing light bulb was left on the catwalk that ended up being knocked to a lower level. Poor housekeeping practiced by not removing material from the work area after task completion. | 09. Improper Placement | 2. Struck By (Hit By Moving Object) | [5 empty] | Property Damage |  | Robert Martin | Replacement light bulbs broken |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Brent Case | Thielsch | Kyle Veon |  | 3rd Party Property/Equipment |  | Robert Martin | [71 empty] | 18830406
8837 | Muskogee Power Plant | 2019-04-23 14:00 | Contractor struck card reader to the southeast inner plant gate with vehicle damaging card reader | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Zackary Thompson | 2019-06-19 08:35 | 2019-04-24 11:23 | 2019-04-24 11:23 | 2019-05-21 10:31 | 2019-05-07 14:00 | 2019-04-23 14:30 | 2019-06-11 21:25 |  |  | Southeast inner plant gate |  |  | Robert Wright | Approved Bob Wright | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Zackary Thompson |  | Contractor truck was entering the inner plant southeast gate when material loaded on the flatbed struck the gate card reader causing the faceplate to fall off. Material was not loaded with in the frame of the flatbed. Contractor immediately repaired card reader and notified an operations member who was in the area. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | Operations |  | Lucas Akerman | Zackary Thompson |  | Carol Rollins | Reviewed for corrective action and causes | Carol Rollins |  | Low |  |  |  |  | 5.06 Lack of situational awareness | 6.02 Inadequate practice | [10 empty] | Material loaded outside the frame of the flatbed struck and damaged card reader | 08. Improper Loading | 2. Struck By (Hit By Moving Object) | [68 empty] | Card reader was already repaired by contractor that damaged it when the incident was reported | 0 |  | Fixed Equipment | [20 empty] | none
8838 | Shawnee Service Center | 2019-04-23 14:30 | Member was pulling through driveway entrance and struck a pole sticking out at angle from entrance. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Stacy Ragan | 2019-04-24 15:44 | 2019-04-24 13:22 | 2019-04-24 13:22 | 2019-04-24 14:04 | 2019-05-07 14:30 | 2019-04-24 13:07 | 2019-04-24 14:08 |  |  | 12201 NE 59th Street, Spencer, OK |  |  | Brent Perdue | approved. | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Stacy Ragan |  | Member was pulling into driveway. When pulling into driveway entrance the member focused on tree limbs hanging on the driver side of the driveway. The member lost sight of the pole that was sticking into the entrance at a 70 to 85 degree angle. The passenger side mirror struck the pole. The passenger side window was shattered when the mirror was knocked into the window. |  |  |  | Shawnee Service Center | FALSE |  | FALSE | Construction Services |  | Kevin Rich | Stacy Ragan |  | Chad Self | Approved Thanks | Chad Self |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | struck fixed object | 11. Improper Position for Task | 1. Struck Against (Running or Bumping Into) | [74 empty] | TRUE |  | spencer | Struck Fixed Object | Drove Forward Into Object | 2007-09-30 19:00 |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Cloudy |  |  | none
8839 | Sooner Power Plant | 2019-04-24 14:30 | First Aid. Members were replacing butterfly isolation valve. Member bumped manual override on solenoid and exhaust from solenoid blew fly ash in his left eye back behind safety PPE. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Supply | Justin Nealis | 2019-05-15 13:55 | 2019-04-25 07:41 | 2019-04-25 07:41 | 2019-05-06 15:58 | 2019-05-08 14:30 | 2019-04-24 14:30 | 2019-05-09 11:33 |  | 2019-05-07 07:25 | 2G7 Precip hopper butterfly isolation valve. Mezzanine #2 precipitator. |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Justin Nealis |  | Electrician 1 was lead on precipitator work during unit 2 maintenance outage. They found a butterfly isolation valve broke on the bottom of 2G7 hopper. It was decided that the electricians could replace the isolation valve so the mechanical craft could work on the feeder when the unit returned. Other mechanical work was priority during the outage. Electrician 1 and electrician 2 talked to mechanical SME's to make sure there wasn't any tricks or unforeseen obstacles and to talk about hazards. Electrician 1 blew the area around the valve clean to free it from ash and oiled mounting studs. The next day electrician 1 was in and out of meetings. Electrician 2 and electrician 3 continued precipitator work. Electrician 2 and 3 started the butterfly valve replacement. Electrician 3 was laying down on the grating removing the last nut when his arm bumped the manual override on the top gate solenoid (see pic of hopper/feeder layout). Air exhausted out of the solenoid and blew fly ash behind his safety glasses into his left eye. Member shut his eyes, and requested electrician 2's assistance. Electrician 2 escorted electrician 2 down the stairs to the cart and transported electrician 3 to the confined space trailer and notified supervisor. Supervisor requested other confined space member to assist electrician 2 in flushing electrician 3’s eyes. They escorted affected member to #1 bottom ash eye wash station. They turned on the water, but nothing came out. They then escorted the affected member to water treatment and began flushing his eyes. They flushed for 15 minutes until affected member thought everything was out. Supervisor talked to affected member and affected member thought everything was out of his eyes and wished for no treatment. Member was advised if anything changed to call supervisor unless it was an urgent emergency. Affected member the next morning said everything was good. On the SWP it was noted to wear dust mask for respiratory mitigation but nothing around further protecting the eyes. The assessment chart states working on pressurized ash system to wear 12 calorie arc hood. With LOTO and where they were at in the system there was not a hazard of pressurized ash from the system. The unidentified exposure of solenoid exhaust had not been identified. Both members were inexperienced with the specific job. It was noticed that the solenoid didn’t have a protective cover over the manual override but others around it did. Members did identify ash as an initial hazard when they blew down the area the day before. The valve area was clean but the grating next to toe board still had a significant amount of ash which was were the solenoid resides.. The bottom ash eye wash station was valve’d out for other work. Eye wash was valve’d in and checked the next day. Stand down conversation amongst the electricians was had and was determine that the precip area at a minimum foam backed glasses should be worn. Dependent on the job full faced respirator or face shield shall be worn. |  |  | FALSE | Sooner Power Plant | FALSE |  | FALSE | Maintenance |  | Timothy Foster | Justin Nealis |  | Frank Brixey | Approve - Brixey 5/9/2019 | Frank Brixey |  | Medium |  |  |  |  | 5.01 Lack of experience | [11 empty] | Lack of experience and precipitator hoppers/feeders. Was unaware the operation of solenoid valve. | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) |  | Approved by Brady Sowell on 5/7/2019 | [24 empty] | FALSE | [5 empty] | 2019-04-24 07:00 | 0 | 0 | Flushed eyes in eyewash station for 15 minutes | FALSE | Male | Compressed air from solenoid exhausted fly ash into eye. |  | TRUE | Clint Mcclure |  | First Aid | Clint Mcclure |  |  |  |  | Foreign Body |  | FALSE |  | Plant Electrician II | Eye |  | Left |  | William Cash |  |  | 4/24/2019 7:00:00 AM | 1 year | FALSE |  |  | Fly ash | [25 empty] | 9583445
8839 | Sooner Power Plant | 2019-04-24 14:30 | First Aid. Members were replacing butterfly isolation valve. Member bumped manual override on solenoid and exhaust from solenoid blew fly ash in his left eye back behind safety PPE. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Supply | Justin Nealis | 2019-05-15 13:55 | 2019-04-25 07:41 | 2019-04-25 07:41 | 2019-05-06 15:58 | 2019-05-08 14:30 | 2019-04-24 14:30 | 2019-05-09 11:33 |  | 2019-05-07 07:25 | 2G7 Precip hopper butterfly isolation valve. Mezzanine #2 precipitator. |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Justin Nealis |  | Electrician 1 was lead on precipitator work during unit 2 maintenance outage. They found a butterfly isolation valve broke on the bottom of 2G7 hopper. It was decided that the electricians could replace the isolation valve so the mechanical craft could work on the feeder when the unit returned. Other mechanical work was priority during the outage. Electrician 1 and electrician 2 talked to mechanical SME's to make sure there wasn't any tricks or unforeseen obstacles and to talk about hazards. Electrician 1 blew the area around the valve clean to free it from ash and oiled mounting studs. The next day electrician 1 was in and out of meetings. Electrician 2 and electrician 3 continued precipitator work. Electrician 2 and 3 started the butterfly valve replacement. Electrician 3 was laying down on the grating removing the last nut when his arm bumped the manual override on the top gate solenoid (see pic of hopper/feeder layout). Air exhausted out of the solenoid and blew fly ash behind his safety glasses into his left eye. Member shut his eyes, and requested electrician 2's assistance. Electrician 2 escorted electrician 2 down the stairs to the cart and transported electrician 3 to the confined space trailer and notified supervisor. Supervisor requested other confined space member to assist electrician 2 in flushing electrician 3’s eyes. They escorted affected member to #1 bottom ash eye wash station. They turned on the water, but nothing came out. They then escorted the affected member to water treatment and began flushing his eyes. They flushed for 15 minutes until affected member thought everything was out. Supervisor talked to affected member and affected member thought everything was out of his eyes and wished for no treatment. Member was advised if anything changed to call supervisor unless it was an urgent emergency. Affected member the next morning said everything was good. On the SWP it was noted to wear dust mask for respiratory mitigation but nothing around further protecting the eyes. The assessment chart states working on pressurized ash system to wear 12 calorie arc hood. With LOTO and where they were at in the system there was not a hazard of pressurized ash from the system. The unidentified exposure of solenoid exhaust had not been identified. Both members were inexperienced with the specific job. It was noticed that the solenoid didn’t have a protective cover over the manual override but others around it did. Members did identify ash as an initial hazard when they blew down the area the day before. The valve area was clean but the grating next to toe board still had a significant amount of ash which was were the solenoid resides.. The bottom ash eye wash station was valve’d out for other work. Eye wash was valve’d in and checked the next day. Stand down conversation amongst the electricians was had and was determine that the precip area at a minimum foam backed glasses should be worn. Dependent on the job full faced respirator or face shield shall be worn. |  |  | FALSE | Sooner Power Plant | FALSE |  | FALSE | Maintenance |  | Timothy Foster | Justin Nealis |  | Frank Brixey | Approve - Brixey 5/9/2019 | Frank Brixey |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Lack of experience and precipitator hoppers/feeders. Was unaware the operation of solenoid valve. | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) |  | Approved by Brady Sowell on 5/7/2019 | [24 empty] | FALSE | [5 empty] | 2019-04-24 07:00 | 0 | 0 | Flushed eyes in eyewash station for 15 minutes | FALSE | Male | Compressed air from solenoid exhausted fly ash into eye. |  | TRUE | Clint Mcclure |  | First Aid | Clint Mcclure |  |  |  |  | Foreign Body |  | FALSE |  | Plant Electrician II | Eye |  | Left |  | William Cash |  |  | 4/24/2019 7:00:00 AM | 1 year | FALSE |  |  | Fly ash | [25 empty] | 9583445
8840 | McClain Power Plant | 2019-04-24 16:30 | Member was lining up cooling tower bleach skid for operation. while opening up pump suction, member felt moisture on neck. member looked to his left and noticed a stream of bleach coming from suction line. Member was not injured. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Supply | John Gilginas | 2019-05-15 07:50 | 2019-04-25 15:26 | 2019-04-25 15:26 | 2019-05-10 09:45 | 2019-05-08 16:30 | 2019-04-25 15:15 | 2019-05-13 14:21 |  |  | McClain power plant cooling tower bleach pump house. |  |  | Tanner Brady | Assisted in investigation and have reviewed | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | John Gilginas |  | At McClain Power Plant at 1645 on April 24th, 2019 there was an operations member that was lining up bravo bleach pump for normal operation. The cooling tower was out of service for outage and not running. The member saw it best to treat cooling tower with the electric pumps to treat water with bleach. The member walked up to the bleach pump house and went in to open up the suctions of both A and B pump. Member went to turn the valves to start adding bleach back into the cooling tower and after opening the suction valve the Member felt residue on the back of his neck and shoulder. The operating intern that was with him standing outside of the bleach house noticed that there was a small pin hole sized leak in the clear suction line. The operator immediately isolated the suction line so there was no flow. The pump was off at the time and the bleach came out of the suction line due to the head pressure. The member removed his shirt and changed clothing, and also wiped body down with wet paper towel to remove any bleach from the skin. The member was wearing safety glasses at the time of the incident. This incident was ranked low as it was a system operational error that hit the back of his neck and shirt. In this case, the pin hole leak in the pump suction line would have not been found until the system had been lined up. Which was the case here, once there was head pressure from the tank on the system, the leak was noticed. while looking at the system a possible sealed pump head could solve this problem. |  |  | FALSE | McClain Power Plant | FALSE |  | TRUE | Operations |  | Shannon Agotness | John Gilginas |  | Heath Biehl | I am satisfied with the investigation and corrective actions listed. | Heath Biehl |  | Low | [12 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | Head pressure from line pushing bleach through clear pin hole | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure | [92 empty] | none
8841 | Sooner Power Plant | 2019-04-29 01:00 | At approximately 0100hrs member was returning LOTO and closing 480V breakers up. Member closed the breaker for #1 main turbine left stop valve after seat drain. when it closed, there was a loud pop and some smoke that came out of the breaker cubicle. He then opened the breaker back up and the event was over. | Level 2 |  | FALSE | Property Damage | Donnie Jones | Jesse Murray |  |  | Power Supply | Jimmie Allen | 2019-06-13 09:10 | 2019-04-29 01:32 | 2019-04-29 01:32 | 2019-05-24 19:50 | 2019-05-13 01:00 | 2019-04-29 01:00 | 2019-05-29 15:06 |  | 2019-05-28 07:15 | Sooner Power Plant Unit 1 main switchgear |  |  | Jesse Murray | Approve. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Jimmie Allen |  | The close contactor was bypassed around the overload protection. It was the open contactor that was burnt up. Looks like it flashed across on the top side of the overloads. It would be typical to have an open command from DCS when the unit is offline. This explains why the valve attempted to drive open when the breaker was closed. The motor was found to have a bunch of shorted turns in the windings. Evans got the motor for rebuild and suspect overloading. At this time, initial investigation reveals that close contactor bypassing the overloads let the motor get hot and shorted the turns. Then when the open contactor tried to open with the overloads in play it flashed across them. These cubicles are designed to keep this kind of event inside. Cal rating on the bus is 2.71@ 18in. With the event on the down-stream side of the breaker the calorie rating would be less but unknown how much less. Overloads were sized correctly. Still awaiting on the MOV from Evans to further troubleshoot at this time. Torque settings will be verified on the valve and inspect all wiring from breaker to motor. Evans currently has motor rewinding it. Another note is that this motor was rewound back in December. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Operations |  | Tim Chaplin | Jimmie Allen |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium | [11 empty] | 12.01.3 Inadequate preventative adjustment/assembly |  |  |  |  | At approximately 0100hrs member was returning LOTO and closing 480V breakers up. Member closed the breaker for #1 main turbine left stop valve after seat drain. when it closed, there was a loud pop and some smoke that came out of the breaker cubicle. He then opened the breaker back up and the event was over. | 26. Fire & Explosion Hazards | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Brady Sowell approved following the changes. I am sending this Incident back for 2 reasons. 1. It is labeled as a close call. It appears the incident caused damage and has cost us $4500. This would mean it needs to be marked "no" for close call and the incident type will be property damage. 2. The basic cause that was selected is lack of experience. I do not see how that connects with the investigation results. There are 2 ways we can fix this. Give further details in the investigation description to explain how a lack of experience could have caused this failure. Or we can re-evaluate to see if we have the right immediate cause selected. IT sounds like the cause may have been more around a repair defect or inadequate repair. Also for the "cause description" it should not be a copy of what is in the initial report. This field is to state what caused the contactor to arc. | [66 empty] | Damage to breaker | 4500 | Tim Chaplin | Fire | [20 empty] | None
8842 | South District Service Center | 2019-04-25 15:30 | Tree crew rear ended by public vehicle while waiting at red light. No injuries. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Christopher Martin | 2019-05-24 10:37 | 2019-04-29 08:55 | 2019-04-29 08:55 | 2019-05-09 15:09 | 2019-05-09 15:30 | 2019-04-25 18:30 | 2019-05-21 14:36 |  | 2019-05-09 15:12 | Highway nine and 60th St in Norman |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Christopher Martin |  | Tree crew rear ended by public vehicle while waiting at red light. No injuries. See investigation report that is attached |  |  |  | South District Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Christopher Martin | Christopher Martin |  |  | Approved. |  |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | struck by public vehicle | 19. Failure to React, Correct | 2. Struck By (Hit By Moving Object) |  | approved. |  |  |  | Vehicle |  | Christopher Martin | [5 empty] | 2. Struck By (Hit By Moving Object) | Christopher Martin | Asplundh Tree Experts | Chance Selman |  |  |  | Christopher Martin | [71 empty] | `none
8843 | Metro Service Center | 2019-04-22 09:30 | Jarraff operator was trimming and cut down guy with cutting blade. location was flagged. | Level 1 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Richard Norton | 2019-05-29 14:28 | 2019-04-29 09:16 | 2019-04-29 09:16 | 2019-05-29 13:56 | 2019-05-06 09:30 | 2019-04-29 09:07 | 2019-05-29 14:04 |  |  | Vegetation contractor cut down guy with equipment |  |  | Jerrie Looney | J. Looney, 5/29/19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Richard Norton |  | Jarraff operator was trimming in an area that was previously flagged, due to tall brush around guy wire he cut with saw blade. |  |  |  | Metro Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Richard Norton | Richard Norton |  |  | Reviewed with Forester and Vendor. Vendor supplied additional information showing actions taken to prevent future occurrence. |  |  | Low |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.13 Inadequate or incorrect performance feedback | [7 empty] | No spotter present | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Richard Norton | Cut down guy wire |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Richard Norton | Asplundh Tree Expert | Casey Collins |  | Industrial/Heavy Equipment |  | Richard Norton |  |  |  |  | FALSE | [66 empty] | None
8844 | Metro Service Center | 2019-04-19 | A DCC Dispatcher directed a single circuit switching order; due to a previous multi circuit switching order being completed this changed the single circuit switching to multiple circuit switching. This caused the field switchman to inadvertently tie two circuits together without matching voltage. | Level 2 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Douglas Mack | 2019-06-05 09:54 | 2019-04-30 10:46 |  | 2019-06-04 17:11 | 2019-05-31 | 2019-04-30 10:30 | 2019-06-04 23:09 |  | 2019-06-04 17:27 | Metro DCC |  |  | Lindle Coleman | Approved | T&D Ops |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Douglas Mack |  | A DCC Dispatcher directed a single circuit switching order; which due to a previous multi circuit switching order being completed this changed the single circuit switching to multiple circuit switching. This caused the field switchman to inadvertently tie two circuits together without matching voltage. On 4-19-2019, a contractor called to perform switching order D-0759 from 2018. Dispatcher 1 had the area of South District OKC where the switching was to take place. The contractor called at 1:33 pm , placed on hold for the correct dispatcher, then spoke to Dispatcher 1 at 1:36 pm and Dispatcher 1 said he would find the switching and call him back. 2:13 pm, Contractor called and was placed on hold by another dispatcher, waiting to talk to Dispatcher 1 2:17 pm, Contractor was on hold until now, spoke to Dispatcher 1 and Dispatcher 1 realized he forgot to pull the switching and forgot to call Contractor back, so Dispatcher 1 went and pulled the switching order from the switching book. 2:19 pm , Dispatcher 1 read the switching and Contractor repeated it back. 2:47 pm, Contractor called in to give times to Dispatcher 1 -the switching order was completed. Dispatcher 1 did not take it off of the maps or file the switching order as it was the end of his shift. Instead Dispatcher 2 took over for South at shift change at 3 pm, which is when Dispatcher 2 found that this was now a multiple circuit switching order when he went to return the maps and file the switching. To summarize what happened: On 9/4/18 a single run of underground primary cable went out around 6am. The switching order was written that day to return to normal once a scheduled repair was done. Switching order D-0759 as this was a single circuit line. On 9/18/19, M-1203 that was written on 7/27/18 but not completed until 9/18/18 was performed which reconfigured the circuit. The switching order D-0759 was returned to normal on 4/19/19, due to the circuit configuration on M-1203, this should have been an “M” switching order. No injuries occurred, no outages and the switching was performed and the maps are now correct. The N.O. 64496 is now a 2 circuit N.O. and will remain that way. Dispatcher 2 sent the email at 4:09 pm and Dispatcher 1 has email on his cell phone and Dispatcher 1 called me and texted me multiple times upset that he had made an error. He knew that everyone was safe as he did take the return times from Contractor. I have spoken with Dispatcher 1 and he said he does know that he should look at the maps every time before starting a switching order. Some things that affected this decision to not look at the maps was that Dispatcher 1 was busy and had multiple switching orders going, he was leaving for vacation the next morning and he felt bad for not calling Contractor back like he said he would. To try and speed this up, Dispatcher 1 chose not too check the maps before going over the switching. Dispatcher 1 has taken full responsibility and I will share that with him as his Supervisor, I need to encourage members to always ask for help and to take the time to review the maps every time. Dispatcher 1 feels bad for making a mistake and understands there will be an investigation. |  |  |  | Metro Service Center | FALSE |  | FALSE | System Operations |  | Gregory Gilkey | Tyler Hartman |  | Dallas Rowley | I approve of this incident investigation along with associated corrective actions. D. Rowley | Dallas Rowley |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Failure to verify accuracy of map model and system circuit configuration, and identify changes | 36. Inadequate Preparation, Planning | 9. Abnormal Operation |  | approve of investigation findings and corrective actions. cm | [90 empty] | n/a
8844 | Metro Service Center | 2019-04-19 | A DCC Dispatcher directed a single circuit switching order; due to a previous multi circuit switching order being completed this changed the single circuit switching to multiple circuit switching. This caused the field switchman to inadvertently tie two circuits together without matching voltage. | Level 2 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Douglas Mack | 2019-06-05 09:54 | 2019-04-30 10:46 |  | 2019-06-04 17:11 | 2019-05-31 | 2019-04-30 10:30 | 2019-06-04 23:09 |  | 2019-06-04 17:27 | Metro DCC |  |  | Lindle Coleman | Approved | T&D Ops |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Douglas Mack |  | A DCC Dispatcher directed a single circuit switching order; which due to a previous multi circuit switching order being completed this changed the single circuit switching to multiple circuit switching. This caused the field switchman to inadvertently tie two circuits together without matching voltage. On 4-19-2019, a contractor called to perform switching order D-0759 from 2018. Dispatcher 1 had the area of South District OKC where the switching was to take place. The contractor called at 1:33 pm , placed on hold for the correct dispatcher, then spoke to Dispatcher 1 at 1:36 pm and Dispatcher 1 said he would find the switching and call him back. 2:13 pm, Contractor called and was placed on hold by another dispatcher, waiting to talk to Dispatcher 1 2:17 pm, Contractor was on hold until now, spoke to Dispatcher 1 and Dispatcher 1 realized he forgot to pull the switching and forgot to call Contractor back, so Dispatcher 1 went and pulled the switching order from the switching book. 2:19 pm , Dispatcher 1 read the switching and Contractor repeated it back. 2:47 pm, Contractor called in to give times to Dispatcher 1 -the switching order was completed. Dispatcher 1 did not take it off of the maps or file the switching order as it was the end of his shift. Instead Dispatcher 2 took over for South at shift change at 3 pm, which is when Dispatcher 2 found that this was now a multiple circuit switching order when he went to return the maps and file the switching. To summarize what happened: On 9/4/18 a single run of underground primary cable went out around 6am. The switching order was written that day to return to normal once a scheduled repair was done. Switching order D-0759 as this was a single circuit line. On 9/18/19, M-1203 that was written on 7/27/18 but not completed until 9/18/18 was performed which reconfigured the circuit. The switching order D-0759 was returned to normal on 4/19/19, due to the circuit configuration on M-1203, this should have been an “M” switching order. No injuries occurred, no outages and the switching was performed and the maps are now correct. The N.O. 64496 is now a 2 circuit N.O. and will remain that way. Dispatcher 2 sent the email at 4:09 pm and Dispatcher 1 has email on his cell phone and Dispatcher 1 called me and texted me multiple times upset that he had made an error. He knew that everyone was safe as he did take the return times from Contractor. I have spoken with Dispatcher 1 and he said he does know that he should look at the maps every time before starting a switching order. Some things that affected this decision to not look at the maps was that Dispatcher 1 was busy and had multiple switching orders going, he was leaving for vacation the next morning and he felt bad for not calling Contractor back like he said he would. To try and speed this up, Dispatcher 1 chose not too check the maps before going over the switching. Dispatcher 1 has taken full responsibility and I will share that with him as his Supervisor, I need to encourage members to always ask for help and to take the time to review the maps every time. Dispatcher 1 feels bad for making a mistake and understands there will be an investigation. |  |  |  | Metro Service Center | FALSE |  | FALSE | System Operations |  | Gregory Gilkey | Tyler Hartman |  | Dallas Rowley | I approve of this incident investigation along with associated corrective actions. D. Rowley | Dallas Rowley |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Did not use proper tool, did not verify current map model for accuracy or for changes in system configuration. | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation |  | approve of investigation findings and corrective actions. cm | [90 empty] | n/a
8844 | Metro Service Center | 2019-04-19 | A DCC Dispatcher directed a single circuit switching order; due to a previous multi circuit switching order being completed this changed the single circuit switching to multiple circuit switching. This caused the field switchman to inadvertently tie two circuits together without matching voltage. | Level 2 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Douglas Mack | 2019-06-05 09:54 | 2019-04-30 10:46 |  | 2019-06-04 17:11 | 2019-05-31 | 2019-04-30 10:30 | 2019-06-04 23:09 |  | 2019-06-04 17:27 | Metro DCC |  |  | Lindle Coleman | Approved | T&D Ops |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Douglas Mack |  | A DCC Dispatcher directed a single circuit switching order; which due to a previous multi circuit switching order being completed this changed the single circuit switching to multiple circuit switching. This caused the field switchman to inadvertently tie two circuits together without matching voltage. On 4-19-2019, a contractor called to perform switching order D-0759 from 2018. Dispatcher 1 had the area of South District OKC where the switching was to take place. The contractor called at 1:33 pm , placed on hold for the correct dispatcher, then spoke to Dispatcher 1 at 1:36 pm and Dispatcher 1 said he would find the switching and call him back. 2:13 pm, Contractor called and was placed on hold by another dispatcher, waiting to talk to Dispatcher 1 2:17 pm, Contractor was on hold until now, spoke to Dispatcher 1 and Dispatcher 1 realized he forgot to pull the switching and forgot to call Contractor back, so Dispatcher 1 went and pulled the switching order from the switching book. 2:19 pm , Dispatcher 1 read the switching and Contractor repeated it back. 2:47 pm, Contractor called in to give times to Dispatcher 1 -the switching order was completed. Dispatcher 1 did not take it off of the maps or file the switching order as it was the end of his shift. Instead Dispatcher 2 took over for South at shift change at 3 pm, which is when Dispatcher 2 found that this was now a multiple circuit switching order when he went to return the maps and file the switching. To summarize what happened: On 9/4/18 a single run of underground primary cable went out around 6am. The switching order was written that day to return to normal once a scheduled repair was done. Switching order D-0759 as this was a single circuit line. On 9/18/19, M-1203 that was written on 7/27/18 but not completed until 9/18/18 was performed which reconfigured the circuit. The switching order D-0759 was returned to normal on 4/19/19, due to the circuit configuration on M-1203, this should have been an “M” switching order. No injuries occurred, no outages and the switching was performed and the maps are now correct. The N.O. 64496 is now a 2 circuit N.O. and will remain that way. Dispatcher 2 sent the email at 4:09 pm and Dispatcher 1 has email on his cell phone and Dispatcher 1 called me and texted me multiple times upset that he had made an error. He knew that everyone was safe as he did take the return times from Contractor. I have spoken with Dispatcher 1 and he said he does know that he should look at the maps every time before starting a switching order. Some things that affected this decision to not look at the maps was that Dispatcher 1 was busy and had multiple switching orders going, he was leaving for vacation the next morning and he felt bad for not calling Contractor back like he said he would. To try and speed this up, Dispatcher 1 chose not too check the maps before going over the switching. Dispatcher 1 has taken full responsibility and I will share that with him as his Supervisor, I need to encourage members to always ask for help and to take the time to review the maps every time. Dispatcher 1 feels bad for making a mistake and understands there will be an investigation. |  |  |  | Metro Service Center | FALSE |  | FALSE | System Operations |  | Gregory Gilkey | Tyler Hartman |  | Dallas Rowley | I approve of this incident investigation along with associated corrective actions. D. Rowley | Dallas Rowley |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | failure to verify accuracy of written switching compared to system circuit configuration. | 36. Inadequate Preparation, Planning | 9. Abnormal Operation |  | approve of investigation findings and corrective actions. cm | [90 empty] | n/a
8845 | Metro Service Center | 2019-04-30 11:00 | Company vehicle was rear ended by a public vehicle while stopped at a red light. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Brent Boles | 2019-05-03 10:30 | 2019-04-30 12:29 | 2019-04-30 12:29 | 2019-04-30 12:33 | 2019-05-14 11:00 | 2019-04-30 12:23 |  |  |  | Red light at NE 4th & Lincoln (Off Ramp from Broadway Extension) |  |  | Terry Hackett | Due to no negligence or OGE method to prevent this incident a detailed investigation was not completed. Reviewed and approved TMH | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE |  |  | Company vehicle was rear ended by a public vehicle while stopped at a red light. Company vehicle was not damaged. Public vehicle received damage to front bumper, but was operational. Police were called and a report was filed (see attachments) |  |  |  | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Taylor Barnett | Brent Boles |  |  |  | Gary Lassley |  | Low | [93 empty] | FALSE |  | Oklahoma City | Public Vehicle Struck OGE | OGE Vehicle Stopped/Parked | 2018-03-11 19:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Rain
8846 | Metro Service Center | 2019-04-29 16:15 | traveling north bound on I-35 just south of the Hefner exit. As I passed a mowing crew I felt an impact on the front right side of the truck accompanied by a loud noise. I exited the highway to inspect and noticed a small hole in the grill of the truck. | Level 1 |  | FALSE | Property Damage |  |  |  |  | OGE Energy Corp | Lindle Coleman | 2019-05-31 08:09 | 2019-04-30 13:20 | 2019-04-30 13:20 | 2019-04-30 13:38 | 2019-05-13 15:15 | 2019-04-29 16:20 | 2019-05-31 07:08 |  |  | traveling north bound on I-35 just south of the Hefner exit. |  |  | Jerrod Moser | approve | Enterprise Services |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Lindle Coleman |  | On 4-29-19 at 4:15 P.M I was traveling north bound on I-35 just south of the Hefner exit. As I passed a mowing crew I felt an impact on the front right side of the truck accompanied by a loud noise. I exited the highway to inspect and noticed a small hole in the grill of the truck. I made contact with the workers who were mowing however they did not speak English. |  |  |  | Metro Service Center | FALSE |  | FALSE | Other |  | Luke Kennedy | Lindle Coleman |  | Jerrod Moser | approve | Jerrod Moser |  | Low | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | traveling north bound on I-35 just south of the Hefner exit. As I passed a mowing crew I felt an impact on the front right side of the truck accompanied by a loud noise. I exited the highway to inspect and noticed a small hole in the grill of the truck. I made contact with the workers who were mowing however they did not speak English. | 39. Road Conditions | 2. Struck By (Hit By Moving Object) | [68 empty] | Small hole in front grill | 300 | Luke Kennedy | Vehicle (not related to operation of vehicle) |  | F03-1456 | [18 empty] | none
8847 | Muskogee Service Center | 2019-04-29 11:00 | While driving down oil field road which was very rough, Top section of ladder bounced out of ladder rack and was laying on top of truck. Bottom section was strapped in. No damage to truck or ladder. | Level 2 |  | TRUE | Vehicle |  |  |  |  | Power Delivery | Janssen Coomer | 2019-05-24 11:37 | 2019-04-30 15:43 | 2019-04-30 15:43 | 2019-05-06 07:52 | 2019-05-13 11:00 | 2019-04-30 08:00 | 2019-05-24 11:33 |  | 2019-05-06 09:26 | 7 miles west of Mounds, OK, on oil field road. |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Janssen Coomer |  | Need a longer ladder to be adequately secured in ladder rack. |  |  |  | Muskogee Service Center | FALSE |  | TRUE | PD Operations Services |  | Franklin Polston | Janssen Coomer |  | Darryl Splawn | Replacement ladder for this vehicle has been completed and all Meter Tech vehicles have been inspected for proper fitting and securing of existing ladders. | Darryl Splawn |  | Medium | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | Replace 16 foot ladder with 20 foot ladder to be adequately secured in ladder rack. | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure |  | good job on finding a corrective action to prevent the issue from occurring again. | [90 empty] | none
8849 | South District Service Center | 2019-05-01 11:30 | Public vehicle struck left rear side of the track hole trailer. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Gary Parks | 2019-05-06 07:32 | 2019-05-01 13:45 | 2019-05-01 13:45 | 2019-05-01 13:51 | 2019-05-15 10:30 | 2019-05-01 13:32 |  |  |  | Eastbound outside lane of I-240 east of I-35 |  |  | Luke Kennedy | Member was following company expectations and responded appropriately 5/6/19 | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | [6 empty] | South District Service Center | FALSE |  | FALSE | Construction Services |  | Dusty Stejskal | Gary Parks |  |  |  | Terry Garrett |  | Low | [93 empty] | FALSE |  | Oklahoma City | Public Vehicle Struck OGE | Both Vehicles Moving | 2008-10-19 19:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Cloudy
8850 | Sooner Power Plant | 2019-05-01 13:00 | Scaffold ladder contacted lagging on bottom side of boiler causing damage to the lagging. Scaffold was not damaged. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Lance Lantz | 2019-05-28 06:37 | 2019-05-01 16:34 | 2019-05-01 16:34 | 2019-05-15 11:25 | 2019-05-15 13:00 | 2019-05-01 15:21 | 2019-05-20 07:58 |  |  | Sooner PP Unit 1 Northwest Corner of Seal Trough |  |  | Brady Sowell | Approved by Brady Sowell | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Lance Lantz |  | On Wednesday, April 1st Aerotek member and OG&E operation’s members that were working on cleaning out unit 1 boiler seal trough reported damage to the lagging on the bottom side of the boiler in the northwest corner. This damaged appeared to have been caused by a scaffold that was erected in the area. Upon further investigation into how the scaffold came into contact with the boiler. It was determined that unit 1 boiler was removed from service on Tuesday, April 16th. Request was made on Saturday, April 20th to have scaffold erected on all four corners of unit 1 boiler seal trough. The northeast and southeast scaffolds were erected the same day the request was made. The northwest and southwest scaffolds were erected on Monday, April 22nd. Unit 1 boiler was returned to service on Wednesday, April 24th. When the boiler grew after being returned to service the lagging contacted the ladder of the scaffold in the northwest corner causing damage to the lagging. The scaffold in the northwest corner was built a little higher than the other three scaffolds due to piping and other obstructions in the area. None of the other scaffolds made contact and no damage was done to the scaffold ladder that contacted the lagging. Other information found during the investigation is that before construction of the scaffolds operations and the plant contact discussed the potential for the unit to return to service. It was discussed that if the unit was returned to service the boiler would grow approximately 12”, but the area around the seal troughs would not move. This information was relayed to the Brock site supervisor. When it was determined the unit was being returned to service the plant contact and Brock site supervisor went through the scaffold log to ensure that no scaffolds would be affected by the thermal growth or moving parts. It was determined that all scaffolds should be clear of any obstructions. Brock members thought the lagging that was above the scaffold on the north side was part of some duct work that is in the area and did not think it would move. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Maintenance |  | Brady Sowell | Lance Lantz |  | Frank Brixey | What action items could we put in place to prevent or communicate the Unit is coming back online to prevent this in the future? Brixey - 5/13/19 Approve- Brixey 5/20/19 | Frank Brixey |  | Low |  |  |  |  | 5.01 Lack of experience | [10 empty] | 16.03. Inadequate communication between different organizations | Scaffold access ladder was erected to high | 11. Improper Position for Task | 1. Struck Against (Running or Bumping Into) | [68 empty] | Lagging was pushed up between supports, bending lagging and pulling sheet metal screws out of trim pieces. | 2500 |  | Fixed Equipment | [20 empty] | 9581494
8851 | Horseshoe Lake Power Plant | 2019-05-01 11:00 | Siemens members were removing stuck studs from the HP/IP shell of the unit 8 turbine. The injured worker was under the HPIP turbine helping to remove studs. A worker above the injured worker lost control of a wrench and it struck the worker in the head causing a minor laceration. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Daniel Perry | 2019-06-26 09:07 | 2019-05-02 12:04 | 2019-05-02 12:04 | 2019-05-08 20:03 | 2019-05-15 10:00 | 2019-05-01 11:36 | 2019-06-10 08:24 |  |  | Horseshoe Lake Unit 8 HP/IP turbine |  |  | Guillermo Sarmiento | 06/14/19 - still working on this. 06/17/2019 - Have reviewed and make changes. Will close out after covering new findings on the weekly call. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Daniel Perry |  | On May 1, 2019, two Siemens members were tasked with removing stuck studs from the HP/IP shell of the unit 8 turbine. Contractor #1 was utilizing a pipe wrench to remove the stuck bolts with contractor #2 was assisting with the job. At some point in time, contractor #2 removed his hard hat in order to obtain better access into a restrictive area where the work was taking place. During the course of the task, contractor #1 lost some control of the pipe wrench which resulted in striking contractor #2 on the head causing a minor lacerations. First aid was immediately administered. Siemens immediately contacted Work Care for further guidance. OGE was immediately notified of the incident as well. Findings: • Take 5 was conducted for this task was missing information. o Step 1 needs more information concerning the steps that will be conducted. o Step 3 did not adequately identify risk and defenses. o Take 5 did not include risk assessment concerning the removal of PPE (hard hat). o Incident report and confirmation of corrective actions were provided to OGE in a timely manner. • Information in the Contractor Reference Guide and our SSOP concerning hard hats are not 100% consistent. • Procedure and Reference guide should note the process to follow if a deviation from the process or PPE is needed. • OGE Leadership discussed the issue and corrective actions with Siemens supervisor. Covered the importance of performing hazard assessments if and when bump caps need to be utilized. • Siemens found their bump caps that were in there kits and also order additional ones. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Maintenance |  | Daniel Perry | Daniel Perry |  | Robert Doupe | I approve | Robert Doupe |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Member below was positioned in a potential line of fire and the member above did not recognize the situation. Precautions were not take to provide protection to member below if control was lost of the wrench. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | [5 empty] | Injury / Illness |  | Daniel Perry |  | Wrench hit member in the head. | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Terry Creed | Siemens | Mike Wauqu | Contusion |  | Head | Daniel Perry | Top | FALSE | [69 empty] | 9581777
8851 | Horseshoe Lake Power Plant | 2019-05-01 11:00 | Siemens members were removing stuck studs from the HP/IP shell of the unit 8 turbine. The injured worker was under the HPIP turbine helping to remove studs. A worker above the injured worker lost control of a wrench and it struck the worker in the head causing a minor laceration. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Daniel Perry | 2019-06-26 09:07 | 2019-05-02 12:04 | 2019-05-02 12:04 | 2019-05-08 20:03 | 2019-05-15 10:00 | 2019-05-01 11:36 | 2019-06-10 08:24 |  |  | Horseshoe Lake Unit 8 HP/IP turbine |  |  | Guillermo Sarmiento | 06/14/19 - still working on this. 06/17/2019 - Have reviewed and make changes. Will close out after covering new findings on the weekly call. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Daniel Perry |  | On May 1, 2019, two Siemens members were tasked with removing stuck studs from the HP/IP shell of the unit 8 turbine. Contractor #1 was utilizing a pipe wrench to remove the stuck bolts with contractor #2 was assisting with the job. At some point in time, contractor #2 removed his hard hat in order to obtain better access into a restrictive area where the work was taking place. During the course of the task, contractor #1 lost some control of the pipe wrench which resulted in striking contractor #2 on the head causing a minor lacerations. First aid was immediately administered. Siemens immediately contacted Work Care for further guidance. OGE was immediately notified of the incident as well. Findings: • Take 5 was conducted for this task was missing information. o Step 1 needs more information concerning the steps that will be conducted. o Step 3 did not adequately identify risk and defenses. o Take 5 did not include risk assessment concerning the removal of PPE (hard hat). o Incident report and confirmation of corrective actions were provided to OGE in a timely manner. • Information in the Contractor Reference Guide and our SSOP concerning hard hats are not 100% consistent. • Procedure and Reference guide should note the process to follow if a deviation from the process or PPE is needed. • OGE Leadership discussed the issue and corrective actions with Siemens supervisor. Covered the importance of performing hazard assessments if and when bump caps need to be utilized. • Siemens found their bump caps that were in there kits and also order additional ones. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Maintenance |  | Daniel Perry | Daniel Perry |  | Robert Doupe | I approve | Robert Doupe |  | Low | [12 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | Member working below was not wearing a hardhat due to limited space. | 07. Failing to Use PPE Properly | 2. Struck By (Hit By Moving Object) | [5 empty] | Injury / Illness |  | Daniel Perry |  | Wrench hit member in the head. | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Terry Creed | Siemens | Mike Wauqu | Contusion |  | Head | Daniel Perry | Top | FALSE | [69 empty] | 9581777
8852 | South District Service Center | 2019-05-02 09:30 | Member was performing switching in transformer and felt discomfort in shoulder. Member stopped working and reported to his supervisor. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Joshua Fisk | 2019-05-10 07:25 | 2019-05-02 13:35 | 2019-05-02 13:35 | 2019-05-07 18:54 | 2019-05-16 09:30 | 2019-05-02 13:24 | 2019-05-09 16:44 |  | 2019-05-09 13:46 | In transformer near SW 74th and Penn. |  |  | Lindle Coleman | returned for investigation and reassignment approved 5/10/19 | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Joshua Fisk |  | The member began work on 5/02/2019 a 7 am by performing the stretching routine with the collective South District team. The first ticket of the day was to trouble shoot an outage at S.W. 74th and S. Penn at WEOKIE credit union. Through the trouble shooting process the member concluded that 3 phases in an underground transformer needed to be parked on parking stands and then close the normal open UG elbows in the same transformer. Performing the first part of the switching the member parked 2 phases, and while in the process of parking the 3rd phase is when he felt the discomfort/pain. Facts gathered from investigation: • Worked an 8 hour day on service the day before, 05/01/2019, from 7am to 3:30. • Started day on 05/02/2019 as normal at the Norman office at 7 am. • Performed stretches at beginning of our shift. • Stretching is a required routine for every day • Parked 2 of 3 phases prior to the incident • Member used an approved shotgun stick • While parking the last elbow, pain was experienced in the right shoulder area. • Feet were on dry ground when performing task • There was no slipping of feet • Power Quality member stopped to assist the injured member. |  |  | FALSE | South District Service Center | FALSE |  | FALSE | Construction Services |  | Toby Tilley | Joshua Fisk |  | Chad Self | Approved | Chad Self |  | Medium | [9 empty] | 10.04 Inadequate monitoring of construction |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | muscle tear while pushing insulated stick. | 24. Congestion or Restricted Action | 11. Overstress, Overpressure, Overexertion, Ergonomic |  | good details on the description | [24 empty] | FALSE |  |  | 2010-08-30 | 1976-09-09 |  | 2019-05-02 07:00 | 34 | 210 |  | FALSE |  | Member was parking primary on a parking stand and felt discomfort in his shoulder. |  | FALSE | Toby Tilley |  | Recordable | Toby Tilley |  |  |  |  | Sprain/Strain |  | TRUE |  | Service Technician | Shoulder | Injury | Right | TRUE | Joshua Fisk | TRUE | 2019 | 5/2/2019 7:00:00 AM |  | FALSE |  |  | The force of pushing the elbow on the parking stand | [25 empty] | none
8852 | South District Service Center | 2019-05-02 09:30 | Member was performing switching in transformer and felt discomfort in shoulder. Member stopped working and reported to his supervisor. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Joshua Fisk | 2019-05-10 07:25 | 2019-05-02 13:35 | 2019-05-02 13:35 | 2019-05-07 18:54 | 2019-05-16 09:30 | 2019-05-02 13:24 | 2019-05-09 16:44 |  | 2019-05-09 13:46 | In transformer near SW 74th and Penn. |  |  | Lindle Coleman | returned for investigation and reassignment approved 5/10/19 | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Joshua Fisk |  | The member began work on 5/02/2019 a 7 am by performing the stretching routine with the collective South District team. The first ticket of the day was to trouble shoot an outage at S.W. 74th and S. Penn at WEOKIE credit union. Through the trouble shooting process the member concluded that 3 phases in an underground transformer needed to be parked on parking stands and then close the normal open UG elbows in the same transformer. Performing the first part of the switching the member parked 2 phases, and while in the process of parking the 3rd phase is when he felt the discomfort/pain. Facts gathered from investigation: • Worked an 8 hour day on service the day before, 05/01/2019, from 7am to 3:30. • Started day on 05/02/2019 as normal at the Norman office at 7 am. • Performed stretches at beginning of our shift. • Stretching is a required routine for every day • Parked 2 of 3 phases prior to the incident • Member used an approved shotgun stick • While parking the last elbow, pain was experienced in the right shoulder area. • Feet were on dry ground when performing task • There was no slipping of feet • Power Quality member stopped to assist the injured member. |  |  | FALSE | South District Service Center | FALSE |  | FALSE | Construction Services |  | Toby Tilley | Joshua Fisk |  | Chad Self | Approved | Chad Self |  | Medium | [9 empty] | 10.02 Inadequate consideration of human factors/ergonomics |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | muscle tear while pushing insulated stick. | 24. Congestion or Restricted Action | 11. Overstress, Overpressure, Overexertion, Ergonomic |  | good details on the description | [24 empty] | FALSE |  |  | 2010-08-30 | 1976-09-09 |  | 2019-05-02 07:00 | 34 | 210 |  | FALSE |  | Member was parking primary on a parking stand and felt discomfort in his shoulder. |  | FALSE | Toby Tilley |  | Recordable | Toby Tilley |  |  |  |  | Sprain/Strain |  | TRUE |  | Service Technician | Shoulder | Injury | Right | TRUE | Joshua Fisk | TRUE | 2019 | 5/2/2019 7:00:00 AM |  | FALSE |  |  | The force of pushing the elbow on the parking stand | [25 empty] | none
8853 | Durant Service Center | 2019-05-02 10:30 | While working to restore power from storm damage, members were maneuvering through work site. While backing with a spotter on the driver side the truck backed over down lines in the mud. When the rear wheels went over the wire, a single steel core of #4 ACSR popped up out of the mud on the passenger side of the truck. The single steel core went over the tail pipe and began pulling on the exhaust and resulted in it being bent. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Delivery | Lyle Just | 2019-05-06 09:54 | 2019-05-03 09:35 | 2019-05-03 09:35 | 2019-05-03 10:16 | 2019-05-16 10:30 | 2019-05-03 08:03 | 2019-05-06 08:46 |  |  | around 24600 Old Hwy 70 Durant OK |  |  | Terry Hackett | Reviewed/Approved TMH | T&D Ops |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Lyle Just |  | While working to restore power from storm damage, members were maneuvering through work site. While backing with a spotter on the driver side the truck driver backed over down lines in the mud. When the rear wheels went over the wire, a single steel core of #4 ACSR popped up out of the mud on the passenger side of the truck. The single steel core went over the tail pipe and began pulling on the exhaust and resulted in it being bent. |  |  |  | Durant Service Center | FALSE |  | FALSE | Construction Services |  | Shad Barnett | Lyle Just |  | Chad Inman | I'm Ok with this. CI | Chad Inman |  | Low |  |  | 3.09 Constrained movement | 4.05 Extreme concentration/perception demands | [12 empty] | wire got caught on exhaust | 18. Failure to Check, Monitor | 6. Caught On (Snagged, Hung) | [68 empty] | Bent exhaust pipe | 200 | Shad Barnett | Vehicle (not related to operation of vehicle) |  | f07-521 | [18 empty] | 8588593
8854 | Muskogee Service Center | 2019-05-02 12:00 | While working storm work member was working with DCC to close bypass switch on re-closer station. Fuse blew back igniting the oil on re-closer and damaging extendo stick. Member was working from the ground and no injury occurred. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Delivery | Michael Fox | 2019-05-28 15:39 | 2019-05-03 13:23 | 2019-05-03 13:23 | 2019-05-09 09:41 | 2019-05-16 12:00 | 2019-05-03 12:46 | 2019-05-24 19:00 |  | 2019-05-13 06:53 | Jamestown circuit feeder line off main road approximately 60 ft . |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Michael Fox |  | We were called to go to Braggs to try and get the town back on, At the top of the hill we have re-closer station, all three were blown. We the proceeded to talk walk out the line and found a large tree laying on line, West tree service came out and removed tree limb from line. We went back to re-closer station and noticed oil on re-closer, we decided to bypass station due to the oil. I called Randy and told him that we are going to have to walk out the blind section, Randy sent two more men to help walk out the blind section. After walking out line we found no cause for the fuse to blow. We decided to open 3 solid blades to reduce the load. I called Greg to close C phase bypass after I opened the solid blades, Greg called me back and said the ground and the re-closers were on fire. I went back to the sight and put the ground fire out but the re-closer station was not truck accessible, The re-closer fire burned out on it's own Local fire department was called to the location. We then asked for a large bucket come out to isolate the re-closer station and close the bypass switch and the fuse held. When re-closer ignited one of the extendos were still in the air and caught the brunt of the damage. |  |  |  | Muskogee Service Center | FALSE |  | TRUE | Construction Services |  | James Evans | Michael Fox |  | Chad Inman | I'm satisfied with the investigation. CI | Chad Inman |  | Medium | [9 empty] | 10.03 Inadequate standards, specifications and/or design criteria | [6 empty] | Service member was called to go to Braggs to try and get the town back on, at the top of the hill we have re-closer station, and all three were blown. Member then proceeded to walk out the line and found a large tree laying on line, West tree service came out and removed tree limb from line. Member went back to re-closer station and noticed oil on re-closer, and then decided to bypass station due to the oil. Member called Supervisor and told him that they are going to have to walk out the blind section, Supervisors sent two more men to help walk out the blind section. After walking out line members found no cause for the fuse to blow. Members then decided to open 3 solid blades to reduce the load. Member called other member that was there to close C phase bypass after he opened the solid blades, member that closed C phase, called back and said the ground and the re-closers were on fire. Went back to the sight and put the ground fire out but the re-closer station was not truck accessible, the re-closer fire burned out on its own. Local fire department was called to the location. Members then asked for a large bucket to come out to isolate the re-closer station and close the bypass switch and the fuse held. When the re-closer ignited, the extendo stick was still in the air which resulted in damage. | 26. Fire & Explosion Hazards | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved | [90 empty] | NA
8854 | Muskogee Service Center | 2019-05-02 12:00 | While working storm work member was working with DCC to close bypass switch on re-closer station. Fuse blew back igniting the oil on re-closer and damaging extendo stick. Member was working from the ground and no injury occurred. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Delivery | Michael Fox | 2019-05-28 15:39 | 2019-05-03 13:23 | 2019-05-03 13:23 | 2019-05-09 09:41 | 2019-05-16 12:00 | 2019-05-03 12:46 | 2019-05-24 19:00 |  | 2019-05-13 06:53 | Jamestown circuit feeder line off main road approximately 60 ft . |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Property Damage |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Michael Fox |  | We were called to go to Braggs to try and get the town back on, At the top of the hill we have re-closer station, all three were blown. We the proceeded to talk walk out the line and found a large tree laying on line, West tree service came out and removed tree limb from line. We went back to re-closer station and noticed oil on re-closer, we decided to bypass station due to the oil. I called Randy and told him that we are going to have to walk out the blind section, Randy sent two more men to help walk out the blind section. After walking out line we found no cause for the fuse to blow. We decided to open 3 solid blades to reduce the load. I called Greg to close C phase bypass after I opened the solid blades, Greg called me back and said the ground and the re-closers were on fire. I went back to the sight and put the ground fire out but the re-closer station was not truck accessible, The re-closer fire burned out on it's own Local fire department was called to the location. We then asked for a large bucket come out to isolate the re-closer station and close the bypass switch and the fuse held. When re-closer ignited one of the extendos were still in the air and caught the brunt of the damage. |  |  |  | Muskogee Service Center | FALSE |  | TRUE | Construction Services |  | James Evans | Michael Fox |  | Chad Inman | I'm satisfied with the investigation. CI | Chad Inman |  | Medium | [9 empty] | 10.03 Inadequate standards, specifications and/or design criteria | [6 empty] | Service member was called to go to Braggs to try and get the town back on, at the top of the hill we have re-closer station, and all three were blown. Member then proceeded to walk out the line and found a large tree laying on line, West tree service came out and removed tree limb from line. Member went back to re-closer station and noticed oil on re-closer, and then decided to bypass station due to the oil. Member called Supervisor and told him that they are going to have to walk out the blind section, Supervisors sent two more men to help walk out the blind section. After walking out line members found no cause for the fuse to blow. Members then decided to open 3 solid blades to reduce the load. Member called other member that was there to close C phase bypass after he opened the solid blades, member that closed C phase, called back and said the ground and the re-closers were on fire. Went back to the sight and put the ground fire out but the re-closer station was not truck accessible, the re-closer fire burned out on its own. Local fire department was called to the location. Members then asked for a large bucket to come out to isolate the re-closer station and close the bypass switch and the fuse held. When the re-closer ignited, the extendo stick was still in the air which resulted in damage. | 26. Fire & Explosion Hazards | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved | [90 empty] | NA
8855 | Muskogee Power Plant | 2019-05-07 11:00 | Contracting member was witnessed hanging rigging while working on fuel pipe not designed to be stood on. The pipe he stood on was apx 10 feet from the next level of grating. | Level 2 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services |  | 2019-06-06 16:33 | 2019-05-07 12:35 | 2019-05-07 12:35 | 2019-05-23 17:08 | 2019-05-21 16:00 | 2019-05-07 12:30 | 2019-06-04 07:31 |  | 2019-06-03 15:19 | Unit 4 Level 5 Above Low Pressure Skid |  |  | William Young | Reviewed and approved. WCY 6/6/19 | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | The contracting member took a short cut by not planning out a work activity. The action was not malicious but still was not appropriate. The member was incorrectly tied off while he was standing on a process pipe not meant for standing. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | UTS - Capital Projects |  |  |  |  | Christopher Lelak | No commnent CBL 06/04/19 | Christopher Lelak |  | Medium |  |  |  | 4.09 Preoccupation with problems | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction | [9 empty] | 16.06 Inadequate communication methods | Contracting member took a shortcut with standing on a process pipe as a standing platform. He also improperly attached his safety harness to a handrail. | 11. Improper Position for Task | 3. Fall from Elevation to Lower Level |  | No additional comments. MLH 6/3/19 |  |  |  | Injury / Illness | [7 empty] | 3. Fall from Elevation to Lower Level |  | TEIC | N/A | [75 empty] | none
8855 | Muskogee Power Plant | 2019-05-07 11:00 | Contracting member was witnessed hanging rigging while working on fuel pipe not designed to be stood on. The pipe he stood on was apx 10 feet from the next level of grating. | Level 2 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services |  | 2019-06-06 16:33 | 2019-05-07 12:35 | 2019-05-07 12:35 | 2019-05-23 17:08 | 2019-05-21 16:00 | 2019-05-07 12:30 | 2019-06-04 07:31 |  | 2019-06-03 15:19 | Unit 4 Level 5 Above Low Pressure Skid |  |  | William Young | Reviewed and approved. WCY 6/6/19 | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | The contracting member took a short cut by not planning out a work activity. The action was not malicious but still was not appropriate. The member was incorrectly tied off while he was standing on a process pipe not meant for standing. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | UTS - Capital Projects |  |  |  |  | Christopher Lelak | No commnent CBL 06/04/19 | Christopher Lelak |  | Medium |  |  |  | 4.09 Preoccupation with problems | 5.06 Lack of situational awareness | 6.01 Inadequate initial instruction | [9 empty] | 16.06 Inadequate communication methods | Contracting member took a shortcut with standing on a process pipe as a standing platform. He also improperly attached his safety harness to a handrail. | 11. Improper Position for Task | 3. Fall from Elevation to Lower Level |  | No additional comments. MLH 6/3/19 |  |  |  | Injury / Illness | [7 empty] | 3. Fall from Elevation to Lower Level |  | TEIC | N/A | [75 empty] | none
8855 | Muskogee Power Plant | 2019-05-07 11:00 | Contracting member was witnessed hanging rigging while working on fuel pipe not designed to be stood on. The pipe he stood on was apx 10 feet from the next level of grating. | Level 2 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services |  | 2019-06-06 16:33 | 2019-05-07 12:35 | 2019-05-07 12:35 | 2019-05-23 17:08 | 2019-05-21 16:00 | 2019-05-07 12:30 | 2019-06-04 07:31 |  | 2019-06-03 15:19 | Unit 4 Level 5 Above Low Pressure Skid |  |  | William Young | Reviewed and approved. WCY 6/6/19 | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | The contracting member took a short cut by not planning out a work activity. The action was not malicious but still was not appropriate. The member was incorrectly tied off while he was standing on a process pipe not meant for standing. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | UTS - Capital Projects |  |  |  |  | Christopher Lelak | No commnent CBL 06/04/19 | Christopher Lelak |  | Medium |  |  |  | 4.09 Preoccupation with problems | 5.06 Lack of situational awareness | 6.02 Inadequate practice | [9 empty] | 16.06 Inadequate communication methods | Contracting member took a shortcut with standing on a process pipe as a standing platform. He also improperly attached his safety harness to a handrail. | 11. Improper Position for Task | 3. Fall from Elevation to Lower Level |  | No additional comments. MLH 6/3/19 |  |  |  | Injury / Illness | [7 empty] | 3. Fall from Elevation to Lower Level |  | TEIC | N/A | [75 empty] | none
8855 | Muskogee Power Plant | 2019-05-07 11:00 | Contracting member was witnessed hanging rigging while working on fuel pipe not designed to be stood on. The pipe he stood on was apx 10 feet from the next level of grating. | Level 2 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services |  | 2019-06-06 16:33 | 2019-05-07 12:35 | 2019-05-07 12:35 | 2019-05-23 17:08 | 2019-05-21 16:00 | 2019-05-07 12:30 | 2019-06-04 07:31 |  | 2019-06-03 15:19 | Unit 4 Level 5 Above Low Pressure Skid |  |  | William Young | Reviewed and approved. WCY 6/6/19 | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | The contracting member took a short cut by not planning out a work activity. The action was not malicious but still was not appropriate. The member was incorrectly tied off while he was standing on a process pipe not meant for standing. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | UTS - Capital Projects |  |  |  |  | Christopher Lelak | No commnent CBL 06/04/19 | Christopher Lelak |  | Medium |  |  |  | 4.04 Routine, monotony, demand for uneventful vigilance | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction | [9 empty] | 16.06 Inadequate communication methods | Contracting member took a shortcut with standing on a process pipe as a standing platform. He also improperly attached his safety harness to a handrail. | 11. Improper Position for Task | 3. Fall from Elevation to Lower Level |  | No additional comments. MLH 6/3/19 |  |  |  | Injury / Illness | [7 empty] | 3. Fall from Elevation to Lower Level |  | TEIC | N/A | [75 empty] | none
8855 | Muskogee Power Plant | 2019-05-07 11:00 | Contracting member was witnessed hanging rigging while working on fuel pipe not designed to be stood on. The pipe he stood on was apx 10 feet from the next level of grating. | Level 2 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services |  | 2019-06-06 16:33 | 2019-05-07 12:35 | 2019-05-07 12:35 | 2019-05-23 17:08 | 2019-05-21 16:00 | 2019-05-07 12:30 | 2019-06-04 07:31 |  | 2019-06-03 15:19 | Unit 4 Level 5 Above Low Pressure Skid |  |  | William Young | Reviewed and approved. WCY 6/6/19 | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | The contracting member took a short cut by not planning out a work activity. The action was not malicious but still was not appropriate. The member was incorrectly tied off while he was standing on a process pipe not meant for standing. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | UTS - Capital Projects |  |  |  |  | Christopher Lelak | No commnent CBL 06/04/19 | Christopher Lelak |  | Medium |  |  |  | 4.04 Routine, monotony, demand for uneventful vigilance | 5.06 Lack of situational awareness | 6.01 Inadequate initial instruction | [9 empty] | 16.06 Inadequate communication methods | Contracting member took a shortcut with standing on a process pipe as a standing platform. He also improperly attached his safety harness to a handrail. | 11. Improper Position for Task | 3. Fall from Elevation to Lower Level |  | No additional comments. MLH 6/3/19 |  |  |  | Injury / Illness | [7 empty] | 3. Fall from Elevation to Lower Level |  | TEIC | N/A | [75 empty] | none
8855 | Muskogee Power Plant | 2019-05-07 11:00 | Contracting member was witnessed hanging rigging while working on fuel pipe not designed to be stood on. The pipe he stood on was apx 10 feet from the next level of grating. | Level 2 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services |  | 2019-06-06 16:33 | 2019-05-07 12:35 | 2019-05-07 12:35 | 2019-05-23 17:08 | 2019-05-21 16:00 | 2019-05-07 12:30 | 2019-06-04 07:31 |  | 2019-06-03 15:19 | Unit 4 Level 5 Above Low Pressure Skid |  |  | William Young | Reviewed and approved. WCY 6/6/19 | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | The contracting member took a short cut by not planning out a work activity. The action was not malicious but still was not appropriate. The member was incorrectly tied off while he was standing on a process pipe not meant for standing. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | UTS - Capital Projects |  |  |  |  | Christopher Lelak | No commnent CBL 06/04/19 | Christopher Lelak |  | Medium |  |  |  | 4.04 Routine, monotony, demand for uneventful vigilance | 5.06 Lack of situational awareness | 6.02 Inadequate practice | [9 empty] | 16.06 Inadequate communication methods | Contracting member took a shortcut with standing on a process pipe as a standing platform. He also improperly attached his safety harness to a handrail. | 11. Improper Position for Task | 3. Fall from Elevation to Lower Level |  | No additional comments. MLH 6/3/19 |  |  |  | Injury / Illness | [7 empty] | 3. Fall from Elevation to Lower Level |  | TEIC | N/A | [75 empty] | none
8856 | Seminole PP; EGX Gath/Trans | 2019-05-07 12:30 | Vendor on site to remove mobile office trailer/container for contractor ECA as project work is winding down. While trying to load the container onto the bed of the semi-trailer truck, one of the truck's fenders contacted the chain link fence around the gas yard. The result was minor damage to the chain link fabric. | Level 1 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services |  | 2019-07-01 08:25 | 2019-05-07 16:10 | 2019-05-07 16:10 | 2019-06-14 12:27 | 2019-05-21 12:30 | 2019-05-07 16:03 | 2019-06-14 14:13 |  |  | Seminole Plant Unit gas yard at Unit 3 |  |  | Chrysty Dorsey | Reviewed. | UTS |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | Truck driver came to the site with truck that was not capable to load the container as it should have been loaded, i.e., the winch on the truck was inoperable and he tried to get it loaded despite this shortcoming. Driver should have been sent off site until he could return with the proper equipment. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Capital Projects |  | Danny Pogue |  |  | Christopher Lelak | No Comments - CBL 06/14/19 | Christopher Lelak |  | Low | [12 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | Truck driver's task was to retrieve a connex container and haul it off site. Truck's winch line required to load connex container was inoperable, so he proceeded to try to drag the container around and pull it up onto his trailer. In the process, the truck's fender contacted the site chain link fence and induced minor damage to the fence. | 23. Defective Tools, Equipment or Materials | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  |  | Damage to chain link fabric |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Danny Pogue | Electrical Corporation of America | Glen (last name unknown) |  | Vehicle (not related to vehicle's operation) | [6 empty] | FALSE | [66 empty] | 1646031
8857 | Metro Service Center | 2019-05-07 09:30 | Public vehicle drove through road closed barricades and rear ended 1 ton truck being used a buffer vehicle. All workzone controls were in place and no injury to company members occurred. | Level 2 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Jimmy Combs | 2019-06-04 14:50 | 2019-05-08 06:41 | 2019-05-08 06:41 | 2019-05-20 09:30 | 2019-05-21 09:30 | 2019-05-08 06:34 | 2019-06-04 14:27 |  | 2019-05-28 15:24 | Harrah turnpike job ne10 .5 miles east of peebly rd. |  |  | Lindle Coleman | I agree great job | T&D Ops |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Jimmy Combs |  | Public vehicle drove through road closed barricades and rear ended 1 ton truck being used a buffer vehicle. All workzone controls were in place and no injury to company members occurred. Facts Ascertained: Equipment operator was at the back of the crane on the drivers side operating the outrigger controls when the public driver struck the buffer vehicle Equipment operator noticed the public driver was going to make impact with the buffer vehicle moments prior to occurrence. When the operator realized the public driver was not going to swerve he ran from between the vehicles in order to get out of the line of fire. Upon impact the public vehicle caught fire in the drivers side of the engine compartment Equipment operator grabbed the extinguisher from the buffer vehicle and put the fire out When struck the buffer vehicle moved forward approximately 3' leaving 34" between the buffer and the crane Workzone safety and controls were covered in the documented tailboard and all members reviewed/signed Approximately 1 mile clear line of site to our workzone 2 road closed barricades were in place at the intersection of peebly and 10th 1 road closed sign, 1 trucks entering and exiting roadway sign, 1 lane closed ahead sign where in place between the intersection of Peebly and 10th Members were wearing class 2 vests Cones were out behind the buffer vehicle Public driver stated he was tired and was trying to get to Norman Norman was in the opposite direction of his travel |  |  |  | Metro Service Center | FALSE |  | FALSE | Construction Services |  | James Wickizer | Hershel Goodson |  | Gary Lassley | I cannot express how proud I am of the crew. What a great example of "Live Safely and Take Charge". The Crew not only had all the proper traffic control out, but also had the foresight to install a buffer truck between them and the public. This could have ended up being a catastrophic accident if it were not for the Take Charge attitude of the crew. I also want to commend the Equipment Operators quick response of putting out the fire in the public vehicle. | Gary Lassley |  | Medium |  |  | 3.03 Fatigue due to lack of rest | [13 empty] | public driver went thru barricades | 19. Failure to React, Correct | 2. Struck By (Hit By Moving Object) |  | Reviewed and approved TMH 5/28/19 | [72 empty] | FALSE |  | Harrah | Public Vehicle Struck OGE | OGE Vehicle Stopped/Parked | 2015-08-16 19:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear |  |  | 1686840
8858 | Shawnee Service Center | 2019-05-08 07:30 | Member began to slow down with the flow of traffic. At this time he was rear ended by a public driver causing minor damage to the bumper of the company truck. Both drivers were unharmed. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Mark Martin | 2019-05-09 15:07 | 2019-05-08 10:13 | 2019-05-08 10:13 | 2019-05-09 15:03 | 2019-05-22 06:30 | 2019-05-08 10:03 |  |  |  | westbound on I-40 just west of the I-35 northbound exit |  |  | Luke Kennedy | Could not fill out detailed description in draft mode. I'm assuming because it is ranked as a non chargeable low. All pictures of incident and pertinent information has been attached. | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | [6 empty] | Shawnee Service Center | FALSE |  | FALSE | Construction Services |  | Todd Munson | Mark Martin |  |  |  | Terry Garrett |  | Low | [93 empty] | FALSE |  | Oklahoma City | Public Vehicle Struck OGE | Public Driver Failed To Yield | 2018-05-02 19:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Rain
8859 | Mustang Power Plant | 2019-05-10 13:00 | Contractor was not signed on to LOTO while terminating 120 volt emergency alert speaker. LOTO was in place. No injuries occurred. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kristopher Gasaway | 2019-07-22 08:44 | 2019-05-10 14:18 | 2019-05-10 14:18 | 2019-07-16 15:25 | 2019-05-24 13:00 | 2019-05-10 13:47 | 2019-07-17 07:02 |  | 2019-07-16 15:39 | Unit 12, emergency alert speaker located by PCM |  |  | Jesse Murray | Returning for a few reasons discussed on call. We need to require Federal to give us a complete investigation since they are the GC OGE has the arrangement with. We need to review if Federal has a Contractor Management Procedure in ISNworld. Add C.A. to input a change request to LOTO SOP to Require Locks. Jesse Murray 6-12-19 | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kristopher Gasaway |  | On May 10, 2019 Mustang Energy Center experienced a LOTO incident. Goddard Enterprises had a field technician and an electrician on site to install the plant emergency alert system. The field technician was at Mustang two days previous walking down the job scope/locations and discussing what he and the electrician would be doing and where they would be placing the speakers for the alert system. During the pre-work visit the technician stated he would be terminating Ethernet cables and programming the system, and the electrician would run conduit and wiring. On the day of the incident, two OGE Members approached the field technician and noticed that he was terminating 120v wiring, so they asked if he was on the LOTO for the electrical. The technician stated that he had seen the danger tags and believed it was safe for him to work on the electrical wiring, but didn’t know he had to sign on anything. The OGE members stopped his work and took him to the control room to report the incident. They also had a conversation with him on the LOTO procedure, and how to go about signing on the MSOS. There was a LOTO in place for the electrician to complete his work and the wiring was de-energized, but the technician was not asked to sign on to it. The plant contact believed that the field technician was only going to be terminating Ethernet cables at the speakers, not the 120vac wires. After review, the technician had completed the proper orientation and was signed onto the SWP with the electrician that he was working with, but not the LOTO. After the incident is was determined that the field technician should’ve had his own SWP due to the differences in work scope between him and the electrician. If he would’ve filled out his own SWP, he may have listed the 120v wiring, and we would’ve known to have him sign on the LOTO. The job was originally issued to Federal Signal Corp, and they sub contracted it to Goddard Enterprises. Goddard Enterprises is not in ISNet. |  |  |  | Mustang Power Plant | FALSE |  | TRUE | Other |  | Charles Lilly | Kristopher Gasaway |  | William Sanders | Approve | William Sanders |  | Medium |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.06 Inadequate work planning or programming | [7 empty] | Lack of good communication between technician and plant contact. | 20. Failure to Communicate, Coordinate | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Attached Federal Signals sub contractor agreement. Reviewed items from initial call. |  |  |  | Clearance / LOTO |  | Kristopher Gasaway | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Charles Lilly | Goddard Enterprises | Logan Shelts |  |  |  | Kristopher Gasaway
8859 | Mustang Power Plant | 2019-05-10 13:00 | Contractor was not signed on to LOTO while terminating 120 volt emergency alert speaker. LOTO was in place. No injuries occurred. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kristopher Gasaway | 2019-07-22 08:44 | 2019-05-10 14:18 | 2019-05-10 14:18 | 2019-07-16 15:25 | 2019-05-24 13:00 | 2019-05-10 13:47 | 2019-07-17 07:02 |  | 2019-07-16 15:39 | Unit 12, emergency alert speaker located by PCM |  |  | Jesse Murray | Returning for a few reasons discussed on call. We need to require Federal to give us a complete investigation since they are the GC OGE has the arrangement with. We need to review if Federal has a Contractor Management Procedure in ISNworld. Add C.A. to input a change request to LOTO SOP to Require Locks. Jesse Murray 6-12-19 | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kristopher Gasaway |  | On May 10, 2019 Mustang Energy Center experienced a LOTO incident. Goddard Enterprises had a field technician and an electrician on site to install the plant emergency alert system. The field technician was at Mustang two days previous walking down the job scope/locations and discussing what he and the electrician would be doing and where they would be placing the speakers for the alert system. During the pre-work visit the technician stated he would be terminating Ethernet cables and programming the system, and the electrician would run conduit and wiring. On the day of the incident, two OGE Members approached the field technician and noticed that he was terminating 120v wiring, so they asked if he was on the LOTO for the electrical. The technician stated that he had seen the danger tags and believed it was safe for him to work on the electrical wiring, but didn’t know he had to sign on anything. The OGE members stopped his work and took him to the control room to report the incident. They also had a conversation with him on the LOTO procedure, and how to go about signing on the MSOS. There was a LOTO in place for the electrician to complete his work and the wiring was de-energized, but the technician was not asked to sign on to it. The plant contact believed that the field technician was only going to be terminating Ethernet cables at the speakers, not the 120vac wires. After review, the technician had completed the proper orientation and was signed onto the SWP with the electrician that he was working with, but not the LOTO. After the incident is was determined that the field technician should’ve had his own SWP due to the differences in work scope between him and the electrician. If he would’ve filled out his own SWP, he may have listed the 120v wiring, and we would’ve known to have him sign on the LOTO. The job was originally issued to Federal Signal Corp, and they sub contracted it to Goddard Enterprises. Goddard Enterprises is not in ISNet. |  |  |  | Mustang Power Plant | FALSE |  | TRUE | Other |  | Charles Lilly | Kristopher Gasaway |  | William Sanders | Approve | William Sanders |  | Medium |  |  |  |  | 5.05 Misunderstood directions |  |  |  | 9.06 Inadequate work planning or programming | [7 empty] | Lack of good communication between technician and plant contact. | 20. Failure to Communicate, Coordinate | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Attached Federal Signals sub contractor agreement. Reviewed items from initial call. |  |  |  | Clearance / LOTO |  | Kristopher Gasaway | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Charles Lilly | Goddard Enterprises | Logan Shelts |  |  |  | Kristopher Gasaway
8860 | Muskogee Power Plant | 2019-05-14 04:30 | Member was returning a nitrogen bottle to the empty rack when he made contact with a Post Indicating Valve on the passenger side of the truck. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Supply |  | 2019-07-02 09:44 | 2019-05-14 17:27 | 2019-05-14 17:27 | 2019-06-19 13:20 | 2019-05-28 04:30 | 2019-05-14 17:03 | 2019-06-28 13:25 |  |  | MKPP South of MK6 GSU against the retaining wall. |  |  | Robert Wright | Approved Bob Wright | Power Supply |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Zackary Thompson |  | Member was returning an empty N2 bottle to the bottle storage rack when company truck struck PIV 17 located a few feet NW of bottle storage rack. Member was driving between the PIV and storage rack. Member was working alone and felt the safer path was to drive forward as opposed to backing the truck to the storage rack. The passenger side back quarter panel of the truck was dented, the PIV was not damaged. Member had completed a SWP, but did not identify the hazard of the tight space between the bottle storage rack and PIV. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | Operations |  | Zackary Thompson |  |  |  | Reviewed SPC 6/28/2019 |  |  | Low | [9 empty] | 10.02 Inadequate consideration of human factors/ergonomics | [6 empty] | Member positioned truck parallel to N2 bottle storage to avoid the hazard of backing the truck to the bottle storage. Member was working alone and felt he had a safer path pulling parallel as opposed to backing the truck. | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) | [74 empty] | TRUE |  | Fort Gibson | Struck Fixed Object | Turned Into Object | 2004-10-03 19:00 |  | FALSE |  |  | Night |  |  | Concrete/Pavement |  | Cloudy |  |  | None
8861 | Sooner Power Plant | 2019-05-15 07:30 | Scaffold pole was bent when it came into contact with boiler water circulation pump piping after Sooner unit 1 was returned to service from outage. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Lance Lantz | 2019-06-20 09:59 | 2019-05-15 10:27 | 2019-05-15 10:27 | 2019-06-03 12:55 | 2019-05-29 07:30 | 2019-05-15 07:30 | 2019-06-10 11:50 |  |  | Sooner Power Plant Unit 1, Level 3, D Boiler Water Circulation Pump |  |  | Brady Sowell | Approved | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Lance Lantz |  | On April 26, 2019 a request was given to Brock for the erection of scaffolding on unit 1 D boiler water circulation pump. The scaffold was erected on April 29, 2019. The scaffold was built in stages to facilitate different parts of the removal process. The scaffold was modified numerous times throughout the process of removing the pump, cleaning flanges, and reinstalling the pump. On May 9, 2019 work was completed on the pump and Brock was asked to dismantle the scaffolding except for the lower deck. Brock was asked to leave the lower deck in place, because the electricians would need to check rotation once the unit was returned to service and the pump could be bump tested. Brock was instructed to ensure that all scaffolding was down and cleared from any equipment that might move or grow during start up. Unit 1 was returned to service on May 14, 2019. On May 15, 2019 the operation shift supervisor contacted the Brock plant contact with concerns of the scaffold pole that had made contact with the piping and was bent. The Brock site supervisor and the plant contact went and inspected the site and found that one horizontal scaffold pole was running over the top of the mid-rail on the hand rail and under the piping was bent. After further investigation it was found that Brock site supervisor and the plant contact reviewed the scaffold log to determine that all scaffolds built in areas around equipment that moves during start-up was dismantled. Both parties knew the lower deck and legs were still in place on the 1D boiler water circulation pump, but understood that all connecting points were more than 12” away from any piping or component of the pump. The scaffold pole that was bent was running parallel to a horizontal run of piping. The piping had a tee in it that was overlooked as being an obstruction that could contact the scaffolding. The scaffold pole was cut out and the rest of the scaffold was dismantled on May 15, 2019. There was no other damage to the scaffolding and no damage to the piping. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Maintenance |  | Allen Moore | Lance Lantz |  | Frank Brixey | Approve- Brixey 5/30/2019 | Frank Brixey |  | Low |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.06 Inadequate work planning or programming | [7 empty] | The scaffold pole that was bent was running parallel to a horizontal run of piping. The piping had a tee in it that was overlooked as being an obstruction that could contact the scaffolding. | 11. Improper Position for Task | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Lance Lantz | Scaffold pole bent |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Allen Moore | Brock | Chuck Robbins |  | Portable Tool |  | Lance Lantz |  |  |  | 1D Boiler Water Circulation Pump Piping | TRUE | [66 empty] | 9578456
8861 | Sooner Power Plant | 2019-05-15 07:30 | Scaffold pole was bent when it came into contact with boiler water circulation pump piping after Sooner unit 1 was returned to service from outage. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Lance Lantz | 2019-06-20 09:59 | 2019-05-15 10:27 | 2019-05-15 10:27 | 2019-06-03 12:55 | 2019-05-29 07:30 | 2019-05-15 07:30 | 2019-06-10 11:50 |  |  | Sooner Power Plant Unit 1, Level 3, D Boiler Water Circulation Pump |  |  | Brady Sowell | Approved | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Lance Lantz |  | On April 26, 2019 a request was given to Brock for the erection of scaffolding on unit 1 D boiler water circulation pump. The scaffold was erected on April 29, 2019. The scaffold was built in stages to facilitate different parts of the removal process. The scaffold was modified numerous times throughout the process of removing the pump, cleaning flanges, and reinstalling the pump. On May 9, 2019 work was completed on the pump and Brock was asked to dismantle the scaffolding except for the lower deck. Brock was asked to leave the lower deck in place, because the electricians would need to check rotation once the unit was returned to service and the pump could be bump tested. Brock was instructed to ensure that all scaffolding was down and cleared from any equipment that might move or grow during start up. Unit 1 was returned to service on May 14, 2019. On May 15, 2019 the operation shift supervisor contacted the Brock plant contact with concerns of the scaffold pole that had made contact with the piping and was bent. The Brock site supervisor and the plant contact went and inspected the site and found that one horizontal scaffold pole was running over the top of the mid-rail on the hand rail and under the piping was bent. After further investigation it was found that Brock site supervisor and the plant contact reviewed the scaffold log to determine that all scaffolds built in areas around equipment that moves during start-up was dismantled. Both parties knew the lower deck and legs were still in place on the 1D boiler water circulation pump, but understood that all connecting points were more than 12” away from any piping or component of the pump. The scaffold pole that was bent was running parallel to a horizontal run of piping. The piping had a tee in it that was overlooked as being an obstruction that could contact the scaffolding. The scaffold pole was cut out and the rest of the scaffold was dismantled on May 15, 2019. There was no other damage to the scaffolding and no damage to the piping. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Maintenance |  | Allen Moore | Lance Lantz |  | Frank Brixey | Approve- Brixey 5/30/2019 | Frank Brixey |  | Low |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming | [7 empty] | The scaffold pole that was bent was running parallel to a horizontal run of piping. The piping had a tee in it that was overlooked as being an obstruction that could contact the scaffolding. | 11. Improper Position for Task | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Lance Lantz | Scaffold pole bent |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Allen Moore | Brock | Chuck Robbins |  | Portable Tool |  | Lance Lantz |  |  |  | 1D Boiler Water Circulation Pump Piping | TRUE | [66 empty] | 9578456
8862 | Seminole PP; EGX Gath/Trans | 2019-05-16 10:30 | Contractor stepped off generator step onto the ground and stepped on a snake | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Timothy Coffey | 2019-06-13 09:09 | 2019-05-16 11:57 | 2019-05-16 11:57 | 2019-05-16 15:00 | 2019-05-30 10:30 | 2019-05-16 11:52 | 2019-06-07 11:02 |  | 2019-05-22 08:40 | Parking area on North side of Admin building South of Unit 2 Main Power Transformer |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Timothy Coffey |  | Contractor stated he was stepping off the rental generator and when he stepped onto the concrete he felt something squishy under his foot. He looked down he saw he was stepping on a snake. At this time he killed the snake. I observed the dead snake. He did not state how he killed the snake. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | TRUE | Other |  | Timothy Coffey | Timothy Coffey |  | Justin Stahl | Corrective action to have conversation with contractor about looking before stepping will help prevent further incidents. | Justin Stahl |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | contractor stepped onto a snake | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | . |  |  |  | Injury / Illness |  | Timothy Coffey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Timothy Coffey | United Rentals | James Clodfelter |  |  |  | Timothy Coffey | [71 empty] | 9576978
8863 | Seminole PP; EGX Gath/Trans | 2019-05-15 17:00 | Operator and contractor heard loud noise in 13.8kV switchgear area. Upon arriving at switchgear the operator saw smoke coming from switchgear in the area of breaker 012. There were no injuries. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Paul Schoelen | 2019-06-20 11:09 | 2019-05-16 16:20 | 2019-05-16 16:20 | 2019-06-06 17:07 | 2019-05-29 17:00 | 2019-05-15 17:00 | 2019-06-18 07:20 |  | 2019-06-14 13:52 | SM3 13.8kV switchgear |  |  | Jesse Murray | I approve. Jesse Murray 6-20-19 | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Paul Schoelen |  | Contractor electrician and plant operator working in the area of SM3 switchgear heard a loud noise at the switchgear. Both went to investigate and noticed smoke coming from the Breaker 012 area. Plant operator notified OA and plant electricians. After the bus was cleared out, plant electricians determined the A phase surge arrester was burnt out. All three surge arresters were replaced. The surge arrester performed as designed to protect downstream equipment. The cause for the surge was not determined. They were no system events recorded for that time period. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | Operations |  | Gregory Fry | Paul Schoelen |  | Scott Lee | I approve this incident investigation report. | Scott Lee |  | Medium | [11 empty] | 12.01.1 Inadequate preventative assessment of needs |  |  |  |  | A surge on the 13.8kV system from the substation caused the surge protector to blow out. | 08. Improper Loading | 12. Equipment Failure |  | See workflow comments for reason for returning. CD | [66 empty] | Evidence of electrical arc in breaker cabinet. Investigation is underway to determine the full extent of the damage. | 10000 |  | Process Interruption | [20 empty] | None
8864 | Sooner Power Plant | 2019-05-16 16:00 | *No member injury or equipment damage* On 5/16, members were working on settling basin outage to pump out, clean, and rebuild valves on the basin. LOTO had been hung & issued at 0821 on 5/16. At approx. 1600, members were unbolting sludge pump discharge Clarkson valves to remove & rebuild; when bolts were loosened, a large amount of water sprayed from flange. Members were able to tighten flange to stop water. It was discovered that both units overflow sump pump discharges tie into the same discharge pipe as the sludge pumps’ discharge due to changes to comply with CCR rules, and overflow sump pumps were still in operation. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Kellan Keeter | 2019-07-09 07:50 | 2019-05-16 22:25 | 2019-05-16 22:25 | 2019-06-18 10:06 | 2019-05-30 16:00 | 2019-05-16 18:30 | 2019-06-21 11:10 |  | 2019-06-20 12:12 | Sooner Settling basin sludge pumps. |  |  | Jesse Murray | This is a perfect example of an incident where Configuration Control process should be followed especially when it pertains to new processes implemented. In this particular case, the changes were made in the field but the LOTO templates were not changed to reflect different case scenarios to secure zero energy. Also, the drawings were poorly updated and communicated. I approve. I approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | On Thursday, May 16, 2019 at approximately 1600 hours, during the yearly settling basin outage, members were continuing to work on tasks related to the cleaning and replacing of valves on the settling basin. All valves had been taken out and replaced at this point the last two valves to be replaced were the sludge pump discharge valves in the settling basin. Even though the “First Break Procedure” has not been finalized, Maintenance members do follow an unofficial version of it: by cutting away from person, and loosening one bolt at time. As reflected in member’s SWP, the box for “First –Break Procedure Followed” was checked. Using this method member began to take the flange off going to the discharge valve on B sludge pump. Once, he started to loosen the bolts on this flange it began to have a discharge of water. This discharge seemed to have more pressure than head pressure and after some time it did not slow down. Therefore, member tightened the bolts back up on flange. Stopped work and reported what he had experienced to his supervisor. The supervisor then reported it to the shift supervisor and management. The LOTO was created and hung in accordance to the 682 request. When referring to the work order 18838745 that was attached to this 682 request. Upon review of it and the email sent by the foreman it was unknown as to the work to be done to the sludge pumps discharge valves. The email does state that “all components of the sludge pumps including air to the Clarkson’s”, then the 682 states “we will need actuating air un-isolated to the Clarkson’s”. Therefore, the sludge pumps were electrically isolated and discharge valves were left un-isolated on this LOTO. The original template for the settling basin was created but after review it was discovered that changes made to the system during the Coal Combustion Residual (CCR) rule made that LOTO inadequate. Therefore, it was determined that the “Overflow Sump Pumps” would not need to be included as they now discharge to the settling ponds. Prior to CCR it would have been required to get one of the pumps because it at that time it would have discharged into the settling basin and the other into the lower ditch that is no longer in service. Both pumps now discharge into a common line that goes to the settling ponds. This line can also discharge into the settling basin, but if “BOTTOM ASH OVERFLOW DISCHARGE TO SETTLING BASIN ISOLATION VALVE” is closed water cannot get into the settling basin, which was included in the LOTO. However, the discharge of the sludge pumps also discharge into this line and through investigation, it was discovered that it will be charged from back pressure coming from the Overflow Sump pumps. Therefore, when the LOTO was created the boundaries were walked down and determined that by getting the 480V breakers to both sludge pumps, #1 & #2 Ash piping drain sumps, recycle basin supply to slope wash ISV (which was later removed as requested by foreman), recycle header minimum flow valve air ISV, and Bottom Ash overflow discharge to settling basin ISV (which would isolate the water from the overflow sumps from getting into the basin). This LOTO was then verified by a qualified individual before it was hung. After members hung and verified the LOTO, there was/is not a way to verify “ZERO ENERGY” on the piping side (under the basin) of this LOTO as there is not any drain valves on the piping below the basin. Members were able to verify that zero water was discharging into the basin, which was the intent of the LOTO. The PAE was qualified on this system prior to the CCR rule, but was unware of the changes made to this system. When PAE verified the boundaries there was not any water going into the settling basin. With the unknown changes to the system the PAE did not realize that the discharge valves could be back pressured from the new line that was installed during the CCR rule. Prior to this outage, proper planning and coordination with all departments involved had not been made aware of scope of work that was going to take place during the outage. It was found that the task list attached to this work order was out dated and incorrect, leading to some of the miscommunication in submitting the correct 682 for the work that was going to be performed. Also, due to the upgrades of the CCR project it was brought to our attention that the prints and drawings were not exposed properly to all members of the plant. Because members were not aware of changes made to the system they were not able to properly verify zero energy on this system. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Justin Buchanan | Alexander Taybah |  | Alexander Taybah | Monday, 06/17/2019, this incident will be sent back to Investigate status to edit some of the findings as discussed with Marc Hodgson (SS) and Brady Sowell (Safety Coordinator). | Alexander Taybah |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.03 Infrequent performance | [7 empty] | 14.02.4 Inadequate communication of standards: training |  |  | Due to the upgrades from Coal Combustion Residual (CCR) the changes made to this system were not updated to the plant nor was the prints and drawings update. The task list for this work order was also out of date. | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) |  | See workflow comments or email. Per Sowell on 5/30. Approved by sowell on 6/20/2019 | [90 empty] | 18838745
8864 | Sooner Power Plant | 2019-05-16 16:00 | *No member injury or equipment damage* On 5/16, members were working on settling basin outage to pump out, clean, and rebuild valves on the basin. LOTO had been hung & issued at 0821 on 5/16. At approx. 1600, members were unbolting sludge pump discharge Clarkson valves to remove & rebuild; when bolts were loosened, a large amount of water sprayed from flange. Members were able to tighten flange to stop water. It was discovered that both units overflow sump pump discharges tie into the same discharge pipe as the sludge pumps’ discharge due to changes to comply with CCR rules, and overflow sump pumps were still in operation. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Kellan Keeter | 2019-07-09 07:50 | 2019-05-16 22:25 | 2019-05-16 22:25 | 2019-06-18 10:06 | 2019-05-30 16:00 | 2019-05-16 18:30 | 2019-06-21 11:10 |  | 2019-06-20 12:12 | Sooner Settling basin sludge pumps. |  |  | Jesse Murray | This is a perfect example of an incident where Configuration Control process should be followed especially when it pertains to new processes implemented. In this particular case, the changes were made in the field but the LOTO templates were not changed to reflect different case scenarios to secure zero energy. Also, the drawings were poorly updated and communicated. I approve. I approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | On Thursday, May 16, 2019 at approximately 1600 hours, during the yearly settling basin outage, members were continuing to work on tasks related to the cleaning and replacing of valves on the settling basin. All valves had been taken out and replaced at this point the last two valves to be replaced were the sludge pump discharge valves in the settling basin. Even though the “First Break Procedure” has not been finalized, Maintenance members do follow an unofficial version of it: by cutting away from person, and loosening one bolt at time. As reflected in member’s SWP, the box for “First –Break Procedure Followed” was checked. Using this method member began to take the flange off going to the discharge valve on B sludge pump. Once, he started to loosen the bolts on this flange it began to have a discharge of water. This discharge seemed to have more pressure than head pressure and after some time it did not slow down. Therefore, member tightened the bolts back up on flange. Stopped work and reported what he had experienced to his supervisor. The supervisor then reported it to the shift supervisor and management. The LOTO was created and hung in accordance to the 682 request. When referring to the work order 18838745 that was attached to this 682 request. Upon review of it and the email sent by the foreman it was unknown as to the work to be done to the sludge pumps discharge valves. The email does state that “all components of the sludge pumps including air to the Clarkson’s”, then the 682 states “we will need actuating air un-isolated to the Clarkson’s”. Therefore, the sludge pumps were electrically isolated and discharge valves were left un-isolated on this LOTO. The original template for the settling basin was created but after review it was discovered that changes made to the system during the Coal Combustion Residual (CCR) rule made that LOTO inadequate. Therefore, it was determined that the “Overflow Sump Pumps” would not need to be included as they now discharge to the settling ponds. Prior to CCR it would have been required to get one of the pumps because it at that time it would have discharged into the settling basin and the other into the lower ditch that is no longer in service. Both pumps now discharge into a common line that goes to the settling ponds. This line can also discharge into the settling basin, but if “BOTTOM ASH OVERFLOW DISCHARGE TO SETTLING BASIN ISOLATION VALVE” is closed water cannot get into the settling basin, which was included in the LOTO. However, the discharge of the sludge pumps also discharge into this line and through investigation, it was discovered that it will be charged from back pressure coming from the Overflow Sump pumps. Therefore, when the LOTO was created the boundaries were walked down and determined that by getting the 480V breakers to both sludge pumps, #1 & #2 Ash piping drain sumps, recycle basin supply to slope wash ISV (which was later removed as requested by foreman), recycle header minimum flow valve air ISV, and Bottom Ash overflow discharge to settling basin ISV (which would isolate the water from the overflow sumps from getting into the basin). This LOTO was then verified by a qualified individual before it was hung. After members hung and verified the LOTO, there was/is not a way to verify “ZERO ENERGY” on the piping side (under the basin) of this LOTO as there is not any drain valves on the piping below the basin. Members were able to verify that zero water was discharging into the basin, which was the intent of the LOTO. The PAE was qualified on this system prior to the CCR rule, but was unware of the changes made to this system. When PAE verified the boundaries there was not any water going into the settling basin. With the unknown changes to the system the PAE did not realize that the discharge valves could be back pressured from the new line that was installed during the CCR rule. Prior to this outage, proper planning and coordination with all departments involved had not been made aware of scope of work that was going to take place during the outage. It was found that the task list attached to this work order was out dated and incorrect, leading to some of the miscommunication in submitting the correct 682 for the work that was going to be performed. Also, due to the upgrades of the CCR project it was brought to our attention that the prints and drawings were not exposed properly to all members of the plant. Because members were not aware of changes made to the system they were not able to properly verify zero energy on this system. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Justin Buchanan | Alexander Taybah |  | Alexander Taybah | Monday, 06/17/2019, this incident will be sent back to Investigate status to edit some of the findings as discussed with Marc Hodgson (SS) and Brady Sowell (Safety Coordinator). | Alexander Taybah |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.03 Infrequent performance | [7 empty] | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Due to the upgrades from Coal Combustion Residual (CCR) the changes made to this system were not updated to the plant nor was the prints and drawings update. The task list for this work order was also out of date. | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) |  | See workflow comments or email. Per Sowell on 5/30. Approved by sowell on 6/20/2019 | [90 empty] | 18838745
8864 | Sooner Power Plant | 2019-05-16 16:00 | *No member injury or equipment damage* On 5/16, members were working on settling basin outage to pump out, clean, and rebuild valves on the basin. LOTO had been hung & issued at 0821 on 5/16. At approx. 1600, members were unbolting sludge pump discharge Clarkson valves to remove & rebuild; when bolts were loosened, a large amount of water sprayed from flange. Members were able to tighten flange to stop water. It was discovered that both units overflow sump pump discharges tie into the same discharge pipe as the sludge pumps’ discharge due to changes to comply with CCR rules, and overflow sump pumps were still in operation. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Kellan Keeter | 2019-07-09 07:50 | 2019-05-16 22:25 | 2019-05-16 22:25 | 2019-06-18 10:06 | 2019-05-30 16:00 | 2019-05-16 18:30 | 2019-06-21 11:10 |  | 2019-06-20 12:12 | Sooner Settling basin sludge pumps. |  |  | Jesse Murray | This is a perfect example of an incident where Configuration Control process should be followed especially when it pertains to new processes implemented. In this particular case, the changes were made in the field but the LOTO templates were not changed to reflect different case scenarios to secure zero energy. Also, the drawings were poorly updated and communicated. I approve. I approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | On Thursday, May 16, 2019 at approximately 1600 hours, during the yearly settling basin outage, members were continuing to work on tasks related to the cleaning and replacing of valves on the settling basin. All valves had been taken out and replaced at this point the last two valves to be replaced were the sludge pump discharge valves in the settling basin. Even though the “First Break Procedure” has not been finalized, Maintenance members do follow an unofficial version of it: by cutting away from person, and loosening one bolt at time. As reflected in member’s SWP, the box for “First –Break Procedure Followed” was checked. Using this method member began to take the flange off going to the discharge valve on B sludge pump. Once, he started to loosen the bolts on this flange it began to have a discharge of water. This discharge seemed to have more pressure than head pressure and after some time it did not slow down. Therefore, member tightened the bolts back up on flange. Stopped work and reported what he had experienced to his supervisor. The supervisor then reported it to the shift supervisor and management. The LOTO was created and hung in accordance to the 682 request. When referring to the work order 18838745 that was attached to this 682 request. Upon review of it and the email sent by the foreman it was unknown as to the work to be done to the sludge pumps discharge valves. The email does state that “all components of the sludge pumps including air to the Clarkson’s”, then the 682 states “we will need actuating air un-isolated to the Clarkson’s”. Therefore, the sludge pumps were electrically isolated and discharge valves were left un-isolated on this LOTO. The original template for the settling basin was created but after review it was discovered that changes made to the system during the Coal Combustion Residual (CCR) rule made that LOTO inadequate. Therefore, it was determined that the “Overflow Sump Pumps” would not need to be included as they now discharge to the settling ponds. Prior to CCR it would have been required to get one of the pumps because it at that time it would have discharged into the settling basin and the other into the lower ditch that is no longer in service. Both pumps now discharge into a common line that goes to the settling ponds. This line can also discharge into the settling basin, but if “BOTTOM ASH OVERFLOW DISCHARGE TO SETTLING BASIN ISOLATION VALVE” is closed water cannot get into the settling basin, which was included in the LOTO. However, the discharge of the sludge pumps also discharge into this line and through investigation, it was discovered that it will be charged from back pressure coming from the Overflow Sump pumps. Therefore, when the LOTO was created the boundaries were walked down and determined that by getting the 480V breakers to both sludge pumps, #1 & #2 Ash piping drain sumps, recycle basin supply to slope wash ISV (which was later removed as requested by foreman), recycle header minimum flow valve air ISV, and Bottom Ash overflow discharge to settling basin ISV (which would isolate the water from the overflow sumps from getting into the basin). This LOTO was then verified by a qualified individual before it was hung. After members hung and verified the LOTO, there was/is not a way to verify “ZERO ENERGY” on the piping side (under the basin) of this LOTO as there is not any drain valves on the piping below the basin. Members were able to verify that zero water was discharging into the basin, which was the intent of the LOTO. The PAE was qualified on this system prior to the CCR rule, but was unware of the changes made to this system. When PAE verified the boundaries there was not any water going into the settling basin. With the unknown changes to the system the PAE did not realize that the discharge valves could be back pressured from the new line that was installed during the CCR rule. Prior to this outage, proper planning and coordination with all departments involved had not been made aware of scope of work that was going to take place during the outage. It was found that the task list attached to this work order was out dated and incorrect, leading to some of the miscommunication in submitting the correct 682 for the work that was going to be performed. Also, due to the upgrades of the CCR project it was brought to our attention that the prints and drawings were not exposed properly to all members of the plant. Because members were not aware of changes made to the system they were not able to properly verify zero energy on this system. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Justin Buchanan | Alexander Taybah |  | Alexander Taybah | Monday, 06/17/2019, this incident will be sent back to Investigate status to edit some of the findings as discussed with Marc Hodgson (SS) and Brady Sowell (Safety Coordinator). | Alexander Taybah |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.03 Infrequent performance | [7 empty] | 14.01.2 Inadequate development of standards: coordination with process design |  |  | Due to the upgrades from Coal Combustion Residual (CCR) the changes made to this system were not updated to the plant nor was the prints and drawings update. The task list for this work order was also out of date. | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) |  | See workflow comments or email. Per Sowell on 5/30. Approved by sowell on 6/20/2019 | [90 empty] | 18838745
8864 | Sooner Power Plant | 2019-05-16 16:00 | *No member injury or equipment damage* On 5/16, members were working on settling basin outage to pump out, clean, and rebuild valves on the basin. LOTO had been hung & issued at 0821 on 5/16. At approx. 1600, members were unbolting sludge pump discharge Clarkson valves to remove & rebuild; when bolts were loosened, a large amount of water sprayed from flange. Members were able to tighten flange to stop water. It was discovered that both units overflow sump pump discharges tie into the same discharge pipe as the sludge pumps’ discharge due to changes to comply with CCR rules, and overflow sump pumps were still in operation. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Kellan Keeter | 2019-07-09 07:50 | 2019-05-16 22:25 | 2019-05-16 22:25 | 2019-06-18 10:06 | 2019-05-30 16:00 | 2019-05-16 18:30 | 2019-06-21 11:10 |  | 2019-06-20 12:12 | Sooner Settling basin sludge pumps. |  |  | Jesse Murray | This is a perfect example of an incident where Configuration Control process should be followed especially when it pertains to new processes implemented. In this particular case, the changes were made in the field but the LOTO templates were not changed to reflect different case scenarios to secure zero energy. Also, the drawings were poorly updated and communicated. I approve. I approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | On Thursday, May 16, 2019 at approximately 1600 hours, during the yearly settling basin outage, members were continuing to work on tasks related to the cleaning and replacing of valves on the settling basin. All valves had been taken out and replaced at this point the last two valves to be replaced were the sludge pump discharge valves in the settling basin. Even though the “First Break Procedure” has not been finalized, Maintenance members do follow an unofficial version of it: by cutting away from person, and loosening one bolt at time. As reflected in member’s SWP, the box for “First –Break Procedure Followed” was checked. Using this method member began to take the flange off going to the discharge valve on B sludge pump. Once, he started to loosen the bolts on this flange it began to have a discharge of water. This discharge seemed to have more pressure than head pressure and after some time it did not slow down. Therefore, member tightened the bolts back up on flange. Stopped work and reported what he had experienced to his supervisor. The supervisor then reported it to the shift supervisor and management. The LOTO was created and hung in accordance to the 682 request. When referring to the work order 18838745 that was attached to this 682 request. Upon review of it and the email sent by the foreman it was unknown as to the work to be done to the sludge pumps discharge valves. The email does state that “all components of the sludge pumps including air to the Clarkson’s”, then the 682 states “we will need actuating air un-isolated to the Clarkson’s”. Therefore, the sludge pumps were electrically isolated and discharge valves were left un-isolated on this LOTO. The original template for the settling basin was created but after review it was discovered that changes made to the system during the Coal Combustion Residual (CCR) rule made that LOTO inadequate. Therefore, it was determined that the “Overflow Sump Pumps” would not need to be included as they now discharge to the settling ponds. Prior to CCR it would have been required to get one of the pumps because it at that time it would have discharged into the settling basin and the other into the lower ditch that is no longer in service. Both pumps now discharge into a common line that goes to the settling ponds. This line can also discharge into the settling basin, but if “BOTTOM ASH OVERFLOW DISCHARGE TO SETTLING BASIN ISOLATION VALVE” is closed water cannot get into the settling basin, which was included in the LOTO. However, the discharge of the sludge pumps also discharge into this line and through investigation, it was discovered that it will be charged from back pressure coming from the Overflow Sump pumps. Therefore, when the LOTO was created the boundaries were walked down and determined that by getting the 480V breakers to both sludge pumps, #1 & #2 Ash piping drain sumps, recycle basin supply to slope wash ISV (which was later removed as requested by foreman), recycle header minimum flow valve air ISV, and Bottom Ash overflow discharge to settling basin ISV (which would isolate the water from the overflow sumps from getting into the basin). This LOTO was then verified by a qualified individual before it was hung. After members hung and verified the LOTO, there was/is not a way to verify “ZERO ENERGY” on the piping side (under the basin) of this LOTO as there is not any drain valves on the piping below the basin. Members were able to verify that zero water was discharging into the basin, which was the intent of the LOTO. The PAE was qualified on this system prior to the CCR rule, but was unware of the changes made to this system. When PAE verified the boundaries there was not any water going into the settling basin. With the unknown changes to the system the PAE did not realize that the discharge valves could be back pressured from the new line that was installed during the CCR rule. Prior to this outage, proper planning and coordination with all departments involved had not been made aware of scope of work that was going to take place during the outage. It was found that the task list attached to this work order was out dated and incorrect, leading to some of the miscommunication in submitting the correct 682 for the work that was going to be performed. Also, due to the upgrades of the CCR project it was brought to our attention that the prints and drawings were not exposed properly to all members of the plant. Because members were not aware of changes made to the system they were not able to properly verify zero energy on this system. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Justin Buchanan | Alexander Taybah |  | Alexander Taybah | Monday, 06/17/2019, this incident will be sent back to Investigate status to edit some of the findings as discussed with Marc Hodgson (SS) and Brady Sowell (Safety Coordinator). | Alexander Taybah |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.03 Infrequent performance | [7 empty] | 14.02.2 Inadequate communication of standards: distribution |  |  | Due to the upgrades from Coal Combustion Residual (CCR) the changes made to this system were not updated to the plant nor was the prints and drawings update. The task list for this work order was also out of date. | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) |  | See workflow comments or email. Per Sowell on 5/30. Approved by sowell on 6/20/2019 | [90 empty] | 18838745
8864 | Sooner Power Plant | 2019-05-16 16:00 | *No member injury or equipment damage* On 5/16, members were working on settling basin outage to pump out, clean, and rebuild valves on the basin. LOTO had been hung & issued at 0821 on 5/16. At approx. 1600, members were unbolting sludge pump discharge Clarkson valves to remove & rebuild; when bolts were loosened, a large amount of water sprayed from flange. Members were able to tighten flange to stop water. It was discovered that both units overflow sump pump discharges tie into the same discharge pipe as the sludge pumps’ discharge due to changes to comply with CCR rules, and overflow sump pumps were still in operation. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Kellan Keeter | 2019-07-09 07:50 | 2019-05-16 22:25 | 2019-05-16 22:25 | 2019-06-18 10:06 | 2019-05-30 16:00 | 2019-05-16 18:30 | 2019-06-21 11:10 |  | 2019-06-20 12:12 | Sooner Settling basin sludge pumps. |  |  | Jesse Murray | This is a perfect example of an incident where Configuration Control process should be followed especially when it pertains to new processes implemented. In this particular case, the changes were made in the field but the LOTO templates were not changed to reflect different case scenarios to secure zero energy. Also, the drawings were poorly updated and communicated. I approve. I approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | On Thursday, May 16, 2019 at approximately 1600 hours, during the yearly settling basin outage, members were continuing to work on tasks related to the cleaning and replacing of valves on the settling basin. All valves had been taken out and replaced at this point the last two valves to be replaced were the sludge pump discharge valves in the settling basin. Even though the “First Break Procedure” has not been finalized, Maintenance members do follow an unofficial version of it: by cutting away from person, and loosening one bolt at time. As reflected in member’s SWP, the box for “First –Break Procedure Followed” was checked. Using this method member began to take the flange off going to the discharge valve on B sludge pump. Once, he started to loosen the bolts on this flange it began to have a discharge of water. This discharge seemed to have more pressure than head pressure and after some time it did not slow down. Therefore, member tightened the bolts back up on flange. Stopped work and reported what he had experienced to his supervisor. The supervisor then reported it to the shift supervisor and management. The LOTO was created and hung in accordance to the 682 request. When referring to the work order 18838745 that was attached to this 682 request. Upon review of it and the email sent by the foreman it was unknown as to the work to be done to the sludge pumps discharge valves. The email does state that “all components of the sludge pumps including air to the Clarkson’s”, then the 682 states “we will need actuating air un-isolated to the Clarkson’s”. Therefore, the sludge pumps were electrically isolated and discharge valves were left un-isolated on this LOTO. The original template for the settling basin was created but after review it was discovered that changes made to the system during the Coal Combustion Residual (CCR) rule made that LOTO inadequate. Therefore, it was determined that the “Overflow Sump Pumps” would not need to be included as they now discharge to the settling ponds. Prior to CCR it would have been required to get one of the pumps because it at that time it would have discharged into the settling basin and the other into the lower ditch that is no longer in service. Both pumps now discharge into a common line that goes to the settling ponds. This line can also discharge into the settling basin, but if “BOTTOM ASH OVERFLOW DISCHARGE TO SETTLING BASIN ISOLATION VALVE” is closed water cannot get into the settling basin, which was included in the LOTO. However, the discharge of the sludge pumps also discharge into this line and through investigation, it was discovered that it will be charged from back pressure coming from the Overflow Sump pumps. Therefore, when the LOTO was created the boundaries were walked down and determined that by getting the 480V breakers to both sludge pumps, #1 & #2 Ash piping drain sumps, recycle basin supply to slope wash ISV (which was later removed as requested by foreman), recycle header minimum flow valve air ISV, and Bottom Ash overflow discharge to settling basin ISV (which would isolate the water from the overflow sumps from getting into the basin). This LOTO was then verified by a qualified individual before it was hung. After members hung and verified the LOTO, there was/is not a way to verify “ZERO ENERGY” on the piping side (under the basin) of this LOTO as there is not any drain valves on the piping below the basin. Members were able to verify that zero water was discharging into the basin, which was the intent of the LOTO. The PAE was qualified on this system prior to the CCR rule, but was unware of the changes made to this system. When PAE verified the boundaries there was not any water going into the settling basin. With the unknown changes to the system the PAE did not realize that the discharge valves could be back pressured from the new line that was installed during the CCR rule. Prior to this outage, proper planning and coordination with all departments involved had not been made aware of scope of work that was going to take place during the outage. It was found that the task list attached to this work order was out dated and incorrect, leading to some of the miscommunication in submitting the correct 682 for the work that was going to be performed. Also, due to the upgrades of the CCR project it was brought to our attention that the prints and drawings were not exposed properly to all members of the plant. Because members were not aware of changes made to the system they were not able to properly verify zero energy on this system. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Justin Buchanan | Alexander Taybah |  | Alexander Taybah | Monday, 06/17/2019, this incident will be sent back to Investigate status to edit some of the findings as discussed with Marc Hodgson (SS) and Brady Sowell (Safety Coordinator). | Alexander Taybah |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.03 Infrequent performance | [7 empty] | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  |  | Due to the upgrades from Coal Combustion Residual (CCR) the changes made to this system were not updated to the plant nor was the prints and drawings update. The task list for this work order was also out of date. | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) |  | See workflow comments or email. Per Sowell on 5/30. Approved by sowell on 6/20/2019 | [90 empty] | 18838745
8864 | Sooner Power Plant | 2019-05-16 16:00 | *No member injury or equipment damage* On 5/16, members were working on settling basin outage to pump out, clean, and rebuild valves on the basin. LOTO had been hung & issued at 0821 on 5/16. At approx. 1600, members were unbolting sludge pump discharge Clarkson valves to remove & rebuild; when bolts were loosened, a large amount of water sprayed from flange. Members were able to tighten flange to stop water. It was discovered that both units overflow sump pump discharges tie into the same discharge pipe as the sludge pumps’ discharge due to changes to comply with CCR rules, and overflow sump pumps were still in operation. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Kellan Keeter | 2019-07-09 07:50 | 2019-05-16 22:25 | 2019-05-16 22:25 | 2019-06-18 10:06 | 2019-05-30 16:00 | 2019-05-16 18:30 | 2019-06-21 11:10 |  | 2019-06-20 12:12 | Sooner Settling basin sludge pumps. |  |  | Jesse Murray | This is a perfect example of an incident where Configuration Control process should be followed especially when it pertains to new processes implemented. In this particular case, the changes were made in the field but the LOTO templates were not changed to reflect different case scenarios to secure zero energy. Also, the drawings were poorly updated and communicated. I approve. I approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | On Thursday, May 16, 2019 at approximately 1600 hours, during the yearly settling basin outage, members were continuing to work on tasks related to the cleaning and replacing of valves on the settling basin. All valves had been taken out and replaced at this point the last two valves to be replaced were the sludge pump discharge valves in the settling basin. Even though the “First Break Procedure” has not been finalized, Maintenance members do follow an unofficial version of it: by cutting away from person, and loosening one bolt at time. As reflected in member’s SWP, the box for “First –Break Procedure Followed” was checked. Using this method member began to take the flange off going to the discharge valve on B sludge pump. Once, he started to loosen the bolts on this flange it began to have a discharge of water. This discharge seemed to have more pressure than head pressure and after some time it did not slow down. Therefore, member tightened the bolts back up on flange. Stopped work and reported what he had experienced to his supervisor. The supervisor then reported it to the shift supervisor and management. The LOTO was created and hung in accordance to the 682 request. When referring to the work order 18838745 that was attached to this 682 request. Upon review of it and the email sent by the foreman it was unknown as to the work to be done to the sludge pumps discharge valves. The email does state that “all components of the sludge pumps including air to the Clarkson’s”, then the 682 states “we will need actuating air un-isolated to the Clarkson’s”. Therefore, the sludge pumps were electrically isolated and discharge valves were left un-isolated on this LOTO. The original template for the settling basin was created but after review it was discovered that changes made to the system during the Coal Combustion Residual (CCR) rule made that LOTO inadequate. Therefore, it was determined that the “Overflow Sump Pumps” would not need to be included as they now discharge to the settling ponds. Prior to CCR it would have been required to get one of the pumps because it at that time it would have discharged into the settling basin and the other into the lower ditch that is no longer in service. Both pumps now discharge into a common line that goes to the settling ponds. This line can also discharge into the settling basin, but if “BOTTOM ASH OVERFLOW DISCHARGE TO SETTLING BASIN ISOLATION VALVE” is closed water cannot get into the settling basin, which was included in the LOTO. However, the discharge of the sludge pumps also discharge into this line and through investigation, it was discovered that it will be charged from back pressure coming from the Overflow Sump pumps. Therefore, when the LOTO was created the boundaries were walked down and determined that by getting the 480V breakers to both sludge pumps, #1 & #2 Ash piping drain sumps, recycle basin supply to slope wash ISV (which was later removed as requested by foreman), recycle header minimum flow valve air ISV, and Bottom Ash overflow discharge to settling basin ISV (which would isolate the water from the overflow sumps from getting into the basin). This LOTO was then verified by a qualified individual before it was hung. After members hung and verified the LOTO, there was/is not a way to verify “ZERO ENERGY” on the piping side (under the basin) of this LOTO as there is not any drain valves on the piping below the basin. Members were able to verify that zero water was discharging into the basin, which was the intent of the LOTO. The PAE was qualified on this system prior to the CCR rule, but was unware of the changes made to this system. When PAE verified the boundaries there was not any water going into the settling basin. With the unknown changes to the system the PAE did not realize that the discharge valves could be back pressured from the new line that was installed during the CCR rule. Prior to this outage, proper planning and coordination with all departments involved had not been made aware of scope of work that was going to take place during the outage. It was found that the task list attached to this work order was out dated and incorrect, leading to some of the miscommunication in submitting the correct 682 for the work that was going to be performed. Also, due to the upgrades of the CCR project it was brought to our attention that the prints and drawings were not exposed properly to all members of the plant. Because members were not aware of changes made to the system they were not able to properly verify zero energy on this system. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Justin Buchanan | Alexander Taybah |  | Alexander Taybah | Monday, 06/17/2019, this incident will be sent back to Investigate status to edit some of the findings as discussed with Marc Hodgson (SS) and Brady Sowell (Safety Coordinator). | Alexander Taybah |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.03 Infrequent performance | [7 empty] | 14.03.2 Inadequate maintenance of standards: updating |  |  | Due to the upgrades from Coal Combustion Residual (CCR) the changes made to this system were not updated to the plant nor was the prints and drawings update. The task list for this work order was also out of date. | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) |  | See workflow comments or email. Per Sowell on 5/30. Approved by sowell on 6/20/2019 | [90 empty] | 18838745
8864 | Sooner Power Plant | 2019-05-16 16:00 | *No member injury or equipment damage* On 5/16, members were working on settling basin outage to pump out, clean, and rebuild valves on the basin. LOTO had been hung & issued at 0821 on 5/16. At approx. 1600, members were unbolting sludge pump discharge Clarkson valves to remove & rebuild; when bolts were loosened, a large amount of water sprayed from flange. Members were able to tighten flange to stop water. It was discovered that both units overflow sump pump discharges tie into the same discharge pipe as the sludge pumps’ discharge due to changes to comply with CCR rules, and overflow sump pumps were still in operation. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Kellan Keeter | 2019-07-09 07:50 | 2019-05-16 22:25 | 2019-05-16 22:25 | 2019-06-18 10:06 | 2019-05-30 16:00 | 2019-05-16 18:30 | 2019-06-21 11:10 |  | 2019-06-20 12:12 | Sooner Settling basin sludge pumps. |  |  | Jesse Murray | This is a perfect example of an incident where Configuration Control process should be followed especially when it pertains to new processes implemented. In this particular case, the changes were made in the field but the LOTO templates were not changed to reflect different case scenarios to secure zero energy. Also, the drawings were poorly updated and communicated. I approve. I approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | On Thursday, May 16, 2019 at approximately 1600 hours, during the yearly settling basin outage, members were continuing to work on tasks related to the cleaning and replacing of valves on the settling basin. All valves had been taken out and replaced at this point the last two valves to be replaced were the sludge pump discharge valves in the settling basin. Even though the “First Break Procedure” has not been finalized, Maintenance members do follow an unofficial version of it: by cutting away from person, and loosening one bolt at time. As reflected in member’s SWP, the box for “First –Break Procedure Followed” was checked. Using this method member began to take the flange off going to the discharge valve on B sludge pump. Once, he started to loosen the bolts on this flange it began to have a discharge of water. This discharge seemed to have more pressure than head pressure and after some time it did not slow down. Therefore, member tightened the bolts back up on flange. Stopped work and reported what he had experienced to his supervisor. The supervisor then reported it to the shift supervisor and management. The LOTO was created and hung in accordance to the 682 request. When referring to the work order 18838745 that was attached to this 682 request. Upon review of it and the email sent by the foreman it was unknown as to the work to be done to the sludge pumps discharge valves. The email does state that “all components of the sludge pumps including air to the Clarkson’s”, then the 682 states “we will need actuating air un-isolated to the Clarkson’s”. Therefore, the sludge pumps were electrically isolated and discharge valves were left un-isolated on this LOTO. The original template for the settling basin was created but after review it was discovered that changes made to the system during the Coal Combustion Residual (CCR) rule made that LOTO inadequate. Therefore, it was determined that the “Overflow Sump Pumps” would not need to be included as they now discharge to the settling ponds. Prior to CCR it would have been required to get one of the pumps because it at that time it would have discharged into the settling basin and the other into the lower ditch that is no longer in service. Both pumps now discharge into a common line that goes to the settling ponds. This line can also discharge into the settling basin, but if “BOTTOM ASH OVERFLOW DISCHARGE TO SETTLING BASIN ISOLATION VALVE” is closed water cannot get into the settling basin, which was included in the LOTO. However, the discharge of the sludge pumps also discharge into this line and through investigation, it was discovered that it will be charged from back pressure coming from the Overflow Sump pumps. Therefore, when the LOTO was created the boundaries were walked down and determined that by getting the 480V breakers to both sludge pumps, #1 & #2 Ash piping drain sumps, recycle basin supply to slope wash ISV (which was later removed as requested by foreman), recycle header minimum flow valve air ISV, and Bottom Ash overflow discharge to settling basin ISV (which would isolate the water from the overflow sumps from getting into the basin). This LOTO was then verified by a qualified individual before it was hung. After members hung and verified the LOTO, there was/is not a way to verify “ZERO ENERGY” on the piping side (under the basin) of this LOTO as there is not any drain valves on the piping below the basin. Members were able to verify that zero water was discharging into the basin, which was the intent of the LOTO. The PAE was qualified on this system prior to the CCR rule, but was unware of the changes made to this system. When PAE verified the boundaries there was not any water going into the settling basin. With the unknown changes to the system the PAE did not realize that the discharge valves could be back pressured from the new line that was installed during the CCR rule. Prior to this outage, proper planning and coordination with all departments involved had not been made aware of scope of work that was going to take place during the outage. It was found that the task list attached to this work order was out dated and incorrect, leading to some of the miscommunication in submitting the correct 682 for the work that was going to be performed. Also, due to the upgrades of the CCR project it was brought to our attention that the prints and drawings were not exposed properly to all members of the plant. Because members were not aware of changes made to the system they were not able to properly verify zero energy on this system. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Justin Buchanan | Alexander Taybah |  | Alexander Taybah | Monday, 06/17/2019, this incident will be sent back to Investigate status to edit some of the findings as discussed with Marc Hodgson (SS) and Brady Sowell (Safety Coordinator). | Alexander Taybah |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.03 Infrequent performance | [7 empty] | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | Due to the upgrades from Coal Combustion Residual (CCR) the changes made to this system were not updated to the plant nor was the prints and drawings update. The task list for this work order was also out of date. | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) |  | See workflow comments or email. Per Sowell on 5/30. Approved by sowell on 6/20/2019 | [90 empty] | 18838745
8864 | Sooner Power Plant | 2019-05-16 16:00 | *No member injury or equipment damage* On 5/16, members were working on settling basin outage to pump out, clean, and rebuild valves on the basin. LOTO had been hung & issued at 0821 on 5/16. At approx. 1600, members were unbolting sludge pump discharge Clarkson valves to remove & rebuild; when bolts were loosened, a large amount of water sprayed from flange. Members were able to tighten flange to stop water. It was discovered that both units overflow sump pump discharges tie into the same discharge pipe as the sludge pumps’ discharge due to changes to comply with CCR rules, and overflow sump pumps were still in operation. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Kellan Keeter | 2019-07-09 07:50 | 2019-05-16 22:25 | 2019-05-16 22:25 | 2019-06-18 10:06 | 2019-05-30 16:00 | 2019-05-16 18:30 | 2019-06-21 11:10 |  | 2019-06-20 12:12 | Sooner Settling basin sludge pumps. |  |  | Jesse Murray | This is a perfect example of an incident where Configuration Control process should be followed especially when it pertains to new processes implemented. In this particular case, the changes were made in the field but the LOTO templates were not changed to reflect different case scenarios to secure zero energy. Also, the drawings were poorly updated and communicated. I approve. I approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | On Thursday, May 16, 2019 at approximately 1600 hours, during the yearly settling basin outage, members were continuing to work on tasks related to the cleaning and replacing of valves on the settling basin. All valves had been taken out and replaced at this point the last two valves to be replaced were the sludge pump discharge valves in the settling basin. Even though the “First Break Procedure” has not been finalized, Maintenance members do follow an unofficial version of it: by cutting away from person, and loosening one bolt at time. As reflected in member’s SWP, the box for “First –Break Procedure Followed” was checked. Using this method member began to take the flange off going to the discharge valve on B sludge pump. Once, he started to loosen the bolts on this flange it began to have a discharge of water. This discharge seemed to have more pressure than head pressure and after some time it did not slow down. Therefore, member tightened the bolts back up on flange. Stopped work and reported what he had experienced to his supervisor. The supervisor then reported it to the shift supervisor and management. The LOTO was created and hung in accordance to the 682 request. When referring to the work order 18838745 that was attached to this 682 request. Upon review of it and the email sent by the foreman it was unknown as to the work to be done to the sludge pumps discharge valves. The email does state that “all components of the sludge pumps including air to the Clarkson’s”, then the 682 states “we will need actuating air un-isolated to the Clarkson’s”. Therefore, the sludge pumps were electrically isolated and discharge valves were left un-isolated on this LOTO. The original template for the settling basin was created but after review it was discovered that changes made to the system during the Coal Combustion Residual (CCR) rule made that LOTO inadequate. Therefore, it was determined that the “Overflow Sump Pumps” would not need to be included as they now discharge to the settling ponds. Prior to CCR it would have been required to get one of the pumps because it at that time it would have discharged into the settling basin and the other into the lower ditch that is no longer in service. Both pumps now discharge into a common line that goes to the settling ponds. This line can also discharge into the settling basin, but if “BOTTOM ASH OVERFLOW DISCHARGE TO SETTLING BASIN ISOLATION VALVE” is closed water cannot get into the settling basin, which was included in the LOTO. However, the discharge of the sludge pumps also discharge into this line and through investigation, it was discovered that it will be charged from back pressure coming from the Overflow Sump pumps. Therefore, when the LOTO was created the boundaries were walked down and determined that by getting the 480V breakers to both sludge pumps, #1 & #2 Ash piping drain sumps, recycle basin supply to slope wash ISV (which was later removed as requested by foreman), recycle header minimum flow valve air ISV, and Bottom Ash overflow discharge to settling basin ISV (which would isolate the water from the overflow sumps from getting into the basin). This LOTO was then verified by a qualified individual before it was hung. After members hung and verified the LOTO, there was/is not a way to verify “ZERO ENERGY” on the piping side (under the basin) of this LOTO as there is not any drain valves on the piping below the basin. Members were able to verify that zero water was discharging into the basin, which was the intent of the LOTO. The PAE was qualified on this system prior to the CCR rule, but was unware of the changes made to this system. When PAE verified the boundaries there was not any water going into the settling basin. With the unknown changes to the system the PAE did not realize that the discharge valves could be back pressured from the new line that was installed during the CCR rule. Prior to this outage, proper planning and coordination with all departments involved had not been made aware of scope of work that was going to take place during the outage. It was found that the task list attached to this work order was out dated and incorrect, leading to some of the miscommunication in submitting the correct 682 for the work that was going to be performed. Also, due to the upgrades of the CCR project it was brought to our attention that the prints and drawings were not exposed properly to all members of the plant. Because members were not aware of changes made to the system they were not able to properly verify zero energy on this system. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Justin Buchanan | Alexander Taybah |  | Alexander Taybah | Monday, 06/17/2019, this incident will be sent back to Investigate status to edit some of the findings as discussed with Marc Hodgson (SS) and Brady Sowell (Safety Coordinator). | Alexander Taybah |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.03 Infrequent performance | [7 empty] | 14.02.1 Inadequate communication of standards: publication |  |  | Due to the upgrades from Coal Combustion Residual (CCR) the changes made to this system were not updated to the plant nor was the prints and drawings update. The task list for this work order was also out of date. | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) |  | See workflow comments or email. Per Sowell on 5/30. Approved by sowell on 6/20/2019 | [90 empty] | 18838745
8864 | Sooner Power Plant | 2019-05-16 16:00 | *No member injury or equipment damage* On 5/16, members were working on settling basin outage to pump out, clean, and rebuild valves on the basin. LOTO had been hung & issued at 0821 on 5/16. At approx. 1600, members were unbolting sludge pump discharge Clarkson valves to remove & rebuild; when bolts were loosened, a large amount of water sprayed from flange. Members were able to tighten flange to stop water. It was discovered that both units overflow sump pump discharges tie into the same discharge pipe as the sludge pumps’ discharge due to changes to comply with CCR rules, and overflow sump pumps were still in operation. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Kellan Keeter | 2019-07-09 07:50 | 2019-05-16 22:25 | 2019-05-16 22:25 | 2019-06-18 10:06 | 2019-05-30 16:00 | 2019-05-16 18:30 | 2019-06-21 11:10 |  | 2019-06-20 12:12 | Sooner Settling basin sludge pumps. |  |  | Jesse Murray | This is a perfect example of an incident where Configuration Control process should be followed especially when it pertains to new processes implemented. In this particular case, the changes were made in the field but the LOTO templates were not changed to reflect different case scenarios to secure zero energy. Also, the drawings were poorly updated and communicated. I approve. I approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | On Thursday, May 16, 2019 at approximately 1600 hours, during the yearly settling basin outage, members were continuing to work on tasks related to the cleaning and replacing of valves on the settling basin. All valves had been taken out and replaced at this point the last two valves to be replaced were the sludge pump discharge valves in the settling basin. Even though the “First Break Procedure” has not been finalized, Maintenance members do follow an unofficial version of it: by cutting away from person, and loosening one bolt at time. As reflected in member’s SWP, the box for “First –Break Procedure Followed” was checked. Using this method member began to take the flange off going to the discharge valve on B sludge pump. Once, he started to loosen the bolts on this flange it began to have a discharge of water. This discharge seemed to have more pressure than head pressure and after some time it did not slow down. Therefore, member tightened the bolts back up on flange. Stopped work and reported what he had experienced to his supervisor. The supervisor then reported it to the shift supervisor and management. The LOTO was created and hung in accordance to the 682 request. When referring to the work order 18838745 that was attached to this 682 request. Upon review of it and the email sent by the foreman it was unknown as to the work to be done to the sludge pumps discharge valves. The email does state that “all components of the sludge pumps including air to the Clarkson’s”, then the 682 states “we will need actuating air un-isolated to the Clarkson’s”. Therefore, the sludge pumps were electrically isolated and discharge valves were left un-isolated on this LOTO. The original template for the settling basin was created but after review it was discovered that changes made to the system during the Coal Combustion Residual (CCR) rule made that LOTO inadequate. Therefore, it was determined that the “Overflow Sump Pumps” would not need to be included as they now discharge to the settling ponds. Prior to CCR it would have been required to get one of the pumps because it at that time it would have discharged into the settling basin and the other into the lower ditch that is no longer in service. Both pumps now discharge into a common line that goes to the settling ponds. This line can also discharge into the settling basin, but if “BOTTOM ASH OVERFLOW DISCHARGE TO SETTLING BASIN ISOLATION VALVE” is closed water cannot get into the settling basin, which was included in the LOTO. However, the discharge of the sludge pumps also discharge into this line and through investigation, it was discovered that it will be charged from back pressure coming from the Overflow Sump pumps. Therefore, when the LOTO was created the boundaries were walked down and determined that by getting the 480V breakers to both sludge pumps, #1 & #2 Ash piping drain sumps, recycle basin supply to slope wash ISV (which was later removed as requested by foreman), recycle header minimum flow valve air ISV, and Bottom Ash overflow discharge to settling basin ISV (which would isolate the water from the overflow sumps from getting into the basin). This LOTO was then verified by a qualified individual before it was hung. After members hung and verified the LOTO, there was/is not a way to verify “ZERO ENERGY” on the piping side (under the basin) of this LOTO as there is not any drain valves on the piping below the basin. Members were able to verify that zero water was discharging into the basin, which was the intent of the LOTO. The PAE was qualified on this system prior to the CCR rule, but was unware of the changes made to this system. When PAE verified the boundaries there was not any water going into the settling basin. With the unknown changes to the system the PAE did not realize that the discharge valves could be back pressured from the new line that was installed during the CCR rule. Prior to this outage, proper planning and coordination with all departments involved had not been made aware of scope of work that was going to take place during the outage. It was found that the task list attached to this work order was out dated and incorrect, leading to some of the miscommunication in submitting the correct 682 for the work that was going to be performed. Also, due to the upgrades of the CCR project it was brought to our attention that the prints and drawings were not exposed properly to all members of the plant. Because members were not aware of changes made to the system they were not able to properly verify zero energy on this system. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Justin Buchanan | Alexander Taybah |  | Alexander Taybah | Monday, 06/17/2019, this incident will be sent back to Investigate status to edit some of the findings as discussed with Marc Hodgson (SS) and Brady Sowell (Safety Coordinator). | Alexander Taybah |  | Medium |  |  |  |  | 5.04 Inadequate update training | 6.03 Infrequent performance | [7 empty] | 14.02.4 Inadequate communication of standards: training |  |  | Due to the upgrades from Coal Combustion Residual (CCR) the changes made to this system were not updated to the plant nor was the prints and drawings update. The task list for this work order was also out of date. | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) |  | See workflow comments or email. Per Sowell on 5/30. Approved by sowell on 6/20/2019 | [90 empty] | 18838745
8864 | Sooner Power Plant | 2019-05-16 16:00 | *No member injury or equipment damage* On 5/16, members were working on settling basin outage to pump out, clean, and rebuild valves on the basin. LOTO had been hung & issued at 0821 on 5/16. At approx. 1600, members were unbolting sludge pump discharge Clarkson valves to remove & rebuild; when bolts were loosened, a large amount of water sprayed from flange. Members were able to tighten flange to stop water. It was discovered that both units overflow sump pump discharges tie into the same discharge pipe as the sludge pumps’ discharge due to changes to comply with CCR rules, and overflow sump pumps were still in operation. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Kellan Keeter | 2019-07-09 07:50 | 2019-05-16 22:25 | 2019-05-16 22:25 | 2019-06-18 10:06 | 2019-05-30 16:00 | 2019-05-16 18:30 | 2019-06-21 11:10 |  | 2019-06-20 12:12 | Sooner Settling basin sludge pumps. |  |  | Jesse Murray | This is a perfect example of an incident where Configuration Control process should be followed especially when it pertains to new processes implemented. In this particular case, the changes were made in the field but the LOTO templates were not changed to reflect different case scenarios to secure zero energy. Also, the drawings were poorly updated and communicated. I approve. I approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | On Thursday, May 16, 2019 at approximately 1600 hours, during the yearly settling basin outage, members were continuing to work on tasks related to the cleaning and replacing of valves on the settling basin. All valves had been taken out and replaced at this point the last two valves to be replaced were the sludge pump discharge valves in the settling basin. Even though the “First Break Procedure” has not been finalized, Maintenance members do follow an unofficial version of it: by cutting away from person, and loosening one bolt at time. As reflected in member’s SWP, the box for “First –Break Procedure Followed” was checked. Using this method member began to take the flange off going to the discharge valve on B sludge pump. Once, he started to loosen the bolts on this flange it began to have a discharge of water. This discharge seemed to have more pressure than head pressure and after some time it did not slow down. Therefore, member tightened the bolts back up on flange. Stopped work and reported what he had experienced to his supervisor. The supervisor then reported it to the shift supervisor and management. The LOTO was created and hung in accordance to the 682 request. When referring to the work order 18838745 that was attached to this 682 request. Upon review of it and the email sent by the foreman it was unknown as to the work to be done to the sludge pumps discharge valves. The email does state that “all components of the sludge pumps including air to the Clarkson’s”, then the 682 states “we will need actuating air un-isolated to the Clarkson’s”. Therefore, the sludge pumps were electrically isolated and discharge valves were left un-isolated on this LOTO. The original template for the settling basin was created but after review it was discovered that changes made to the system during the Coal Combustion Residual (CCR) rule made that LOTO inadequate. Therefore, it was determined that the “Overflow Sump Pumps” would not need to be included as they now discharge to the settling ponds. Prior to CCR it would have been required to get one of the pumps because it at that time it would have discharged into the settling basin and the other into the lower ditch that is no longer in service. Both pumps now discharge into a common line that goes to the settling ponds. This line can also discharge into the settling basin, but if “BOTTOM ASH OVERFLOW DISCHARGE TO SETTLING BASIN ISOLATION VALVE” is closed water cannot get into the settling basin, which was included in the LOTO. However, the discharge of the sludge pumps also discharge into this line and through investigation, it was discovered that it will be charged from back pressure coming from the Overflow Sump pumps. Therefore, when the LOTO was created the boundaries were walked down and determined that by getting the 480V breakers to both sludge pumps, #1 & #2 Ash piping drain sumps, recycle basin supply to slope wash ISV (which was later removed as requested by foreman), recycle header minimum flow valve air ISV, and Bottom Ash overflow discharge to settling basin ISV (which would isolate the water from the overflow sumps from getting into the basin). This LOTO was then verified by a qualified individual before it was hung. After members hung and verified the LOTO, there was/is not a way to verify “ZERO ENERGY” on the piping side (under the basin) of this LOTO as there is not any drain valves on the piping below the basin. Members were able to verify that zero water was discharging into the basin, which was the intent of the LOTO. The PAE was qualified on this system prior to the CCR rule, but was unware of the changes made to this system. When PAE verified the boundaries there was not any water going into the settling basin. With the unknown changes to the system the PAE did not realize that the discharge valves could be back pressured from the new line that was installed during the CCR rule. Prior to this outage, proper planning and coordination with all departments involved had not been made aware of scope of work that was going to take place during the outage. It was found that the task list attached to this work order was out dated and incorrect, leading to some of the miscommunication in submitting the correct 682 for the work that was going to be performed. Also, due to the upgrades of the CCR project it was brought to our attention that the prints and drawings were not exposed properly to all members of the plant. Because members were not aware of changes made to the system they were not able to properly verify zero energy on this system. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Justin Buchanan | Alexander Taybah |  | Alexander Taybah | Monday, 06/17/2019, this incident will be sent back to Investigate status to edit some of the findings as discussed with Marc Hodgson (SS) and Brady Sowell (Safety Coordinator). | Alexander Taybah |  | Medium |  |  |  |  | 5.04 Inadequate update training | 6.03 Infrequent performance | [7 empty] | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Due to the upgrades from Coal Combustion Residual (CCR) the changes made to this system were not updated to the plant nor was the prints and drawings update. The task list for this work order was also out of date. | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) |  | See workflow comments or email. Per Sowell on 5/30. Approved by sowell on 6/20/2019 | [90 empty] | 18838745
8864 | Sooner Power Plant | 2019-05-16 16:00 | *No member injury or equipment damage* On 5/16, members were working on settling basin outage to pump out, clean, and rebuild valves on the basin. LOTO had been hung & issued at 0821 on 5/16. At approx. 1600, members were unbolting sludge pump discharge Clarkson valves to remove & rebuild; when bolts were loosened, a large amount of water sprayed from flange. Members were able to tighten flange to stop water. It was discovered that both units overflow sump pump discharges tie into the same discharge pipe as the sludge pumps’ discharge due to changes to comply with CCR rules, and overflow sump pumps were still in operation. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Kellan Keeter | 2019-07-09 07:50 | 2019-05-16 22:25 | 2019-05-16 22:25 | 2019-06-18 10:06 | 2019-05-30 16:00 | 2019-05-16 18:30 | 2019-06-21 11:10 |  | 2019-06-20 12:12 | Sooner Settling basin sludge pumps. |  |  | Jesse Murray | This is a perfect example of an incident where Configuration Control process should be followed especially when it pertains to new processes implemented. In this particular case, the changes were made in the field but the LOTO templates were not changed to reflect different case scenarios to secure zero energy. Also, the drawings were poorly updated and communicated. I approve. I approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | On Thursday, May 16, 2019 at approximately 1600 hours, during the yearly settling basin outage, members were continuing to work on tasks related to the cleaning and replacing of valves on the settling basin. All valves had been taken out and replaced at this point the last two valves to be replaced were the sludge pump discharge valves in the settling basin. Even though the “First Break Procedure” has not been finalized, Maintenance members do follow an unofficial version of it: by cutting away from person, and loosening one bolt at time. As reflected in member’s SWP, the box for “First –Break Procedure Followed” was checked. Using this method member began to take the flange off going to the discharge valve on B sludge pump. Once, he started to loosen the bolts on this flange it began to have a discharge of water. This discharge seemed to have more pressure than head pressure and after some time it did not slow down. Therefore, member tightened the bolts back up on flange. Stopped work and reported what he had experienced to his supervisor. The supervisor then reported it to the shift supervisor and management. The LOTO was created and hung in accordance to the 682 request. When referring to the work order 18838745 that was attached to this 682 request. Upon review of it and the email sent by the foreman it was unknown as to the work to be done to the sludge pumps discharge valves. The email does state that “all components of the sludge pumps including air to the Clarkson’s”, then the 682 states “we will need actuating air un-isolated to the Clarkson’s”. Therefore, the sludge pumps were electrically isolated and discharge valves were left un-isolated on this LOTO. The original template for the settling basin was created but after review it was discovered that changes made to the system during the Coal Combustion Residual (CCR) rule made that LOTO inadequate. Therefore, it was determined that the “Overflow Sump Pumps” would not need to be included as they now discharge to the settling ponds. Prior to CCR it would have been required to get one of the pumps because it at that time it would have discharged into the settling basin and the other into the lower ditch that is no longer in service. Both pumps now discharge into a common line that goes to the settling ponds. This line can also discharge into the settling basin, but if “BOTTOM ASH OVERFLOW DISCHARGE TO SETTLING BASIN ISOLATION VALVE” is closed water cannot get into the settling basin, which was included in the LOTO. However, the discharge of the sludge pumps also discharge into this line and through investigation, it was discovered that it will be charged from back pressure coming from the Overflow Sump pumps. Therefore, when the LOTO was created the boundaries were walked down and determined that by getting the 480V breakers to both sludge pumps, #1 & #2 Ash piping drain sumps, recycle basin supply to slope wash ISV (which was later removed as requested by foreman), recycle header minimum flow valve air ISV, and Bottom Ash overflow discharge to settling basin ISV (which would isolate the water from the overflow sumps from getting into the basin). This LOTO was then verified by a qualified individual before it was hung. After members hung and verified the LOTO, there was/is not a way to verify “ZERO ENERGY” on the piping side (under the basin) of this LOTO as there is not any drain valves on the piping below the basin. Members were able to verify that zero water was discharging into the basin, which was the intent of the LOTO. The PAE was qualified on this system prior to the CCR rule, but was unware of the changes made to this system. When PAE verified the boundaries there was not any water going into the settling basin. With the unknown changes to the system the PAE did not realize that the discharge valves could be back pressured from the new line that was installed during the CCR rule. Prior to this outage, proper planning and coordination with all departments involved had not been made aware of scope of work that was going to take place during the outage. It was found that the task list attached to this work order was out dated and incorrect, leading to some of the miscommunication in submitting the correct 682 for the work that was going to be performed. Also, due to the upgrades of the CCR project it was brought to our attention that the prints and drawings were not exposed properly to all members of the plant. Because members were not aware of changes made to the system they were not able to properly verify zero energy on this system. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Justin Buchanan | Alexander Taybah |  | Alexander Taybah | Monday, 06/17/2019, this incident will be sent back to Investigate status to edit some of the findings as discussed with Marc Hodgson (SS) and Brady Sowell (Safety Coordinator). | Alexander Taybah |  | Medium |  |  |  |  | 5.04 Inadequate update training | 6.03 Infrequent performance | [7 empty] | 14.01.2 Inadequate development of standards: coordination with process design |  |  | Due to the upgrades from Coal Combustion Residual (CCR) the changes made to this system were not updated to the plant nor was the prints and drawings update. The task list for this work order was also out of date. | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) |  | See workflow comments or email. Per Sowell on 5/30. Approved by sowell on 6/20/2019 | [90 empty] | 18838745
8864 | Sooner Power Plant | 2019-05-16 16:00 | *No member injury or equipment damage* On 5/16, members were working on settling basin outage to pump out, clean, and rebuild valves on the basin. LOTO had been hung & issued at 0821 on 5/16. At approx. 1600, members were unbolting sludge pump discharge Clarkson valves to remove & rebuild; when bolts were loosened, a large amount of water sprayed from flange. Members were able to tighten flange to stop water. It was discovered that both units overflow sump pump discharges tie into the same discharge pipe as the sludge pumps’ discharge due to changes to comply with CCR rules, and overflow sump pumps were still in operation. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Kellan Keeter | 2019-07-09 07:50 | 2019-05-16 22:25 | 2019-05-16 22:25 | 2019-06-18 10:06 | 2019-05-30 16:00 | 2019-05-16 18:30 | 2019-06-21 11:10 |  | 2019-06-20 12:12 | Sooner Settling basin sludge pumps. |  |  | Jesse Murray | This is a perfect example of an incident where Configuration Control process should be followed especially when it pertains to new processes implemented. In this particular case, the changes were made in the field but the LOTO templates were not changed to reflect different case scenarios to secure zero energy. Also, the drawings were poorly updated and communicated. I approve. I approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | On Thursday, May 16, 2019 at approximately 1600 hours, during the yearly settling basin outage, members were continuing to work on tasks related to the cleaning and replacing of valves on the settling basin. All valves had been taken out and replaced at this point the last two valves to be replaced were the sludge pump discharge valves in the settling basin. Even though the “First Break Procedure” has not been finalized, Maintenance members do follow an unofficial version of it: by cutting away from person, and loosening one bolt at time. As reflected in member’s SWP, the box for “First –Break Procedure Followed” was checked. Using this method member began to take the flange off going to the discharge valve on B sludge pump. Once, he started to loosen the bolts on this flange it began to have a discharge of water. This discharge seemed to have more pressure than head pressure and after some time it did not slow down. Therefore, member tightened the bolts back up on flange. Stopped work and reported what he had experienced to his supervisor. The supervisor then reported it to the shift supervisor and management. The LOTO was created and hung in accordance to the 682 request. When referring to the work order 18838745 that was attached to this 682 request. Upon review of it and the email sent by the foreman it was unknown as to the work to be done to the sludge pumps discharge valves. The email does state that “all components of the sludge pumps including air to the Clarkson’s”, then the 682 states “we will need actuating air un-isolated to the Clarkson’s”. Therefore, the sludge pumps were electrically isolated and discharge valves were left un-isolated on this LOTO. The original template for the settling basin was created but after review it was discovered that changes made to the system during the Coal Combustion Residual (CCR) rule made that LOTO inadequate. Therefore, it was determined that the “Overflow Sump Pumps” would not need to be included as they now discharge to the settling ponds. Prior to CCR it would have been required to get one of the pumps because it at that time it would have discharged into the settling basin and the other into the lower ditch that is no longer in service. Both pumps now discharge into a common line that goes to the settling ponds. This line can also discharge into the settling basin, but if “BOTTOM ASH OVERFLOW DISCHARGE TO SETTLING BASIN ISOLATION VALVE” is closed water cannot get into the settling basin, which was included in the LOTO. However, the discharge of the sludge pumps also discharge into this line and through investigation, it was discovered that it will be charged from back pressure coming from the Overflow Sump pumps. Therefore, when the LOTO was created the boundaries were walked down and determined that by getting the 480V breakers to both sludge pumps, #1 & #2 Ash piping drain sumps, recycle basin supply to slope wash ISV (which was later removed as requested by foreman), recycle header minimum flow valve air ISV, and Bottom Ash overflow discharge to settling basin ISV (which would isolate the water from the overflow sumps from getting into the basin). This LOTO was then verified by a qualified individual before it was hung. After members hung and verified the LOTO, there was/is not a way to verify “ZERO ENERGY” on the piping side (under the basin) of this LOTO as there is not any drain valves on the piping below the basin. Members were able to verify that zero water was discharging into the basin, which was the intent of the LOTO. The PAE was qualified on this system prior to the CCR rule, but was unware of the changes made to this system. When PAE verified the boundaries there was not any water going into the settling basin. With the unknown changes to the system the PAE did not realize that the discharge valves could be back pressured from the new line that was installed during the CCR rule. Prior to this outage, proper planning and coordination with all departments involved had not been made aware of scope of work that was going to take place during the outage. It was found that the task list attached to this work order was out dated and incorrect, leading to some of the miscommunication in submitting the correct 682 for the work that was going to be performed. Also, due to the upgrades of the CCR project it was brought to our attention that the prints and drawings were not exposed properly to all members of the plant. Because members were not aware of changes made to the system they were not able to properly verify zero energy on this system. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Justin Buchanan | Alexander Taybah |  | Alexander Taybah | Monday, 06/17/2019, this incident will be sent back to Investigate status to edit some of the findings as discussed with Marc Hodgson (SS) and Brady Sowell (Safety Coordinator). | Alexander Taybah |  | Medium |  |  |  |  | 5.04 Inadequate update training | 6.03 Infrequent performance | [7 empty] | 14.02.2 Inadequate communication of standards: distribution |  |  | Due to the upgrades from Coal Combustion Residual (CCR) the changes made to this system were not updated to the plant nor was the prints and drawings update. The task list for this work order was also out of date. | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) |  | See workflow comments or email. Per Sowell on 5/30. Approved by sowell on 6/20/2019 | [90 empty] | 18838745
8864 | Sooner Power Plant | 2019-05-16 16:00 | *No member injury or equipment damage* On 5/16, members were working on settling basin outage to pump out, clean, and rebuild valves on the basin. LOTO had been hung & issued at 0821 on 5/16. At approx. 1600, members were unbolting sludge pump discharge Clarkson valves to remove & rebuild; when bolts were loosened, a large amount of water sprayed from flange. Members were able to tighten flange to stop water. It was discovered that both units overflow sump pump discharges tie into the same discharge pipe as the sludge pumps’ discharge due to changes to comply with CCR rules, and overflow sump pumps were still in operation. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Kellan Keeter | 2019-07-09 07:50 | 2019-05-16 22:25 | 2019-05-16 22:25 | 2019-06-18 10:06 | 2019-05-30 16:00 | 2019-05-16 18:30 | 2019-06-21 11:10 |  | 2019-06-20 12:12 | Sooner Settling basin sludge pumps. |  |  | Jesse Murray | This is a perfect example of an incident where Configuration Control process should be followed especially when it pertains to new processes implemented. In this particular case, the changes were made in the field but the LOTO templates were not changed to reflect different case scenarios to secure zero energy. Also, the drawings were poorly updated and communicated. I approve. I approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | On Thursday, May 16, 2019 at approximately 1600 hours, during the yearly settling basin outage, members were continuing to work on tasks related to the cleaning and replacing of valves on the settling basin. All valves had been taken out and replaced at this point the last two valves to be replaced were the sludge pump discharge valves in the settling basin. Even though the “First Break Procedure” has not been finalized, Maintenance members do follow an unofficial version of it: by cutting away from person, and loosening one bolt at time. As reflected in member’s SWP, the box for “First –Break Procedure Followed” was checked. Using this method member began to take the flange off going to the discharge valve on B sludge pump. Once, he started to loosen the bolts on this flange it began to have a discharge of water. This discharge seemed to have more pressure than head pressure and after some time it did not slow down. Therefore, member tightened the bolts back up on flange. Stopped work and reported what he had experienced to his supervisor. The supervisor then reported it to the shift supervisor and management. The LOTO was created and hung in accordance to the 682 request. When referring to the work order 18838745 that was attached to this 682 request. Upon review of it and the email sent by the foreman it was unknown as to the work to be done to the sludge pumps discharge valves. The email does state that “all components of the sludge pumps including air to the Clarkson’s”, then the 682 states “we will need actuating air un-isolated to the Clarkson’s”. Therefore, the sludge pumps were electrically isolated and discharge valves were left un-isolated on this LOTO. The original template for the settling basin was created but after review it was discovered that changes made to the system during the Coal Combustion Residual (CCR) rule made that LOTO inadequate. Therefore, it was determined that the “Overflow Sump Pumps” would not need to be included as they now discharge to the settling ponds. Prior to CCR it would have been required to get one of the pumps because it at that time it would have discharged into the settling basin and the other into the lower ditch that is no longer in service. Both pumps now discharge into a common line that goes to the settling ponds. This line can also discharge into the settling basin, but if “BOTTOM ASH OVERFLOW DISCHARGE TO SETTLING BASIN ISOLATION VALVE” is closed water cannot get into the settling basin, which was included in the LOTO. However, the discharge of the sludge pumps also discharge into this line and through investigation, it was discovered that it will be charged from back pressure coming from the Overflow Sump pumps. Therefore, when the LOTO was created the boundaries were walked down and determined that by getting the 480V breakers to both sludge pumps, #1 & #2 Ash piping drain sumps, recycle basin supply to slope wash ISV (which was later removed as requested by foreman), recycle header minimum flow valve air ISV, and Bottom Ash overflow discharge to settling basin ISV (which would isolate the water from the overflow sumps from getting into the basin). This LOTO was then verified by a qualified individual before it was hung. After members hung and verified the LOTO, there was/is not a way to verify “ZERO ENERGY” on the piping side (under the basin) of this LOTO as there is not any drain valves on the piping below the basin. Members were able to verify that zero water was discharging into the basin, which was the intent of the LOTO. The PAE was qualified on this system prior to the CCR rule, but was unware of the changes made to this system. When PAE verified the boundaries there was not any water going into the settling basin. With the unknown changes to the system the PAE did not realize that the discharge valves could be back pressured from the new line that was installed during the CCR rule. Prior to this outage, proper planning and coordination with all departments involved had not been made aware of scope of work that was going to take place during the outage. It was found that the task list attached to this work order was out dated and incorrect, leading to some of the miscommunication in submitting the correct 682 for the work that was going to be performed. Also, due to the upgrades of the CCR project it was brought to our attention that the prints and drawings were not exposed properly to all members of the plant. Because members were not aware of changes made to the system they were not able to properly verify zero energy on this system. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Justin Buchanan | Alexander Taybah |  | Alexander Taybah | Monday, 06/17/2019, this incident will be sent back to Investigate status to edit some of the findings as discussed with Marc Hodgson (SS) and Brady Sowell (Safety Coordinator). | Alexander Taybah |  | Medium |  |  |  |  | 5.04 Inadequate update training | 6.03 Infrequent performance | [7 empty] | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  |  | Due to the upgrades from Coal Combustion Residual (CCR) the changes made to this system were not updated to the plant nor was the prints and drawings update. The task list for this work order was also out of date. | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) |  | See workflow comments or email. Per Sowell on 5/30. Approved by sowell on 6/20/2019 | [90 empty] | 18838745
8864 | Sooner Power Plant | 2019-05-16 16:00 | *No member injury or equipment damage* On 5/16, members were working on settling basin outage to pump out, clean, and rebuild valves on the basin. LOTO had been hung & issued at 0821 on 5/16. At approx. 1600, members were unbolting sludge pump discharge Clarkson valves to remove & rebuild; when bolts were loosened, a large amount of water sprayed from flange. Members were able to tighten flange to stop water. It was discovered that both units overflow sump pump discharges tie into the same discharge pipe as the sludge pumps’ discharge due to changes to comply with CCR rules, and overflow sump pumps were still in operation. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Kellan Keeter | 2019-07-09 07:50 | 2019-05-16 22:25 | 2019-05-16 22:25 | 2019-06-18 10:06 | 2019-05-30 16:00 | 2019-05-16 18:30 | 2019-06-21 11:10 |  | 2019-06-20 12:12 | Sooner Settling basin sludge pumps. |  |  | Jesse Murray | This is a perfect example of an incident where Configuration Control process should be followed especially when it pertains to new processes implemented. In this particular case, the changes were made in the field but the LOTO templates were not changed to reflect different case scenarios to secure zero energy. Also, the drawings were poorly updated and communicated. I approve. I approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | On Thursday, May 16, 2019 at approximately 1600 hours, during the yearly settling basin outage, members were continuing to work on tasks related to the cleaning and replacing of valves on the settling basin. All valves had been taken out and replaced at this point the last two valves to be replaced were the sludge pump discharge valves in the settling basin. Even though the “First Break Procedure” has not been finalized, Maintenance members do follow an unofficial version of it: by cutting away from person, and loosening one bolt at time. As reflected in member’s SWP, the box for “First –Break Procedure Followed” was checked. Using this method member began to take the flange off going to the discharge valve on B sludge pump. Once, he started to loosen the bolts on this flange it began to have a discharge of water. This discharge seemed to have more pressure than head pressure and after some time it did not slow down. Therefore, member tightened the bolts back up on flange. Stopped work and reported what he had experienced to his supervisor. The supervisor then reported it to the shift supervisor and management. The LOTO was created and hung in accordance to the 682 request. When referring to the work order 18838745 that was attached to this 682 request. Upon review of it and the email sent by the foreman it was unknown as to the work to be done to the sludge pumps discharge valves. The email does state that “all components of the sludge pumps including air to the Clarkson’s”, then the 682 states “we will need actuating air un-isolated to the Clarkson’s”. Therefore, the sludge pumps were electrically isolated and discharge valves were left un-isolated on this LOTO. The original template for the settling basin was created but after review it was discovered that changes made to the system during the Coal Combustion Residual (CCR) rule made that LOTO inadequate. Therefore, it was determined that the “Overflow Sump Pumps” would not need to be included as they now discharge to the settling ponds. Prior to CCR it would have been required to get one of the pumps because it at that time it would have discharged into the settling basin and the other into the lower ditch that is no longer in service. Both pumps now discharge into a common line that goes to the settling ponds. This line can also discharge into the settling basin, but if “BOTTOM ASH OVERFLOW DISCHARGE TO SETTLING BASIN ISOLATION VALVE” is closed water cannot get into the settling basin, which was included in the LOTO. However, the discharge of the sludge pumps also discharge into this line and through investigation, it was discovered that it will be charged from back pressure coming from the Overflow Sump pumps. Therefore, when the LOTO was created the boundaries were walked down and determined that by getting the 480V breakers to both sludge pumps, #1 & #2 Ash piping drain sumps, recycle basin supply to slope wash ISV (which was later removed as requested by foreman), recycle header minimum flow valve air ISV, and Bottom Ash overflow discharge to settling basin ISV (which would isolate the water from the overflow sumps from getting into the basin). This LOTO was then verified by a qualified individual before it was hung. After members hung and verified the LOTO, there was/is not a way to verify “ZERO ENERGY” on the piping side (under the basin) of this LOTO as there is not any drain valves on the piping below the basin. Members were able to verify that zero water was discharging into the basin, which was the intent of the LOTO. The PAE was qualified on this system prior to the CCR rule, but was unware of the changes made to this system. When PAE verified the boundaries there was not any water going into the settling basin. With the unknown changes to the system the PAE did not realize that the discharge valves could be back pressured from the new line that was installed during the CCR rule. Prior to this outage, proper planning and coordination with all departments involved had not been made aware of scope of work that was going to take place during the outage. It was found that the task list attached to this work order was out dated and incorrect, leading to some of the miscommunication in submitting the correct 682 for the work that was going to be performed. Also, due to the upgrades of the CCR project it was brought to our attention that the prints and drawings were not exposed properly to all members of the plant. Because members were not aware of changes made to the system they were not able to properly verify zero energy on this system. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Justin Buchanan | Alexander Taybah |  | Alexander Taybah | Monday, 06/17/2019, this incident will be sent back to Investigate status to edit some of the findings as discussed with Marc Hodgson (SS) and Brady Sowell (Safety Coordinator). | Alexander Taybah |  | Medium |  |  |  |  | 5.04 Inadequate update training | 6.03 Infrequent performance | [7 empty] | 14.03.2 Inadequate maintenance of standards: updating |  |  | Due to the upgrades from Coal Combustion Residual (CCR) the changes made to this system were not updated to the plant nor was the prints and drawings update. The task list for this work order was also out of date. | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) |  | See workflow comments or email. Per Sowell on 5/30. Approved by sowell on 6/20/2019 | [90 empty] | 18838745
8864 | Sooner Power Plant | 2019-05-16 16:00 | *No member injury or equipment damage* On 5/16, members were working on settling basin outage to pump out, clean, and rebuild valves on the basin. LOTO had been hung & issued at 0821 on 5/16. At approx. 1600, members were unbolting sludge pump discharge Clarkson valves to remove & rebuild; when bolts were loosened, a large amount of water sprayed from flange. Members were able to tighten flange to stop water. It was discovered that both units overflow sump pump discharges tie into the same discharge pipe as the sludge pumps’ discharge due to changes to comply with CCR rules, and overflow sump pumps were still in operation. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Kellan Keeter | 2019-07-09 07:50 | 2019-05-16 22:25 | 2019-05-16 22:25 | 2019-06-18 10:06 | 2019-05-30 16:00 | 2019-05-16 18:30 | 2019-06-21 11:10 |  | 2019-06-20 12:12 | Sooner Settling basin sludge pumps. |  |  | Jesse Murray | This is a perfect example of an incident where Configuration Control process should be followed especially when it pertains to new processes implemented. In this particular case, the changes were made in the field but the LOTO templates were not changed to reflect different case scenarios to secure zero energy. Also, the drawings were poorly updated and communicated. I approve. I approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | On Thursday, May 16, 2019 at approximately 1600 hours, during the yearly settling basin outage, members were continuing to work on tasks related to the cleaning and replacing of valves on the settling basin. All valves had been taken out and replaced at this point the last two valves to be replaced were the sludge pump discharge valves in the settling basin. Even though the “First Break Procedure” has not been finalized, Maintenance members do follow an unofficial version of it: by cutting away from person, and loosening one bolt at time. As reflected in member’s SWP, the box for “First –Break Procedure Followed” was checked. Using this method member began to take the flange off going to the discharge valve on B sludge pump. Once, he started to loosen the bolts on this flange it began to have a discharge of water. This discharge seemed to have more pressure than head pressure and after some time it did not slow down. Therefore, member tightened the bolts back up on flange. Stopped work and reported what he had experienced to his supervisor. The supervisor then reported it to the shift supervisor and management. The LOTO was created and hung in accordance to the 682 request. When referring to the work order 18838745 that was attached to this 682 request. Upon review of it and the email sent by the foreman it was unknown as to the work to be done to the sludge pumps discharge valves. The email does state that “all components of the sludge pumps including air to the Clarkson’s”, then the 682 states “we will need actuating air un-isolated to the Clarkson’s”. Therefore, the sludge pumps were electrically isolated and discharge valves were left un-isolated on this LOTO. The original template for the settling basin was created but after review it was discovered that changes made to the system during the Coal Combustion Residual (CCR) rule made that LOTO inadequate. Therefore, it was determined that the “Overflow Sump Pumps” would not need to be included as they now discharge to the settling ponds. Prior to CCR it would have been required to get one of the pumps because it at that time it would have discharged into the settling basin and the other into the lower ditch that is no longer in service. Both pumps now discharge into a common line that goes to the settling ponds. This line can also discharge into the settling basin, but if “BOTTOM ASH OVERFLOW DISCHARGE TO SETTLING BASIN ISOLATION VALVE” is closed water cannot get into the settling basin, which was included in the LOTO. However, the discharge of the sludge pumps also discharge into this line and through investigation, it was discovered that it will be charged from back pressure coming from the Overflow Sump pumps. Therefore, when the LOTO was created the boundaries were walked down and determined that by getting the 480V breakers to both sludge pumps, #1 & #2 Ash piping drain sumps, recycle basin supply to slope wash ISV (which was later removed as requested by foreman), recycle header minimum flow valve air ISV, and Bottom Ash overflow discharge to settling basin ISV (which would isolate the water from the overflow sumps from getting into the basin). This LOTO was then verified by a qualified individual before it was hung. After members hung and verified the LOTO, there was/is not a way to verify “ZERO ENERGY” on the piping side (under the basin) of this LOTO as there is not any drain valves on the piping below the basin. Members were able to verify that zero water was discharging into the basin, which was the intent of the LOTO. The PAE was qualified on this system prior to the CCR rule, but was unware of the changes made to this system. When PAE verified the boundaries there was not any water going into the settling basin. With the unknown changes to the system the PAE did not realize that the discharge valves could be back pressured from the new line that was installed during the CCR rule. Prior to this outage, proper planning and coordination with all departments involved had not been made aware of scope of work that was going to take place during the outage. It was found that the task list attached to this work order was out dated and incorrect, leading to some of the miscommunication in submitting the correct 682 for the work that was going to be performed. Also, due to the upgrades of the CCR project it was brought to our attention that the prints and drawings were not exposed properly to all members of the plant. Because members were not aware of changes made to the system they were not able to properly verify zero energy on this system. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Justin Buchanan | Alexander Taybah |  | Alexander Taybah | Monday, 06/17/2019, this incident will be sent back to Investigate status to edit some of the findings as discussed with Marc Hodgson (SS) and Brady Sowell (Safety Coordinator). | Alexander Taybah |  | Medium |  |  |  |  | 5.04 Inadequate update training | 6.03 Infrequent performance | [7 empty] | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | Due to the upgrades from Coal Combustion Residual (CCR) the changes made to this system were not updated to the plant nor was the prints and drawings update. The task list for this work order was also out of date. | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) |  | See workflow comments or email. Per Sowell on 5/30. Approved by sowell on 6/20/2019 | [90 empty] | 18838745
8864 | Sooner Power Plant | 2019-05-16 16:00 | *No member injury or equipment damage* On 5/16, members were working on settling basin outage to pump out, clean, and rebuild valves on the basin. LOTO had been hung & issued at 0821 on 5/16. At approx. 1600, members were unbolting sludge pump discharge Clarkson valves to remove & rebuild; when bolts were loosened, a large amount of water sprayed from flange. Members were able to tighten flange to stop water. It was discovered that both units overflow sump pump discharges tie into the same discharge pipe as the sludge pumps’ discharge due to changes to comply with CCR rules, and overflow sump pumps were still in operation. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Kellan Keeter | 2019-07-09 07:50 | 2019-05-16 22:25 | 2019-05-16 22:25 | 2019-06-18 10:06 | 2019-05-30 16:00 | 2019-05-16 18:30 | 2019-06-21 11:10 |  | 2019-06-20 12:12 | Sooner Settling basin sludge pumps. |  |  | Jesse Murray | This is a perfect example of an incident where Configuration Control process should be followed especially when it pertains to new processes implemented. In this particular case, the changes were made in the field but the LOTO templates were not changed to reflect different case scenarios to secure zero energy. Also, the drawings were poorly updated and communicated. I approve. I approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | On Thursday, May 16, 2019 at approximately 1600 hours, during the yearly settling basin outage, members were continuing to work on tasks related to the cleaning and replacing of valves on the settling basin. All valves had been taken out and replaced at this point the last two valves to be replaced were the sludge pump discharge valves in the settling basin. Even though the “First Break Procedure” has not been finalized, Maintenance members do follow an unofficial version of it: by cutting away from person, and loosening one bolt at time. As reflected in member’s SWP, the box for “First –Break Procedure Followed” was checked. Using this method member began to take the flange off going to the discharge valve on B sludge pump. Once, he started to loosen the bolts on this flange it began to have a discharge of water. This discharge seemed to have more pressure than head pressure and after some time it did not slow down. Therefore, member tightened the bolts back up on flange. Stopped work and reported what he had experienced to his supervisor. The supervisor then reported it to the shift supervisor and management. The LOTO was created and hung in accordance to the 682 request. When referring to the work order 18838745 that was attached to this 682 request. Upon review of it and the email sent by the foreman it was unknown as to the work to be done to the sludge pumps discharge valves. The email does state that “all components of the sludge pumps including air to the Clarkson’s”, then the 682 states “we will need actuating air un-isolated to the Clarkson’s”. Therefore, the sludge pumps were electrically isolated and discharge valves were left un-isolated on this LOTO. The original template for the settling basin was created but after review it was discovered that changes made to the system during the Coal Combustion Residual (CCR) rule made that LOTO inadequate. Therefore, it was determined that the “Overflow Sump Pumps” would not need to be included as they now discharge to the settling ponds. Prior to CCR it would have been required to get one of the pumps because it at that time it would have discharged into the settling basin and the other into the lower ditch that is no longer in service. Both pumps now discharge into a common line that goes to the settling ponds. This line can also discharge into the settling basin, but if “BOTTOM ASH OVERFLOW DISCHARGE TO SETTLING BASIN ISOLATION VALVE” is closed water cannot get into the settling basin, which was included in the LOTO. However, the discharge of the sludge pumps also discharge into this line and through investigation, it was discovered that it will be charged from back pressure coming from the Overflow Sump pumps. Therefore, when the LOTO was created the boundaries were walked down and determined that by getting the 480V breakers to both sludge pumps, #1 & #2 Ash piping drain sumps, recycle basin supply to slope wash ISV (which was later removed as requested by foreman), recycle header minimum flow valve air ISV, and Bottom Ash overflow discharge to settling basin ISV (which would isolate the water from the overflow sumps from getting into the basin). This LOTO was then verified by a qualified individual before it was hung. After members hung and verified the LOTO, there was/is not a way to verify “ZERO ENERGY” on the piping side (under the basin) of this LOTO as there is not any drain valves on the piping below the basin. Members were able to verify that zero water was discharging into the basin, which was the intent of the LOTO. The PAE was qualified on this system prior to the CCR rule, but was unware of the changes made to this system. When PAE verified the boundaries there was not any water going into the settling basin. With the unknown changes to the system the PAE did not realize that the discharge valves could be back pressured from the new line that was installed during the CCR rule. Prior to this outage, proper planning and coordination with all departments involved had not been made aware of scope of work that was going to take place during the outage. It was found that the task list attached to this work order was out dated and incorrect, leading to some of the miscommunication in submitting the correct 682 for the work that was going to be performed. Also, due to the upgrades of the CCR project it was brought to our attention that the prints and drawings were not exposed properly to all members of the plant. Because members were not aware of changes made to the system they were not able to properly verify zero energy on this system. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Justin Buchanan | Alexander Taybah |  | Alexander Taybah | Monday, 06/17/2019, this incident will be sent back to Investigate status to edit some of the findings as discussed with Marc Hodgson (SS) and Brady Sowell (Safety Coordinator). | Alexander Taybah |  | Medium |  |  |  |  | 5.04 Inadequate update training | 6.03 Infrequent performance | [7 empty] | 14.02.1 Inadequate communication of standards: publication |  |  | Due to the upgrades from Coal Combustion Residual (CCR) the changes made to this system were not updated to the plant nor was the prints and drawings update. The task list for this work order was also out of date. | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) |  | See workflow comments or email. Per Sowell on 5/30. Approved by sowell on 6/20/2019 | [90 empty] | 18838745
8864 | Sooner Power Plant | 2019-05-16 16:00 | *No member injury or equipment damage* On 5/16, members were working on settling basin outage to pump out, clean, and rebuild valves on the basin. LOTO had been hung & issued at 0821 on 5/16. At approx. 1600, members were unbolting sludge pump discharge Clarkson valves to remove & rebuild; when bolts were loosened, a large amount of water sprayed from flange. Members were able to tighten flange to stop water. It was discovered that both units overflow sump pump discharges tie into the same discharge pipe as the sludge pumps’ discharge due to changes to comply with CCR rules, and overflow sump pumps were still in operation. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Kellan Keeter | 2019-07-09 07:50 | 2019-05-16 22:25 | 2019-05-16 22:25 | 2019-06-18 10:06 | 2019-05-30 16:00 | 2019-05-16 18:30 | 2019-06-21 11:10 |  | 2019-06-20 12:12 | Sooner Settling basin sludge pumps. |  |  | Jesse Murray | This is a perfect example of an incident where Configuration Control process should be followed especially when it pertains to new processes implemented. In this particular case, the changes were made in the field but the LOTO templates were not changed to reflect different case scenarios to secure zero energy. Also, the drawings were poorly updated and communicated. I approve. I approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | On Thursday, May 16, 2019 at approximately 1600 hours, during the yearly settling basin outage, members were continuing to work on tasks related to the cleaning and replacing of valves on the settling basin. All valves had been taken out and replaced at this point the last two valves to be replaced were the sludge pump discharge valves in the settling basin. Even though the “First Break Procedure” has not been finalized, Maintenance members do follow an unofficial version of it: by cutting away from person, and loosening one bolt at time. As reflected in member’s SWP, the box for “First –Break Procedure Followed” was checked. Using this method member began to take the flange off going to the discharge valve on B sludge pump. Once, he started to loosen the bolts on this flange it began to have a discharge of water. This discharge seemed to have more pressure than head pressure and after some time it did not slow down. Therefore, member tightened the bolts back up on flange. Stopped work and reported what he had experienced to his supervisor. The supervisor then reported it to the shift supervisor and management. The LOTO was created and hung in accordance to the 682 request. When referring to the work order 18838745 that was attached to this 682 request. Upon review of it and the email sent by the foreman it was unknown as to the work to be done to the sludge pumps discharge valves. The email does state that “all components of the sludge pumps including air to the Clarkson’s”, then the 682 states “we will need actuating air un-isolated to the Clarkson’s”. Therefore, the sludge pumps were electrically isolated and discharge valves were left un-isolated on this LOTO. The original template for the settling basin was created but after review it was discovered that changes made to the system during the Coal Combustion Residual (CCR) rule made that LOTO inadequate. Therefore, it was determined that the “Overflow Sump Pumps” would not need to be included as they now discharge to the settling ponds. Prior to CCR it would have been required to get one of the pumps because it at that time it would have discharged into the settling basin and the other into the lower ditch that is no longer in service. Both pumps now discharge into a common line that goes to the settling ponds. This line can also discharge into the settling basin, but if “BOTTOM ASH OVERFLOW DISCHARGE TO SETTLING BASIN ISOLATION VALVE” is closed water cannot get into the settling basin, which was included in the LOTO. However, the discharge of the sludge pumps also discharge into this line and through investigation, it was discovered that it will be charged from back pressure coming from the Overflow Sump pumps. Therefore, when the LOTO was created the boundaries were walked down and determined that by getting the 480V breakers to both sludge pumps, #1 & #2 Ash piping drain sumps, recycle basin supply to slope wash ISV (which was later removed as requested by foreman), recycle header minimum flow valve air ISV, and Bottom Ash overflow discharge to settling basin ISV (which would isolate the water from the overflow sumps from getting into the basin). This LOTO was then verified by a qualified individual before it was hung. After members hung and verified the LOTO, there was/is not a way to verify “ZERO ENERGY” on the piping side (under the basin) of this LOTO as there is not any drain valves on the piping below the basin. Members were able to verify that zero water was discharging into the basin, which was the intent of the LOTO. The PAE was qualified on this system prior to the CCR rule, but was unware of the changes made to this system. When PAE verified the boundaries there was not any water going into the settling basin. With the unknown changes to the system the PAE did not realize that the discharge valves could be back pressured from the new line that was installed during the CCR rule. Prior to this outage, proper planning and coordination with all departments involved had not been made aware of scope of work that was going to take place during the outage. It was found that the task list attached to this work order was out dated and incorrect, leading to some of the miscommunication in submitting the correct 682 for the work that was going to be performed. Also, due to the upgrades of the CCR project it was brought to our attention that the prints and drawings were not exposed properly to all members of the plant. Because members were not aware of changes made to the system they were not able to properly verify zero energy on this system. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Justin Buchanan | Alexander Taybah |  | Alexander Taybah | Monday, 06/17/2019, this incident will be sent back to Investigate status to edit some of the findings as discussed with Marc Hodgson (SS) and Brady Sowell (Safety Coordinator). | Alexander Taybah |  | Medium |  |  |  | 4.07 Confusing directions/demands | 5.04 Inadequate update training |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications | 10.06 Inadequate or improper controls | [5 empty] | 16.04 Inadequate communication between work groups | Lack of proper planning, scope of work provided, and the miscommunication in the 682. | 20. Failure to Communicate, Coordinate | 2. Struck By (Hit By Moving Object) |  | See workflow comments or email. Per Sowell on 5/30. Approved by sowell on 6/20/2019 | [90 empty] | 18838745
8864 | Sooner Power Plant | 2019-05-16 16:00 | *No member injury or equipment damage* On 5/16, members were working on settling basin outage to pump out, clean, and rebuild valves on the basin. LOTO had been hung & issued at 0821 on 5/16. At approx. 1600, members were unbolting sludge pump discharge Clarkson valves to remove & rebuild; when bolts were loosened, a large amount of water sprayed from flange. Members were able to tighten flange to stop water. It was discovered that both units overflow sump pump discharges tie into the same discharge pipe as the sludge pumps’ discharge due to changes to comply with CCR rules, and overflow sump pumps were still in operation. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Kellan Keeter | 2019-07-09 07:50 | 2019-05-16 22:25 | 2019-05-16 22:25 | 2019-06-18 10:06 | 2019-05-30 16:00 | 2019-05-16 18:30 | 2019-06-21 11:10 |  | 2019-06-20 12:12 | Sooner Settling basin sludge pumps. |  |  | Jesse Murray | This is a perfect example of an incident where Configuration Control process should be followed especially when it pertains to new processes implemented. In this particular case, the changes were made in the field but the LOTO templates were not changed to reflect different case scenarios to secure zero energy. Also, the drawings were poorly updated and communicated. I approve. I approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | On Thursday, May 16, 2019 at approximately 1600 hours, during the yearly settling basin outage, members were continuing to work on tasks related to the cleaning and replacing of valves on the settling basin. All valves had been taken out and replaced at this point the last two valves to be replaced were the sludge pump discharge valves in the settling basin. Even though the “First Break Procedure” has not been finalized, Maintenance members do follow an unofficial version of it: by cutting away from person, and loosening one bolt at time. As reflected in member’s SWP, the box for “First –Break Procedure Followed” was checked. Using this method member began to take the flange off going to the discharge valve on B sludge pump. Once, he started to loosen the bolts on this flange it began to have a discharge of water. This discharge seemed to have more pressure than head pressure and after some time it did not slow down. Therefore, member tightened the bolts back up on flange. Stopped work and reported what he had experienced to his supervisor. The supervisor then reported it to the shift supervisor and management. The LOTO was created and hung in accordance to the 682 request. When referring to the work order 18838745 that was attached to this 682 request. Upon review of it and the email sent by the foreman it was unknown as to the work to be done to the sludge pumps discharge valves. The email does state that “all components of the sludge pumps including air to the Clarkson’s”, then the 682 states “we will need actuating air un-isolated to the Clarkson’s”. Therefore, the sludge pumps were electrically isolated and discharge valves were left un-isolated on this LOTO. The original template for the settling basin was created but after review it was discovered that changes made to the system during the Coal Combustion Residual (CCR) rule made that LOTO inadequate. Therefore, it was determined that the “Overflow Sump Pumps” would not need to be included as they now discharge to the settling ponds. Prior to CCR it would have been required to get one of the pumps because it at that time it would have discharged into the settling basin and the other into the lower ditch that is no longer in service. Both pumps now discharge into a common line that goes to the settling ponds. This line can also discharge into the settling basin, but if “BOTTOM ASH OVERFLOW DISCHARGE TO SETTLING BASIN ISOLATION VALVE” is closed water cannot get into the settling basin, which was included in the LOTO. However, the discharge of the sludge pumps also discharge into this line and through investigation, it was discovered that it will be charged from back pressure coming from the Overflow Sump pumps. Therefore, when the LOTO was created the boundaries were walked down and determined that by getting the 480V breakers to both sludge pumps, #1 & #2 Ash piping drain sumps, recycle basin supply to slope wash ISV (which was later removed as requested by foreman), recycle header minimum flow valve air ISV, and Bottom Ash overflow discharge to settling basin ISV (which would isolate the water from the overflow sumps from getting into the basin). This LOTO was then verified by a qualified individual before it was hung. After members hung and verified the LOTO, there was/is not a way to verify “ZERO ENERGY” on the piping side (under the basin) of this LOTO as there is not any drain valves on the piping below the basin. Members were able to verify that zero water was discharging into the basin, which was the intent of the LOTO. The PAE was qualified on this system prior to the CCR rule, but was unware of the changes made to this system. When PAE verified the boundaries there was not any water going into the settling basin. With the unknown changes to the system the PAE did not realize that the discharge valves could be back pressured from the new line that was installed during the CCR rule. Prior to this outage, proper planning and coordination with all departments involved had not been made aware of scope of work that was going to take place during the outage. It was found that the task list attached to this work order was out dated and incorrect, leading to some of the miscommunication in submitting the correct 682 for the work that was going to be performed. Also, due to the upgrades of the CCR project it was brought to our attention that the prints and drawings were not exposed properly to all members of the plant. Because members were not aware of changes made to the system they were not able to properly verify zero energy on this system. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Justin Buchanan | Alexander Taybah |  | Alexander Taybah | Monday, 06/17/2019, this incident will be sent back to Investigate status to edit some of the findings as discussed with Marc Hodgson (SS) and Brady Sowell (Safety Coordinator). | Alexander Taybah |  | Medium |  |  |  | 4.07 Confusing directions/demands | 5.04 Inadequate update training |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications | 10.06 Inadequate or improper controls | [5 empty] | 16.08 Incorrect instructions | Lack of proper planning, scope of work provided, and the miscommunication in the 682. | 20. Failure to Communicate, Coordinate | 2. Struck By (Hit By Moving Object) |  | See workflow comments or email. Per Sowell on 5/30. Approved by sowell on 6/20/2019 | [90 empty] | 18838745
8864 | Sooner Power Plant | 2019-05-16 16:00 | *No member injury or equipment damage* On 5/16, members were working on settling basin outage to pump out, clean, and rebuild valves on the basin. LOTO had been hung & issued at 0821 on 5/16. At approx. 1600, members were unbolting sludge pump discharge Clarkson valves to remove & rebuild; when bolts were loosened, a large amount of water sprayed from flange. Members were able to tighten flange to stop water. It was discovered that both units overflow sump pump discharges tie into the same discharge pipe as the sludge pumps’ discharge due to changes to comply with CCR rules, and overflow sump pumps were still in operation. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Kellan Keeter | 2019-07-09 07:50 | 2019-05-16 22:25 | 2019-05-16 22:25 | 2019-06-18 10:06 | 2019-05-30 16:00 | 2019-05-16 18:30 | 2019-06-21 11:10 |  | 2019-06-20 12:12 | Sooner Settling basin sludge pumps. |  |  | Jesse Murray | This is a perfect example of an incident where Configuration Control process should be followed especially when it pertains to new processes implemented. In this particular case, the changes were made in the field but the LOTO templates were not changed to reflect different case scenarios to secure zero energy. Also, the drawings were poorly updated and communicated. I approve. I approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | On Thursday, May 16, 2019 at approximately 1600 hours, during the yearly settling basin outage, members were continuing to work on tasks related to the cleaning and replacing of valves on the settling basin. All valves had been taken out and replaced at this point the last two valves to be replaced were the sludge pump discharge valves in the settling basin. Even though the “First Break Procedure” has not been finalized, Maintenance members do follow an unofficial version of it: by cutting away from person, and loosening one bolt at time. As reflected in member’s SWP, the box for “First –Break Procedure Followed” was checked. Using this method member began to take the flange off going to the discharge valve on B sludge pump. Once, he started to loosen the bolts on this flange it began to have a discharge of water. This discharge seemed to have more pressure than head pressure and after some time it did not slow down. Therefore, member tightened the bolts back up on flange. Stopped work and reported what he had experienced to his supervisor. The supervisor then reported it to the shift supervisor and management. The LOTO was created and hung in accordance to the 682 request. When referring to the work order 18838745 that was attached to this 682 request. Upon review of it and the email sent by the foreman it was unknown as to the work to be done to the sludge pumps discharge valves. The email does state that “all components of the sludge pumps including air to the Clarkson’s”, then the 682 states “we will need actuating air un-isolated to the Clarkson’s”. Therefore, the sludge pumps were electrically isolated and discharge valves were left un-isolated on this LOTO. The original template for the settling basin was created but after review it was discovered that changes made to the system during the Coal Combustion Residual (CCR) rule made that LOTO inadequate. Therefore, it was determined that the “Overflow Sump Pumps” would not need to be included as they now discharge to the settling ponds. Prior to CCR it would have been required to get one of the pumps because it at that time it would have discharged into the settling basin and the other into the lower ditch that is no longer in service. Both pumps now discharge into a common line that goes to the settling ponds. This line can also discharge into the settling basin, but if “BOTTOM ASH OVERFLOW DISCHARGE TO SETTLING BASIN ISOLATION VALVE” is closed water cannot get into the settling basin, which was included in the LOTO. However, the discharge of the sludge pumps also discharge into this line and through investigation, it was discovered that it will be charged from back pressure coming from the Overflow Sump pumps. Therefore, when the LOTO was created the boundaries were walked down and determined that by getting the 480V breakers to both sludge pumps, #1 & #2 Ash piping drain sumps, recycle basin supply to slope wash ISV (which was later removed as requested by foreman), recycle header minimum flow valve air ISV, and Bottom Ash overflow discharge to settling basin ISV (which would isolate the water from the overflow sumps from getting into the basin). This LOTO was then verified by a qualified individual before it was hung. After members hung and verified the LOTO, there was/is not a way to verify “ZERO ENERGY” on the piping side (under the basin) of this LOTO as there is not any drain valves on the piping below the basin. Members were able to verify that zero water was discharging into the basin, which was the intent of the LOTO. The PAE was qualified on this system prior to the CCR rule, but was unware of the changes made to this system. When PAE verified the boundaries there was not any water going into the settling basin. With the unknown changes to the system the PAE did not realize that the discharge valves could be back pressured from the new line that was installed during the CCR rule. Prior to this outage, proper planning and coordination with all departments involved had not been made aware of scope of work that was going to take place during the outage. It was found that the task list attached to this work order was out dated and incorrect, leading to some of the miscommunication in submitting the correct 682 for the work that was going to be performed. Also, due to the upgrades of the CCR project it was brought to our attention that the prints and drawings were not exposed properly to all members of the plant. Because members were not aware of changes made to the system they were not able to properly verify zero energy on this system. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Justin Buchanan | Alexander Taybah |  | Alexander Taybah | Monday, 06/17/2019, this incident will be sent back to Investigate status to edit some of the findings as discussed with Marc Hodgson (SS) and Brady Sowell (Safety Coordinator). | Alexander Taybah |  | Medium |  |  |  | 4.07 Confusing directions/demands | 5.04 Inadequate update training |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications | 10.06 Inadequate or improper controls | [5 empty] | 16.03. Inadequate communication between different organizations | Lack of proper planning, scope of work provided, and the miscommunication in the 682. | 20. Failure to Communicate, Coordinate | 2. Struck By (Hit By Moving Object) |  | See workflow comments or email. Per Sowell on 5/30. Approved by sowell on 6/20/2019 | [90 empty] | 18838745
8864 | Sooner Power Plant | 2019-05-16 16:00 | *No member injury or equipment damage* On 5/16, members were working on settling basin outage to pump out, clean, and rebuild valves on the basin. LOTO had been hung & issued at 0821 on 5/16. At approx. 1600, members were unbolting sludge pump discharge Clarkson valves to remove & rebuild; when bolts were loosened, a large amount of water sprayed from flange. Members were able to tighten flange to stop water. It was discovered that both units overflow sump pump discharges tie into the same discharge pipe as the sludge pumps’ discharge due to changes to comply with CCR rules, and overflow sump pumps were still in operation. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Kellan Keeter | 2019-07-09 07:50 | 2019-05-16 22:25 | 2019-05-16 22:25 | 2019-06-18 10:06 | 2019-05-30 16:00 | 2019-05-16 18:30 | 2019-06-21 11:10 |  | 2019-06-20 12:12 | Sooner Settling basin sludge pumps. |  |  | Jesse Murray | This is a perfect example of an incident where Configuration Control process should be followed especially when it pertains to new processes implemented. In this particular case, the changes were made in the field but the LOTO templates were not changed to reflect different case scenarios to secure zero energy. Also, the drawings were poorly updated and communicated. I approve. I approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | On Thursday, May 16, 2019 at approximately 1600 hours, during the yearly settling basin outage, members were continuing to work on tasks related to the cleaning and replacing of valves on the settling basin. All valves had been taken out and replaced at this point the last two valves to be replaced were the sludge pump discharge valves in the settling basin. Even though the “First Break Procedure” has not been finalized, Maintenance members do follow an unofficial version of it: by cutting away from person, and loosening one bolt at time. As reflected in member’s SWP, the box for “First –Break Procedure Followed” was checked. Using this method member began to take the flange off going to the discharge valve on B sludge pump. Once, he started to loosen the bolts on this flange it began to have a discharge of water. This discharge seemed to have more pressure than head pressure and after some time it did not slow down. Therefore, member tightened the bolts back up on flange. Stopped work and reported what he had experienced to his supervisor. The supervisor then reported it to the shift supervisor and management. The LOTO was created and hung in accordance to the 682 request. When referring to the work order 18838745 that was attached to this 682 request. Upon review of it and the email sent by the foreman it was unknown as to the work to be done to the sludge pumps discharge valves. The email does state that “all components of the sludge pumps including air to the Clarkson’s”, then the 682 states “we will need actuating air un-isolated to the Clarkson’s”. Therefore, the sludge pumps were electrically isolated and discharge valves were left un-isolated on this LOTO. The original template for the settling basin was created but after review it was discovered that changes made to the system during the Coal Combustion Residual (CCR) rule made that LOTO inadequate. Therefore, it was determined that the “Overflow Sump Pumps” would not need to be included as they now discharge to the settling ponds. Prior to CCR it would have been required to get one of the pumps because it at that time it would have discharged into the settling basin and the other into the lower ditch that is no longer in service. Both pumps now discharge into a common line that goes to the settling ponds. This line can also discharge into the settling basin, but if “BOTTOM ASH OVERFLOW DISCHARGE TO SETTLING BASIN ISOLATION VALVE” is closed water cannot get into the settling basin, which was included in the LOTO. However, the discharge of the sludge pumps also discharge into this line and through investigation, it was discovered that it will be charged from back pressure coming from the Overflow Sump pumps. Therefore, when the LOTO was created the boundaries were walked down and determined that by getting the 480V breakers to both sludge pumps, #1 & #2 Ash piping drain sumps, recycle basin supply to slope wash ISV (which was later removed as requested by foreman), recycle header minimum flow valve air ISV, and Bottom Ash overflow discharge to settling basin ISV (which would isolate the water from the overflow sumps from getting into the basin). This LOTO was then verified by a qualified individual before it was hung. After members hung and verified the LOTO, there was/is not a way to verify “ZERO ENERGY” on the piping side (under the basin) of this LOTO as there is not any drain valves on the piping below the basin. Members were able to verify that zero water was discharging into the basin, which was the intent of the LOTO. The PAE was qualified on this system prior to the CCR rule, but was unware of the changes made to this system. When PAE verified the boundaries there was not any water going into the settling basin. With the unknown changes to the system the PAE did not realize that the discharge valves could be back pressured from the new line that was installed during the CCR rule. Prior to this outage, proper planning and coordination with all departments involved had not been made aware of scope of work that was going to take place during the outage. It was found that the task list attached to this work order was out dated and incorrect, leading to some of the miscommunication in submitting the correct 682 for the work that was going to be performed. Also, due to the upgrades of the CCR project it was brought to our attention that the prints and drawings were not exposed properly to all members of the plant. Because members were not aware of changes made to the system they were not able to properly verify zero energy on this system. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Justin Buchanan | Alexander Taybah |  | Alexander Taybah | Monday, 06/17/2019, this incident will be sent back to Investigate status to edit some of the findings as discussed with Marc Hodgson (SS) and Brady Sowell (Safety Coordinator). | Alexander Taybah |  | Medium |  |  |  | 4.07 Confusing directions/demands | 5.04 Inadequate update training |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications | 10.03 Inadequate standards, specifications and/or design criteria | [5 empty] | 16.04 Inadequate communication between work groups | Lack of proper planning, scope of work provided, and the miscommunication in the 682. | 20. Failure to Communicate, Coordinate | 2. Struck By (Hit By Moving Object) |  | See workflow comments or email. Per Sowell on 5/30. Approved by sowell on 6/20/2019 | [90 empty] | 18838745
8864 | Sooner Power Plant | 2019-05-16 16:00 | *No member injury or equipment damage* On 5/16, members were working on settling basin outage to pump out, clean, and rebuild valves on the basin. LOTO had been hung & issued at 0821 on 5/16. At approx. 1600, members were unbolting sludge pump discharge Clarkson valves to remove & rebuild; when bolts were loosened, a large amount of water sprayed from flange. Members were able to tighten flange to stop water. It was discovered that both units overflow sump pump discharges tie into the same discharge pipe as the sludge pumps’ discharge due to changes to comply with CCR rules, and overflow sump pumps were still in operation. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Kellan Keeter | 2019-07-09 07:50 | 2019-05-16 22:25 | 2019-05-16 22:25 | 2019-06-18 10:06 | 2019-05-30 16:00 | 2019-05-16 18:30 | 2019-06-21 11:10 |  | 2019-06-20 12:12 | Sooner Settling basin sludge pumps. |  |  | Jesse Murray | This is a perfect example of an incident where Configuration Control process should be followed especially when it pertains to new processes implemented. In this particular case, the changes were made in the field but the LOTO templates were not changed to reflect different case scenarios to secure zero energy. Also, the drawings were poorly updated and communicated. I approve. I approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | On Thursday, May 16, 2019 at approximately 1600 hours, during the yearly settling basin outage, members were continuing to work on tasks related to the cleaning and replacing of valves on the settling basin. All valves had been taken out and replaced at this point the last two valves to be replaced were the sludge pump discharge valves in the settling basin. Even though the “First Break Procedure” has not been finalized, Maintenance members do follow an unofficial version of it: by cutting away from person, and loosening one bolt at time. As reflected in member’s SWP, the box for “First –Break Procedure Followed” was checked. Using this method member began to take the flange off going to the discharge valve on B sludge pump. Once, he started to loosen the bolts on this flange it began to have a discharge of water. This discharge seemed to have more pressure than head pressure and after some time it did not slow down. Therefore, member tightened the bolts back up on flange. Stopped work and reported what he had experienced to his supervisor. The supervisor then reported it to the shift supervisor and management. The LOTO was created and hung in accordance to the 682 request. When referring to the work order 18838745 that was attached to this 682 request. Upon review of it and the email sent by the foreman it was unknown as to the work to be done to the sludge pumps discharge valves. The email does state that “all components of the sludge pumps including air to the Clarkson’s”, then the 682 states “we will need actuating air un-isolated to the Clarkson’s”. Therefore, the sludge pumps were electrically isolated and discharge valves were left un-isolated on this LOTO. The original template for the settling basin was created but after review it was discovered that changes made to the system during the Coal Combustion Residual (CCR) rule made that LOTO inadequate. Therefore, it was determined that the “Overflow Sump Pumps” would not need to be included as they now discharge to the settling ponds. Prior to CCR it would have been required to get one of the pumps because it at that time it would have discharged into the settling basin and the other into the lower ditch that is no longer in service. Both pumps now discharge into a common line that goes to the settling ponds. This line can also discharge into the settling basin, but if “BOTTOM ASH OVERFLOW DISCHARGE TO SETTLING BASIN ISOLATION VALVE” is closed water cannot get into the settling basin, which was included in the LOTO. However, the discharge of the sludge pumps also discharge into this line and through investigation, it was discovered that it will be charged from back pressure coming from the Overflow Sump pumps. Therefore, when the LOTO was created the boundaries were walked down and determined that by getting the 480V breakers to both sludge pumps, #1 & #2 Ash piping drain sumps, recycle basin supply to slope wash ISV (which was later removed as requested by foreman), recycle header minimum flow valve air ISV, and Bottom Ash overflow discharge to settling basin ISV (which would isolate the water from the overflow sumps from getting into the basin). This LOTO was then verified by a qualified individual before it was hung. After members hung and verified the LOTO, there was/is not a way to verify “ZERO ENERGY” on the piping side (under the basin) of this LOTO as there is not any drain valves on the piping below the basin. Members were able to verify that zero water was discharging into the basin, which was the intent of the LOTO. The PAE was qualified on this system prior to the CCR rule, but was unware of the changes made to this system. When PAE verified the boundaries there was not any water going into the settling basin. With the unknown changes to the system the PAE did not realize that the discharge valves could be back pressured from the new line that was installed during the CCR rule. Prior to this outage, proper planning and coordination with all departments involved had not been made aware of scope of work that was going to take place during the outage. It was found that the task list attached to this work order was out dated and incorrect, leading to some of the miscommunication in submitting the correct 682 for the work that was going to be performed. Also, due to the upgrades of the CCR project it was brought to our attention that the prints and drawings were not exposed properly to all members of the plant. Because members were not aware of changes made to the system they were not able to properly verify zero energy on this system. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Justin Buchanan | Alexander Taybah |  | Alexander Taybah | Monday, 06/17/2019, this incident will be sent back to Investigate status to edit some of the findings as discussed with Marc Hodgson (SS) and Brady Sowell (Safety Coordinator). | Alexander Taybah |  | Medium |  |  |  | 4.07 Confusing directions/demands | 5.04 Inadequate update training |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications | 10.03 Inadequate standards, specifications and/or design criteria | [5 empty] | 16.08 Incorrect instructions | Lack of proper planning, scope of work provided, and the miscommunication in the 682. | 20. Failure to Communicate, Coordinate | 2. Struck By (Hit By Moving Object) |  | See workflow comments or email. Per Sowell on 5/30. Approved by sowell on 6/20/2019 | [90 empty] | 18838745
8864 | Sooner Power Plant | 2019-05-16 16:00 | *No member injury or equipment damage* On 5/16, members were working on settling basin outage to pump out, clean, and rebuild valves on the basin. LOTO had been hung & issued at 0821 on 5/16. At approx. 1600, members were unbolting sludge pump discharge Clarkson valves to remove & rebuild; when bolts were loosened, a large amount of water sprayed from flange. Members were able to tighten flange to stop water. It was discovered that both units overflow sump pump discharges tie into the same discharge pipe as the sludge pumps’ discharge due to changes to comply with CCR rules, and overflow sump pumps were still in operation. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Kellan Keeter | 2019-07-09 07:50 | 2019-05-16 22:25 | 2019-05-16 22:25 | 2019-06-18 10:06 | 2019-05-30 16:00 | 2019-05-16 18:30 | 2019-06-21 11:10 |  | 2019-06-20 12:12 | Sooner Settling basin sludge pumps. |  |  | Jesse Murray | This is a perfect example of an incident where Configuration Control process should be followed especially when it pertains to new processes implemented. In this particular case, the changes were made in the field but the LOTO templates were not changed to reflect different case scenarios to secure zero energy. Also, the drawings were poorly updated and communicated. I approve. I approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | On Thursday, May 16, 2019 at approximately 1600 hours, during the yearly settling basin outage, members were continuing to work on tasks related to the cleaning and replacing of valves on the settling basin. All valves had been taken out and replaced at this point the last two valves to be replaced were the sludge pump discharge valves in the settling basin. Even though the “First Break Procedure” has not been finalized, Maintenance members do follow an unofficial version of it: by cutting away from person, and loosening one bolt at time. As reflected in member’s SWP, the box for “First –Break Procedure Followed” was checked. Using this method member began to take the flange off going to the discharge valve on B sludge pump. Once, he started to loosen the bolts on this flange it began to have a discharge of water. This discharge seemed to have more pressure than head pressure and after some time it did not slow down. Therefore, member tightened the bolts back up on flange. Stopped work and reported what he had experienced to his supervisor. The supervisor then reported it to the shift supervisor and management. The LOTO was created and hung in accordance to the 682 request. When referring to the work order 18838745 that was attached to this 682 request. Upon review of it and the email sent by the foreman it was unknown as to the work to be done to the sludge pumps discharge valves. The email does state that “all components of the sludge pumps including air to the Clarkson’s”, then the 682 states “we will need actuating air un-isolated to the Clarkson’s”. Therefore, the sludge pumps were electrically isolated and discharge valves were left un-isolated on this LOTO. The original template for the settling basin was created but after review it was discovered that changes made to the system during the Coal Combustion Residual (CCR) rule made that LOTO inadequate. Therefore, it was determined that the “Overflow Sump Pumps” would not need to be included as they now discharge to the settling ponds. Prior to CCR it would have been required to get one of the pumps because it at that time it would have discharged into the settling basin and the other into the lower ditch that is no longer in service. Both pumps now discharge into a common line that goes to the settling ponds. This line can also discharge into the settling basin, but if “BOTTOM ASH OVERFLOW DISCHARGE TO SETTLING BASIN ISOLATION VALVE” is closed water cannot get into the settling basin, which was included in the LOTO. However, the discharge of the sludge pumps also discharge into this line and through investigation, it was discovered that it will be charged from back pressure coming from the Overflow Sump pumps. Therefore, when the LOTO was created the boundaries were walked down and determined that by getting the 480V breakers to both sludge pumps, #1 & #2 Ash piping drain sumps, recycle basin supply to slope wash ISV (which was later removed as requested by foreman), recycle header minimum flow valve air ISV, and Bottom Ash overflow discharge to settling basin ISV (which would isolate the water from the overflow sumps from getting into the basin). This LOTO was then verified by a qualified individual before it was hung. After members hung and verified the LOTO, there was/is not a way to verify “ZERO ENERGY” on the piping side (under the basin) of this LOTO as there is not any drain valves on the piping below the basin. Members were able to verify that zero water was discharging into the basin, which was the intent of the LOTO. The PAE was qualified on this system prior to the CCR rule, but was unware of the changes made to this system. When PAE verified the boundaries there was not any water going into the settling basin. With the unknown changes to the system the PAE did not realize that the discharge valves could be back pressured from the new line that was installed during the CCR rule. Prior to this outage, proper planning and coordination with all departments involved had not been made aware of scope of work that was going to take place during the outage. It was found that the task list attached to this work order was out dated and incorrect, leading to some of the miscommunication in submitting the correct 682 for the work that was going to be performed. Also, due to the upgrades of the CCR project it was brought to our attention that the prints and drawings were not exposed properly to all members of the plant. Because members were not aware of changes made to the system they were not able to properly verify zero energy on this system. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Justin Buchanan | Alexander Taybah |  | Alexander Taybah | Monday, 06/17/2019, this incident will be sent back to Investigate status to edit some of the findings as discussed with Marc Hodgson (SS) and Brady Sowell (Safety Coordinator). | Alexander Taybah |  | Medium |  |  |  | 4.07 Confusing directions/demands | 5.04 Inadequate update training |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications | 10.03 Inadequate standards, specifications and/or design criteria | [5 empty] | 16.03. Inadequate communication between different organizations | Lack of proper planning, scope of work provided, and the miscommunication in the 682. | 20. Failure to Communicate, Coordinate | 2. Struck By (Hit By Moving Object) |  | See workflow comments or email. Per Sowell on 5/30. Approved by sowell on 6/20/2019 | [90 empty] | 18838745
8864 | Sooner Power Plant | 2019-05-16 16:00 | *No member injury or equipment damage* On 5/16, members were working on settling basin outage to pump out, clean, and rebuild valves on the basin. LOTO had been hung & issued at 0821 on 5/16. At approx. 1600, members were unbolting sludge pump discharge Clarkson valves to remove & rebuild; when bolts were loosened, a large amount of water sprayed from flange. Members were able to tighten flange to stop water. It was discovered that both units overflow sump pump discharges tie into the same discharge pipe as the sludge pumps’ discharge due to changes to comply with CCR rules, and overflow sump pumps were still in operation. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Kellan Keeter | 2019-07-09 07:50 | 2019-05-16 22:25 | 2019-05-16 22:25 | 2019-06-18 10:06 | 2019-05-30 16:00 | 2019-05-16 18:30 | 2019-06-21 11:10 |  | 2019-06-20 12:12 | Sooner Settling basin sludge pumps. |  |  | Jesse Murray | This is a perfect example of an incident where Configuration Control process should be followed especially when it pertains to new processes implemented. In this particular case, the changes were made in the field but the LOTO templates were not changed to reflect different case scenarios to secure zero energy. Also, the drawings were poorly updated and communicated. I approve. I approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | On Thursday, May 16, 2019 at approximately 1600 hours, during the yearly settling basin outage, members were continuing to work on tasks related to the cleaning and replacing of valves on the settling basin. All valves had been taken out and replaced at this point the last two valves to be replaced were the sludge pump discharge valves in the settling basin. Even though the “First Break Procedure” has not been finalized, Maintenance members do follow an unofficial version of it: by cutting away from person, and loosening one bolt at time. As reflected in member’s SWP, the box for “First –Break Procedure Followed” was checked. Using this method member began to take the flange off going to the discharge valve on B sludge pump. Once, he started to loosen the bolts on this flange it began to have a discharge of water. This discharge seemed to have more pressure than head pressure and after some time it did not slow down. Therefore, member tightened the bolts back up on flange. Stopped work and reported what he had experienced to his supervisor. The supervisor then reported it to the shift supervisor and management. The LOTO was created and hung in accordance to the 682 request. When referring to the work order 18838745 that was attached to this 682 request. Upon review of it and the email sent by the foreman it was unknown as to the work to be done to the sludge pumps discharge valves. The email does state that “all components of the sludge pumps including air to the Clarkson’s”, then the 682 states “we will need actuating air un-isolated to the Clarkson’s”. Therefore, the sludge pumps were electrically isolated and discharge valves were left un-isolated on this LOTO. The original template for the settling basin was created but after review it was discovered that changes made to the system during the Coal Combustion Residual (CCR) rule made that LOTO inadequate. Therefore, it was determined that the “Overflow Sump Pumps” would not need to be included as they now discharge to the settling ponds. Prior to CCR it would have been required to get one of the pumps because it at that time it would have discharged into the settling basin and the other into the lower ditch that is no longer in service. Both pumps now discharge into a common line that goes to the settling ponds. This line can also discharge into the settling basin, but if “BOTTOM ASH OVERFLOW DISCHARGE TO SETTLING BASIN ISOLATION VALVE” is closed water cannot get into the settling basin, which was included in the LOTO. However, the discharge of the sludge pumps also discharge into this line and through investigation, it was discovered that it will be charged from back pressure coming from the Overflow Sump pumps. Therefore, when the LOTO was created the boundaries were walked down and determined that by getting the 480V breakers to both sludge pumps, #1 & #2 Ash piping drain sumps, recycle basin supply to slope wash ISV (which was later removed as requested by foreman), recycle header minimum flow valve air ISV, and Bottom Ash overflow discharge to settling basin ISV (which would isolate the water from the overflow sumps from getting into the basin). This LOTO was then verified by a qualified individual before it was hung. After members hung and verified the LOTO, there was/is not a way to verify “ZERO ENERGY” on the piping side (under the basin) of this LOTO as there is not any drain valves on the piping below the basin. Members were able to verify that zero water was discharging into the basin, which was the intent of the LOTO. The PAE was qualified on this system prior to the CCR rule, but was unware of the changes made to this system. When PAE verified the boundaries there was not any water going into the settling basin. With the unknown changes to the system the PAE did not realize that the discharge valves could be back pressured from the new line that was installed during the CCR rule. Prior to this outage, proper planning and coordination with all departments involved had not been made aware of scope of work that was going to take place during the outage. It was found that the task list attached to this work order was out dated and incorrect, leading to some of the miscommunication in submitting the correct 682 for the work that was going to be performed. Also, due to the upgrades of the CCR project it was brought to our attention that the prints and drawings were not exposed properly to all members of the plant. Because members were not aware of changes made to the system they were not able to properly verify zero energy on this system. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Justin Buchanan | Alexander Taybah |  | Alexander Taybah | Monday, 06/17/2019, this incident will be sent back to Investigate status to edit some of the findings as discussed with Marc Hodgson (SS) and Brady Sowell (Safety Coordinator). | Alexander Taybah |  | Medium |  |  |  | 4.07 Confusing directions/demands | 5.04 Inadequate update training |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications | 10.05 Inadequate assessment of operational readiness | [5 empty] | 16.04 Inadequate communication between work groups | Lack of proper planning, scope of work provided, and the miscommunication in the 682. | 20. Failure to Communicate, Coordinate | 2. Struck By (Hit By Moving Object) |  | See workflow comments or email. Per Sowell on 5/30. Approved by sowell on 6/20/2019 | [90 empty] | 18838745
8864 | Sooner Power Plant | 2019-05-16 16:00 | *No member injury or equipment damage* On 5/16, members were working on settling basin outage to pump out, clean, and rebuild valves on the basin. LOTO had been hung & issued at 0821 on 5/16. At approx. 1600, members were unbolting sludge pump discharge Clarkson valves to remove & rebuild; when bolts were loosened, a large amount of water sprayed from flange. Members were able to tighten flange to stop water. It was discovered that both units overflow sump pump discharges tie into the same discharge pipe as the sludge pumps’ discharge due to changes to comply with CCR rules, and overflow sump pumps were still in operation. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Kellan Keeter | 2019-07-09 07:50 | 2019-05-16 22:25 | 2019-05-16 22:25 | 2019-06-18 10:06 | 2019-05-30 16:00 | 2019-05-16 18:30 | 2019-06-21 11:10 |  | 2019-06-20 12:12 | Sooner Settling basin sludge pumps. |  |  | Jesse Murray | This is a perfect example of an incident where Configuration Control process should be followed especially when it pertains to new processes implemented. In this particular case, the changes were made in the field but the LOTO templates were not changed to reflect different case scenarios to secure zero energy. Also, the drawings were poorly updated and communicated. I approve. I approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | On Thursday, May 16, 2019 at approximately 1600 hours, during the yearly settling basin outage, members were continuing to work on tasks related to the cleaning and replacing of valves on the settling basin. All valves had been taken out and replaced at this point the last two valves to be replaced were the sludge pump discharge valves in the settling basin. Even though the “First Break Procedure” has not been finalized, Maintenance members do follow an unofficial version of it: by cutting away from person, and loosening one bolt at time. As reflected in member’s SWP, the box for “First –Break Procedure Followed” was checked. Using this method member began to take the flange off going to the discharge valve on B sludge pump. Once, he started to loosen the bolts on this flange it began to have a discharge of water. This discharge seemed to have more pressure than head pressure and after some time it did not slow down. Therefore, member tightened the bolts back up on flange. Stopped work and reported what he had experienced to his supervisor. The supervisor then reported it to the shift supervisor and management. The LOTO was created and hung in accordance to the 682 request. When referring to the work order 18838745 that was attached to this 682 request. Upon review of it and the email sent by the foreman it was unknown as to the work to be done to the sludge pumps discharge valves. The email does state that “all components of the sludge pumps including air to the Clarkson’s”, then the 682 states “we will need actuating air un-isolated to the Clarkson’s”. Therefore, the sludge pumps were electrically isolated and discharge valves were left un-isolated on this LOTO. The original template for the settling basin was created but after review it was discovered that changes made to the system during the Coal Combustion Residual (CCR) rule made that LOTO inadequate. Therefore, it was determined that the “Overflow Sump Pumps” would not need to be included as they now discharge to the settling ponds. Prior to CCR it would have been required to get one of the pumps because it at that time it would have discharged into the settling basin and the other into the lower ditch that is no longer in service. Both pumps now discharge into a common line that goes to the settling ponds. This line can also discharge into the settling basin, but if “BOTTOM ASH OVERFLOW DISCHARGE TO SETTLING BASIN ISOLATION VALVE” is closed water cannot get into the settling basin, which was included in the LOTO. However, the discharge of the sludge pumps also discharge into this line and through investigation, it was discovered that it will be charged from back pressure coming from the Overflow Sump pumps. Therefore, when the LOTO was created the boundaries were walked down and determined that by getting the 480V breakers to both sludge pumps, #1 & #2 Ash piping drain sumps, recycle basin supply to slope wash ISV (which was later removed as requested by foreman), recycle header minimum flow valve air ISV, and Bottom Ash overflow discharge to settling basin ISV (which would isolate the water from the overflow sumps from getting into the basin). This LOTO was then verified by a qualified individual before it was hung. After members hung and verified the LOTO, there was/is not a way to verify “ZERO ENERGY” on the piping side (under the basin) of this LOTO as there is not any drain valves on the piping below the basin. Members were able to verify that zero water was discharging into the basin, which was the intent of the LOTO. The PAE was qualified on this system prior to the CCR rule, but was unware of the changes made to this system. When PAE verified the boundaries there was not any water going into the settling basin. With the unknown changes to the system the PAE did not realize that the discharge valves could be back pressured from the new line that was installed during the CCR rule. Prior to this outage, proper planning and coordination with all departments involved had not been made aware of scope of work that was going to take place during the outage. It was found that the task list attached to this work order was out dated and incorrect, leading to some of the miscommunication in submitting the correct 682 for the work that was going to be performed. Also, due to the upgrades of the CCR project it was brought to our attention that the prints and drawings were not exposed properly to all members of the plant. Because members were not aware of changes made to the system they were not able to properly verify zero energy on this system. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Justin Buchanan | Alexander Taybah |  | Alexander Taybah | Monday, 06/17/2019, this incident will be sent back to Investigate status to edit some of the findings as discussed with Marc Hodgson (SS) and Brady Sowell (Safety Coordinator). | Alexander Taybah |  | Medium |  |  |  | 4.07 Confusing directions/demands | 5.04 Inadequate update training |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications | 10.05 Inadequate assessment of operational readiness | [5 empty] | 16.08 Incorrect instructions | Lack of proper planning, scope of work provided, and the miscommunication in the 682. | 20. Failure to Communicate, Coordinate | 2. Struck By (Hit By Moving Object) |  | See workflow comments or email. Per Sowell on 5/30. Approved by sowell on 6/20/2019 | [90 empty] | 18838745
8864 | Sooner Power Plant | 2019-05-16 16:00 | *No member injury or equipment damage* On 5/16, members were working on settling basin outage to pump out, clean, and rebuild valves on the basin. LOTO had been hung & issued at 0821 on 5/16. At approx. 1600, members were unbolting sludge pump discharge Clarkson valves to remove & rebuild; when bolts were loosened, a large amount of water sprayed from flange. Members were able to tighten flange to stop water. It was discovered that both units overflow sump pump discharges tie into the same discharge pipe as the sludge pumps’ discharge due to changes to comply with CCR rules, and overflow sump pumps were still in operation. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Kellan Keeter | 2019-07-09 07:50 | 2019-05-16 22:25 | 2019-05-16 22:25 | 2019-06-18 10:06 | 2019-05-30 16:00 | 2019-05-16 18:30 | 2019-06-21 11:10 |  | 2019-06-20 12:12 | Sooner Settling basin sludge pumps. |  |  | Jesse Murray | This is a perfect example of an incident where Configuration Control process should be followed especially when it pertains to new processes implemented. In this particular case, the changes were made in the field but the LOTO templates were not changed to reflect different case scenarios to secure zero energy. Also, the drawings were poorly updated and communicated. I approve. I approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | On Thursday, May 16, 2019 at approximately 1600 hours, during the yearly settling basin outage, members were continuing to work on tasks related to the cleaning and replacing of valves on the settling basin. All valves had been taken out and replaced at this point the last two valves to be replaced were the sludge pump discharge valves in the settling basin. Even though the “First Break Procedure” has not been finalized, Maintenance members do follow an unofficial version of it: by cutting away from person, and loosening one bolt at time. As reflected in member’s SWP, the box for “First –Break Procedure Followed” was checked. Using this method member began to take the flange off going to the discharge valve on B sludge pump. Once, he started to loosen the bolts on this flange it began to have a discharge of water. This discharge seemed to have more pressure than head pressure and after some time it did not slow down. Therefore, member tightened the bolts back up on flange. Stopped work and reported what he had experienced to his supervisor. The supervisor then reported it to the shift supervisor and management. The LOTO was created and hung in accordance to the 682 request. When referring to the work order 18838745 that was attached to this 682 request. Upon review of it and the email sent by the foreman it was unknown as to the work to be done to the sludge pumps discharge valves. The email does state that “all components of the sludge pumps including air to the Clarkson’s”, then the 682 states “we will need actuating air un-isolated to the Clarkson’s”. Therefore, the sludge pumps were electrically isolated and discharge valves were left un-isolated on this LOTO. The original template for the settling basin was created but after review it was discovered that changes made to the system during the Coal Combustion Residual (CCR) rule made that LOTO inadequate. Therefore, it was determined that the “Overflow Sump Pumps” would not need to be included as they now discharge to the settling ponds. Prior to CCR it would have been required to get one of the pumps because it at that time it would have discharged into the settling basin and the other into the lower ditch that is no longer in service. Both pumps now discharge into a common line that goes to the settling ponds. This line can also discharge into the settling basin, but if “BOTTOM ASH OVERFLOW DISCHARGE TO SETTLING BASIN ISOLATION VALVE” is closed water cannot get into the settling basin, which was included in the LOTO. However, the discharge of the sludge pumps also discharge into this line and through investigation, it was discovered that it will be charged from back pressure coming from the Overflow Sump pumps. Therefore, when the LOTO was created the boundaries were walked down and determined that by getting the 480V breakers to both sludge pumps, #1 & #2 Ash piping drain sumps, recycle basin supply to slope wash ISV (which was later removed as requested by foreman), recycle header minimum flow valve air ISV, and Bottom Ash overflow discharge to settling basin ISV (which would isolate the water from the overflow sumps from getting into the basin). This LOTO was then verified by a qualified individual before it was hung. After members hung and verified the LOTO, there was/is not a way to verify “ZERO ENERGY” on the piping side (under the basin) of this LOTO as there is not any drain valves on the piping below the basin. Members were able to verify that zero water was discharging into the basin, which was the intent of the LOTO. The PAE was qualified on this system prior to the CCR rule, but was unware of the changes made to this system. When PAE verified the boundaries there was not any water going into the settling basin. With the unknown changes to the system the PAE did not realize that the discharge valves could be back pressured from the new line that was installed during the CCR rule. Prior to this outage, proper planning and coordination with all departments involved had not been made aware of scope of work that was going to take place during the outage. It was found that the task list attached to this work order was out dated and incorrect, leading to some of the miscommunication in submitting the correct 682 for the work that was going to be performed. Also, due to the upgrades of the CCR project it was brought to our attention that the prints and drawings were not exposed properly to all members of the plant. Because members were not aware of changes made to the system they were not able to properly verify zero energy on this system. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Justin Buchanan | Alexander Taybah |  | Alexander Taybah | Monday, 06/17/2019, this incident will be sent back to Investigate status to edit some of the findings as discussed with Marc Hodgson (SS) and Brady Sowell (Safety Coordinator). | Alexander Taybah |  | Medium |  |  |  | 4.07 Confusing directions/demands | 5.04 Inadequate update training |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications | 10.05 Inadequate assessment of operational readiness | [5 empty] | 16.03. Inadequate communication between different organizations | Lack of proper planning, scope of work provided, and the miscommunication in the 682. | 20. Failure to Communicate, Coordinate | 2. Struck By (Hit By Moving Object) |  | See workflow comments or email. Per Sowell on 5/30. Approved by sowell on 6/20/2019 | [90 empty] | 18838745
8864 | Sooner Power Plant | 2019-05-16 16:00 | *No member injury or equipment damage* On 5/16, members were working on settling basin outage to pump out, clean, and rebuild valves on the basin. LOTO had been hung & issued at 0821 on 5/16. At approx. 1600, members were unbolting sludge pump discharge Clarkson valves to remove & rebuild; when bolts were loosened, a large amount of water sprayed from flange. Members were able to tighten flange to stop water. It was discovered that both units overflow sump pump discharges tie into the same discharge pipe as the sludge pumps’ discharge due to changes to comply with CCR rules, and overflow sump pumps were still in operation. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Kellan Keeter | 2019-07-09 07:50 | 2019-05-16 22:25 | 2019-05-16 22:25 | 2019-06-18 10:06 | 2019-05-30 16:00 | 2019-05-16 18:30 | 2019-06-21 11:10 |  | 2019-06-20 12:12 | Sooner Settling basin sludge pumps. |  |  | Jesse Murray | This is a perfect example of an incident where Configuration Control process should be followed especially when it pertains to new processes implemented. In this particular case, the changes were made in the field but the LOTO templates were not changed to reflect different case scenarios to secure zero energy. Also, the drawings were poorly updated and communicated. I approve. I approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | On Thursday, May 16, 2019 at approximately 1600 hours, during the yearly settling basin outage, members were continuing to work on tasks related to the cleaning and replacing of valves on the settling basin. All valves had been taken out and replaced at this point the last two valves to be replaced were the sludge pump discharge valves in the settling basin. Even though the “First Break Procedure” has not been finalized, Maintenance members do follow an unofficial version of it: by cutting away from person, and loosening one bolt at time. As reflected in member’s SWP, the box for “First –Break Procedure Followed” was checked. Using this method member began to take the flange off going to the discharge valve on B sludge pump. Once, he started to loosen the bolts on this flange it began to have a discharge of water. This discharge seemed to have more pressure than head pressure and after some time it did not slow down. Therefore, member tightened the bolts back up on flange. Stopped work and reported what he had experienced to his supervisor. The supervisor then reported it to the shift supervisor and management. The LOTO was created and hung in accordance to the 682 request. When referring to the work order 18838745 that was attached to this 682 request. Upon review of it and the email sent by the foreman it was unknown as to the work to be done to the sludge pumps discharge valves. The email does state that “all components of the sludge pumps including air to the Clarkson’s”, then the 682 states “we will need actuating air un-isolated to the Clarkson’s”. Therefore, the sludge pumps were electrically isolated and discharge valves were left un-isolated on this LOTO. The original template for the settling basin was created but after review it was discovered that changes made to the system during the Coal Combustion Residual (CCR) rule made that LOTO inadequate. Therefore, it was determined that the “Overflow Sump Pumps” would not need to be included as they now discharge to the settling ponds. Prior to CCR it would have been required to get one of the pumps because it at that time it would have discharged into the settling basin and the other into the lower ditch that is no longer in service. Both pumps now discharge into a common line that goes to the settling ponds. This line can also discharge into the settling basin, but if “BOTTOM ASH OVERFLOW DISCHARGE TO SETTLING BASIN ISOLATION VALVE” is closed water cannot get into the settling basin, which was included in the LOTO. However, the discharge of the sludge pumps also discharge into this line and through investigation, it was discovered that it will be charged from back pressure coming from the Overflow Sump pumps. Therefore, when the LOTO was created the boundaries were walked down and determined that by getting the 480V breakers to both sludge pumps, #1 & #2 Ash piping drain sumps, recycle basin supply to slope wash ISV (which was later removed as requested by foreman), recycle header minimum flow valve air ISV, and Bottom Ash overflow discharge to settling basin ISV (which would isolate the water from the overflow sumps from getting into the basin). This LOTO was then verified by a qualified individual before it was hung. After members hung and verified the LOTO, there was/is not a way to verify “ZERO ENERGY” on the piping side (under the basin) of this LOTO as there is not any drain valves on the piping below the basin. Members were able to verify that zero water was discharging into the basin, which was the intent of the LOTO. The PAE was qualified on this system prior to the CCR rule, but was unware of the changes made to this system. When PAE verified the boundaries there was not any water going into the settling basin. With the unknown changes to the system the PAE did not realize that the discharge valves could be back pressured from the new line that was installed during the CCR rule. Prior to this outage, proper planning and coordination with all departments involved had not been made aware of scope of work that was going to take place during the outage. It was found that the task list attached to this work order was out dated and incorrect, leading to some of the miscommunication in submitting the correct 682 for the work that was going to be performed. Also, due to the upgrades of the CCR project it was brought to our attention that the prints and drawings were not exposed properly to all members of the plant. Because members were not aware of changes made to the system they were not able to properly verify zero energy on this system. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Justin Buchanan | Alexander Taybah |  | Alexander Taybah | Monday, 06/17/2019, this incident will be sent back to Investigate status to edit some of the findings as discussed with Marc Hodgson (SS) and Brady Sowell (Safety Coordinator). | Alexander Taybah |  | Medium |  |  |  | 4.07 Confusing directions/demands | 5.04 Inadequate update training |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications | 10.08 Inadequate evaluation of changes | [5 empty] | 16.04 Inadequate communication between work groups | Lack of proper planning, scope of work provided, and the miscommunication in the 682. | 20. Failure to Communicate, Coordinate | 2. Struck By (Hit By Moving Object) |  | See workflow comments or email. Per Sowell on 5/30. Approved by sowell on 6/20/2019 | [90 empty] | 18838745
8864 | Sooner Power Plant | 2019-05-16 16:00 | *No member injury or equipment damage* On 5/16, members were working on settling basin outage to pump out, clean, and rebuild valves on the basin. LOTO had been hung & issued at 0821 on 5/16. At approx. 1600, members were unbolting sludge pump discharge Clarkson valves to remove & rebuild; when bolts were loosened, a large amount of water sprayed from flange. Members were able to tighten flange to stop water. It was discovered that both units overflow sump pump discharges tie into the same discharge pipe as the sludge pumps’ discharge due to changes to comply with CCR rules, and overflow sump pumps were still in operation. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Kellan Keeter | 2019-07-09 07:50 | 2019-05-16 22:25 | 2019-05-16 22:25 | 2019-06-18 10:06 | 2019-05-30 16:00 | 2019-05-16 18:30 | 2019-06-21 11:10 |  | 2019-06-20 12:12 | Sooner Settling basin sludge pumps. |  |  | Jesse Murray | This is a perfect example of an incident where Configuration Control process should be followed especially when it pertains to new processes implemented. In this particular case, the changes were made in the field but the LOTO templates were not changed to reflect different case scenarios to secure zero energy. Also, the drawings were poorly updated and communicated. I approve. I approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | On Thursday, May 16, 2019 at approximately 1600 hours, during the yearly settling basin outage, members were continuing to work on tasks related to the cleaning and replacing of valves on the settling basin. All valves had been taken out and replaced at this point the last two valves to be replaced were the sludge pump discharge valves in the settling basin. Even though the “First Break Procedure” has not been finalized, Maintenance members do follow an unofficial version of it: by cutting away from person, and loosening one bolt at time. As reflected in member’s SWP, the box for “First –Break Procedure Followed” was checked. Using this method member began to take the flange off going to the discharge valve on B sludge pump. Once, he started to loosen the bolts on this flange it began to have a discharge of water. This discharge seemed to have more pressure than head pressure and after some time it did not slow down. Therefore, member tightened the bolts back up on flange. Stopped work and reported what he had experienced to his supervisor. The supervisor then reported it to the shift supervisor and management. The LOTO was created and hung in accordance to the 682 request. When referring to the work order 18838745 that was attached to this 682 request. Upon review of it and the email sent by the foreman it was unknown as to the work to be done to the sludge pumps discharge valves. The email does state that “all components of the sludge pumps including air to the Clarkson’s”, then the 682 states “we will need actuating air un-isolated to the Clarkson’s”. Therefore, the sludge pumps were electrically isolated and discharge valves were left un-isolated on this LOTO. The original template for the settling basin was created but after review it was discovered that changes made to the system during the Coal Combustion Residual (CCR) rule made that LOTO inadequate. Therefore, it was determined that the “Overflow Sump Pumps” would not need to be included as they now discharge to the settling ponds. Prior to CCR it would have been required to get one of the pumps because it at that time it would have discharged into the settling basin and the other into the lower ditch that is no longer in service. Both pumps now discharge into a common line that goes to the settling ponds. This line can also discharge into the settling basin, but if “BOTTOM ASH OVERFLOW DISCHARGE TO SETTLING BASIN ISOLATION VALVE” is closed water cannot get into the settling basin, which was included in the LOTO. However, the discharge of the sludge pumps also discharge into this line and through investigation, it was discovered that it will be charged from back pressure coming from the Overflow Sump pumps. Therefore, when the LOTO was created the boundaries were walked down and determined that by getting the 480V breakers to both sludge pumps, #1 & #2 Ash piping drain sumps, recycle basin supply to slope wash ISV (which was later removed as requested by foreman), recycle header minimum flow valve air ISV, and Bottom Ash overflow discharge to settling basin ISV (which would isolate the water from the overflow sumps from getting into the basin). This LOTO was then verified by a qualified individual before it was hung. After members hung and verified the LOTO, there was/is not a way to verify “ZERO ENERGY” on the piping side (under the basin) of this LOTO as there is not any drain valves on the piping below the basin. Members were able to verify that zero water was discharging into the basin, which was the intent of the LOTO. The PAE was qualified on this system prior to the CCR rule, but was unware of the changes made to this system. When PAE verified the boundaries there was not any water going into the settling basin. With the unknown changes to the system the PAE did not realize that the discharge valves could be back pressured from the new line that was installed during the CCR rule. Prior to this outage, proper planning and coordination with all departments involved had not been made aware of scope of work that was going to take place during the outage. It was found that the task list attached to this work order was out dated and incorrect, leading to some of the miscommunication in submitting the correct 682 for the work that was going to be performed. Also, due to the upgrades of the CCR project it was brought to our attention that the prints and drawings were not exposed properly to all members of the plant. Because members were not aware of changes made to the system they were not able to properly verify zero energy on this system. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Justin Buchanan | Alexander Taybah |  | Alexander Taybah | Monday, 06/17/2019, this incident will be sent back to Investigate status to edit some of the findings as discussed with Marc Hodgson (SS) and Brady Sowell (Safety Coordinator). | Alexander Taybah |  | Medium |  |  |  | 4.07 Confusing directions/demands | 5.04 Inadequate update training |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications | 10.08 Inadequate evaluation of changes | [5 empty] | 16.08 Incorrect instructions | Lack of proper planning, scope of work provided, and the miscommunication in the 682. | 20. Failure to Communicate, Coordinate | 2. Struck By (Hit By Moving Object) |  | See workflow comments or email. Per Sowell on 5/30. Approved by sowell on 6/20/2019 | [90 empty] | 18838745
8864 | Sooner Power Plant | 2019-05-16 16:00 | *No member injury or equipment damage* On 5/16, members were working on settling basin outage to pump out, clean, and rebuild valves on the basin. LOTO had been hung & issued at 0821 on 5/16. At approx. 1600, members were unbolting sludge pump discharge Clarkson valves to remove & rebuild; when bolts were loosened, a large amount of water sprayed from flange. Members were able to tighten flange to stop water. It was discovered that both units overflow sump pump discharges tie into the same discharge pipe as the sludge pumps’ discharge due to changes to comply with CCR rules, and overflow sump pumps were still in operation. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Kellan Keeter | 2019-07-09 07:50 | 2019-05-16 22:25 | 2019-05-16 22:25 | 2019-06-18 10:06 | 2019-05-30 16:00 | 2019-05-16 18:30 | 2019-06-21 11:10 |  | 2019-06-20 12:12 | Sooner Settling basin sludge pumps. |  |  | Jesse Murray | This is a perfect example of an incident where Configuration Control process should be followed especially when it pertains to new processes implemented. In this particular case, the changes were made in the field but the LOTO templates were not changed to reflect different case scenarios to secure zero energy. Also, the drawings were poorly updated and communicated. I approve. I approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | On Thursday, May 16, 2019 at approximately 1600 hours, during the yearly settling basin outage, members were continuing to work on tasks related to the cleaning and replacing of valves on the settling basin. All valves had been taken out and replaced at this point the last two valves to be replaced were the sludge pump discharge valves in the settling basin. Even though the “First Break Procedure” has not been finalized, Maintenance members do follow an unofficial version of it: by cutting away from person, and loosening one bolt at time. As reflected in member’s SWP, the box for “First –Break Procedure Followed” was checked. Using this method member began to take the flange off going to the discharge valve on B sludge pump. Once, he started to loosen the bolts on this flange it began to have a discharge of water. This discharge seemed to have more pressure than head pressure and after some time it did not slow down. Therefore, member tightened the bolts back up on flange. Stopped work and reported what he had experienced to his supervisor. The supervisor then reported it to the shift supervisor and management. The LOTO was created and hung in accordance to the 682 request. When referring to the work order 18838745 that was attached to this 682 request. Upon review of it and the email sent by the foreman it was unknown as to the work to be done to the sludge pumps discharge valves. The email does state that “all components of the sludge pumps including air to the Clarkson’s”, then the 682 states “we will need actuating air un-isolated to the Clarkson’s”. Therefore, the sludge pumps were electrically isolated and discharge valves were left un-isolated on this LOTO. The original template for the settling basin was created but after review it was discovered that changes made to the system during the Coal Combustion Residual (CCR) rule made that LOTO inadequate. Therefore, it was determined that the “Overflow Sump Pumps” would not need to be included as they now discharge to the settling ponds. Prior to CCR it would have been required to get one of the pumps because it at that time it would have discharged into the settling basin and the other into the lower ditch that is no longer in service. Both pumps now discharge into a common line that goes to the settling ponds. This line can also discharge into the settling basin, but if “BOTTOM ASH OVERFLOW DISCHARGE TO SETTLING BASIN ISOLATION VALVE” is closed water cannot get into the settling basin, which was included in the LOTO. However, the discharge of the sludge pumps also discharge into this line and through investigation, it was discovered that it will be charged from back pressure coming from the Overflow Sump pumps. Therefore, when the LOTO was created the boundaries were walked down and determined that by getting the 480V breakers to both sludge pumps, #1 & #2 Ash piping drain sumps, recycle basin supply to slope wash ISV (which was later removed as requested by foreman), recycle header minimum flow valve air ISV, and Bottom Ash overflow discharge to settling basin ISV (which would isolate the water from the overflow sumps from getting into the basin). This LOTO was then verified by a qualified individual before it was hung. After members hung and verified the LOTO, there was/is not a way to verify “ZERO ENERGY” on the piping side (under the basin) of this LOTO as there is not any drain valves on the piping below the basin. Members were able to verify that zero water was discharging into the basin, which was the intent of the LOTO. The PAE was qualified on this system prior to the CCR rule, but was unware of the changes made to this system. When PAE verified the boundaries there was not any water going into the settling basin. With the unknown changes to the system the PAE did not realize that the discharge valves could be back pressured from the new line that was installed during the CCR rule. Prior to this outage, proper planning and coordination with all departments involved had not been made aware of scope of work that was going to take place during the outage. It was found that the task list attached to this work order was out dated and incorrect, leading to some of the miscommunication in submitting the correct 682 for the work that was going to be performed. Also, due to the upgrades of the CCR project it was brought to our attention that the prints and drawings were not exposed properly to all members of the plant. Because members were not aware of changes made to the system they were not able to properly verify zero energy on this system. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Justin Buchanan | Alexander Taybah |  | Alexander Taybah | Monday, 06/17/2019, this incident will be sent back to Investigate status to edit some of the findings as discussed with Marc Hodgson (SS) and Brady Sowell (Safety Coordinator). | Alexander Taybah |  | Medium |  |  |  | 4.07 Confusing directions/demands | 5.04 Inadequate update training |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications | 10.08 Inadequate evaluation of changes | [5 empty] | 16.03. Inadequate communication between different organizations | Lack of proper planning, scope of work provided, and the miscommunication in the 682. | 20. Failure to Communicate, Coordinate | 2. Struck By (Hit By Moving Object) |  | See workflow comments or email. Per Sowell on 5/30. Approved by sowell on 6/20/2019 | [90 empty] | 18838745
8865 | Metro Service Center | 2019-05-16 11:30 | Seminole 345/138kV Bank 2 had tripped off. Bank was cleared for sub ops to check. Bank 2 tripped due to issue on PS (Power Supply) side of bank. PS wanted to establish LOTO back to the low side of transformer. PS Asked permission to hang LOTO on Bank 2 Switch 047 for a boundary. TCC gave the ok but there were two other boundaries that need to be open and tagged. Possible exposer to secondary sources. | Level 2 |  | FALSE | System Operational Incident |  |  |  |  | Transco | Darrell Fuller | 2019-07-02 13:11 | 2019-05-18 11:09 |  | 2019-06-28 09:56 | 2019-06-27 11:30 | 2019-05-16 18:00 | 2019-07-02 10:08 |  | 2019-07-01 12:05 | Seminole Substation |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Darrell Fuller |  | Seminole Bank 345/138 kV2 had tripped off. TCC System Operators cleared Bank 2 for sub ops to check early that morning. It was determined that Bank 2 tripped due to an issue on the Power Supply side of Bank 2. Additional switching was conducted to isolate Bank 2 at the high and low side bank switches and its tertiary. Power Supply cleared equipment under a LOTO to make repairs / investigate to / on the suspected area. For additional safety, PS ask permission from TCC to place a LOTO device on switch 047 as an upstream boundary. TCC System Operator gave permission for the LOTO device to be place on 047 but did not make known to PS that 2 additional boundaries needed to be tagged out in order to isolate all potential energy sources. Those devices, 049F and 1MB2PT1 were not isolated thus, there was the possibility of energization from these two sources. At shift change, the out going System Operator discussed with the on coming System Operator the placing of the LOTO device on 047. The out going System Operator(1) told the on coming System Operator (3) to look the placement of the LOTO tag over as he had just learned of it when the other operator(2) left for the day. Upon review, Operator 3 called PS and asked if they were indeed using 047 as a boundary. Operator 3 was told yes they were. At that point Operator 3 advised PS that they didn't have all required clearance boundaries isolated and needed to halt work immediately. |  |  |  | Metro Service Center | FALSE |  | FALSE | System Operations |  | Errol Goad | Darrell Fuller |  | Dallas Rowley | Approve. D. Rowley | Dallas Rowley |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.03 Infrequent performance |  |  | 9.11 Inadequate matching of individual qualifications and job/task requirements | [6 empty] | 16.04 Inadequate communication between work groups | System Operator (2) failed to make known to Power Supply workers, all potential energy sources. This led to an improper LOTO being established. | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation |  | reviewed and agree with corrective actions cm | [90 empty] | none
8865 | Metro Service Center | 2019-05-16 11:30 | Seminole 345/138kV Bank 2 had tripped off. Bank was cleared for sub ops to check. Bank 2 tripped due to issue on PS (Power Supply) side of bank. PS wanted to establish LOTO back to the low side of transformer. PS Asked permission to hang LOTO on Bank 2 Switch 047 for a boundary. TCC gave the ok but there were two other boundaries that need to be open and tagged. Possible exposer to secondary sources. | Level 2 |  | FALSE | System Operational Incident |  |  |  |  | Transco | Darrell Fuller | 2019-07-02 13:11 | 2019-05-18 11:09 |  | 2019-06-28 09:56 | 2019-06-27 11:30 | 2019-05-16 18:00 | 2019-07-02 10:08 |  | 2019-07-01 12:05 | Seminole Substation |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Darrell Fuller |  | Seminole Bank 345/138 kV2 had tripped off. TCC System Operators cleared Bank 2 for sub ops to check early that morning. It was determined that Bank 2 tripped due to an issue on the Power Supply side of Bank 2. Additional switching was conducted to isolate Bank 2 at the high and low side bank switches and its tertiary. Power Supply cleared equipment under a LOTO to make repairs / investigate to / on the suspected area. For additional safety, PS ask permission from TCC to place a LOTO device on switch 047 as an upstream boundary. TCC System Operator gave permission for the LOTO device to be place on 047 but did not make known to PS that 2 additional boundaries needed to be tagged out in order to isolate all potential energy sources. Those devices, 049F and 1MB2PT1 were not isolated thus, there was the possibility of energization from these two sources. At shift change, the out going System Operator discussed with the on coming System Operator the placing of the LOTO device on 047. The out going System Operator(1) told the on coming System Operator (3) to look the placement of the LOTO tag over as he had just learned of it when the other operator(2) left for the day. Upon review, Operator 3 called PS and asked if they were indeed using 047 as a boundary. Operator 3 was told yes they were. At that point Operator 3 advised PS that they didn't have all required clearance boundaries isolated and needed to halt work immediately. |  |  |  | Metro Service Center | FALSE |  | FALSE | System Operations |  | Errol Goad | Darrell Fuller |  | Dallas Rowley | Approve. D. Rowley | Dallas Rowley |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.03 Infrequent performance |  |  | 9.11 Inadequate matching of individual qualifications and job/task requirements | [6 empty] | 16.01 Inadequate horizontal communication between peers | System Operator (2) failed to make known to Power Supply workers, all potential energy sources. This led to an improper LOTO being established. | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation |  | reviewed and agree with corrective actions cm | [90 empty] | none
8865 | Metro Service Center | 2019-05-16 11:30 | Seminole 345/138kV Bank 2 had tripped off. Bank was cleared for sub ops to check. Bank 2 tripped due to issue on PS (Power Supply) side of bank. PS wanted to establish LOTO back to the low side of transformer. PS Asked permission to hang LOTO on Bank 2 Switch 047 for a boundary. TCC gave the ok but there were two other boundaries that need to be open and tagged. Possible exposer to secondary sources. | Level 2 |  | FALSE | System Operational Incident |  |  |  |  | Transco | Darrell Fuller | 2019-07-02 13:11 | 2019-05-18 11:09 |  | 2019-06-28 09:56 | 2019-06-27 11:30 | 2019-05-16 18:00 | 2019-07-02 10:08 |  | 2019-07-01 12:05 | Seminole Substation |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Darrell Fuller |  | Seminole Bank 345/138 kV2 had tripped off. TCC System Operators cleared Bank 2 for sub ops to check early that morning. It was determined that Bank 2 tripped due to an issue on the Power Supply side of Bank 2. Additional switching was conducted to isolate Bank 2 at the high and low side bank switches and its tertiary. Power Supply cleared equipment under a LOTO to make repairs / investigate to / on the suspected area. For additional safety, PS ask permission from TCC to place a LOTO device on switch 047 as an upstream boundary. TCC System Operator gave permission for the LOTO device to be place on 047 but did not make known to PS that 2 additional boundaries needed to be tagged out in order to isolate all potential energy sources. Those devices, 049F and 1MB2PT1 were not isolated thus, there was the possibility of energization from these two sources. At shift change, the out going System Operator discussed with the on coming System Operator the placing of the LOTO device on 047. The out going System Operator(1) told the on coming System Operator (3) to look the placement of the LOTO tag over as he had just learned of it when the other operator(2) left for the day. Upon review, Operator 3 called PS and asked if they were indeed using 047 as a boundary. Operator 3 was told yes they were. At that point Operator 3 advised PS that they didn't have all required clearance boundaries isolated and needed to halt work immediately. |  |  |  | Metro Service Center | FALSE |  | FALSE | System Operations |  | Errol Goad | Darrell Fuller |  | Dallas Rowley | Approve. D. Rowley | Dallas Rowley |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance |  |  | 9.11 Inadequate matching of individual qualifications and job/task requirements | [6 empty] | 16.04 Inadequate communication between work groups | System Operator (2) failed to make known to Power Supply workers, all potential energy sources. This led to an improper LOTO being established. | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation |  | reviewed and agree with corrective actions cm | [90 empty] | none
8865 | Metro Service Center | 2019-05-16 11:30 | Seminole 345/138kV Bank 2 had tripped off. Bank was cleared for sub ops to check. Bank 2 tripped due to issue on PS (Power Supply) side of bank. PS wanted to establish LOTO back to the low side of transformer. PS Asked permission to hang LOTO on Bank 2 Switch 047 for a boundary. TCC gave the ok but there were two other boundaries that need to be open and tagged. Possible exposer to secondary sources. | Level 2 |  | FALSE | System Operational Incident |  |  |  |  | Transco | Darrell Fuller | 2019-07-02 13:11 | 2019-05-18 11:09 |  | 2019-06-28 09:56 | 2019-06-27 11:30 | 2019-05-16 18:00 | 2019-07-02 10:08 |  | 2019-07-01 12:05 | Seminole Substation |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Darrell Fuller |  | Seminole Bank 345/138 kV2 had tripped off. TCC System Operators cleared Bank 2 for sub ops to check early that morning. It was determined that Bank 2 tripped due to an issue on the Power Supply side of Bank 2. Additional switching was conducted to isolate Bank 2 at the high and low side bank switches and its tertiary. Power Supply cleared equipment under a LOTO to make repairs / investigate to / on the suspected area. For additional safety, PS ask permission from TCC to place a LOTO device on switch 047 as an upstream boundary. TCC System Operator gave permission for the LOTO device to be place on 047 but did not make known to PS that 2 additional boundaries needed to be tagged out in order to isolate all potential energy sources. Those devices, 049F and 1MB2PT1 were not isolated thus, there was the possibility of energization from these two sources. At shift change, the out going System Operator discussed with the on coming System Operator the placing of the LOTO device on 047. The out going System Operator(1) told the on coming System Operator (3) to look the placement of the LOTO tag over as he had just learned of it when the other operator(2) left for the day. Upon review, Operator 3 called PS and asked if they were indeed using 047 as a boundary. Operator 3 was told yes they were. At that point Operator 3 advised PS that they didn't have all required clearance boundaries isolated and needed to halt work immediately. |  |  |  | Metro Service Center | FALSE |  | FALSE | System Operations |  | Errol Goad | Darrell Fuller |  | Dallas Rowley | Approve. D. Rowley | Dallas Rowley |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance |  |  | 9.11 Inadequate matching of individual qualifications and job/task requirements | [6 empty] | 16.01 Inadequate horizontal communication between peers | System Operator (2) failed to make known to Power Supply workers, all potential energy sources. This led to an improper LOTO being established. | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation |  | reviewed and agree with corrective actions cm | [90 empty] | none
8866 | Metro Service Center | 2019-05-18 08:30 | Member used multi range to test elastamold switch dead. As the multi range made contact a flash occurred. Member sustained first degree burns to left side of cheek and ear. | Level 3 |  | FALSE | Member Injury |  | Lindle Coleman | `assigned after discussion with ops leaders | 2019-05-20 11:04 | Power Delivery | Quay Prough | 2019-06-20 09:53 | 2019-05-18 14:10 | 2019-05-18 14:10 | 2019-06-11 13:17 | 2019-06-01 07:30 | 2019-05-18 14:01 | 2019-06-11 14:11 | 2019-06-11 16:42 | 2019-06-11 12:24 | First Oklahoma Tower vault |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Travis Sallee |  | On May 18th the network crew began switching to take a scheduled outage at Leadership Square to complete the installation of a new ATO. The initial steps included de-energizing and removing the temporary feed to leadership square, which involved switching the ATO at First Oklahoma Tower vault and the Library switching cubicle. After switching at these two locations was complete, the two members working in the First Oklahoma Tower vault proceeded to test for dead and to install grounds on the ATO bushings. The plan was to place grounds on the dead side of the ATO switch, which had been opened and mechanically disengaged to isolate the feed to the Library Cubicle and Leadership Square. The bushing caps where removed and a multi-range meter with a bushing cone was installed on the end of a six-foot hot stick and used to test for dead. As soon as the multi-range was inserted into the bushing, a flash occurred resulting in 1st-degree burns to the member who was on the end of the hot stick. The other member was standing off to the side and not injured by the flash. The subsequent investigation has revealed four (4) possible root causes which contributed to the incident. These are humidity, possible contamination of test equipment and/or switches, and spacing/location of equipment grounds. Lastly, the use of quick trip, or hotline tag, could have reduced the incident energy by greater than 90%, but this practice is currently not an accepted procedure for switching and testing for hot/dead. Testing and evaluation of the equipment have not revealed a direct cause for the flash. However, there are a few factors that have been identified as the root causes and which likely contributed to the incident. First, there’s no indication that the Arc Flash was due to tracking across the ATO bushing, so the most likely cause is the close proximity of the bleeder, or static ground, of the bushing cap located above the bushing which was checked with the multi-range. Secondly, the ATO switch itself has been tested, and there’s no indication that the ATO switch failed or contributed to the flash. While this is somewhat inconclusive, the evidence suggests that the most likely point of failure was between the multi-range and the bleeder cable, and as the Arc Fault continued to evolve it made contact with the case ground and other static ground wires. Unfortunately, an exact or singular root cause is impossible to identify, but it seems very likely that the combination of humidity and moisture along with the close proximity of the equipment grounds created an ideal environment for an Arc Flash involving 34.5 kV voltages. Steve Chisolm provided data which suggest that distances less than 4.5 - 6 inches between an energized conductors and ground has a 50 percent probability of flashover. This number is subjective due to the environmental conditions listed and may be overestimated since it doesn’t appear our members have experienced such high failure rates. However, the compact equipment design is inadequate to ensure that the probability of such flash incidents is low enough that enhanced PPE, hotline tags, and engineering changes are not warranted. The corrective actions identified are to enhance PPE to require face shield and glasses, or baklava and goggles so that all skin is covered and protected from such incidents when working with 34.5kV voltages in UG vaults when 34.5 kV conductor is exposed for testing or switching. Secondly, we should consider enabling the quick trip, or hotline tag, on the feeder circuits any time a 34.5 kV conductor is removed or exposed for testing and switching. The clearing time for this incident was 38 cycles and the incident energy is estimated at one calorie. However, had the quick trip/hotline tag been enabled, it’s estimated the incident energy would have been reduced by more than 90 percent because clearing time would be between two and four cycles. A 90 percent reduction in incident energy significantly reduces the impact of such incidents and very likely eliminates the potential for injury to the member. Lastly, we should explore long term engineering solutions that offer better hot/dead testing methods and identify equipment that provides better protection from similar hazards related to design features which create hazard exposure conditions. | Luke Kennedy | Travis Sallee | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Partner with System Lab to establish routine testing of multi-range meters and insulation. Establish a work practice that addresses enhanced PPE requirements. Work with Engineering to determine the feasibility of adding quick trips to Network UG Vaults. UTL will conduct hands on arc-flash training with all affected members. | Gary Lassley | Lindle Coleman | High |  |  | 3.09 Constrained movement | [10 empty] | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Root Cause: Dirty insulation materials, combined with high humidity, and possible water contamination caused an arc to track through the flowerpot insulation in the multi-range voltage detector across a T-Body and come in contact with the bleeder wire on the back side of the T-Body. Once the path was formed, the bleeder wire was vaporized and the arc transferred to the equipment case. Evidence: • The bleeder wire on the back of both A phase an B phase T-Bodies were vaporized. At 4000A, 20awg copper will vaporize in a few milliseconds. • There are weld marks on the top of the case. • The multi-range voltage detector’s flowerpot insulation appears old as the rubber is beginning to break down. • There was standing water in the vault. This means humidity was likely significant. • The event report shows approximately 30 amps of current tracking somewhere, which preceded the flash event by 2ms. When the waveform hit peak voltage, the flash started. This behavior is consistent with insulation breakdown of other events. • This was likely not a flash through air given that the 1/1000 chance for 34.5kv to flashover is 6.25 inches with an overvoltage surge of 3x. Since there appears no evidence of a voltage surge, the 1/1000 chance would reduce to 1.5 inches. 50/50 is 1 inch. • It did not flash over to static wires. This is because a flashover to a static wire would have vaporized a large section of the wire, and all static wires were accounted for. One was damaged, however, this could be the result of the fireball. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. However It's my understanding that the statement on high humidity cannot be quantified and is theoretical that it contributed to the flash. It was not a single issues, therefore % humidity has not been addressed as a specific corrective action item to address actual % of humidity that would make a difference while performing the task. Is there a further need to identify a % where we would not perform the task. None has been determined | Upon investigation the team concluded that the corrective actions assigned are the most effective means of limiting exposure to arc flash potential. | [24 empty] | FALSE |  | Days away from Work (H) | 2017-09-11 | 1978-10-10 |  | 2019-05-18 06:00 | 10 | 0 |  | FALSE |  | flash occurred when testing switch dead |  |  | Jonathan Kern |  | Days Away from Work | Jonathan Kern | TRUE |  | St. Anthony hospital |  | Burn: Welding/Flash |  | TRUE |  | Cable Splicer Appr | Head | Injury | Left | TRUE | Sean Canright | TRUE | 2019 | 5/18/2019 6:00:00 AM |  | TRUE | FALSE | TRUE | the flash | [25 empty] | N/A
8866 | Metro Service Center | 2019-05-18 08:30 | Member used multi range to test elastamold switch dead. As the multi range made contact a flash occurred. Member sustained first degree burns to left side of cheek and ear. | Level 3 |  | FALSE | Member Injury |  | Lindle Coleman | `assigned after discussion with ops leaders | 2019-05-20 11:04 | Power Delivery | Quay Prough | 2019-06-20 09:53 | 2019-05-18 14:10 | 2019-05-18 14:10 | 2019-06-11 13:17 | 2019-06-01 07:30 | 2019-05-18 14:01 | 2019-06-11 14:11 | 2019-06-11 16:42 | 2019-06-11 12:24 | First Oklahoma Tower vault |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Travis Sallee |  | On May 18th the network crew began switching to take a scheduled outage at Leadership Square to complete the installation of a new ATO. The initial steps included de-energizing and removing the temporary feed to leadership square, which involved switching the ATO at First Oklahoma Tower vault and the Library switching cubicle. After switching at these two locations was complete, the two members working in the First Oklahoma Tower vault proceeded to test for dead and to install grounds on the ATO bushings. The plan was to place grounds on the dead side of the ATO switch, which had been opened and mechanically disengaged to isolate the feed to the Library Cubicle and Leadership Square. The bushing caps where removed and a multi-range meter with a bushing cone was installed on the end of a six-foot hot stick and used to test for dead. As soon as the multi-range was inserted into the bushing, a flash occurred resulting in 1st-degree burns to the member who was on the end of the hot stick. The other member was standing off to the side and not injured by the flash. The subsequent investigation has revealed four (4) possible root causes which contributed to the incident. These are humidity, possible contamination of test equipment and/or switches, and spacing/location of equipment grounds. Lastly, the use of quick trip, or hotline tag, could have reduced the incident energy by greater than 90%, but this practice is currently not an accepted procedure for switching and testing for hot/dead. Testing and evaluation of the equipment have not revealed a direct cause for the flash. However, there are a few factors that have been identified as the root causes and which likely contributed to the incident. First, there’s no indication that the Arc Flash was due to tracking across the ATO bushing, so the most likely cause is the close proximity of the bleeder, or static ground, of the bushing cap located above the bushing which was checked with the multi-range. Secondly, the ATO switch itself has been tested, and there’s no indication that the ATO switch failed or contributed to the flash. While this is somewhat inconclusive, the evidence suggests that the most likely point of failure was between the multi-range and the bleeder cable, and as the Arc Fault continued to evolve it made contact with the case ground and other static ground wires. Unfortunately, an exact or singular root cause is impossible to identify, but it seems very likely that the combination of humidity and moisture along with the close proximity of the equipment grounds created an ideal environment for an Arc Flash involving 34.5 kV voltages. Steve Chisolm provided data which suggest that distances less than 4.5 - 6 inches between an energized conductors and ground has a 50 percent probability of flashover. This number is subjective due to the environmental conditions listed and may be overestimated since it doesn’t appear our members have experienced such high failure rates. However, the compact equipment design is inadequate to ensure that the probability of such flash incidents is low enough that enhanced PPE, hotline tags, and engineering changes are not warranted. The corrective actions identified are to enhance PPE to require face shield and glasses, or baklava and goggles so that all skin is covered and protected from such incidents when working with 34.5kV voltages in UG vaults when 34.5 kV conductor is exposed for testing or switching. Secondly, we should consider enabling the quick trip, or hotline tag, on the feeder circuits any time a 34.5 kV conductor is removed or exposed for testing and switching. The clearing time for this incident was 38 cycles and the incident energy is estimated at one calorie. However, had the quick trip/hotline tag been enabled, it’s estimated the incident energy would have been reduced by more than 90 percent because clearing time would be between two and four cycles. A 90 percent reduction in incident energy significantly reduces the impact of such incidents and very likely eliminates the potential for injury to the member. Lastly, we should explore long term engineering solutions that offer better hot/dead testing methods and identify equipment that provides better protection from similar hazards related to design features which create hazard exposure conditions. | Robert White | Travis Sallee | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Partner with System Lab to establish routine testing of multi-range meters and insulation. Establish a work practice that addresses enhanced PPE requirements. Work with Engineering to determine the feasibility of adding quick trips to Network UG Vaults. UTL will conduct hands on arc-flash training with all affected members. | Gary Lassley | Lindle Coleman | High |  |  | 3.09 Constrained movement | [10 empty] | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Root Cause: Dirty insulation materials, combined with high humidity, and possible water contamination caused an arc to track through the flowerpot insulation in the multi-range voltage detector across a T-Body and come in contact with the bleeder wire on the back side of the T-Body. Once the path was formed, the bleeder wire was vaporized and the arc transferred to the equipment case. Evidence: • The bleeder wire on the back of both A phase an B phase T-Bodies were vaporized. At 4000A, 20awg copper will vaporize in a few milliseconds. • There are weld marks on the top of the case. • The multi-range voltage detector’s flowerpot insulation appears old as the rubber is beginning to break down. • There was standing water in the vault. This means humidity was likely significant. • The event report shows approximately 30 amps of current tracking somewhere, which preceded the flash event by 2ms. When the waveform hit peak voltage, the flash started. This behavior is consistent with insulation breakdown of other events. • This was likely not a flash through air given that the 1/1000 chance for 34.5kv to flashover is 6.25 inches with an overvoltage surge of 3x. Since there appears no evidence of a voltage surge, the 1/1000 chance would reduce to 1.5 inches. 50/50 is 1 inch. • It did not flash over to static wires. This is because a flashover to a static wire would have vaporized a large section of the wire, and all static wires were accounted for. One was damaged, however, this could be the result of the fireball. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. However It's my understanding that the statement on high humidity cannot be quantified and is theoretical that it contributed to the flash. It was not a single issues, therefore % humidity has not been addressed as a specific corrective action item to address actual % of humidity that would make a difference while performing the task. Is there a further need to identify a % where we would not perform the task. None has been determined | Upon investigation the team concluded that the corrective actions assigned are the most effective means of limiting exposure to arc flash potential. | [24 empty] | FALSE |  | Days away from Work (H) | 2017-09-11 | 1978-10-10 |  | 2019-05-18 06:00 | 10 | 0 |  | FALSE |  | flash occurred when testing switch dead |  |  | Jonathan Kern |  | Days Away from Work | Jonathan Kern | TRUE |  | St. Anthony hospital |  | Burn: Welding/Flash |  | TRUE |  | Cable Splicer Appr | Head | Injury | Left | TRUE | Sean Canright | TRUE | 2019 | 5/18/2019 6:00:00 AM |  | TRUE | FALSE | TRUE | the flash | [25 empty] | N/A
8866 | Metro Service Center | 2019-05-18 08:30 | Member used multi range to test elastamold switch dead. As the multi range made contact a flash occurred. Member sustained first degree burns to left side of cheek and ear. | Level 3 |  | FALSE | Member Injury |  | Lindle Coleman | `assigned after discussion with ops leaders | 2019-05-20 11:04 | Power Delivery | Quay Prough | 2019-06-20 09:53 | 2019-05-18 14:10 | 2019-05-18 14:10 | 2019-06-11 13:17 | 2019-06-01 07:30 | 2019-05-18 14:01 | 2019-06-11 14:11 | 2019-06-11 16:42 | 2019-06-11 12:24 | First Oklahoma Tower vault |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Travis Sallee |  | On May 18th the network crew began switching to take a scheduled outage at Leadership Square to complete the installation of a new ATO. The initial steps included de-energizing and removing the temporary feed to leadership square, which involved switching the ATO at First Oklahoma Tower vault and the Library switching cubicle. After switching at these two locations was complete, the two members working in the First Oklahoma Tower vault proceeded to test for dead and to install grounds on the ATO bushings. The plan was to place grounds on the dead side of the ATO switch, which had been opened and mechanically disengaged to isolate the feed to the Library Cubicle and Leadership Square. The bushing caps where removed and a multi-range meter with a bushing cone was installed on the end of a six-foot hot stick and used to test for dead. As soon as the multi-range was inserted into the bushing, a flash occurred resulting in 1st-degree burns to the member who was on the end of the hot stick. The other member was standing off to the side and not injured by the flash. The subsequent investigation has revealed four (4) possible root causes which contributed to the incident. These are humidity, possible contamination of test equipment and/or switches, and spacing/location of equipment grounds. Lastly, the use of quick trip, or hotline tag, could have reduced the incident energy by greater than 90%, but this practice is currently not an accepted procedure for switching and testing for hot/dead. Testing and evaluation of the equipment have not revealed a direct cause for the flash. However, there are a few factors that have been identified as the root causes and which likely contributed to the incident. First, there’s no indication that the Arc Flash was due to tracking across the ATO bushing, so the most likely cause is the close proximity of the bleeder, or static ground, of the bushing cap located above the bushing which was checked with the multi-range. Secondly, the ATO switch itself has been tested, and there’s no indication that the ATO switch failed or contributed to the flash. While this is somewhat inconclusive, the evidence suggests that the most likely point of failure was between the multi-range and the bleeder cable, and as the Arc Fault continued to evolve it made contact with the case ground and other static ground wires. Unfortunately, an exact or singular root cause is impossible to identify, but it seems very likely that the combination of humidity and moisture along with the close proximity of the equipment grounds created an ideal environment for an Arc Flash involving 34.5 kV voltages. Steve Chisolm provided data which suggest that distances less than 4.5 - 6 inches between an energized conductors and ground has a 50 percent probability of flashover. This number is subjective due to the environmental conditions listed and may be overestimated since it doesn’t appear our members have experienced such high failure rates. However, the compact equipment design is inadequate to ensure that the probability of such flash incidents is low enough that enhanced PPE, hotline tags, and engineering changes are not warranted. The corrective actions identified are to enhance PPE to require face shield and glasses, or baklava and goggles so that all skin is covered and protected from such incidents when working with 34.5kV voltages in UG vaults when 34.5 kV conductor is exposed for testing or switching. Secondly, we should consider enabling the quick trip, or hotline tag, on the feeder circuits any time a 34.5 kV conductor is removed or exposed for testing and switching. The clearing time for this incident was 38 cycles and the incident energy is estimated at one calorie. However, had the quick trip/hotline tag been enabled, it’s estimated the incident energy would have been reduced by more than 90 percent because clearing time would be between two and four cycles. A 90 percent reduction in incident energy significantly reduces the impact of such incidents and very likely eliminates the potential for injury to the member. Lastly, we should explore long term engineering solutions that offer better hot/dead testing methods and identify equipment that provides better protection from similar hazards related to design features which create hazard exposure conditions. | Chad Inman | Travis Sallee | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Partner with System Lab to establish routine testing of multi-range meters and insulation. Establish a work practice that addresses enhanced PPE requirements. Work with Engineering to determine the feasibility of adding quick trips to Network UG Vaults. UTL will conduct hands on arc-flash training with all affected members. | Gary Lassley | Lindle Coleman | High |  |  | 3.09 Constrained movement | [10 empty] | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Root Cause: Dirty insulation materials, combined with high humidity, and possible water contamination caused an arc to track through the flowerpot insulation in the multi-range voltage detector across a T-Body and come in contact with the bleeder wire on the back side of the T-Body. Once the path was formed, the bleeder wire was vaporized and the arc transferred to the equipment case. Evidence: • The bleeder wire on the back of both A phase an B phase T-Bodies were vaporized. At 4000A, 20awg copper will vaporize in a few milliseconds. • There are weld marks on the top of the case. • The multi-range voltage detector’s flowerpot insulation appears old as the rubber is beginning to break down. • There was standing water in the vault. This means humidity was likely significant. • The event report shows approximately 30 amps of current tracking somewhere, which preceded the flash event by 2ms. When the waveform hit peak voltage, the flash started. This behavior is consistent with insulation breakdown of other events. • This was likely not a flash through air given that the 1/1000 chance for 34.5kv to flashover is 6.25 inches with an overvoltage surge of 3x. Since there appears no evidence of a voltage surge, the 1/1000 chance would reduce to 1.5 inches. 50/50 is 1 inch. • It did not flash over to static wires. This is because a flashover to a static wire would have vaporized a large section of the wire, and all static wires were accounted for. One was damaged, however, this could be the result of the fireball. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. However It's my understanding that the statement on high humidity cannot be quantified and is theoretical that it contributed to the flash. It was not a single issues, therefore % humidity has not been addressed as a specific corrective action item to address actual % of humidity that would make a difference while performing the task. Is there a further need to identify a % where we would not perform the task. None has been determined | Upon investigation the team concluded that the corrective actions assigned are the most effective means of limiting exposure to arc flash potential. | [24 empty] | FALSE |  | Days away from Work (H) | 2017-09-11 | 1978-10-10 |  | 2019-05-18 06:00 | 10 | 0 |  | FALSE |  | flash occurred when testing switch dead |  |  | Jonathan Kern |  | Days Away from Work | Jonathan Kern | TRUE |  | St. Anthony hospital |  | Burn: Welding/Flash |  | TRUE |  | Cable Splicer Appr | Head | Injury | Left | TRUE | Sean Canright | TRUE | 2019 | 5/18/2019 6:00:00 AM |  | TRUE | FALSE | TRUE | the flash | [25 empty] | N/A
8867 | Horseshoe Lake Power Plant | 2019-05-20 10:30 | Vehicle struck temporary guarding around light pole while backing | Level 2 |  | FALSE | Vehicle |  |  |  |  | OG&E Corp Services | Robert Butler | 2019-06-17 08:27 | 2019-05-20 11:23 | 2019-05-20 11:23 | 2019-06-14 14:40 | 2019-06-03 10:30 | 2019-05-20 11:02 | 2019-06-17 08:01 |  | 2019-06-14 15:35 | Horseshoe Lake Power Plant Unit 8 Cooling Tower Switch Gear Bldg |  |  | William Young | Please explain how road conditions is a causal factor and if it is a causal factor there should be a corrective action to address it. W. Young 6/6/19. Per Bob Butler there was no issue with the road. Approved. WCY 6/17/19 | UTS |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Robert Butler |  | Member was attempting to dewater containments surrounding acid and bleach tanks associated with Horseshoe Unit 8 cooling tower. Pumps that remove water from these containments showed to have no power. Member was investigating lack of power and drove to Unit 8 cooling tower switch gear house which supplies power to the chlorination building. Member found power was off due to construction being done on the new cooling tower make-up line. Member decided to backup rather than pull forward due to construction going on at the North end of the cooling tower. Member attempted to back between a temporary guard around a downed light pole and a ballard protecting an electrical man-hole. Member lost track of temporary guarding and struck it with passenger side door of company truck. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | UTS - Envir. & Process Chem |  | Thomas Gent | Robert Butler |  | Les Waller | I have reviewed the incident and agree with Supervisor corrective action. LW. 6.5.19 | Les Waller |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Struck temporary guarding surrounding light pole base while backing. | 15. Using Equipment Improperly | 1. Struck Against (Running or Bumping Into) |  | Agree with Supervisor corrective action J. Looney, 6.14.19 | [72 empty] | TRUE |  | Harrah | Struck Fixed Object | Backing Related | 2000-02-28 |  | FALSE |  |  | Day Light |  |  | Gravel |  | Cloudy |  |  | 3350729
8868 | Sooner Power Plant | 2019-05-20 11:30 | Members were walking across mezzanine level and noticed stud laying on grating. Stud fell out of pipe flange 9' above grating. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Michael Dowell | 2019-06-10 20:28 | 2019-05-21 13:32 | 2019-05-21 13:32 | 2019-06-01 14:24 | 2019-06-03 11:30 | 2019-05-21 13:27 | 2019-06-03 12:44 |  |  | Sooner PP Unit #1 mezzanine level |  |  | Brady Sowell | approved | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Michael Dowell |  | Piping had not been serviced in some time. There was a stud missing from flange as well as the one that loosened and fell. It is difficult to pinpoint exactly what happened, but likely that stud was not tightened when piping was initially assembled. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Andrew Leach | Michael Dowell |  | Frank Brixey | Approve- Brixey 6/3/2019 | Frank Brixey |  | Low | [5 empty] | 6.01 Inadequate initial instruction | [10 empty] | Studs were not properly tightened when piping was assembled. | 18. Failure to Check, Monitor | 2. Struck By (Hit By Moving Object) | [92 empty] | none
8869 | Enid Service Center | 2019-05-21 14:00 | A vender (Davey Resource Group) work planner Joseph McFeeters was driving to a location in Enid, OK to meet up with waiting saw crews. Joseph said he was thinking about what he was going to tell the crews about the rest of the day. He didn't realize he was approaching a 4 way stop intersection. He said he dodged the other vehicle but couldn't miss hitting it. Didn't appear to be any injury with other person, and Joseph said he was not injured. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Grant Ehlen | 2019-07-23 12:29 | 2019-05-21 15:38 | 2019-05-21 15:37 | 2019-07-10 09:27 | 2019-06-04 19:00 | 2019-05-21 14:51 | 2019-07-17 14:58 |  | 2019-07-15 14:26 | 4 way stop in Enid area. |  |  | William Young | Corrective action reviewed with OGE legal, Jerrod Moser and recommendation is to revise current corrective action to not allow Davey employee Joseph McFeeters to return to work on OGE sites and/or projects. WCY 6/28/2019 | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Grant Ehlen |  | DRG work planner (Joseph McFeeters) working in Enid, OK leading WTS tree crews to locations. Joseph was headed to crew showup location to guide crews to lunch. He was traveling north on hwy 81 and said he was thinking about where he was going to lead crew and what to tell them. He said he didn't realize he had driven through a red light at a controlled intersection. Joseph said he swerved to avoid a collision yet the other vehicle did collide into the side of Josephs contract vehicle. The collision forced Josephs truck over the curb and into the ditch. The police were called and their reports are attached. Joseph said neither he nor the other vehicle driver were not injured. Joseph was directed by his company to take a drug test. |  |  |  | Enid Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Grant Ehlen |  |  |  | Joseph has met with counselor and completed additional drug testing. He has been in contact with Physician. Counselor has given OK to return to work on June 21. He will submit to random drug testing for 1.5 years. OG&E approves return. Joseph is good help and has never shown indication of being impaired. |  |  | Medium |  |  |  | 4.09 Preoccupation with problems | 5.06 Lack of situational awareness | [11 empty] | Distracted driving resulting in running a red light and causing a collision. | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) |  | Approved. J. Looney, 7/15/19 |  |  |  | Vehicle |  | Grant Ehlen | [5 empty] | 1. Struck Against (Running or Bumping Into) | Grant Ehlen | Davey Resource Group | Joseph McFeeters | [8 empty] | FALSE
8870 | Ft Smith Service Center | 2019-05-22 10:00 | Member arrived at the staging area for the jobsite and parked in the middle of the lot to call the customer. He made the call to discuss job scope and was on the phone approximately 10 minutes. Member did not exit the vehicle during of after the call. When he finished talking he proceeded to pull away while making a sharp right turn and struck a metal pylon that was in the middle of the parking lot. Caused damage to right front fender and front bumper. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Sean Spicer | 2019-06-04 15:41 | 2019-05-23 09:35 | 2019-05-23 09:35 | 2019-06-04 13:28 | 2019-06-05 10:00 | 2019-05-22 10:30 | 2019-06-04 14:41 |  |  | Staging area for jobsite at 9501 Black Bear Trl, Ft. Smith, AR |  |  | Hannah Everett | This is a good reminder to discuss the importance of engagement. Approved. | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Sean Spicer |  | Member arrived at the staging area for the jobsite and parked in the middle of the lot to call the customer. He made the call to discuss job scope and was on the phone approximately 10 minutes. Member did not exit the vehicle during of after the call. When he finished talking he proceeded to pull away while making a sharp right turn and struck a metal pylon that was in the middle of the parking lot. Caused damage to right front fender and front bumper. Member immediately called supervisor and incident was reported to security. Member completed defensive driving course 8/17/2017 and is not due until 2020. |  |  |  | Ft Smith Service Center | FALSE |  | FALSE | Construction Services |  | Allen Snowden | Sean Spicer |  | Charles Kolp | Reviewed all is good | Charles Kolp |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Member arrived at the staging area for the jobsite and parked in the middle of the lot to call the customer. He made the call to discuss job scope and was on the phone approximately 10 minutes. Member did not exit the vehicle during of after the call. When he finished talking he proceeded to pull away while making a sharp right turn and struck a metal pylon that was in the middle of the parking lot. Caused damage to right front fender and front bumper | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) | [74 empty] | TRUE |  | Fort Smith | Struck Fixed Object | Turned Into Object | 2000-12-05 18:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear |  |  | `NA
8871 | Ft Smith Service Center | 2019-05-21 16:00 | Service tech attempted to step over a drainage ditch and his foot slid a few inches, he heard a pop from his right leg. He notified the supervisor of the incident and that his leg had some minor swelling. | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Sean Spicer | 2019-06-10 07:46 | 2019-05-23 10:16 | 2019-05-23 10:16 | 2019-06-04 13:53 | 2019-06-04 16:00 | 2019-05-22 16:30 | 2019-06-07 15:56 |  |  | 824 Hillside Fort Smith, AR |  |  | Hannah Everett | Reviewed for approval | T&D Ops |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Sean Spicer |  | Known Facts: Member was working storm and was crossing ditch to check meter base for damage. He was not carrying any equipment at the time. He stepped on the concrete culvert while crossing ditch, was about 2 ft wide. Member called notified supervisor when the incident happened. Member then called supervisor the next morning and requested medical attention with concerns of swelling. Member has actively participated in OGE Athlete program. |  |  | FALSE | Ft Smith Service Center | FALSE |  | FALSE | Construction Services |  | Joshua Smith | Sean Spicer |  | Chad Inman | Along with communicating, I would like conversation documented and signed. CI | Chad Inman |  | Low | [9 empty] | 10.02 Inadequate consideration of human factors/ergonomics | [6 empty] | Service tech attempted to step over a drainage ditch and his foot slid a few inches, he heard a pop from his right leg. He notified the supervisor of the incident and that his leg had some minor swelling. | 09. Improper Placement | 11. Overstress, Overpressure, Overexertion, Ergonomic | [26 empty] | FALSE |  | Days away from Work (H) | 2007-04-30 | 1980-07-11 |  | 2019-05-21 06:00 | 34 | 27 |  | FALSE |  | Stepped over drainage ditch and slipped a little bit |  |  | Joshua Smith |  | Days Away from Work | Joshua Smith | TRUE |  | Baptist Health- Fort Smith | Andrew D Daniel, MD | Sprain/Strain |  | TRUE |  | Service Technician | Calf | Injury | Right | TRUE | Sean Spicer | TRUE | 2019 | 5/21/2019 6:00:00 AM | 12 | TRUE | FALSE | TRUE | ground, wet dirt/grass | Walking | [24 empty] | NA
8872 | Sooner Power Plant | 2019-05-22 14:00 | Member was moving a pump from the evaporation pond back to the plant using a forklift. The pump was in the crate that it was shipped in. The bottom of the crate broke due to the weight of the pump. The pump fell to the ground 18" below. Minor scratches on the pump. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Trent Novotny | 2019-06-10 20:27 | 2019-05-23 14:17 | 2019-05-23 14:17 | 2019-05-30 14:24 | 2019-06-05 14:00 | 2019-05-22 14:00 | 2019-06-03 12:41 |  |  | Sooner PP Road returning from Evap. Pond |  |  | Brady Sowell | Approved by Brady Sowell on 6/3/2019. Very thorough explanation and easy to understand. | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Trent Novotny |  | Member was transporting a pump back from the evaporation pond in it's original shipping crate. The member was using the Skytrak forklift to transport the pump and was driving around 10 mph. The dirt road was smooth with minimal wash board. (Pic 1) The forks on the Skytrak were spread wide but still within the fork pockets of the pallet. (Pic 2) The daily inspection sheet for the Skytrak was filled out that morning.(Pic 10) As the member was driving the center stringer of the pallet collapsed and the pump fell through and hit the ground. (Pic 3 & 4) The top slat of the pallet was 3/4" pine or douglas fir. (Pic 5) There was also a piece of 7/16" wafer board placed on top of the top slats. (Pic 6) The pallet didn't seem to be rotten or old wood, but the wood was soft. The pump weighs approximately 2150 pounds. (Pic 9) The weight of the pump was too much for the type of wood that was used. The damage to the pump was minimal. There was some paint scratched on either side of the pump. (Pic 7 & 8) A SWP was filled out at the job site. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Maintenance |  | Charles Thomas | Trent Novotny |  | Frank Brixey | The corrective action should be assigned to someone at the plant to relay issue to the vendor. Warehouse does not make that communication. We could file a SCAR or we can get with a planner to get us the contact information. Brixey 5/28/2019 Approve- -Brixey 6/3/2019 | Frank Brixey |  | Low | [10 empty] | 11.04 Inadequate mode or route of shipment | [5 empty] | Wood selected for the pallet should have been able to hold 2150 pounds. | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure | [68 empty] | Scratched paint on the exterior of the pump. | 20 | Charles Thomas | Industrial/Heavy Equipment | [20 empty] | 9582885
8874 | Northeast District Service Cen | 2019-05-27 13:30 | Contract member was in the process of installing grounds. Tail end of ground made contact with top side of energized cutout and a small flash occurred. No injury occurred and circuit breaker did not operate. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Delivery | Jeffrey Gleim | 2019-06-11 16:44 | 2019-05-28 13:29 | 2019-05-28 13:29 | 2019-06-07 09:52 | 2019-06-10 13:30 | 2019-05-28 13:17 | 2019-06-10 15:48 |  | 2019-06-10 11:20 | Sapulpa Ok Intersection of Birch and Hobson |  |  | Lindle Coleman | Approved | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Jeffrey Gleim |  | see attached report |  |  |  | Northeast District Service Cen | FALSE |  | TRUE | Construction Services |  | Jeffrey Gleim | Jeffrey Gleim |  | Chad Inman | Reviewed attachment and approved. CI | Chad Inman |  | Medium |  |  |  |  | 5.03 Inadequate initial training | [11 empty] | See attached contractor report | 09. Improper Placement | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Reviewed |  |  |  | System Outage |  | Jeffrey Gleim | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Jeffrey Gleim | utility solutions inc. | in process |  |  |  | Jeffrey Gleim | [71 empty] | nonoe
8874 | Northeast District Service Cen | 2019-05-27 13:30 | Contract member was in the process of installing grounds. Tail end of ground made contact with top side of energized cutout and a small flash occurred. No injury occurred and circuit breaker did not operate. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Delivery | Jeffrey Gleim | 2019-06-11 16:44 | 2019-05-28 13:29 | 2019-05-28 13:29 | 2019-06-07 09:52 | 2019-06-10 13:30 | 2019-05-28 13:17 | 2019-06-10 15:48 |  | 2019-06-10 11:20 | Sapulpa Ok Intersection of Birch and Hobson |  |  | Lindle Coleman | Approved | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Jeffrey Gleim |  | see attached report |  |  |  | Northeast District Service Cen | FALSE |  | TRUE | Construction Services |  | Jeffrey Gleim | Jeffrey Gleim |  | Chad Inman | Reviewed attachment and approved. CI | Chad Inman |  | Medium |  |  |  |  | 5.03 Inadequate initial training | [11 empty] | See attached contractor report | 09. Improper Placement | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Reviewed |  |  |  | Injury / Illness |  | Jeffrey Gleim | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Jeffrey Gleim | utility solutions inc. | in process |  |  |  | Jeffrey Gleim | [71 empty] | nonoe
8875 | Seminole PP; EGX Gath/Trans | 2019-05-29 08:30 | Member was rebuilding condensate sample pump. While removing pump housing it slipped and member attempted to catch the housing before it contacted the lab bench. The edge of the housing hit members right middle finger causing small blood blister. | Level 1 |  | FALSE | Member Injury |  |  |  |  | OG&E Corp Services | Robert Butler | 2019-06-04 12:51 | 2019-05-29 09:54 | 2019-05-29 09:54 | 2019-05-29 10:16 | 2019-06-12 08:30 | 2019-05-29 09:35 |  |  |  | Seminole chemistry lab |  |  | Jerrie Looney | Approved. 6/4/19 J. Looney | UTS |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | [5 empty] | FALSE | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | UTS - Envir. & Process Chem |  | Jonathan McClure | Robert Butler |  |  |  | Les Waller |  | Low | [45 empty] | FALSE |  |  | 2006-11-27 | 1973-01-25 |  | 2019-05-29 07:00 | 0 | 0 |  | FALSE |  | Housing from sample pump slipped from hand. Member attempted to prevent housing from hitting lab bench. |  | FALSE | Jonathan McClure |  | First Aid | Jonathan McClure |  |  |  |  | Abrasion |  | FALSE |  | Plant Chemist Senior | Finger |  | Right | FALSE | Robert Butler | FALSE |  | 5/29/2019 7:00:00 AM | 12 | FALSE |  |  | Sample pump housing | Rebuilding sample pump
8876 | Metro Service Center | 2019-05-30 09:30 | Member was driving in the Enid pole yard looking for materials. when he struck a gravel pile. damaged front. Member left cones around gravel pile after hitting it. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | John Legg | 2019-08-07 10:45 | 2019-05-30 12:22 | 2019-05-30 12:22 | 2019-06-20 08:34 | 2019-06-13 09:30 | 2019-05-30 12:13 | 2019-07-31 08:10 |  |  | Enid district pole yard |  |  | Marcus Huddleston | No additional comments. MLH 8/7/19 | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | TRUE |  | FALSE | TRUE | John Legg |  | Member was driving in the Enid pole yard looking for materials. when he struck a gravel pile. damaged front. Member left cones around gravel pile after hitting it. |  |  |  | Metro Service Center | FALSE |  | FALSE | Resource Planning & Coord |  | Lewis Wilson | John Legg |  | Nicole Rhodes | Reviewed and spoke with Lewis. | Nicole Rhodes |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [10 empty] | 16.04 Inadequate communication between work groups | Member drove onto a pile of gravel in middle of pole yard. | 02. Failure to Warn | 1. Struck Against (Running or Bumping Into) | [68 empty] | Damage to front bumper | 200 | Lewis Wilson | Vehicle (not related to operation of vehicle) |  | Foe-1484 | FALSE |  | Enid | Struck Fixed Object | Drove Forward Into Object | 2006-10-23 19:00 |  | FALSE |  |  | Day Light |  |  | Gravel |  | Cloudy |  |  | 7777777
8876 | Metro Service Center | 2019-05-30 09:30 | Member was driving in the Enid pole yard looking for materials. when he struck a gravel pile. damaged front. Member left cones around gravel pile after hitting it. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Delivery | John Legg | 2019-08-07 10:45 | 2019-05-30 12:22 | 2019-05-30 12:22 | 2019-06-20 08:34 | 2019-06-13 09:30 | 2019-05-30 12:13 | 2019-07-31 08:10 |  |  | Enid district pole yard |  |  | Marcus Huddleston | No additional comments. MLH 8/7/19 | T&D Ops |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | TRUE | John Legg |  | Member was driving in the Enid pole yard looking for materials. when he struck a gravel pile. damaged front. Member left cones around gravel pile after hitting it. |  |  |  | Metro Service Center | FALSE |  | FALSE | Resource Planning & Coord |  | Lewis Wilson | John Legg |  | Nicole Rhodes | Reviewed and spoke with Lewis. | Nicole Rhodes |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [10 empty] | 16.04 Inadequate communication between work groups | Member drove onto a pile of gravel in middle of pole yard. | 02. Failure to Warn | 1. Struck Against (Running or Bumping Into) | [68 empty] | Damage to front bumper | 200 | Lewis Wilson | Vehicle (not related to operation of vehicle) |  | Foe-1484 | FALSE |  | Enid | Struck Fixed Object | Drove Forward Into Object | 2006-10-23 19:00 |  | FALSE |  |  | Day Light |  |  | Gravel |  | Cloudy |  |  | 7777777
8877 | Seminole PP; EGX Gath/Trans | 2019-05-31 10:30 | An operator working in the area noticed that the locking device cable used to LOTO the 2A condenser vacuum pump suction isolation valve was no longer attached to the grating that was being used as the attachment point for the cable. | Level 1 |  | TRUE | Property Damage | Donnie Jones |  |  |  | Power Supply | Gregory Fry | 2019-07-08 09:18 | 2019-05-31 12:41 | 2019-05-31 12:41 | 2019-06-21 00:07 | 2019-06-14 10:30 | 2019-05-31 11:42 | 2019-06-24 12:56 |  |  | 2A condenser vacuum pump suction isolation valve |  |  | Chrysty Dorsey | See workflow comments for reason being sent back for investigation. | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Gregory Fry |  | An Operator working in the area of SM2 condenser noticed that the locking device cable used to LOTO the 2A condenser vacuum pump suction isolation valve was no longer attached to the grating that was being used as the attachment point for the cable. The operator discovered the cable had been pulled through the clamp and the plastic cable coating had been removed. He then notified the Shift Supervisor of his findings. At that time the SS attached some temporary locking devices and locks so that the boundary could be secured. The PAE holding the affected LOTO was not at the plant so the O&M manager removed the PAE lock on the lock box so that the boundary could be reestablished. After completing his work, the operator passed back by the same valve and saw the cable was loose again. This time the cable was still locked but it had been pulled loose from the grating. The operator inspected the grating and saw there were some grating bars that were not welded to the pipe penetration. There had been a lot of traffic observed moving scaffolding in that area around the time of the finding. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | TRUE | Operations |  | Robert Chew | Gregory Fry |  | Paul Schoelen | Review complete | Paul Schoelen |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | An operator working in the area noticed that the locking device cable used to LOTO the 2A condenser vacuum pump suction isolation valve was no longer attached to the grating that was being used as the attachment point for the cable. | 09. Improper Placement | 6. Caught On (Snagged, Hung) | [92 empty] | none
8878 | Metro Service Center | 2019-06-04 10:00 | Contractor driving on city street, snagged wire breaking two poles. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Richard Norton | 2019-06-17 06:37 | 2019-06-04 10:41 | 2019-06-04 10:41 | 2019-06-04 11:01 | 2019-06-18 10:00 | 2019-06-04 10:23 | 2019-06-14 11:36 |  | 2019-06-12 14:00 | 827 N. Jefferson, Seminole Oklahoma |  |  | William Young | Corrective actions entered. Approved. WCY 6/17/2019 | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Richard Norton |  | Wright tree bucket truck was driving down city street in Seminole Oklahoma, snagged overhead secondary wire at 827 N Jefferson, two poles were broke and pulled over with one pole landing on chipper being pulled by bucket truck. |  |  |  | Metro Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Richard Norton | Richard Norton |  |  | I visited the site. Observed the truck and the location of the incident. Conclusion is that the wire was not installed or maintained per NESC 203C2,C3 standards at 16' above all grades of the roadway. Likely due to pole degradation and lean. Crew did not recognize the wire as low. Fault is primarily OG&E for failure to maintain wire at appropriated height, and secondary on crew for lack of situational awareness. Wright has addressed the situation on their end and no significant damage occurred to the truck or chipper. OG&E will be responsible for repairing and replacing the two poles and the street lights. No further action anticipated |  |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance | [10 empty] | Wright tree bucket truck was driving down city street in Seminole Oklahoma, snagged overhead secondary wire at 827 N Jefferson, two poles were broke and pulled over with one pole landing on chipper being pulled by bucket truck. | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) |  | Investigation revealed driver failed to identify low hanging line, snagged line and pulled down 2 utility poles. Drive was not accustomed to driving a bucket truck and associated height of vehicle. Approved. J. Looney, 6/12/19 |  |  |  | Vehicle |  | Richard Norton | [5 empty] | 1. Struck Against (Running or Bumping Into) | Richard Norton | Wright Tree | Tylar Cornish |  |  |  | Richard Norton |  |  |  |  | FALSE | [66 empty] | 46001204
8879 | Metro Service Center | 2019-06-04 11:30 | While pulling in new conductor the old phase broke where sleeve had been cut out. Guard structures were in place at all crossings and across HWY 60. Phase broke above foreign distribution crossing resulting in the tail of the broke phase tripping the fused circuit. Semi truck made contact with the low phase resulting in a broke antenna and damaged sun visor. No injury occurred and line was secured. | Level 2 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Jimmy Combs | 2019-06-18 14:55 | 2019-06-04 14:04 |  | 2019-06-10 08:58 | 2019-07-16 11:30 | 2019-06-04 13:52 | 2019-06-18 13:43 |  | 2019-06-11 08:04 | 1/4 mile south of HWY 60 business and HWY 60 Intersection Ponca City Ok |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Jimmy Combs |  | While pulling in new conductor the old phase broke where sleeve had been cut out. Guard structures were in place at all crossings and across HWY 60. Phase broke above foreign distribution crossing resulting in the tail of the broke phase tripping the fused circuit. Semi truck made contact with the low phase resulting in a broke antenna and damaged sun visor. No injury occurred and line was secured. Facts Ascertained: All lines had HLHO or were fused Each distribution and thoroughfare had guard structures in place Rolling grounds were being utilized Equipotential mats were in place at stringing equipment Cover up was used on our distribution crossings but not the co-ops due to unknown incident energy exposure Steel core of old 477 conductor that was being used to pull in new conductor broke where sleeves had been removed. Phase broke in mid span over distribution crossing allowing the tail to make contact with the circuit (circuit tripped immediately) Phase came to rest on guard structure at hwy 60 and was approximately 10' off the ground Semi truck antenna and sun visor received minor damages |  |  |  | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Jimmie Walters | Jimmy Combs |  | Gary Lassley | Jimmy Combs to visit with all Transmission Crew to ensure they Cutout 15' or more of wire when replacing sleeves to ensure wear point is removed. Ensure adequate guard structures or other controls are in place to prevent vehicles from making contact with conductor if it fails | Gary Lassley |  | Medium | [12 empty] | 13.07 Inadequate removal and replacement of unsuitable items |  |  |  | Sleeves are a common point of wear on the steel core and cannot be visually discovered. | 23. Defective Tools, Equipment or Materials | 1. Struck Against (Running or Bumping Into) |  | Reviewed approved. Crew followed work practice to mitigate the risk associated with pulling in wire (equipotential grounding mats, cover up, HLHO or fused circuit, guard structures, and rolling grounds). Appropriate measures are being implemented to prevent reoccurrence. | [90 empty] | 1646810
8880 | General Service Center | 2019-06-04 10:30 | Public motorist notified driver that truck axle was smoking. Driver pulled thru light to get off on shoulder to asses problem. Driver immediately noticed smoke and flames coming from inside of front Driver side axle. Member extinguished fire. | Level 3 |  | FALSE | Property Damage | Stephen Merrill | William Young | Change Director to Nimmo. | 2019-06-04 15:00 | OGE Energy Corp | Charles Shetley | 2019-07-31 11:46 | 2019-06-04 14:32 | 2019-06-04 14:32 | 2019-06-24 08:14 | 2019-06-18 15:30 | 2019-06-04 14:19 | 2019-07-03 11:52 | 2019-07-05 10:32 | 2019-06-24 08:15 | Stop light at Hwy 177 & Benson Park Rd southbound. |  |  | Stephen Merrill | Ok to be closed. | Enterprise Services |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Cody Vinyard |  | Truck F10-230 was taken to Rush to have A/C looked at and repaired. While there it was noted that the truck was due for a PM. Rush found wheel seals leaking and a few other items. Fleet approved repairs to be made and Rush repaired truck. When the truck was returned to Heavy Haul the driver that dropped it off told Heavy Haul that the ABS light was on and truck just needed to go to get an alignment. Truck was taken the next morning to Goodyear for an alignment. Upon completion of the wheel alignment F10-230 was then driven (ABS Light still on) to Shawnee and the fire occurred just past the intersection of Hwy 177 & Benson Park Rd (southbound). After the truck was returned to Rush to inspect and fix the damage from the fire, it was found that the wheel bearing race was not installed correctly which caused the wheel bearing to fail. This caused the axle grease to leak onto the hot brake shoes and catch fire. It was found that the ABS light was indicating that the Wheel Bearing race was not installed correctly. | Nathan Gooch | Cody Vinyard |  | General Service Center | FALSE |  | FALSE | Supply Chain |  | Tracy Kitchens | Charles Shetley |  | George Wicks | Incident completed thoroughly | George Wicks | William Young | High | [11 empty] | 12.01.3 Inadequate preventative adjustment/assembly | 13.05 Inadequate adjustment/repair/maintenance |  | 15.05 Inadequate maintenance |  | Wheel Bearing Race was not installed correctly. | 06. Using Defective Equipment | 12. Equipment Failure | Reviewed and approved. WCY 7/5/2019 | Approved, Cody Vinyard | [66 empty] | Fire to front axle. | 500 | Tracy Kitchens | Fire |  | F10-230 | [18 empty] | 4125730
8880 | General Service Center | 2019-06-04 10:30 | Public motorist notified driver that truck axle was smoking. Driver pulled thru light to get off on shoulder to asses problem. Driver immediately noticed smoke and flames coming from inside of front Driver side axle. Member extinguished fire. | Level 3 |  | FALSE | Property Damage | Stephen Merrill | William Young | Change Director to Nimmo. | 2019-06-04 15:00 | OGE Energy Corp | Charles Shetley | 2019-07-31 11:46 | 2019-06-04 14:32 | 2019-06-04 14:32 | 2019-06-24 08:14 | 2019-06-18 15:30 | 2019-06-04 14:19 | 2019-07-03 11:52 | 2019-07-05 10:32 | 2019-06-24 08:15 | Stop light at Hwy 177 & Benson Park Rd southbound. |  |  | Stephen Merrill | Ok to be closed. | Enterprise Services |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Cody Vinyard |  | Truck F10-230 was taken to Rush to have A/C looked at and repaired. While there it was noted that the truck was due for a PM. Rush found wheel seals leaking and a few other items. Fleet approved repairs to be made and Rush repaired truck. When the truck was returned to Heavy Haul the driver that dropped it off told Heavy Haul that the ABS light was on and truck just needed to go to get an alignment. Truck was taken the next morning to Goodyear for an alignment. Upon completion of the wheel alignment F10-230 was then driven (ABS Light still on) to Shawnee and the fire occurred just past the intersection of Hwy 177 & Benson Park Rd (southbound). After the truck was returned to Rush to inspect and fix the damage from the fire, it was found that the wheel bearing race was not installed correctly which caused the wheel bearing to fail. This caused the axle grease to leak onto the hot brake shoes and catch fire. It was found that the ABS light was indicating that the Wheel Bearing race was not installed correctly. | Charles Shetley | Cody Vinyard |  | General Service Center | FALSE |  | FALSE | Supply Chain |  | Tracy Kitchens | Charles Shetley |  | George Wicks | Incident completed thoroughly | George Wicks | William Young | High | [11 empty] | 12.01.3 Inadequate preventative adjustment/assembly | 13.05 Inadequate adjustment/repair/maintenance |  | 15.05 Inadequate maintenance |  | Wheel Bearing Race was not installed correctly. | 06. Using Defective Equipment | 12. Equipment Failure | Reviewed and approved. WCY 7/5/2019 | Approved, Cody Vinyard | [66 empty] | Fire to front axle. | 500 | Tracy Kitchens | Fire |  | F10-230 | [18 empty] | 4125730
8881 | Metro Service Center | 2019-06-06 10:00 | While traveling eastbound company vehicle approached a public vehicle that was illegally parked (i.e. In loading zone and protruding into member's lane of travel). Oncoming traffic was approaching, which prevented company vehicle from getting over. This resulted in the company vehicle's mirror making contact with the public vehicles driver side mirror. Minor damage to the public vehicles mirror was sustained. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Sean Canright | 2019-06-10 11:16 | 2019-06-06 15:22 | 2019-06-06 15:22 | 2019-06-06 15:28 | 2019-06-20 10:00 | 2019-06-06 15:09 |  |  |  | Park And Harvey in front of the Library |  |  | Terry Hackett | Reviewed/Approved. Incident and prevention controls have been reviewed with underground group on 6/10/19 | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE |  |  | While traveling eastbound company vehicle approached a public vehicle that was illegally parked (i.e. In loading zone and protruding into member's lane of travel). Oncoming traffic was approaching, which prevented company vehicle from getting over. This resulted in the company vehicle's mirror making contact with the public vehicles driver side mirror. Minor damage to the public vehicles mirror was sustained. Facts Ascertained: No damage was sustained to company vehicle Glass on driver side mirror was broke on public vehicle Member was driving approximately 25mph and did not react accordingly to the illegally parked vehicle (both public vehicle driver and member are partially at fault for the incident). |  |  |  | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Jamie Mosser | Sean Canright |  |  |  | Gary Lassley |  | Low | [93 empty] | TRUE |  | Oklahoma City | OGE Vehicle Struck Other Vehicle | Struck Stopped/Parked Vehicle | 2018-10-21 19:00 |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Cloudy
8882 | Horseshoe Lake Power Plant | 2019-06-07 09:30 | While positioning semi trailer with drill stem and matting, trailer load of matting made contact with light pole knocking pole off base. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-06-14 13:37 | 2019-06-07 11:05 | 2019-06-07 11:05 | 2019-06-07 12:01 | 2019-06-21 09:30 | 2019-06-07 09:30 | 2019-06-10 09:40 |  |  | Horseshoe Lake Power Plant Unit 8 cooling tower north west corner |  |  | Chrysty Dorsey | Approved | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | While positioning trailer with drill stems and matting material, driver was backing into drill site with out a spotter and made contact with plant light pole with matting material on trailer, breaking pole base mount. While investigating incident, plant contact noticed matting material was setting offset on trailer and not contained within the rails on the trailer. The contractor had not been utilizing a spotter while backing. Contractor was asked for their Job Safety Analysis (JSA) that they had been conducting daily and the line item 9 was checked no, indicating no spotter was assigned that day to that job. Another factor in the incident was another contractors dozer was parked blocking the view of the light pole from the truck driver. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Special Services |  | Paul Johnson | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  | 2.06 Poor coordination |  |  | 5.06 Lack of situational awareness |  | 7.06 Improper attempt to save time or effort |  | 9.06 Inadequate work planning or programming | [7 empty] | Contractor failed to use a spotter when backing into congested area. | 02. Failure to Warn | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Kelly Casey | light pole broken |  |  |  |  | 2. Struck By (Hit By Moving Object) | Paul Johnson | Cherokee Drilling | Troy Townsend |  | Fixed Equipment |  | Kelly Casey |  |  |  |  | FALSE | [66 empty] | 615604
8883 | Horseshoe Lake Power Plant | 2019-06-07 11:00 | contractor came in contact with exposed 120v lighting circuit wiring. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Wade Gabbert | 2019-07-14 12:40 | 2019-06-07 13:38 | 2019-06-07 13:38 | 2019-06-25 16:24 | 2019-06-21 11:00 | 2019-06-07 13:15 | 2019-07-08 07:32 |  | 2019-07-05 09:23 | Horseshoe Lake Station Unit 6 boiler basement |  |  | Jesse Murray | I approve. Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Thomas Herron |  | On 6-7-19 Contractors were building scaffolding to abate insulation under unit 6 boiler. Contractor reported to Mechanical Maintenance foreman that his back contacted exposed wiring and possibly felt a shock. Mechanical Maintenance foreman contacted ICE Maintenance foreman. Investigation revealed the exposed wiring (picture attached) was energized. It appears a light had been removed or fallen in the past from this octagon box. Lighting circuit was isolated, exposed wires were insulated and installed into octagon box with a proper blank off cover. Circuit was re-energized and contractor work resumed. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Maintenance |  | Wade Gabbert | Wade Gabbert |  | Daniel Perry | I have reviewed this investigation and I approve. | Daniel Perry |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Assessment of worksite should have revealed exposed wiring. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Have reviewed and agree with the findings. |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Wade Gabbert | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Wade Gabbert | EAI | EAI |  |  |  | Wade Gabbert | [71 empty] | 9584782
8884 | Ardmore Service Center | 2019-06-05 10:00 | While performing commissioning tests following the installation of a new relay terminal, technician applied current on the wrong CT block inside 138kv breaker. This substation has a 138kv ring bus and several brands of breakers. The technician assumed the CT block configuration in the second breaker they were working in was the same as the previous breaker. | Level 2 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Bradley Kosemund | 2019-06-26 07:16 | 2019-06-07 13:39 |  | 2019-06-07 14:22 | 2019-07-17 10:00 | 2019-06-05 10:00 | 2019-06-25 07:35 |  | 2019-06-11 09:16 | Caney Creek substation near Kingston Oklahoma |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Bradley Kosemund |  | Contract construction crew had completed their part of a relay terminal replacement of removing old relay equipment and installing and wiring new relay equipment. At this point of the job the contract relay engineer and his employee had been on site a couple day programming relays and testing. Ardmore substation operations also had a relay technician on site for commissioning of this new terminal per our OGE procedures to verify all theory of operation works as expected. The contract relay testing engineer was leading the testing but also taking time to explain everything they tested and why to the OGE relay technician. The relay terminal being replaced was the Caney Creek/Brown/Bodle 138kv line so the 12.5kv transformer bank 1 load was moved so the 138kv bus could be cleared from 186M to 183L and then to Little City substation switch 138. In a ring bus configuration breakers 183 and 186 trip on a Brown Bodle line fault. On a Russett line fault (Madill Tap) breakers 186 and 185 trip. When the technician hooked the leads up to the incorrect CT block and injected current the Russett line relay saw that current and tripped breaker 185. This was the first contract commissioning project given to the OGE relay technician so the contract relay engineer was doing a lot of training for our member along with his own technician during this testing. The first breaker they ran current on was a Siemens brand and the second one, the one where the mistake was made was an ABB breaker. These different brand breakers have different CT block layouts. |  |  |  | Ardmore Service Center | FALSE |  | FALSE | PD Operations Services |  |  | Bradley Kosemund |  | James Hutchison | This type of incident has occurred in the past and the RUG team is working on a process/checklist/tailboard to help in identifying possible opportunities that could lead to a technician getting on or operating a device that was not intended. I will follow up with the RUG team of the progression of this project. | James Hutchison |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Lack of verification of proper lead connection | 18. Failure to Check, Monitor | 9. Abnormal Operation |  | I agree with the investigation and corrective action. All policies were followed, this was a human error. We can provide more oversight but prints are available already. cm | [90 empty] | 1646427
8885 | River Valley | 2019-06-06 16:30 | While preparing for a welding job at the bottom of 10,001x belt structure, welding lead was strung down the crane bay. There were two sections of lead that were tied together by tweco design connections. At some point the leads twisted and came loose from each other and fell 15'. This portion coiled in the bottom of the bay area. This is an approximate 55' height from top to the bottom floor. At the time of the incident no welding work was being performed. The member lowering from the top level down had a spotter at the bottom keeping members free from the area and potential hazards. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Jeremiah Perryman | 2019-06-25 07:14 | 2019-06-07 14:27 | 2019-06-07 14:27 | 2019-06-12 14:08 | 2019-06-20 16:30 | 2019-06-07 13:39 | 2019-06-25 06:55 |  |  | This happened at the bottom 10,000 1x belt River Valley Power Plant. |  |  | Anthony Gillespie | Investigation is appropriate and corrective actions will prevent further incidents from occurring. | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Jeremiah Perryman |  | We found that with a Tweeco junction suspended the lead could twist and allow the factory connection to release. |  |  |  | River Valley | FALSE |  | FALSE | Fuel Supply |  | Todd Mead | Jeremiah Perryman |  | Timothy Chancellor | Agree with recommendation to use whip checks and preference to use solid lead if available. | Timothy Chancellor |  | Low | 1.01 Inappropriate height, weight, size, strength, reach, etc. | [11 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | The leads were connected by a factory Tweeco connector. With the lead suspended it is possible to get a twist in the leads to open the connection and leads to separate. | 03. Failure to Secure | 3. Fall from Elevation to Lower Level | [68 empty] | Leads and connection were not damaged | 20 | Todd Mead | Portable Tool | [20 empty] | 484179
8886 | River Valley | 2019-06-04 15:00 | Member was removing bolts from the combustor outlet manway. The member dropped the bolt and it fell between the grating and the boiler and landed on the level below him (4th floor). | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Melton Morris | 2019-07-09 07:31 | 2019-06-07 14:49 | 2019-06-07 14:49 | 2019-06-10 14:39 | 2019-06-18 15:00 | 2019-06-04 15:00 | 2019-06-25 06:58 |  | 2019-06-20 07:38 | River Valley 2B boiler, 5th floor combustor outlet manway |  |  | Jesse Murray | I Approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Melton Morris |  | Member was removing the manway cover from 2B boiler combustor outlet and dropped one of the bolts between the boiler and the grating. |  |  |  | River Valley | FALSE |  | TRUE | Operations |  | Joe Maggard | Melton Morris |  | Timothy Chancellor | Covered with teams to refresh procedure around barricades and use of fire blankets in gap between grating and boiler when removing bolts. | Timothy Chancellor |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Member did not recognize hazard of the gap between the boiler and the grating. | 21. Inadequate Guards or Barriers | 2. Struck By (Hit By Moving Object) |  | Case reviewed. Approved as is. | [90 empty] | 9784705
8887 | Horseshoe Lake Power Plant | 2019-06-06 03:30 | insulation from the lower front wall header on unit 6 came loose and allowed block (PACM)) insulation to fall to the basement floor. The insulation was saturated with water before the failure occurred so possible member exposure was negligible. waiting on air sample results. | Level 2 |  | FALSE | Property Damage | Cristina McQuistion | Jesse Murray | …………... |  | Power Supply | Wade Gabbert | 2019-07-09 07:21 | 2019-06-07 16:01 | 2019-06-07 16:01 | 2019-06-20 13:43 | 2019-06-20 03:30 | 2019-06-07 15:35 | 2019-07-02 15:05 |  | 2019-06-24 12:20 | Horseshoe Lake Station unit 6 boiler lower wall header insulation failure. |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Diana Edwards |  | On Thursday June 6th at approximately 0200 hours, an operator discovered insulation on the basement floor from the front wall header in unit 6. Operator immediately reported the event to the Operating Authority. Area was then barricaded completely in order to inform other of the hazard and to prevent entry. It was believed that Unit #6 appeared to have a tube leak. Water was left in the boiler to assist with the identification of the leak. Members indicated that leaving the water in the boiler is a common practice used to help identify boiler leaks. In this case, the water was able to leak through the to the lower front wall header on Unit #6 and was absorbed by the insulation material. Maintenance members were in the process of installing the skyclimber in order to be able to access the tubes and find the leak. During the evening shift on 06/052019, the insulation lower front wall header on unit 6 became saturated with water causing the block insulation material to fall to the basement floor. Operator performing rounds found the material laying in the floor and immediately barricaded the area. The EAI 2 man crew was notified as soon as they arrived to work on 06/06/2019 and they immediately proceeded to clean up the material that had fallen to the floor; which was completely saturated with water from the boiler. EAI also took bulk samples and determined the material to be positive for asbestos. The OGE Sr. Asbestos Coordinator was contacted and arrived onsite to assist with the cleanup process. The area remained barricaded and the insulation material on the front header wall continued to remain wet and dripping. This prevented the material from becoming airborne and minimizing risk of exposure to asbestos. Darwin Chestnut from EAI, arrived onsite to oversee the response. Darwin then contacted a third party air monitoring firm, scaffolding crew, and abatement crew. The scaffolding crew arrived onsite and began to erect scaffolding in order to access the location from which it fell off from. An emergency NESHAP notification was filed with the Oklahoma Dept. of Labor. A negative pressure containment was built by EAI and the abatement process was completed. The abatement process was regulated by ODOL asbestos inspectors. The mitigation for this incident is to reinsulate with non-asbestos containing material. The new insulation is then be properly marked as “asbestos free” for future reference in conjunction with other PACM remediations. Air monitoring results were send off for analysis. Results were received on 06/19/2019 and indicated that airborne concentration of asbestos was well below the permissible exposure limit. Findings: • Members acted appropriately and with haste in order to isolate the area and notify management personnel. • Need to include contact number for Asbestos Coordinator in the control room. • We have never had an incident where water from the boiler leaked through like this. o Need to revisit if this could happened in other areas or units in the future. • Abatement was conducted and abated more then what was damaged to remove as much material as possible. • The guidance for notification for incidents such as this is in the Asbestos Management Plan SSOP; will roll-out soon. • Air borne concentration were below Permissible Exposure Limits. • Preparation for installing sky climber include asbestos exposure assessment. o Will evaluate other units to identify need to perform same exposure assessments. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Operations |  | Wade Gabbert | Wade Gabbert |  | Michael Kennedy | I have reviewed the action items and ready to move forward. | Michael Kennedy |  | Medium |  |  |  |  | 5.01 Lack of experience | [11 empty] | PCAM insulation became saturated and fell to the basement level floor. | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level |  | 6/21/19 still reviewing | [66 empty] | insulation | 25700 | Derek Hart | Structural | [20 empty] | n/a
8888 | Horseshoe Lake Power Plant | 2019-06-07 13:00 | Siemens member was under the HP/IP upper half inner shell and raised up and hit his back on a centering pin. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Daniel Perry | 2019-06-26 09:07 | 2019-06-07 19:27 | 2019-06-07 19:27 | 2019-06-14 14:57 | 2019-06-21 13:00 | 2019-06-07 19:03 | 2019-06-17 07:49 |  |  | Horseshoe Lake turbine deck south end. |  |  | Guillermo Sarmiento | 06/17/19 - I have reviewed and approve this incident and it is ready to be on the call list. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Daniel Perry |  | On Friday, June 7th a Siemens member was assigned to prepare the inside of the HP/IP inner cylinder cover for installation for tops-on alignment. He mentioned he was inside it the day before performing miscellaneous work with no issues. The incident occurred when he raised up from a squatted position and jammed his upper back into the center balance plane solid pipe protruding down from the top of the cylinder. The protrusion struck the Siemens member between his shoulder blades. Siemens member reported that it knocked the breath out of him, but he did not report the incident right away. He was going to work through it. Instead of his condition improving, it got worse. He reported the incident approximately one hour later and at that that time the Siemens Project Manager contacted Work Care. Siemens member reported that he was experiencing some numbness in his right arm and fingers and was then taken to the clinic for further evaluation. X-rays did not indicate any serious damage but it was sent to a 2nd radiologist for further review. It was determined that he had a deep tissue bruise due to the impact. The Siemens employee will follow back with the doctor in a week; he is on restricted duties until he is cleared. Findings: • Clearance in this space was not substantial enough to allow entrants to walk completely upright. • In the future, Siemens will raise the cylinder higher to help alleviate the condition; approximately 24”. • Any protrusions will be protected in the future with a cover (pool noodle for example). • Take 5 was very detailed but it did not identify the protrusion. • Lighting may have played a factor but it was unclear if more light would have helped with situational awareness. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Maintenance |  | Daniel Perry | Daniel Perry |  | Daniel Perry | I have reviewed this investigation and I approve. | Daniel Perry |  | Low |  | 2.10 Memory failure |  |  | 5.02 Inadequate orientation | [11 empty] | Member lost situational awareness of the area he was working in. | 11. Improper Position for Task | 1. Struck Against (Running or Bumping Into) | [5 empty] | Injury / Illness |  | Daniel Perry |  | Bruise on back. | FALSE |  |  | 1. Struck Against (Running or Bumping Into) | Daniel Perry | Siemens | Dusty Rogers | Contusion |  | Back | Daniel Perry | Upper | FALSE | [69 empty] | 9581777
8888 | Horseshoe Lake Power Plant | 2019-06-07 13:00 | Siemens member was under the HP/IP upper half inner shell and raised up and hit his back on a centering pin. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Daniel Perry | 2019-06-26 09:07 | 2019-06-07 19:27 | 2019-06-07 19:27 | 2019-06-14 14:57 | 2019-06-21 13:00 | 2019-06-07 19:03 | 2019-06-17 07:49 |  |  | Horseshoe Lake turbine deck south end. |  |  | Guillermo Sarmiento | 06/17/19 - I have reviewed and approve this incident and it is ready to be on the call list. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Daniel Perry |  | On Friday, June 7th a Siemens member was assigned to prepare the inside of the HP/IP inner cylinder cover for installation for tops-on alignment. He mentioned he was inside it the day before performing miscellaneous work with no issues. The incident occurred when he raised up from a squatted position and jammed his upper back into the center balance plane solid pipe protruding down from the top of the cylinder. The protrusion struck the Siemens member between his shoulder blades. Siemens member reported that it knocked the breath out of him, but he did not report the incident right away. He was going to work through it. Instead of his condition improving, it got worse. He reported the incident approximately one hour later and at that that time the Siemens Project Manager contacted Work Care. Siemens member reported that he was experiencing some numbness in his right arm and fingers and was then taken to the clinic for further evaluation. X-rays did not indicate any serious damage but it was sent to a 2nd radiologist for further review. It was determined that he had a deep tissue bruise due to the impact. The Siemens employee will follow back with the doctor in a week; he is on restricted duties until he is cleared. Findings: • Clearance in this space was not substantial enough to allow entrants to walk completely upright. • In the future, Siemens will raise the cylinder higher to help alleviate the condition; approximately 24”. • Any protrusions will be protected in the future with a cover (pool noodle for example). • Take 5 was very detailed but it did not identify the protrusion. • Lighting may have played a factor but it was unclear if more light would have helped with situational awareness. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Maintenance |  | Daniel Perry | Daniel Perry |  | Daniel Perry | I have reviewed this investigation and I approve. | Daniel Perry |  | Low |  | 2.10 Memory failure |  |  | 5.06 Lack of situational awareness | [11 empty] | Member lost situational awareness of the area he was working in. | 11. Improper Position for Task | 1. Struck Against (Running or Bumping Into) | [5 empty] | Injury / Illness |  | Daniel Perry |  | Bruise on back. | FALSE |  |  | 1. Struck Against (Running or Bumping Into) | Daniel Perry | Siemens | Dusty Rogers | Contusion |  | Back | Daniel Perry | Upper | FALSE | [69 empty] | 9581777
8889 | Metro Service Center | 2019-06-10 11:30 | OGE vehicle merging to oncoming traffic to on ramp for I35 rear ended vehicle in frotn | Level 2 |  | FALSE | Vehicle |  |  |  |  | OGE Energy Corp | Phillip Messer | 2019-10-29 12:39 | 2019-06-10 13:11 | 2019-06-10 13:11 | 2019-09-17 08:51 | 2019-06-24 11:30 | 2019-06-10 13:05 | 2019-10-25 11:07 |  | 2019-09-18 14:47 | I240 off ramp onto I35 north |  |  | William Young | Brent has taken the OSU course twice. I think the corrective action should be to attend the National Safety Council DDC course. Please update the corrective action. WCY 8/8/19 | Enterprise Services |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Phillip Messer |  | OGE vehicle (f05-300) returning from GSC to Metro while taking the I-240 off ramp onto I-35. Public and OGE vehicles were traveling on the I 240 off ramp. Public vehicle slowed and came to stop. OGE vehicle was unable to stop and struck Public vehicle in the rear. No injuries, both vehicles were operational. Police report filed, |  |  |  | Metro Service Center | FALSE |  | FALSE | Real Estate |  | Brent Miller | Phillip Messer |  | Vance Krebs | Approved , Vance Krebs 8/5/19 | Vance Krebs |  | Medium |  | 2.07 Slow reaction time | [14 empty] | OGE vehicle merging to oncoming traffic to on ramp for I35 rear ended vehicle in front | 11. Improper Position for Task | 1. Struck Against (Running or Bumping Into) |  | Approved, Cody Vinyard | [72 empty] | TRUE |  | OKC | OGE Vehicle Struck Other Vehicle | OGE Driver Failed To Yield | 2013-12-18 18:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
8890 | Ardmore Service Center | 2019-05-31 12:00 | Section of broke pole rolled off line truck while turning onto Broadway No injury no damages no citation | Level 2 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Carl Williams | 2019-06-26 13:25 | 2019-06-10 16:00 | 2019-06-10 16:00 | 2019-06-24 15:53 | 2019-06-14 12:00 | 2019-06-10 15:51 | 2019-06-26 13:05 |  | 2019-06-25 18:59 | Washington and Broadway intersection |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Carl Williams |  | Crew had completed job of replacing a broke pole. They placed the longest section of the pole on the pole racks of the line truck and the smallest section (approximately 8') in the belly of the line truck. Crew did not secure the section of the pole in the belly of the line truck prior to leaving the worksite. While turning onto Broadway the small section of pole rolled out of the line truck and came to rest under the back wheel of a public vehicle. No injury no damages no citation Facts Ascertained: 8' section of pole Driver did not load pole on line truck All members were driving separate vehicles Driver was on his 2nd day of being approved to drive for the company Driver did not conduct a 360 Crew did not recognize or discuss pole securement Pole rolled off of the belly of the line truck and came to rest under the rear bumper and against the back tire of Hyundai. Line crew and police officers inspected for damage and discovered none. Crew did not recognize that section of pole was not secured OGE DOT driver program does not train on load securement |  |  |  | Ardmore Service Center | FALSE |  | FALSE | Construction Services |  |  | Kenneth McKinzie |  | Chad Inman | I approve the corrective actions. CI | Chad Inman |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching | [7 empty] | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  | 16.01 Inadequate horizontal communication between peers | Load was not secured 360 was not conducted. | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) |  | Reviewed/Approved | [72 empty] | TRUE |  | Ardmore | Other | Loss of Cargo/Material | 2019-05-19 19:00 |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Clear |  |  | NA
8890 | Ardmore Service Center | 2019-05-31 12:00 | Section of broke pole rolled off line truck while turning onto Broadway No injury no damages no citation | Level 2 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Carl Williams | 2019-06-26 13:25 | 2019-06-10 16:00 | 2019-06-10 16:00 | 2019-06-24 15:53 | 2019-06-14 12:00 | 2019-06-10 15:51 | 2019-06-26 13:05 |  | 2019-06-25 18:59 | Washington and Broadway intersection |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Carl Williams |  | Crew had completed job of replacing a broke pole. They placed the longest section of the pole on the pole racks of the line truck and the smallest section (approximately 8') in the belly of the line truck. Crew did not secure the section of the pole in the belly of the line truck prior to leaving the worksite. While turning onto Broadway the small section of pole rolled out of the line truck and came to rest under the back wheel of a public vehicle. No injury no damages no citation Facts Ascertained: 8' section of pole Driver did not load pole on line truck All members were driving separate vehicles Driver was on his 2nd day of being approved to drive for the company Driver did not conduct a 360 Crew did not recognize or discuss pole securement Pole rolled off of the belly of the line truck and came to rest under the rear bumper and against the back tire of Hyundai. Line crew and police officers inspected for damage and discovered none. Crew did not recognize that section of pole was not secured OGE DOT driver program does not train on load securement |  |  |  | Ardmore Service Center | FALSE |  | FALSE | Construction Services |  |  | Kenneth McKinzie |  | Chad Inman | I approve the corrective actions. CI | Chad Inman |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.04 Lack of coaching | [7 empty] | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  | 16.01 Inadequate horizontal communication between peers | Load was not secured 360 was not conducted. | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) |  | Reviewed/Approved | [72 empty] | TRUE |  | Ardmore | Other | Loss of Cargo/Material | 2019-05-19 19:00 |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Clear |  |  | NA
8890 | Ardmore Service Center | 2019-05-31 12:00 | Section of broke pole rolled off line truck while turning onto Broadway No injury no damages no citation | Level 2 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Carl Williams | 2019-06-26 13:25 | 2019-06-10 16:00 | 2019-06-10 16:00 | 2019-06-24 15:53 | 2019-06-14 12:00 | 2019-06-10 15:51 | 2019-06-26 13:05 |  | 2019-06-25 18:59 | Washington and Broadway intersection |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Carl Williams |  | Crew had completed job of replacing a broke pole. They placed the longest section of the pole on the pole racks of the line truck and the smallest section (approximately 8') in the belly of the line truck. Crew did not secure the section of the pole in the belly of the line truck prior to leaving the worksite. While turning onto Broadway the small section of pole rolled out of the line truck and came to rest under the back wheel of a public vehicle. No injury no damages no citation Facts Ascertained: 8' section of pole Driver did not load pole on line truck All members were driving separate vehicles Driver was on his 2nd day of being approved to drive for the company Driver did not conduct a 360 Crew did not recognize or discuss pole securement Pole rolled off of the belly of the line truck and came to rest under the rear bumper and against the back tire of Hyundai. Line crew and police officers inspected for damage and discovered none. Crew did not recognize that section of pole was not secured OGE DOT driver program does not train on load securement |  |  |  | Ardmore Service Center | FALSE |  | FALSE | Construction Services |  |  | Kenneth McKinzie |  | Chad Inman | I approve the corrective actions. CI | Chad Inman |  | Medium | [8 empty] | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | New hire orientation and CDL program does not cover load securement | 02. Failure to Warn | 1. Struck Against (Running or Bumping Into) |  | Reviewed/Approved | [72 empty] | TRUE |  | Ardmore | Other | Loss of Cargo/Material | 2019-05-19 19:00 |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Clear |  |  | NA
8891 | Ada Service Center | 2019-06-10 13:00 | While sitting at a stop light Company vehicle was struck by public vehicle. Company vehicle sustained minor damage to driver side rear bin. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Terry Looney | 2019-06-11 07:51 | 2019-06-11 07:32 | 2019-06-11 07:32 | 2019-06-11 07:37 | 2019-06-24 13:00 | 2019-06-10 13:00 |  |  |  | 200 block of Mississippi E 9th and Mississippi Ada Okla. |  |  | Terry Hackett | No preventative action on the member's part could have prevented this incident. Police report will be uploaded as soon as it is available for supporting documentation. | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | [6 empty] | Ada Service Center | FALSE |  | FALSE | Construction Services |  | Kevin Graham | Terry Looney |  |  |  | Chad Inman |  | Low | [93 empty] | FALSE |  | Ada | Public Vehicle Struck OGE | OGE Vehicle Stopped/Parked | 1997-07-13 19:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
8892 | Metro Service Center | 2019-06-11 08:00 | this is a first aid. member reported tick bite on right leg causing minor discomfort | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Jimmy Combs | 2019-06-22 17:53 | 2019-06-11 14:57 | 2019-06-11 14:57 | 2019-06-11 15:01 | 2019-06-25 08:00 | 2019-06-11 14:52 |  |  |  | unknown |  |  | Terry Hackett | Bite has healed. Members have been encouraged to use the company provided insect repellent and check for ticks. | T&D Ops |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | [5 empty] | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Edward Cate | Jimmy Combs |  |  |  | Gary Lassley |  | Low | [45 empty] | FALSE |  |  | 2004-09-21 | 1968-08-27 |  | 2019-06-11 06:00 | 0 | 0 | removed tick and applied antibiotic | FALSE |  | tick bite |  | TRUE | Edward Cate |  | First Aid | Edward Cate |  |  |  |  | Insect/Animal Bite |  | FALSE |  | Equipment Oper | Leg |  | Right | FALSE | Hershel Goodson | FALSE |  | 6/11/2019 6:00:00 AM |  | FALSE |  |  | tick
8893 | Sooner Power Plant | 2019-06-04 13:00 | Contractor was attempting to install a new hy security gate operator at the west contractors lot gate. The gate operator that they purchased was for a 230 volt application so when they attempted to wire it up to 480 volt it resulted in property damage to the new operator. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Jeffery Beck | 2019-06-27 07:54 | 2019-06-11 15:54 | 2019-06-11 15:54 | 2019-06-18 15:58 | 2019-06-18 13:00 | 2019-06-11 15:15 | 2019-06-24 08:42 |  |  | Sooner Power Plant west contractors lot automatic gate operator |  |  | Brady Sowell | approved by brady sowell on 6/27 | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Jeffery Beck |  | Superior fence was the recommended contractor for Hy security gate repairs. An incident has occurred on a recent repair on the contractor’s west automatic gate. They have attempted twice to repair this gate. They ordered a complete new operator for this gate due to multiple issues with the old one. They installed the operator and wired it up and identified the new control board was bad. They then ordered a new control board and returned a second time to install the board and blew the disconnect fuses at least twice while trying to operate the gate after returning the loto. Plant electrician was called to assist. An investigation determined that they had wired the 208 volt operator up to a 480 volt power source. Monte Hazelwood with Superior Fence was contacted and asked what the issue was and he said that the vendor normally sends the proper equipment and it is basically plug and play, and said they do not have a lot of experience with 480. He was going to contact his vendor to see what the issue was, and will be working on getting the proper voltage operator. Superior Fence’s investigation revealed that they received the wrong voltage operator and that their technician did not catch it before installing it. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Engineering & Planning |  | Jeffery Beck | Jeffery Beck |  | Donald Wyckoff | I have reviewed this incident investigation and approve of findings. | Donald Wyckoff |  | Low |  |  |  |  | 5.01 Lack of experience | [5 empty] | 11.05 Inadequate receiving inspection and acceptance | [5 empty] | Vendor supplied the wrong voltage equipment resulting in equipment damage when energized. | 15. Using Equipment Improperly | 9. Abnormal Operation | [5 empty] | Property Damage |  | Jeffery Beck | [5 empty] | 9. Abnormal Operation | Jeffery Beck | Superior Fence | Tim |  |  |  | Tead Haga | [71 empty] | 9583663
8894 | Muskogee Power Plant | 2019-06-13 08:45 | Member was backing the truck into position near the dumpster to unload some material from the truck bed to the dumpster. The truck drivers side mirror contacted the dumpster and the mirror was cracked. | Level 1 |  | FALSE | Vehicle |  |  |  |  | OG&E Corp Services | Charles Smithson | 2019-06-19 08:14 | 2019-06-13 09:09 | 2019-06-13 09:09 | 2019-06-13 10:36 | 2019-06-27 08:45 | 2019-06-13 08:50 | 2019-06-13 13:25 |  |  | East side of MK6 4160/7200 Volt switchgear building. (dumpster) |  |  | Robert Wright | Approved Bob Wright | UTS |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Charles Smithson |  | Member was positioning the pickup as near as possible to the dumpster to allow easy unloading of some bulky materials into the dumpster. As he backed the truck along the side of the dumpster, the mirror contacted the dumpster and was cracked. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | UTS - Envir. & Process Chem |  | Harry Byrne | Charles Smithson |  | Les Waller | I have reviewed the incident and agree with the corrective actions. | Les Waller |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Harry was backing the vehicle, and intentionally attempting to get very close to the dumpster. He failed to monitor the mirror. | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) | [74 empty] | TRUE |  | Fort Gibson | Struck Fixed Object | Backing Related | 2010-01-04 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear |  |  | 9584475
8895 | Sooner Power Plant | 2019-06-12 18:45 | Member got hand caught in Feeder Belt Conveyor while belt was in operation. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Jesse, I have the following members for the investigation team for Bradley Leniger’s recordable Injury that occurred last night, it is my understanding that you will officially make the assignment: Lead: Glen Hughes Pier Supervisor: Scott Ferguson Fuel Supply Member From MK: Rodney Hyslope Glen Hughes Manager of Plant Fuel Supply Sooner Generating Station | 2019-06-13 12:55 | Power Supply | Glen Hughes | 2019-07-16 17:29 | 2019-06-13 09:29 | 2019-06-13 09:29 | 2019-06-24 07:33 | 2019-06-26 18:45 | 2019-06-12 19:00 | 2019-06-26 09:02 | 2019-07-14 12:43 | 2019-06-24 12:54 | Sooner PP Unit 2 Surge Bin Feeder |  |  | Donnie Jones | Approved - Donnie Jones | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Glen Hughes |  | Member Injury overview and timeline Summary: On Wednesday June 12, 2019 a SoonerPP Fuel Supply Member was injured at approximately 1845 just after shift change. Two Fuel Supply members had just started the routine task of walking the belts and were at the Surge Bin Feeders. Member1 noticed that there were two rollers not moving due to coal build up. Member1 start removing the coal at the bottom side at the feeder belt bed. Member2 was observing this, Member1 turned around to retrieve a piece of conduit to remove the remaining coal. During this very short period of time Member2 began trying to remove the same coal from a different approach height with his hand, while trying to remove some more coal between the two rollers his pinky finger part of his glove somehow got between the moving belt and roller and his hand got immediately pulled between the belt and roller. Member1 heard member2 yell and immediately went to find out what had happened. Member2 still had his glove on and removed it from his hand to see how bad he was hurt. Member1 immediately saw the amount of blood coming his hand and escorted member2 back to the Coal Yard where they met with the Fuel Supply Foreman. The Fuel Supply Foreman immediately got him in the truck and called the Operation SS notifying him of the injury and was taking him directly to the emergency room at Stillwater, OK. The Operation SS immediately notified the Fuel Supply Manager of Member2 being transported to the emergency room in Stillwater. Fuel Supply Manager then called Director of SoonerPP to inform him he was leaving home to drive to emergency room. Director then called SoonerPP Safety Professional to meet me at the emergency room. Once at the Emergency room Fuel Supply Manager and Sooner Safety Professional assessed the injury visually and then had a conference call with Director to ensure Member2 was going to be okay and make sure OGE Workman Comp official was notified of the injury to get paperwork started for the injured member. Member2 was treated and released at approximately 2120 at which time Fuel Supply Manager drove member to Walgreens for prescription medication and FS MGR got his prescriptions filled. At approximately 2300 Member2 was safely driven home and arrived at approximately 2300 to his family. Investigation Details of June 12, 2019: At approximately 1830 Member1 took the path of starting at #1 tripper, and Member2 took the path of #2 tripper where they would meet up at the Surge Bin Feeders Just below the Surge Bin (see Attachment Pics “Surge Bin Overview” and “Surge Bin Feeders”). Member1 got to the feeders just prior to Member2 and noticed two rollers on the North side of Surge Bin Feeder “D” not moving due to coal build-up between the two rollers while the belt was running (see attachment pic “Surge Bin Feeder D”). Member1 did not want to leave this situation alone due to the friction that could develop between the rollers and belt which could possibly get too hot over time creating a hot spot or fire over time. Member1 began removing the coal at the bottom side of rollers (see attachment pic “Member1 path to remove coal”), hoping the coal would collapse causing the rollers to become free and begin moving. During this time Member2 came up and observed what member1 was doing. It became apparent to member1 that the coal was not going to collapse between the rollers so he turned away to retrieve a piece of conduit just a few steps away so he could remove coal in a more safe manner. By the time he picked up the conduit he heard member2 yell and he immediately went to member2 to see what happened. Member2 had tried to remove the remaining coal using his hand at a much higher approach at the actual roller height level very close to the moving belt. During this time of attempting to remove the coal Member2 stuck his hand in to access coal between the two rollers at which time the pinky finger of his glove (right hand) got pulled in between the roller and belt (see attachment pic “Member2 path to remove coal”). Member2 was able to get hand removed but was bleeding very badly. At approximately 1855 Member1 escorted Member2 from the boiler down to the truck where he was driven to the coal yard to meet up with the Fuel Supply Foreman. At approximately 1905 Fuel Supply Foreman immediately notified the Operations SS that he was taking his member to the emergency room in Stillwater. Sooner Rescue team member that was on same shift was notified at approximately 2100 to take action in cleaning up the blood trail in accordance with the Blood Borne Pathogen procedure. At approximately 2200 the Fuel Supply Foreman and Fuel Supply Member were notified to write written statements of this event. On Friday June 14, 2019 the Fuel Supply Manager went to the Fuel Supply members home to get his statement of the event. All has been attached to this incident. Factors that contributed to this Injury based on the investigation some related to the corrective actions: **Member used his hand to remove coal by hand while Conveyor was in operation. **Members right hand pinky finger had tendons cut from a prior injury not allowing him to bend finger which contributed to finger sticking out rather than bending downward while removing coal between rollers. **SWP does not mention not to stay out of danger zone of Conveyor. **Coal build up due to wet coal. **Coal build up normally removed using Service Water, there was no Service Water due to a LOTO on the Service water for Conveyor 11. **No tool(s) for removing coal between rollers other than using water. **No procedure to prevent members from putting hands in the danger zone of a conveyor. **No training for members pertaining to what is acceptable behavior for cleaning conveyors, simply based on common knowledge of what we all think is safe behavior and risk tolerance (can vary from member to member). Attached is a cause diagram of this injury. | Rodney Hyslope | Glen Hughes | FALSE | Sooner Power Plant | FALSE |  | FALSE | Fuel Supply |  | Joe Parker | Glen Hughes |  | Kent Wilson | Approved | Kent Wilson | Jesse Murray | High | [6 empty] | 7.13 Inadequate reinforcement of proper behavior |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Member had a high risk tolerance for cleaning coal on a running conveyor. | 17. Failure to Identify Hazard, Risk | 5. Caught In (Pinch and Nip Points) | Added immediate corrective action for identifying the straw man document to be put in effect immediately for Sooner, Muskogee, and River Valley. Approved Jesse Murray | See member injury sub-incident for statements and interview summary. This information was moved to the "Private Document Attachment" in order to protect members personal information. Approved by Brady Sowell on 6/24/2019 | [24 empty] | FALSE |  | Job Transfer or Restriction (I) | 2016-11-07 | 1985-04-18 |  | 2019-06-12 18:00 | 0 | 78 |  | FALSE |  | Member was trying to remove coal between rollers and his hand got caught between the roller and conveyor belt while belt was in operation. |  | FALSE | Bradly Leniger |  | Days Away from Work | Bradly Leniger | TRUE |  | Stillwater Medical Center | Dr. Tanner, ER doctor attending. | Laceration |  | TRUE |  | Fuel Supply Tech I | Hand | Injury | Right | TRUE | Jon Leatherman | TRUE | 2019 | 6/12/2019 6:00:00 PM | 2 years | TRUE | FALSE | TRUE | Combination of moving Conveyor Belt and Roller. | Member had just started the process of walking down the conveyor belt systems. | [24 empty] | xxxxxxx
8895 | Sooner Power Plant | 2019-06-12 18:45 | Member got hand caught in Feeder Belt Conveyor while belt was in operation. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Jesse, I have the following members for the investigation team for Bradley Leniger’s recordable Injury that occurred last night, it is my understanding that you will officially make the assignment: Lead: Glen Hughes Pier Supervisor: Scott Ferguson Fuel Supply Member From MK: Rodney Hyslope Glen Hughes Manager of Plant Fuel Supply Sooner Generating Station | 2019-06-13 12:55 | Power Supply | Glen Hughes | 2019-07-16 17:29 | 2019-06-13 09:29 | 2019-06-13 09:29 | 2019-06-24 07:33 | 2019-06-26 18:45 | 2019-06-12 19:00 | 2019-06-26 09:02 | 2019-07-14 12:43 | 2019-06-24 12:54 | Sooner PP Unit 2 Surge Bin Feeder |  |  | Donnie Jones | Approved - Donnie Jones | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Glen Hughes |  | Member Injury overview and timeline Summary: On Wednesday June 12, 2019 a SoonerPP Fuel Supply Member was injured at approximately 1845 just after shift change. Two Fuel Supply members had just started the routine task of walking the belts and were at the Surge Bin Feeders. Member1 noticed that there were two rollers not moving due to coal build up. Member1 start removing the coal at the bottom side at the feeder belt bed. Member2 was observing this, Member1 turned around to retrieve a piece of conduit to remove the remaining coal. During this very short period of time Member2 began trying to remove the same coal from a different approach height with his hand, while trying to remove some more coal between the two rollers his pinky finger part of his glove somehow got between the moving belt and roller and his hand got immediately pulled between the belt and roller. Member1 heard member2 yell and immediately went to find out what had happened. Member2 still had his glove on and removed it from his hand to see how bad he was hurt. Member1 immediately saw the amount of blood coming his hand and escorted member2 back to the Coal Yard where they met with the Fuel Supply Foreman. The Fuel Supply Foreman immediately got him in the truck and called the Operation SS notifying him of the injury and was taking him directly to the emergency room at Stillwater, OK. The Operation SS immediately notified the Fuel Supply Manager of Member2 being transported to the emergency room in Stillwater. Fuel Supply Manager then called Director of SoonerPP to inform him he was leaving home to drive to emergency room. Director then called SoonerPP Safety Professional to meet me at the emergency room. Once at the Emergency room Fuel Supply Manager and Sooner Safety Professional assessed the injury visually and then had a conference call with Director to ensure Member2 was going to be okay and make sure OGE Workman Comp official was notified of the injury to get paperwork started for the injured member. Member2 was treated and released at approximately 2120 at which time Fuel Supply Manager drove member to Walgreens for prescription medication and FS MGR got his prescriptions filled. At approximately 2300 Member2 was safely driven home and arrived at approximately 2300 to his family. Investigation Details of June 12, 2019: At approximately 1830 Member1 took the path of starting at #1 tripper, and Member2 took the path of #2 tripper where they would meet up at the Surge Bin Feeders Just below the Surge Bin (see Attachment Pics “Surge Bin Overview” and “Surge Bin Feeders”). Member1 got to the feeders just prior to Member2 and noticed two rollers on the North side of Surge Bin Feeder “D” not moving due to coal build-up between the two rollers while the belt was running (see attachment pic “Surge Bin Feeder D”). Member1 did not want to leave this situation alone due to the friction that could develop between the rollers and belt which could possibly get too hot over time creating a hot spot or fire over time. Member1 began removing the coal at the bottom side of rollers (see attachment pic “Member1 path to remove coal”), hoping the coal would collapse causing the rollers to become free and begin moving. During this time Member2 came up and observed what member1 was doing. It became apparent to member1 that the coal was not going to collapse between the rollers so he turned away to retrieve a piece of conduit just a few steps away so he could remove coal in a more safe manner. By the time he picked up the conduit he heard member2 yell and he immediately went to member2 to see what happened. Member2 had tried to remove the remaining coal using his hand at a much higher approach at the actual roller height level very close to the moving belt. During this time of attempting to remove the coal Member2 stuck his hand in to access coal between the two rollers at which time the pinky finger of his glove (right hand) got pulled in between the roller and belt (see attachment pic “Member2 path to remove coal”). Member2 was able to get hand removed but was bleeding very badly. At approximately 1855 Member1 escorted Member2 from the boiler down to the truck where he was driven to the coal yard to meet up with the Fuel Supply Foreman. At approximately 1905 Fuel Supply Foreman immediately notified the Operations SS that he was taking his member to the emergency room in Stillwater. Sooner Rescue team member that was on same shift was notified at approximately 2100 to take action in cleaning up the blood trail in accordance with the Blood Borne Pathogen procedure. At approximately 2200 the Fuel Supply Foreman and Fuel Supply Member were notified to write written statements of this event. On Friday June 14, 2019 the Fuel Supply Manager went to the Fuel Supply members home to get his statement of the event. All has been attached to this incident. Factors that contributed to this Injury based on the investigation some related to the corrective actions: **Member used his hand to remove coal by hand while Conveyor was in operation. **Members right hand pinky finger had tendons cut from a prior injury not allowing him to bend finger which contributed to finger sticking out rather than bending downward while removing coal between rollers. **SWP does not mention not to stay out of danger zone of Conveyor. **Coal build up due to wet coal. **Coal build up normally removed using Service Water, there was no Service Water due to a LOTO on the Service water for Conveyor 11. **No tool(s) for removing coal between rollers other than using water. **No procedure to prevent members from putting hands in the danger zone of a conveyor. **No training for members pertaining to what is acceptable behavior for cleaning conveyors, simply based on common knowledge of what we all think is safe behavior and risk tolerance (can vary from member to member). Attached is a cause diagram of this injury. | Rodney Hyslope | Glen Hughes | FALSE | Sooner Power Plant | FALSE |  | FALSE | Fuel Supply |  | Joe Parker | Glen Hughes |  | Kent Wilson | Approved | Kent Wilson | Jesse Murray | High | [13 empty] | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | No procedure exists for removing coal build up on Coal Conveying systems | 17. Failure to Identify Hazard, Risk | 5. Caught In (Pinch and Nip Points) | Added immediate corrective action for identifying the straw man document to be put in effect immediately for Sooner, Muskogee, and River Valley. Approved Jesse Murray | See member injury sub-incident for statements and interview summary. This information was moved to the "Private Document Attachment" in order to protect members personal information. Approved by Brady Sowell on 6/24/2019 | [24 empty] | FALSE |  | Job Transfer or Restriction (I) | 2016-11-07 | 1985-04-18 |  | 2019-06-12 18:00 | 0 | 78 |  | FALSE |  | Member was trying to remove coal between rollers and his hand got caught between the roller and conveyor belt while belt was in operation. |  | FALSE | Bradly Leniger |  | Days Away from Work | Bradly Leniger | TRUE |  | Stillwater Medical Center | Dr. Tanner, ER doctor attending. | Laceration |  | TRUE |  | Fuel Supply Tech I | Hand | Injury | Right | TRUE | Jon Leatherman | TRUE | 2019 | 6/12/2019 6:00:00 PM | 2 years | TRUE | FALSE | TRUE | Combination of moving Conveyor Belt and Roller. | Member had just started the process of walking down the conveyor belt systems. | [24 empty] | xxxxxxx
8895 | Sooner Power Plant | 2019-06-12 18:45 | Member got hand caught in Feeder Belt Conveyor while belt was in operation. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Jesse, I have the following members for the investigation team for Bradley Leniger’s recordable Injury that occurred last night, it is my understanding that you will officially make the assignment: Lead: Glen Hughes Pier Supervisor: Scott Ferguson Fuel Supply Member From MK: Rodney Hyslope Glen Hughes Manager of Plant Fuel Supply Sooner Generating Station | 2019-06-13 12:55 | Power Supply | Glen Hughes | 2019-07-16 17:29 | 2019-06-13 09:29 | 2019-06-13 09:29 | 2019-06-24 07:33 | 2019-06-26 18:45 | 2019-06-12 19:00 | 2019-06-26 09:02 | 2019-07-14 12:43 | 2019-06-24 12:54 | Sooner PP Unit 2 Surge Bin Feeder |  |  | Donnie Jones | Approved - Donnie Jones | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Glen Hughes |  | Member Injury overview and timeline Summary: On Wednesday June 12, 2019 a SoonerPP Fuel Supply Member was injured at approximately 1845 just after shift change. Two Fuel Supply members had just started the routine task of walking the belts and were at the Surge Bin Feeders. Member1 noticed that there were two rollers not moving due to coal build up. Member1 start removing the coal at the bottom side at the feeder belt bed. Member2 was observing this, Member1 turned around to retrieve a piece of conduit to remove the remaining coal. During this very short period of time Member2 began trying to remove the same coal from a different approach height with his hand, while trying to remove some more coal between the two rollers his pinky finger part of his glove somehow got between the moving belt and roller and his hand got immediately pulled between the belt and roller. Member1 heard member2 yell and immediately went to find out what had happened. Member2 still had his glove on and removed it from his hand to see how bad he was hurt. Member1 immediately saw the amount of blood coming his hand and escorted member2 back to the Coal Yard where they met with the Fuel Supply Foreman. The Fuel Supply Foreman immediately got him in the truck and called the Operation SS notifying him of the injury and was taking him directly to the emergency room at Stillwater, OK. The Operation SS immediately notified the Fuel Supply Manager of Member2 being transported to the emergency room in Stillwater. Fuel Supply Manager then called Director of SoonerPP to inform him he was leaving home to drive to emergency room. Director then called SoonerPP Safety Professional to meet me at the emergency room. Once at the Emergency room Fuel Supply Manager and Sooner Safety Professional assessed the injury visually and then had a conference call with Director to ensure Member2 was going to be okay and make sure OGE Workman Comp official was notified of the injury to get paperwork started for the injured member. Member2 was treated and released at approximately 2120 at which time Fuel Supply Manager drove member to Walgreens for prescription medication and FS MGR got his prescriptions filled. At approximately 2300 Member2 was safely driven home and arrived at approximately 2300 to his family. Investigation Details of June 12, 2019: At approximately 1830 Member1 took the path of starting at #1 tripper, and Member2 took the path of #2 tripper where they would meet up at the Surge Bin Feeders Just below the Surge Bin (see Attachment Pics “Surge Bin Overview” and “Surge Bin Feeders”). Member1 got to the feeders just prior to Member2 and noticed two rollers on the North side of Surge Bin Feeder “D” not moving due to coal build-up between the two rollers while the belt was running (see attachment pic “Surge Bin Feeder D”). Member1 did not want to leave this situation alone due to the friction that could develop between the rollers and belt which could possibly get too hot over time creating a hot spot or fire over time. Member1 began removing the coal at the bottom side of rollers (see attachment pic “Member1 path to remove coal”), hoping the coal would collapse causing the rollers to become free and begin moving. During this time Member2 came up and observed what member1 was doing. It became apparent to member1 that the coal was not going to collapse between the rollers so he turned away to retrieve a piece of conduit just a few steps away so he could remove coal in a more safe manner. By the time he picked up the conduit he heard member2 yell and he immediately went to member2 to see what happened. Member2 had tried to remove the remaining coal using his hand at a much higher approach at the actual roller height level very close to the moving belt. During this time of attempting to remove the coal Member2 stuck his hand in to access coal between the two rollers at which time the pinky finger of his glove (right hand) got pulled in between the roller and belt (see attachment pic “Member2 path to remove coal”). Member2 was able to get hand removed but was bleeding very badly. At approximately 1855 Member1 escorted Member2 from the boiler down to the truck where he was driven to the coal yard to meet up with the Fuel Supply Foreman. At approximately 1905 Fuel Supply Foreman immediately notified the Operations SS that he was taking his member to the emergency room in Stillwater. Sooner Rescue team member that was on same shift was notified at approximately 2100 to take action in cleaning up the blood trail in accordance with the Blood Borne Pathogen procedure. At approximately 2200 the Fuel Supply Foreman and Fuel Supply Member were notified to write written statements of this event. On Friday June 14, 2019 the Fuel Supply Manager went to the Fuel Supply members home to get his statement of the event. All has been attached to this incident. Factors that contributed to this Injury based on the investigation some related to the corrective actions: **Member used his hand to remove coal by hand while Conveyor was in operation. **Members right hand pinky finger had tendons cut from a prior injury not allowing him to bend finger which contributed to finger sticking out rather than bending downward while removing coal between rollers. **SWP does not mention not to stay out of danger zone of Conveyor. **Coal build up due to wet coal. **Coal build up normally removed using Service Water, there was no Service Water due to a LOTO on the Service water for Conveyor 11. **No tool(s) for removing coal between rollers other than using water. **No procedure to prevent members from putting hands in the danger zone of a conveyor. **No training for members pertaining to what is acceptable behavior for cleaning conveyors, simply based on common knowledge of what we all think is safe behavior and risk tolerance (can vary from member to member). Attached is a cause diagram of this injury. | Brady Sowell | Glen Hughes | FALSE | Sooner Power Plant | FALSE |  | FALSE | Fuel Supply |  | Joe Parker | Glen Hughes |  | Kent Wilson | Approved | Kent Wilson | Jesse Murray | High | [6 empty] | 7.13 Inadequate reinforcement of proper behavior |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Member had a high risk tolerance for cleaning coal on a running conveyor. | 17. Failure to Identify Hazard, Risk | 5. Caught In (Pinch and Nip Points) | Added immediate corrective action for identifying the straw man document to be put in effect immediately for Sooner, Muskogee, and River Valley. Approved Jesse Murray | See member injury sub-incident for statements and interview summary. This information was moved to the "Private Document Attachment" in order to protect members personal information. Approved by Brady Sowell on 6/24/2019 | [24 empty] | FALSE |  | Job Transfer or Restriction (I) | 2016-11-07 | 1985-04-18 |  | 2019-06-12 18:00 | 0 | 78 |  | FALSE |  | Member was trying to remove coal between rollers and his hand got caught between the roller and conveyor belt while belt was in operation. |  | FALSE | Bradly Leniger |  | Days Away from Work | Bradly Leniger | TRUE |  | Stillwater Medical Center | Dr. Tanner, ER doctor attending. | Laceration |  | TRUE |  | Fuel Supply Tech I | Hand | Injury | Right | TRUE | Jon Leatherman | TRUE | 2019 | 6/12/2019 6:00:00 PM | 2 years | TRUE | FALSE | TRUE | Combination of moving Conveyor Belt and Roller. | Member had just started the process of walking down the conveyor belt systems. | [24 empty] | xxxxxxx
8895 | Sooner Power Plant | 2019-06-12 18:45 | Member got hand caught in Feeder Belt Conveyor while belt was in operation. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Jesse, I have the following members for the investigation team for Bradley Leniger’s recordable Injury that occurred last night, it is my understanding that you will officially make the assignment: Lead: Glen Hughes Pier Supervisor: Scott Ferguson Fuel Supply Member From MK: Rodney Hyslope Glen Hughes Manager of Plant Fuel Supply Sooner Generating Station | 2019-06-13 12:55 | Power Supply | Glen Hughes | 2019-07-16 17:29 | 2019-06-13 09:29 | 2019-06-13 09:29 | 2019-06-24 07:33 | 2019-06-26 18:45 | 2019-06-12 19:00 | 2019-06-26 09:02 | 2019-07-14 12:43 | 2019-06-24 12:54 | Sooner PP Unit 2 Surge Bin Feeder |  |  | Donnie Jones | Approved - Donnie Jones | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Glen Hughes |  | Member Injury overview and timeline Summary: On Wednesday June 12, 2019 a SoonerPP Fuel Supply Member was injured at approximately 1845 just after shift change. Two Fuel Supply members had just started the routine task of walking the belts and were at the Surge Bin Feeders. Member1 noticed that there were two rollers not moving due to coal build up. Member1 start removing the coal at the bottom side at the feeder belt bed. Member2 was observing this, Member1 turned around to retrieve a piece of conduit to remove the remaining coal. During this very short period of time Member2 began trying to remove the same coal from a different approach height with his hand, while trying to remove some more coal between the two rollers his pinky finger part of his glove somehow got between the moving belt and roller and his hand got immediately pulled between the belt and roller. Member1 heard member2 yell and immediately went to find out what had happened. Member2 still had his glove on and removed it from his hand to see how bad he was hurt. Member1 immediately saw the amount of blood coming his hand and escorted member2 back to the Coal Yard where they met with the Fuel Supply Foreman. The Fuel Supply Foreman immediately got him in the truck and called the Operation SS notifying him of the injury and was taking him directly to the emergency room at Stillwater, OK. The Operation SS immediately notified the Fuel Supply Manager of Member2 being transported to the emergency room in Stillwater. Fuel Supply Manager then called Director of SoonerPP to inform him he was leaving home to drive to emergency room. Director then called SoonerPP Safety Professional to meet me at the emergency room. Once at the Emergency room Fuel Supply Manager and Sooner Safety Professional assessed the injury visually and then had a conference call with Director to ensure Member2 was going to be okay and make sure OGE Workman Comp official was notified of the injury to get paperwork started for the injured member. Member2 was treated and released at approximately 2120 at which time Fuel Supply Manager drove member to Walgreens for prescription medication and FS MGR got his prescriptions filled. At approximately 2300 Member2 was safely driven home and arrived at approximately 2300 to his family. Investigation Details of June 12, 2019: At approximately 1830 Member1 took the path of starting at #1 tripper, and Member2 took the path of #2 tripper where they would meet up at the Surge Bin Feeders Just below the Surge Bin (see Attachment Pics “Surge Bin Overview” and “Surge Bin Feeders”). Member1 got to the feeders just prior to Member2 and noticed two rollers on the North side of Surge Bin Feeder “D” not moving due to coal build-up between the two rollers while the belt was running (see attachment pic “Surge Bin Feeder D”). Member1 did not want to leave this situation alone due to the friction that could develop between the rollers and belt which could possibly get too hot over time creating a hot spot or fire over time. Member1 began removing the coal at the bottom side of rollers (see attachment pic “Member1 path to remove coal”), hoping the coal would collapse causing the rollers to become free and begin moving. During this time Member2 came up and observed what member1 was doing. It became apparent to member1 that the coal was not going to collapse between the rollers so he turned away to retrieve a piece of conduit just a few steps away so he could remove coal in a more safe manner. By the time he picked up the conduit he heard member2 yell and he immediately went to member2 to see what happened. Member2 had tried to remove the remaining coal using his hand at a much higher approach at the actual roller height level very close to the moving belt. During this time of attempting to remove the coal Member2 stuck his hand in to access coal between the two rollers at which time the pinky finger of his glove (right hand) got pulled in between the roller and belt (see attachment pic “Member2 path to remove coal”). Member2 was able to get hand removed but was bleeding very badly. At approximately 1855 Member1 escorted Member2 from the boiler down to the truck where he was driven to the coal yard to meet up with the Fuel Supply Foreman. At approximately 1905 Fuel Supply Foreman immediately notified the Operations SS that he was taking his member to the emergency room in Stillwater. Sooner Rescue team member that was on same shift was notified at approximately 2100 to take action in cleaning up the blood trail in accordance with the Blood Borne Pathogen procedure. At approximately 2200 the Fuel Supply Foreman and Fuel Supply Member were notified to write written statements of this event. On Friday June 14, 2019 the Fuel Supply Manager went to the Fuel Supply members home to get his statement of the event. All has been attached to this incident. Factors that contributed to this Injury based on the investigation some related to the corrective actions: **Member used his hand to remove coal by hand while Conveyor was in operation. **Members right hand pinky finger had tendons cut from a prior injury not allowing him to bend finger which contributed to finger sticking out rather than bending downward while removing coal between rollers. **SWP does not mention not to stay out of danger zone of Conveyor. **Coal build up due to wet coal. **Coal build up normally removed using Service Water, there was no Service Water due to a LOTO on the Service water for Conveyor 11. **No tool(s) for removing coal between rollers other than using water. **No procedure to prevent members from putting hands in the danger zone of a conveyor. **No training for members pertaining to what is acceptable behavior for cleaning conveyors, simply based on common knowledge of what we all think is safe behavior and risk tolerance (can vary from member to member). Attached is a cause diagram of this injury. | Brady Sowell | Glen Hughes | FALSE | Sooner Power Plant | FALSE |  | FALSE | Fuel Supply |  | Joe Parker | Glen Hughes |  | Kent Wilson | Approved | Kent Wilson | Jesse Murray | High | [13 empty] | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | No procedure exists for removing coal build up on Coal Conveying systems | 17. Failure to Identify Hazard, Risk | 5. Caught In (Pinch and Nip Points) | Added immediate corrective action for identifying the straw man document to be put in effect immediately for Sooner, Muskogee, and River Valley. Approved Jesse Murray | See member injury sub-incident for statements and interview summary. This information was moved to the "Private Document Attachment" in order to protect members personal information. Approved by Brady Sowell on 6/24/2019 | [24 empty] | FALSE |  | Job Transfer or Restriction (I) | 2016-11-07 | 1985-04-18 |  | 2019-06-12 18:00 | 0 | 78 |  | FALSE |  | Member was trying to remove coal between rollers and his hand got caught between the roller and conveyor belt while belt was in operation. |  | FALSE | Bradly Leniger |  | Days Away from Work | Bradly Leniger | TRUE |  | Stillwater Medical Center | Dr. Tanner, ER doctor attending. | Laceration |  | TRUE |  | Fuel Supply Tech I | Hand | Injury | Right | TRUE | Jon Leatherman | TRUE | 2019 | 6/12/2019 6:00:00 PM | 2 years | TRUE | FALSE | TRUE | Combination of moving Conveyor Belt and Roller. | Member had just started the process of walking down the conveyor belt systems. | [24 empty] | xxxxxxx
8895 | Sooner Power Plant | 2019-06-12 18:45 | Member got hand caught in Feeder Belt Conveyor while belt was in operation. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Jesse, I have the following members for the investigation team for Bradley Leniger’s recordable Injury that occurred last night, it is my understanding that you will officially make the assignment: Lead: Glen Hughes Pier Supervisor: Scott Ferguson Fuel Supply Member From MK: Rodney Hyslope Glen Hughes Manager of Plant Fuel Supply Sooner Generating Station | 2019-06-13 12:55 | Power Supply | Glen Hughes | 2019-07-16 17:29 | 2019-06-13 09:29 | 2019-06-13 09:29 | 2019-06-24 07:33 | 2019-06-26 18:45 | 2019-06-12 19:00 | 2019-06-26 09:02 | 2019-07-14 12:43 | 2019-06-24 12:54 | Sooner PP Unit 2 Surge Bin Feeder |  |  | Donnie Jones | Approved - Donnie Jones | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Glen Hughes |  | Member Injury overview and timeline Summary: On Wednesday June 12, 2019 a SoonerPP Fuel Supply Member was injured at approximately 1845 just after shift change. Two Fuel Supply members had just started the routine task of walking the belts and were at the Surge Bin Feeders. Member1 noticed that there were two rollers not moving due to coal build up. Member1 start removing the coal at the bottom side at the feeder belt bed. Member2 was observing this, Member1 turned around to retrieve a piece of conduit to remove the remaining coal. During this very short period of time Member2 began trying to remove the same coal from a different approach height with his hand, while trying to remove some more coal between the two rollers his pinky finger part of his glove somehow got between the moving belt and roller and his hand got immediately pulled between the belt and roller. Member1 heard member2 yell and immediately went to find out what had happened. Member2 still had his glove on and removed it from his hand to see how bad he was hurt. Member1 immediately saw the amount of blood coming his hand and escorted member2 back to the Coal Yard where they met with the Fuel Supply Foreman. The Fuel Supply Foreman immediately got him in the truck and called the Operation SS notifying him of the injury and was taking him directly to the emergency room at Stillwater, OK. The Operation SS immediately notified the Fuel Supply Manager of Member2 being transported to the emergency room in Stillwater. Fuel Supply Manager then called Director of SoonerPP to inform him he was leaving home to drive to emergency room. Director then called SoonerPP Safety Professional to meet me at the emergency room. Once at the Emergency room Fuel Supply Manager and Sooner Safety Professional assessed the injury visually and then had a conference call with Director to ensure Member2 was going to be okay and make sure OGE Workman Comp official was notified of the injury to get paperwork started for the injured member. Member2 was treated and released at approximately 2120 at which time Fuel Supply Manager drove member to Walgreens for prescription medication and FS MGR got his prescriptions filled. At approximately 2300 Member2 was safely driven home and arrived at approximately 2300 to his family. Investigation Details of June 12, 2019: At approximately 1830 Member1 took the path of starting at #1 tripper, and Member2 took the path of #2 tripper where they would meet up at the Surge Bin Feeders Just below the Surge Bin (see Attachment Pics “Surge Bin Overview” and “Surge Bin Feeders”). Member1 got to the feeders just prior to Member2 and noticed two rollers on the North side of Surge Bin Feeder “D” not moving due to coal build-up between the two rollers while the belt was running (see attachment pic “Surge Bin Feeder D”). Member1 did not want to leave this situation alone due to the friction that could develop between the rollers and belt which could possibly get too hot over time creating a hot spot or fire over time. Member1 began removing the coal at the bottom side of rollers (see attachment pic “Member1 path to remove coal”), hoping the coal would collapse causing the rollers to become free and begin moving. During this time Member2 came up and observed what member1 was doing. It became apparent to member1 that the coal was not going to collapse between the rollers so he turned away to retrieve a piece of conduit just a few steps away so he could remove coal in a more safe manner. By the time he picked up the conduit he heard member2 yell and he immediately went to member2 to see what happened. Member2 had tried to remove the remaining coal using his hand at a much higher approach at the actual roller height level very close to the moving belt. During this time of attempting to remove the coal Member2 stuck his hand in to access coal between the two rollers at which time the pinky finger of his glove (right hand) got pulled in between the roller and belt (see attachment pic “Member2 path to remove coal”). Member2 was able to get hand removed but was bleeding very badly. At approximately 1855 Member1 escorted Member2 from the boiler down to the truck where he was driven to the coal yard to meet up with the Fuel Supply Foreman. At approximately 1905 Fuel Supply Foreman immediately notified the Operations SS that he was taking his member to the emergency room in Stillwater. Sooner Rescue team member that was on same shift was notified at approximately 2100 to take action in cleaning up the blood trail in accordance with the Blood Borne Pathogen procedure. At approximately 2200 the Fuel Supply Foreman and Fuel Supply Member were notified to write written statements of this event. On Friday June 14, 2019 the Fuel Supply Manager went to the Fuel Supply members home to get his statement of the event. All has been attached to this incident. Factors that contributed to this Injury based on the investigation some related to the corrective actions: **Member used his hand to remove coal by hand while Conveyor was in operation. **Members right hand pinky finger had tendons cut from a prior injury not allowing him to bend finger which contributed to finger sticking out rather than bending downward while removing coal between rollers. **SWP does not mention not to stay out of danger zone of Conveyor. **Coal build up due to wet coal. **Coal build up normally removed using Service Water, there was no Service Water due to a LOTO on the Service water for Conveyor 11. **No tool(s) for removing coal between rollers other than using water. **No procedure to prevent members from putting hands in the danger zone of a conveyor. **No training for members pertaining to what is acceptable behavior for cleaning conveyors, simply based on common knowledge of what we all think is safe behavior and risk tolerance (can vary from member to member). Attached is a cause diagram of this injury. | Kevin Ferguson | Glen Hughes | FALSE | Sooner Power Plant | FALSE |  | FALSE | Fuel Supply |  | Joe Parker | Glen Hughes |  | Kent Wilson | Approved | Kent Wilson | Jesse Murray | High | [6 empty] | 7.13 Inadequate reinforcement of proper behavior |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Member had a high risk tolerance for cleaning coal on a running conveyor. | 17. Failure to Identify Hazard, Risk | 5. Caught In (Pinch and Nip Points) | Added immediate corrective action for identifying the straw man document to be put in effect immediately for Sooner, Muskogee, and River Valley. Approved Jesse Murray | See member injury sub-incident for statements and interview summary. This information was moved to the "Private Document Attachment" in order to protect members personal information. Approved by Brady Sowell on 6/24/2019 | [24 empty] | FALSE |  | Job Transfer or Restriction (I) | 2016-11-07 | 1985-04-18 |  | 2019-06-12 18:00 | 0 | 78 |  | FALSE |  | Member was trying to remove coal between rollers and his hand got caught between the roller and conveyor belt while belt was in operation. |  | FALSE | Bradly Leniger |  | Days Away from Work | Bradly Leniger | TRUE |  | Stillwater Medical Center | Dr. Tanner, ER doctor attending. | Laceration |  | TRUE |  | Fuel Supply Tech I | Hand | Injury | Right | TRUE | Jon Leatherman | TRUE | 2019 | 6/12/2019 6:00:00 PM | 2 years | TRUE | FALSE | TRUE | Combination of moving Conveyor Belt and Roller. | Member had just started the process of walking down the conveyor belt systems. | [24 empty] | xxxxxxx
8895 | Sooner Power Plant | 2019-06-12 18:45 | Member got hand caught in Feeder Belt Conveyor while belt was in operation. | Level 3 |  | FALSE | Member Injury | Donnie Jones | Jesse Murray | Jesse, I have the following members for the investigation team for Bradley Leniger’s recordable Injury that occurred last night, it is my understanding that you will officially make the assignment: Lead: Glen Hughes Pier Supervisor: Scott Ferguson Fuel Supply Member From MK: Rodney Hyslope Glen Hughes Manager of Plant Fuel Supply Sooner Generating Station | 2019-06-13 12:55 | Power Supply | Glen Hughes | 2019-07-16 17:29 | 2019-06-13 09:29 | 2019-06-13 09:29 | 2019-06-24 07:33 | 2019-06-26 18:45 | 2019-06-12 19:00 | 2019-06-26 09:02 | 2019-07-14 12:43 | 2019-06-24 12:54 | Sooner PP Unit 2 Surge Bin Feeder |  |  | Donnie Jones | Approved - Donnie Jones | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Glen Hughes |  | Member Injury overview and timeline Summary: On Wednesday June 12, 2019 a SoonerPP Fuel Supply Member was injured at approximately 1845 just after shift change. Two Fuel Supply members had just started the routine task of walking the belts and were at the Surge Bin Feeders. Member1 noticed that there were two rollers not moving due to coal build up. Member1 start removing the coal at the bottom side at the feeder belt bed. Member2 was observing this, Member1 turned around to retrieve a piece of conduit to remove the remaining coal. During this very short period of time Member2 began trying to remove the same coal from a different approach height with his hand, while trying to remove some more coal between the two rollers his pinky finger part of his glove somehow got between the moving belt and roller and his hand got immediately pulled between the belt and roller. Member1 heard member2 yell and immediately went to find out what had happened. Member2 still had his glove on and removed it from his hand to see how bad he was hurt. Member1 immediately saw the amount of blood coming his hand and escorted member2 back to the Coal Yard where they met with the Fuel Supply Foreman. The Fuel Supply Foreman immediately got him in the truck and called the Operation SS notifying him of the injury and was taking him directly to the emergency room at Stillwater, OK. The Operation SS immediately notified the Fuel Supply Manager of Member2 being transported to the emergency room in Stillwater. Fuel Supply Manager then called Director of SoonerPP to inform him he was leaving home to drive to emergency room. Director then called SoonerPP Safety Professional to meet me at the emergency room. Once at the Emergency room Fuel Supply Manager and Sooner Safety Professional assessed the injury visually and then had a conference call with Director to ensure Member2 was going to be okay and make sure OGE Workman Comp official was notified of the injury to get paperwork started for the injured member. Member2 was treated and released at approximately 2120 at which time Fuel Supply Manager drove member to Walgreens for prescription medication and FS MGR got his prescriptions filled. At approximately 2300 Member2 was safely driven home and arrived at approximately 2300 to his family. Investigation Details of June 12, 2019: At approximately 1830 Member1 took the path of starting at #1 tripper, and Member2 took the path of #2 tripper where they would meet up at the Surge Bin Feeders Just below the Surge Bin (see Attachment Pics “Surge Bin Overview” and “Surge Bin Feeders”). Member1 got to the feeders just prior to Member2 and noticed two rollers on the North side of Surge Bin Feeder “D” not moving due to coal build-up between the two rollers while the belt was running (see attachment pic “Surge Bin Feeder D”). Member1 did not want to leave this situation alone due to the friction that could develop between the rollers and belt which could possibly get too hot over time creating a hot spot or fire over time. Member1 began removing the coal at the bottom side of rollers (see attachment pic “Member1 path to remove coal”), hoping the coal would collapse causing the rollers to become free and begin moving. During this time Member2 came up and observed what member1 was doing. It became apparent to member1 that the coal was not going to collapse between the rollers so he turned away to retrieve a piece of conduit just a few steps away so he could remove coal in a more safe manner. By the time he picked up the conduit he heard member2 yell and he immediately went to member2 to see what happened. Member2 had tried to remove the remaining coal using his hand at a much higher approach at the actual roller height level very close to the moving belt. During this time of attempting to remove the coal Member2 stuck his hand in to access coal between the two rollers at which time the pinky finger of his glove (right hand) got pulled in between the roller and belt (see attachment pic “Member2 path to remove coal”). Member2 was able to get hand removed but was bleeding very badly. At approximately 1855 Member1 escorted Member2 from the boiler down to the truck where he was driven to the coal yard to meet up with the Fuel Supply Foreman. At approximately 1905 Fuel Supply Foreman immediately notified the Operations SS that he was taking his member to the emergency room in Stillwater. Sooner Rescue team member that was on same shift was notified at approximately 2100 to take action in cleaning up the blood trail in accordance with the Blood Borne Pathogen procedure. At approximately 2200 the Fuel Supply Foreman and Fuel Supply Member were notified to write written statements of this event. On Friday June 14, 2019 the Fuel Supply Manager went to the Fuel Supply members home to get his statement of the event. All has been attached to this incident. Factors that contributed to this Injury based on the investigation some related to the corrective actions: **Member used his hand to remove coal by hand while Conveyor was in operation. **Members right hand pinky finger had tendons cut from a prior injury not allowing him to bend finger which contributed to finger sticking out rather than bending downward while removing coal between rollers. **SWP does not mention not to stay out of danger zone of Conveyor. **Coal build up due to wet coal. **Coal build up normally removed using Service Water, there was no Service Water due to a LOTO on the Service water for Conveyor 11. **No tool(s) for removing coal between rollers other than using water. **No procedure to prevent members from putting hands in the danger zone of a conveyor. **No training for members pertaining to what is acceptable behavior for cleaning conveyors, simply based on common knowledge of what we all think is safe behavior and risk tolerance (can vary from member to member). Attached is a cause diagram of this injury. | Kevin Ferguson | Glen Hughes | FALSE | Sooner Power Plant | FALSE |  | FALSE | Fuel Supply |  | Joe Parker | Glen Hughes |  | Kent Wilson | Approved | Kent Wilson | Jesse Murray | High | [13 empty] | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | No procedure exists for removing coal build up on Coal Conveying systems | 17. Failure to Identify Hazard, Risk | 5. Caught In (Pinch and Nip Points) | Added immediate corrective action for identifying the straw man document to be put in effect immediately for Sooner, Muskogee, and River Valley. Approved Jesse Murray | See member injury sub-incident for statements and interview summary. This information was moved to the "Private Document Attachment" in order to protect members personal information. Approved by Brady Sowell on 6/24/2019 | [24 empty] | FALSE |  | Job Transfer or Restriction (I) | 2016-11-07 | 1985-04-18 |  | 2019-06-12 18:00 | 0 | 78 |  | FALSE |  | Member was trying to remove coal between rollers and his hand got caught between the roller and conveyor belt while belt was in operation. |  | FALSE | Bradly Leniger |  | Days Away from Work | Bradly Leniger | TRUE |  | Stillwater Medical Center | Dr. Tanner, ER doctor attending. | Laceration |  | TRUE |  | Fuel Supply Tech I | Hand | Injury | Right | TRUE | Jon Leatherman | TRUE | 2019 | 6/12/2019 6:00:00 PM | 2 years | TRUE | FALSE | TRUE | Combination of moving Conveyor Belt and Roller. | Member had just started the process of walking down the conveyor belt systems. | [24 empty] | xxxxxxx
8896 | Horseshoe Lake Power Plant | 2019-06-12 13:00 | A feedwater LOTO was returned by members and it was noticed that work being performed under that LOTO was not completed. No member injuries occurred. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Jon Harriet | 2019-07-14 12:59 | 2019-06-13 11:45 | 2019-06-13 11:45 | 2019-07-05 10:16 | 2019-06-26 13:00 | 2019-06-13 10:54 | 2019-07-05 15:16 |  | 2019-07-05 10:17 | Horseshoe Lake Unit 6 chemical sample panel. |  |  | Jesse Murray | Approved Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Guillermo Sarmiento |  | A LOTO was issued on unit 6 feed water in order to fix a tube leak. During the course of this job, maintenance also began work on unit 6 sample line. This project consisted of removing and installing an isolation valve. A hot work and safe work permit were filled out for all jobs. Members working on the sample line project were involved in multiple jobs and going back and forth from one job to the other. Member were also handling other jobs during the course of the day which also includes being plant contact for outage work on unit 8. At some point in time, members got called off the sample line job in order to help fix the tube leak on unit 6. Once the tube leak job was completed, members signed off the LOTO and returned it. During the course of un-tagging the returned LOTO, operations discovered that the sample line project was not completed. Operations finished un-tagging this LOTO. Maintenance foreman was contacted and informed of the incomplete project and was no longer under a LOTO. There was not any work ever performed that was not protected under a LOTO. A new LOTO was issued for the sample line project. Members signed onto the LOTO and proceeded to finish the sample line project. After it was finished, the LOTO for the sample line project was returned. Finding: • Members were involved in multiple jobs throughout the day. • Currently multiple jobs can be performed under a blanket LOTO but each job is not formally tracked. • Work was not performed on the sample line project without an active LOTO. • The PAE for the feed water LOTO did place a lock on the lock box in the LOTO room. • All required documentation was filled out (SWP, LOTO, Hot Work, Confined Space, and etc.) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Maintenance |  | Jon Harriet | Jon Harriet |  | Daniel Perry | I think we need to engage the mechanical foreman and discuss corrective actions for the members involved around reviewing the feedwater system and LOTO procedures. I have reviewed the updated investigation and I approve. DLP 7/5/19. | Daniel Perry |  | Medium | [15 empty] | 16.06 Inadequate communication methods | One of the two jobs under a LOTO was not completed and LOTO was returned. | 20. Failure to Communicate, Coordinate | 2. Struck By (Hit By Moving Object) |  | Have reviewed and agree with the findings and corrective actions. | [90 empty] | TBD
8897 | Horseshoe Lake Power Plant | 2019-06-13 11:30 | While returning a LOTO on the seal oil coolers we found a cable lock, lock, and tag laying on the ground. The valve was found still isolated but not locked and tagged out. It appears that the crimp failed at the anchor on the cable lock. The system was still de-energized at the time. No injuries occurred. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Jon Harriet | 2019-07-14 13:01 | 2019-06-13 14:50 | 2019-06-13 14:50 | 2019-06-21 03:00 | 2019-06-27 11:30 | 2019-06-13 14:24 | 2019-07-02 11:32 |  | 2019-06-24 07:15 | Horseshoe Lake Unit 8 seal oil system |  |  | Jesse Murray | Approved Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Jon Harriet |  | On June 13th at approximately 1330 hours, while returning a LOTO on the Unit 8 seal oil coolers, members identified a boundary valve but the lock and tag were not on it. They then saw the cable lock, lock and danger tag lying on the ground about two feet away from the boundary location. Members immediately stopped the LOTO return process and notified the Operations Foreman. The Operations Foreman checked the valve to be in the closed position, which was the correct position for the LOTO to control hazardous energy. Upon inspection of the cable locking device, the cable had pulled out of the crimped anchor point. There was not any sign of damage on the coating of the cable or to the cable. The PAE was then contacted to help investigate what had occurred. The PAE went and spoke with Siemens Members and the Operations Foreman contacted the OGE Special Services Members who had worked under that LOTO. The Siemens Members said they had seen the device lying on the ground under the valve about three weeks prior and placed it back on the valve. The OGE Special Services Member said that he had installed a new drain on the cooler right by the valve and the device was still on the valve then. The Ops Foreman then spoke to the TFC group who was getting ready to perform the oil flush on the system. One of their members stated that the cable, lock, and tag was laying under the valve on the ground and he had kicked it while working in the area. The LOTO had been in place since March 26, 2019 and the device was noticed to be off and broken but wasn't reported as it should have been. The Ops Foreman stopped work with both the Siemens and TFC Members and communicated the importance of reporting to their plant contact or to operations if they see a boundary device laying on the ground or damaged in any way. With the boundary device off, workers may be at risk and no longer be protected by the LOTO. Ops Foreman was asked to cover this with every crew and formally document it on their tail gate safety meetings. It appears that the cable lock failed and was not tampered with. Findings: • Cable appears to have slipped out of the locking portion of the device. • Cable lock did not have any evidence of tampering therefore it is not believe that it was removed intentionally. • Contract members noticed the device on the ground but did not report it to OGE. • System was fully isolated due therefore no hazardous energy was present at any part of the system. • The valve in question was in the closed position therefore it is not believe that it was tampered with. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Operations |  | Raymond Davis Jr | Jon Harriet |  | Michael Kennedy | I approve to continue with action items. | Michael Kennedy |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [10 empty] | 16.04 Inadequate communication between work groups | A boundary device failed and was not reported when noticed. | 16. Failure to Follow Procedure, Policy, Practice | 12. Equipment Failure |  | Have reviewed and made some changes with Jon's approval. Approved to move forward. | [90 empty] | NA
8898 | North Service Center | 2019-06-13 12:00 | Company vehicle travelling south bound on highway 74 at county road 76 struck public vehicle. | Level 4 |  | FALSE | Vehicle |  | Jerrod Moser | Investigation is to be conducted by the direction of counsel. | 2019-06-14 15:24 | Power Delivery | Jeffrey Warner | 2019-07-22 13:46 | 2019-06-13 15:57 | 2019-06-13 15:57 | 2019-07-09 15:57 | 2019-08-02 | 2019-06-13 15:45 | 2019-07-18 11:54 |  |  | Company Vehicle travelling south bound on highway 74 struck public vehicle |  |  | Jerrod Moser | Approve | T&D Ops |  | Level 4 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Lindle Coleman |  | At the time of the incident, June 13, 2019, 12pm, it was a clear, dry, sunny day. Streets were in proper repair and good condition. Weather conditions were not a factor. Company vehicle travelling south bound on highway 74 at county road 76 struck public vehicle from behind. Public vehicle was traveling south on state highway 74 approaching county road 76. Public vehicle driver stated that they were turning west onto county road. Company vehicle driver stated he did not see any taillights, brake lights or turn signals and did not realize public vehicle was turning to the West, he thought public vehicle was turning to the East due to the public vehicle veering that direction. Company member stated trailer gate and lawnmower blocked public vehicle taillights and made them difficult to see. As public vehicle changed direction and started turning to the West Company vehicle attempted to avoid public driver by veering to the right however company vehicle overtook the public vehicle and made contact. both vehicles went off the road way and came to rest in the ditch. Both vehicles had to be towed from the scene. Company members were not injured. Three public persons involved. Two of the public persons requested transportation to hospital to get checked out, third public person did not request transportation to hospital. Police were called and investigated incident, report attached for details of incident. Supervisor was notified and responded to scene and escorted the company member for post incident testing. Company driver has valid CDL and health certificate, has attended defensive driver training on June 5, 2019. Post incident testing verified no presence of drugs or alcohol. Telemetries showed proper speeds at the time of the incident. Members stated they were wearing their seatbelts. Company vehicle was found to be in proper operating condition, based on proper maintenance and inspection records. Pictures attached and it is noted that the public trailer lights were not plugged into the public vehicle (Truck). Additional Information not related to causal factors was that the daily Driver Vehicle Inspection Report (DVIR) was not completed. It is estimated that damage to company vehicle will be $20, 000 for company repairs. Company vehicle is not considered totaled and will be repairable. Other costs of incident unknown at this time. Attached: Police report, copy of citation, pictures of incident scene, telemetric for the day, telemetric report for May 2019, vehicle repair and maintenance log, driver training records, driver information. | Mark Martin | Lindle Coleman |  | North Service Center | TRUE |  | FALSE | Construction Services |  | Shawn Hill | Jeffrey Warner |  |  | Approve |  |  | Very High |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Needed to apply defensive driving techniques of getting the big picture of the road ahead and maintaining good following distances | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) | [74 empty] | TRUE |  | Crescent | OGE Vehicle Struck Other Vehicle | Both Vehicles Moving | 2018-09-04 19:00 |  | TRUE |  |  | Day Light | 0 | 0 | Asphalt |  | Clear | TRUE | FALSE
8898 | North Service Center | 2019-06-13 12:00 | Company vehicle travelling south bound on highway 74 at county road 76 struck public vehicle. | Level 4 |  | FALSE | Vehicle |  | Jerrod Moser | Investigation is to be conducted by the direction of counsel. | 2019-06-14 15:24 | Power Delivery | Jeffrey Warner | 2019-07-22 13:46 | 2019-06-13 15:57 | 2019-06-13 15:57 | 2019-07-09 15:57 | 2019-08-02 | 2019-06-13 15:45 | 2019-07-18 11:54 |  |  | Company Vehicle travelling south bound on highway 74 struck public vehicle |  |  | Jerrod Moser | Approve | T&D Ops |  | Level 4 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Lindle Coleman |  | At the time of the incident, June 13, 2019, 12pm, it was a clear, dry, sunny day. Streets were in proper repair and good condition. Weather conditions were not a factor. Company vehicle travelling south bound on highway 74 at county road 76 struck public vehicle from behind. Public vehicle was traveling south on state highway 74 approaching county road 76. Public vehicle driver stated that they were turning west onto county road. Company vehicle driver stated he did not see any taillights, brake lights or turn signals and did not realize public vehicle was turning to the West, he thought public vehicle was turning to the East due to the public vehicle veering that direction. Company member stated trailer gate and lawnmower blocked public vehicle taillights and made them difficult to see. As public vehicle changed direction and started turning to the West Company vehicle attempted to avoid public driver by veering to the right however company vehicle overtook the public vehicle and made contact. both vehicles went off the road way and came to rest in the ditch. Both vehicles had to be towed from the scene. Company members were not injured. Three public persons involved. Two of the public persons requested transportation to hospital to get checked out, third public person did not request transportation to hospital. Police were called and investigated incident, report attached for details of incident. Supervisor was notified and responded to scene and escorted the company member for post incident testing. Company driver has valid CDL and health certificate, has attended defensive driver training on June 5, 2019. Post incident testing verified no presence of drugs or alcohol. Telemetries showed proper speeds at the time of the incident. Members stated they were wearing their seatbelts. Company vehicle was found to be in proper operating condition, based on proper maintenance and inspection records. Pictures attached and it is noted that the public trailer lights were not plugged into the public vehicle (Truck). Additional Information not related to causal factors was that the daily Driver Vehicle Inspection Report (DVIR) was not completed. It is estimated that damage to company vehicle will be $20, 000 for company repairs. Company vehicle is not considered totaled and will be repairable. Other costs of incident unknown at this time. Attached: Police report, copy of citation, pictures of incident scene, telemetric for the day, telemetric report for May 2019, vehicle repair and maintenance log, driver training records, driver information. | Luke Kennedy | Lindle Coleman |  | North Service Center | TRUE |  | FALSE | Construction Services |  | Shawn Hill | Jeffrey Warner |  |  | Approve |  |  | Very High |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Needed to apply defensive driving techniques of getting the big picture of the road ahead and maintaining good following distances | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) | [74 empty] | TRUE |  | Crescent | OGE Vehicle Struck Other Vehicle | Both Vehicles Moving | 2018-09-04 19:00 |  | TRUE |  |  | Day Light | 0 | 0 | Asphalt |  | Clear | TRUE | FALSE
8899 | River Valley | 2019-06-13 09:30 | Moving a Hobart refractory mixer with a hand truck. When the contractor pulled the hand truck over, the load was top heavy and broke over faster than expected. He wasn’t ready for the weight of the mixer fell over and smashed his finger between the mixer and the hand truck. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Michael Smith | 2019-08-14 08:38 | 2019-06-13 18:04 | 2019-06-13 18:04 | 2019-06-27 19:20 | 2019-06-27 09:30 | 2019-06-13 10:00 | 2019-07-29 14:56 |  |  | River Valley PP Unit 1B Boiler ground level |  |  | Anthony Gillespie | Creation of and utilization of a lifting procedure for awkward loads such as a mixer should eliminate the worker exposure to a similar lift failure. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Michael Smith |  | Two R-tec employees were moving a Hobart mixer with a hand truck. When the contractor pulled the hand truck over, the load was top heavy and broke over faster than expected. He wasn’t ready for the weight and the mixer fell over smashing his finger between the mixer and the hand truck. |  |  |  | River Valley | FALSE |  | FALSE | Operations |  | James Lilley | Melton Morris |  | Timothy Chancellor | Agree with corrective action. Methodology for transporting this piece of equipment should be reviewed with contractor and new method developed. | Timothy Chancellor |  | Low | [9 empty] | 10.02 Inadequate consideration of human factors/ergonomics |  |  | 13.01 Inadequate assessment of needs and risks |  |  |  | The top heavy mixer overloaded the hand truck operator. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) | [5 empty] | Injury / Illness |  | Michael Smith |  | Smashed his finger | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | James Lilley | R-tec | Jose Flores | Crush/Smash |  | Finger | Michael Smith | Right | TRUE | Company Vehicle | [68 empty] | None
8899 | River Valley | 2019-06-13 09:30 | Moving a Hobart refractory mixer with a hand truck. When the contractor pulled the hand truck over, the load was top heavy and broke over faster than expected. He wasn’t ready for the weight of the mixer fell over and smashed his finger between the mixer and the hand truck. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Michael Smith | 2019-08-14 08:38 | 2019-06-13 18:04 | 2019-06-13 18:04 | 2019-06-27 19:20 | 2019-06-27 09:30 | 2019-06-13 10:00 | 2019-07-29 14:56 |  |  | River Valley PP Unit 1B Boiler ground level |  |  | Anthony Gillespie | Creation of and utilization of a lifting procedure for awkward loads such as a mixer should eliminate the worker exposure to a similar lift failure. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Michael Smith |  | Two R-tec employees were moving a Hobart mixer with a hand truck. When the contractor pulled the hand truck over, the load was top heavy and broke over faster than expected. He wasn’t ready for the weight and the mixer fell over smashing his finger between the mixer and the hand truck. |  |  |  | River Valley | FALSE |  | FALSE | Operations |  | James Lilley | Melton Morris |  | Timothy Chancellor | Agree with corrective action. Methodology for transporting this piece of equipment should be reviewed with contractor and new method developed. | Timothy Chancellor |  | Low | [9 empty] | 10.02 Inadequate consideration of human factors/ergonomics |  |  | 13.02 Inadequate human factors/ergonomics considerations |  |  |  | The top heavy mixer overloaded the hand truck operator. | 08. Improper Loading | 7. Caught Between or Under (Crushed or Amputated) | [5 empty] | Injury / Illness |  | Michael Smith |  | Smashed his finger | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | James Lilley | R-tec | Jose Flores | Crush/Smash |  | Finger | Michael Smith | Right | TRUE | Company Vehicle | [68 empty] | None
8900 | Muskogee Power Plant | 2019-05-21 01:00 | F03-1346 was backed into a fixed object. | Level 2 |  | FALSE | Vehicle |  |  |  |  | OG&E Corp Services | Paul George | 2019-08-06 09:25 | 2019-06-13 22:03 | 2019-06-13 22:03 | 2019-07-30 13:20 | 2019-06-04 | 2019-06-13 21:50 | 2019-07-31 05:26 |  | 2019-07-30 14:45 | Muskogee Power Plant |  |  | William Young | Not approved,7/5/19 Cody Vinyard. The description should not read in 1st person. Please replace all References to "I" with "The Supervisor of Security". The corrective action should read, The Supervisor of Security Will meet with the security guards about the requirements of backing found in SSOP 604.123 General Safety Requirements- Section 6.4 Vehicles. Document on Safety Meeting Minutes form 9000141. 8-6-2019: Reviewed report with Cody Vinyard. Discussed Immediate/Direct cause 31 regarding illumination. There is not a corresponding corrective action for this causal factor. Agreed with Cody to close incident and he will follow-up on the lighting. Will enter a separate CA for Cody to follow-up on this item. WCY. The Incident type needs to also have the Contractor box checked and Reference Global Security as the Contractor. Not Approved, 7/29/19 Cody Vinyard. See Previous Comments. | Enterprise Services |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Paul George |  | On 5/21/2019 I received a call from OGE member Jon Stogsdill who advised the Muskogee Power Plant is expecting major flooding which could start as early as 5/22/2019. The Security Supervisor drove to the Muskogee Power Plant the evening of 5/21/2019 after speaking to Jon The Security Supervisor met with 2 Global Security Guards Jason Jenkins, and Floyd Ryan who were at the main entry point. The Security Supervisor advised both of them the power was going to be cut off to the front gates, and water levels would make the plant inaccessible starting sometime on the 22nd. The Security Supervisor advised both the computer equipment needed to be turned off, disconnected and moved to the admin office to prevent damage. The computers were turned off at both entry points, disconnected and moved into the plant, along with several other items which was done using the OGE security vehicle F03-1346. On 6/5/2019 The Security Supervisor went back to the Muskogee Power Plant to look at the damage the flooding had done, and get temporary buildings set. During my time at the plant. The Security Supervisor spoke to Jason Jenkins and Floy Ryan who were both at the plant. Temporary buildings were established and the computer equipment that had been removed was brought back to the entry point by both Jenkins and Ryan On 6/6/2019 The Security Supervisor received information the rear bumper of the OGE vehicle had been damaged, which believed to have taken place on the evening of 5/21/2019 while the computer equipment was being moved. On 6/7/2019 The Security Supervisor received information that Jason Jenkins, which was one of the guards who moved the computer equipment had resigned and was not answering his phone. On 6/11/2019 The Security Supervisor went back to the Muskogee Power Plant and spoke to Floyd Ryan and to view the vehicle. Ryan told me Jenkins had told him he had backed into a pole with the vehicle, damaging the bumper while they were moving the computer equipment, and that he had notified a plant member, but never stated who he told. The Security Supervisor attempted to call Jenkins again, but my call was not answered. The Security Supervisor check the areas that I believed the vehicle would have traveled while the equipment was being moved. After checking several areas The Security Supervisor was not able to find anything that indicated the OGE security vehicle had backed into it. The damage to the vehicle was confined to the rear bumper, and a mark on the tailgate which appeared to be a light contact point, and appeared to be in line with the contact point on the bumper. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | Other |  | Paul George | Paul George |  | James Finch | All corrective action conducted; therefore, it is recommended this matter be closed. | James Finch |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Vehicle backed into fixed object. | 31. Inadequate or Excess Illumination | 1. Struck Against (Running or Bumping Into) |  | Approved, Cody Vinyard 7/30/19 | [72 empty] | TRUE |  | Ft Gibson | Struck Fixed Object | Backing Related |  |  | FALSE |  |  | Night |  |  | Other |  | Clear
8901 | Sooner Power Plant | 2019-06-16 11:00 | Member contacted a bollard protecting fire hydrant under the ash silos. Bollard was contacted with the bucket of a skid steer while cleaning up bottom ash. Bollard fell over. Skid steer has no damage. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Justin Johnson | 2019-07-08 07:20 | 2019-06-16 14:09 | 2019-06-16 14:09 | 2019-06-24 10:03 | 2019-06-30 11:00 | 2019-06-16 13:46 | 2019-07-01 08:57 |  |  | Ballard protecting fire hydrant under ash silos. |  |  | Brady Sowell | Approved by Brady Sowell | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Justin Johnson |  | Operations member was using a skid steer to remove bottom ash from below the silos. Member was driving in the forward direction when his bucket made contact with the bollard protecting the fire hydrant. Member didn't realize he was as close to the bollard as he was. Member reported that the he noticed the contact because the bollard fell over. Upon inspecting the bollard the outside steel pipe was corroded almost entirely through and the inner concrete also had signs of cracking. The plastic sleeve installed for visibility had a few dings from previous impacts as well. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Operations |  | Mark Welch | Justin Johnson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Low | [9 empty] | 10.02 Inadequate consideration of human factors/ergonomics | [6 empty] | Operations member was using a skid steer to remove bottom ash from below the silos. Member was driving in the forward direction when his bucket made contact with the bollard protecting the fire hydrant. Member didn't realize he was as close to the bollard as he was. Member reported that the he noticed the contact because the bollard fell over. Upon inspecting the bollard the outside steel pipe was corroded almost entirely through and the inner concrete also had signs of cracking. The plastic sleeve installed for visibility had a few dings from previous impacts as well. | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) | [68 empty] | Bollard fallen over, will need replaced. | 1000 | Mark Welch | Fixed Equipment | [20 empty] | 440567
8902 | Sooner Power Plant | 2019-06-16 11:00 | The Dumper Positioner contacted the second locomotive (#9532) on train #NR-036. | Level 3 |  | FALSE | Property Damage | Donnie Jones | Jesse Murray | Assigned per Donnie Jones | 2019-06-20 11:04 | Power Supply | Steven Wojcik | 2019-07-16 17:30 | 2019-06-16 15:51 | 2019-06-16 15:51 | 2019-06-26 19:05 | 2019-06-30 11:00 | 2019-06-16 15:19 | 2019-07-01 07:58 | 2019-07-14 12:51 | 2019-06-27 07:51 | Dumper Positioner |  |  | Donnie Jones | Approved - Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Glen Hughes |  | Incident Summary: On June 16 2019 at approx. 1100 two Fuel Supply Members were beginning the process of dumping Coal Train NR-036 in accordance with OI 327.112 “Initial Spotting and Unloading of Coal Trains”. Member1 and Member2 had pulled 1st train car in and dumped it. As they started to pull in second car using Train Engine Power, both Members heard a loud sound and looked out the window to see that the Positioning Arm had come down and contacted Train Engine 9532. Member1 immediately called the Train Engineer to stop the train since they were on engine power. Fuel Supply members assessed the damage and then called the Fuel Supply Manager. The Fuel Supply Manager instructed them to contact BNSF and Bill McNally of the incident, then call Sooner I&C member to come to the plant to determine if there was something wrong with the logic, that caused the Positioner Arm to inadvertently go down when it was not supposed to. I&C member analyzed the logic and could not determine the cause. Fuel Supply Members then continued to dump the train without further incident. Incident Team Investigation: On June 16, 2019 at approximately 1100 two Fuel Supply Members were beginning to dump Train NR-036 in accordance with SOP. Member1 was operating the controls in the Dumper Control Room and had pulled the 1st train car in using Train Engine Power and dumped it. As they started to pull in second car via train engine power, Member1 and Member2 heard a loud sound and looked out the window to see that the Positioning Arm had come down and contacted train engine (See Attached PICS “Positioner Arm inside of Train Engine”, “Train Engine in the stopped position after leaving the Dumper”, “Damage to train engine from Positioner Arm after Removed”, “Damage Done Inside Train Engine Panel” ). Member1 immediately called the Train Engineer to have them stop the train since they were using Train Engine Power. Member1 then notified the Fuel Supply Foreman of the incident who was at the time pushing in reclaim coal with the dozer. Fuel Supply Foreman then assessed the damage and then called the Fuel Supply Manager. Fuel Supply manger then instructed the Foreman to contact BNSF and Bill McNally (OGE Coal and Rail Manager), then call SoonerPP I&C member to come and investigate the logic to determine the problem before proceeding any further in dumping the train. At approximately 1230 I&C member arrived at the plant and began analyzing the logic to determine what could have caused the dumper positioner arm to go down without a signal. After analyzing the logic there was nothing in the logic that indicated why the Positioner Arm went down. According to the logic when in “Manual Mode” for the Positioner and “Uncouple Car” for Train Mode to get the “OK to Dump” light prior to dumping the first two cars. The only way the positioner arm can come down is to press the following 3 buttons on two different screens: 1.) Positioner Setup Screen (see attached PIC “Dumper Setup Screen”) 2.) Positioner control Button on Positioner Setup Screen (see attached PIC “Positioner Setup Screen”) 3.) Raise and Lower Buttons on Positioner Setup Screen. (see attached PIC “Positioner Setup Screen for Arm raise and lower buttons”) Note: On the Positioner Screen, you have to hold down the button to “Lower” in order to lower it all the way. If you let go, it will stop moving, the same applies to the raise button. Once there was no evidence found by the I&C member of any logic issues Positioner tests were performed to see if the arm would come down without a command in the logic and also prove the logic was working correctly. At approximately 1410 Fuel Supply resumed dumping the train without any further incident. After further investigation by the Investigation Team we did explore the possibility of the arm going down on its own due to “Induced Voltage” causing a false signal to the Positioning Arm which could possibly cause arm to lower inadvertently, but we have no way of knowing this for a fact. The Team did however discuss what is needed to prevent this from occurring again by making changes to the sequence of events that must occur until a permanent change to the logic can be implemented (See Immediate Corrective Action 6982). The long term solution to the logic will eliminate human error or an Induced Voltage anomaly is identified in the following Corrective Actions 6978 and 6979. | Robert Williamson | Glen Hughes |  | Sooner Power Plant | FALSE |  | FALSE | Fuel Supply |  | Martin Schneeberger | Steven Wojcik |  | Kent Wilson | Approved | Kent Wilson | Jesse Murray | High | [9 empty] | 10.06 Inadequate or improper controls | [6 empty] | Dumper Positioner Arm randomly came down as Train Engine was passing by. The problem has been determined to be a control logic anomaly. | 38. Inadequate Communications Hardware, Software, Process | 12. Equipment Failure | Approved Jesse Murray | Approved by Brady Sowell on 6/27/2019 | [66 empty] | Damaged 3 inspection doors, a hand rail, and some mechanical parts inside. | 10000 | Martin Schneeberger | 3rd Party Property/Equipment |  | #9532 | [18 empty] | none
8902 | Sooner Power Plant | 2019-06-16 11:00 | The Dumper Positioner contacted the second locomotive (#9532) on train #NR-036. | Level 3 |  | FALSE | Property Damage | Donnie Jones | Jesse Murray | Assigned per Donnie Jones | 2019-06-20 11:04 | Power Supply | Steven Wojcik | 2019-07-16 17:30 | 2019-06-16 15:51 | 2019-06-16 15:51 | 2019-06-26 19:05 | 2019-06-30 11:00 | 2019-06-16 15:19 | 2019-07-01 07:58 | 2019-07-14 12:51 | 2019-06-27 07:51 | Dumper Positioner |  |  | Donnie Jones | Approved - Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Glen Hughes |  | Incident Summary: On June 16 2019 at approx. 1100 two Fuel Supply Members were beginning the process of dumping Coal Train NR-036 in accordance with OI 327.112 “Initial Spotting and Unloading of Coal Trains”. Member1 and Member2 had pulled 1st train car in and dumped it. As they started to pull in second car using Train Engine Power, both Members heard a loud sound and looked out the window to see that the Positioning Arm had come down and contacted Train Engine 9532. Member1 immediately called the Train Engineer to stop the train since they were on engine power. Fuel Supply members assessed the damage and then called the Fuel Supply Manager. The Fuel Supply Manager instructed them to contact BNSF and Bill McNally of the incident, then call Sooner I&C member to come to the plant to determine if there was something wrong with the logic, that caused the Positioner Arm to inadvertently go down when it was not supposed to. I&C member analyzed the logic and could not determine the cause. Fuel Supply Members then continued to dump the train without further incident. Incident Team Investigation: On June 16, 2019 at approximately 1100 two Fuel Supply Members were beginning to dump Train NR-036 in accordance with SOP. Member1 was operating the controls in the Dumper Control Room and had pulled the 1st train car in using Train Engine Power and dumped it. As they started to pull in second car via train engine power, Member1 and Member2 heard a loud sound and looked out the window to see that the Positioning Arm had come down and contacted train engine (See Attached PICS “Positioner Arm inside of Train Engine”, “Train Engine in the stopped position after leaving the Dumper”, “Damage to train engine from Positioner Arm after Removed”, “Damage Done Inside Train Engine Panel” ). Member1 immediately called the Train Engineer to have them stop the train since they were using Train Engine Power. Member1 then notified the Fuel Supply Foreman of the incident who was at the time pushing in reclaim coal with the dozer. Fuel Supply Foreman then assessed the damage and then called the Fuel Supply Manager. Fuel Supply manger then instructed the Foreman to contact BNSF and Bill McNally (OGE Coal and Rail Manager), then call SoonerPP I&C member to come and investigate the logic to determine the problem before proceeding any further in dumping the train. At approximately 1230 I&C member arrived at the plant and began analyzing the logic to determine what could have caused the dumper positioner arm to go down without a signal. After analyzing the logic there was nothing in the logic that indicated why the Positioner Arm went down. According to the logic when in “Manual Mode” for the Positioner and “Uncouple Car” for Train Mode to get the “OK to Dump” light prior to dumping the first two cars. The only way the positioner arm can come down is to press the following 3 buttons on two different screens: 1.) Positioner Setup Screen (see attached PIC “Dumper Setup Screen”) 2.) Positioner control Button on Positioner Setup Screen (see attached PIC “Positioner Setup Screen”) 3.) Raise and Lower Buttons on Positioner Setup Screen. (see attached PIC “Positioner Setup Screen for Arm raise and lower buttons”) Note: On the Positioner Screen, you have to hold down the button to “Lower” in order to lower it all the way. If you let go, it will stop moving, the same applies to the raise button. Once there was no evidence found by the I&C member of any logic issues Positioner tests were performed to see if the arm would come down without a command in the logic and also prove the logic was working correctly. At approximately 1410 Fuel Supply resumed dumping the train without any further incident. After further investigation by the Investigation Team we did explore the possibility of the arm going down on its own due to “Induced Voltage” causing a false signal to the Positioning Arm which could possibly cause arm to lower inadvertently, but we have no way of knowing this for a fact. The Team did however discuss what is needed to prevent this from occurring again by making changes to the sequence of events that must occur until a permanent change to the logic can be implemented (See Immediate Corrective Action 6982). The long term solution to the logic will eliminate human error or an Induced Voltage anomaly is identified in the following Corrective Actions 6978 and 6979. | Steven Wojcik | Glen Hughes |  | Sooner Power Plant | FALSE |  | FALSE | Fuel Supply |  | Martin Schneeberger | Steven Wojcik |  | Kent Wilson | Approved | Kent Wilson | Jesse Murray | High | [9 empty] | 10.06 Inadequate or improper controls | [6 empty] | Dumper Positioner Arm randomly came down as Train Engine was passing by. The problem has been determined to be a control logic anomaly. | 38. Inadequate Communications Hardware, Software, Process | 12. Equipment Failure | Approved Jesse Murray | Approved by Brady Sowell on 6/27/2019 | [66 empty] | Damaged 3 inspection doors, a hand rail, and some mechanical parts inside. | 10000 | Martin Schneeberger | 3rd Party Property/Equipment |  | #9532 | [18 empty] | none
8902 | Sooner Power Plant | 2019-06-16 11:00 | The Dumper Positioner contacted the second locomotive (#9532) on train #NR-036. | Level 3 |  | FALSE | Property Damage | Donnie Jones | Jesse Murray | Assigned per Donnie Jones | 2019-06-20 11:04 | Power Supply | Steven Wojcik | 2019-07-16 17:30 | 2019-06-16 15:51 | 2019-06-16 15:51 | 2019-06-26 19:05 | 2019-06-30 11:00 | 2019-06-16 15:19 | 2019-07-01 07:58 | 2019-07-14 12:51 | 2019-06-27 07:51 | Dumper Positioner |  |  | Donnie Jones | Approved - Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Glen Hughes |  | Incident Summary: On June 16 2019 at approx. 1100 two Fuel Supply Members were beginning the process of dumping Coal Train NR-036 in accordance with OI 327.112 “Initial Spotting and Unloading of Coal Trains”. Member1 and Member2 had pulled 1st train car in and dumped it. As they started to pull in second car using Train Engine Power, both Members heard a loud sound and looked out the window to see that the Positioning Arm had come down and contacted Train Engine 9532. Member1 immediately called the Train Engineer to stop the train since they were on engine power. Fuel Supply members assessed the damage and then called the Fuel Supply Manager. The Fuel Supply Manager instructed them to contact BNSF and Bill McNally of the incident, then call Sooner I&C member to come to the plant to determine if there was something wrong with the logic, that caused the Positioner Arm to inadvertently go down when it was not supposed to. I&C member analyzed the logic and could not determine the cause. Fuel Supply Members then continued to dump the train without further incident. Incident Team Investigation: On June 16, 2019 at approximately 1100 two Fuel Supply Members were beginning to dump Train NR-036 in accordance with SOP. Member1 was operating the controls in the Dumper Control Room and had pulled the 1st train car in using Train Engine Power and dumped it. As they started to pull in second car via train engine power, Member1 and Member2 heard a loud sound and looked out the window to see that the Positioning Arm had come down and contacted train engine (See Attached PICS “Positioner Arm inside of Train Engine”, “Train Engine in the stopped position after leaving the Dumper”, “Damage to train engine from Positioner Arm after Removed”, “Damage Done Inside Train Engine Panel” ). Member1 immediately called the Train Engineer to have them stop the train since they were using Train Engine Power. Member1 then notified the Fuel Supply Foreman of the incident who was at the time pushing in reclaim coal with the dozer. Fuel Supply Foreman then assessed the damage and then called the Fuel Supply Manager. Fuel Supply manger then instructed the Foreman to contact BNSF and Bill McNally (OGE Coal and Rail Manager), then call SoonerPP I&C member to come and investigate the logic to determine the problem before proceeding any further in dumping the train. At approximately 1230 I&C member arrived at the plant and began analyzing the logic to determine what could have caused the dumper positioner arm to go down without a signal. After analyzing the logic there was nothing in the logic that indicated why the Positioner Arm went down. According to the logic when in “Manual Mode” for the Positioner and “Uncouple Car” for Train Mode to get the “OK to Dump” light prior to dumping the first two cars. The only way the positioner arm can come down is to press the following 3 buttons on two different screens: 1.) Positioner Setup Screen (see attached PIC “Dumper Setup Screen”) 2.) Positioner control Button on Positioner Setup Screen (see attached PIC “Positioner Setup Screen”) 3.) Raise and Lower Buttons on Positioner Setup Screen. (see attached PIC “Positioner Setup Screen for Arm raise and lower buttons”) Note: On the Positioner Screen, you have to hold down the button to “Lower” in order to lower it all the way. If you let go, it will stop moving, the same applies to the raise button. Once there was no evidence found by the I&C member of any logic issues Positioner tests were performed to see if the arm would come down without a command in the logic and also prove the logic was working correctly. At approximately 1410 Fuel Supply resumed dumping the train without any further incident. After further investigation by the Investigation Team we did explore the possibility of the arm going down on its own due to “Induced Voltage” causing a false signal to the Positioning Arm which could possibly cause arm to lower inadvertently, but we have no way of knowing this for a fact. The Team did however discuss what is needed to prevent this from occurring again by making changes to the sequence of events that must occur until a permanent change to the logic can be implemented (See Immediate Corrective Action 6982). The long term solution to the logic will eliminate human error or an Induced Voltage anomaly is identified in the following Corrective Actions 6978 and 6979. | Brady Sowell | Glen Hughes |  | Sooner Power Plant | FALSE |  | FALSE | Fuel Supply |  | Martin Schneeberger | Steven Wojcik |  | Kent Wilson | Approved | Kent Wilson | Jesse Murray | High | [9 empty] | 10.06 Inadequate or improper controls | [6 empty] | Dumper Positioner Arm randomly came down as Train Engine was passing by. The problem has been determined to be a control logic anomaly. | 38. Inadequate Communications Hardware, Software, Process | 12. Equipment Failure | Approved Jesse Murray | Approved by Brady Sowell on 6/27/2019 | [66 empty] | Damaged 3 inspection doors, a hand rail, and some mechanical parts inside. | 10000 | Martin Schneeberger | 3rd Party Property/Equipment |  | #9532 | [18 empty] | none
8903 | Ardmore Service Center | 2019-06-17 09:00 | This is a First Aid Member was stung by red wasp | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Terry Looney | 2019-06-21 10:00 | 2019-06-17 15:43 | 2019-06-17 15:43 | 2019-06-17 15:55 | 2019-07-01 09:00 | 2019-06-17 09:15 |  |  |  | 1102 W Taliaferro |  |  | Brent Perdue | due to this being a first aid incident, the detailed description is in the Sub incident section. | T&D Ops |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | [5 empty] | FALSE | Ardmore Service Center | FALSE |  | FALSE | Construction Services |  | David Taylor | Terry Looney |  |  |  | Kenneth McKinzie |  | Low | [45 empty] | FALSE |  |  | 2015-07-13 | 1977-06-19 |  | 2019-06-17 07:00 | 0 | 0 | Member was stung on back of neck once and twice on his back. Member took two over the counter Benadryl. | FALSE |  | Member walked onto porch and knocked on door, there was no answer member turned to walk off of porch and was stung on back of neck once and twice on his back. |  | TRUE | David Taylor |  | First Aid | David Taylor |  |  |  |  | Allergic Reaction |  | FALSE |  | Area Service Technician | Neck |  |  |  | Terry Looney |  |  | 6/17/2019 7:00:00 AM | 4 years | FALSE |  |  | Red Wasp
8904 | Metro Service Center | 2019-06-12 18:30 | Member was in Ponca eating diner, when he came out and did his vehicle 360, he noticed there was some damage under the passenger side tail light above the bumper. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Delivery | Jimmy Combs | 2019-06-18 14:39 | 2019-06-18 06:50 | 2019-06-18 06:50 | 2019-06-18 07:19 | 2019-06-26 18:30 | 2019-06-13 08:00 | 2019-06-18 13:34 |  |  | Damage noticed at restaurant parking lot in Ponca City |  |  | Cody Magby | approved and agree with Gary. Try to avoid crowded parking lots as much as possible and stay towards perimeter cm | T&D Ops |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Jimmy Combs |  | Discussing incident with the member he said he pulled through a double spot to avoid backing. He ate dinner and came out and did his 360, this is when he noticed the damage. Proceeded to drive across the street to pick up some material. He notified his supervisor of the damage |  |  |  | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Darran Johnson | Jimmy Combs |  | Gary Lassley | If possible try to park the vehicle in a less crowded area, and try to park where you have a view of the vehicle. | Gary Lassley |  | Low | [8 empty] | 9.06 Inadequate work planning or programming | [7 empty] | Crowded public parking lot | 24. Congestion or Restricted Action | 2. Struck By (Hit By Moving Object) | [68 empty] | Dent and scratch under passenger side rear tail light | 800 | Darran Johnson | Vehicle (not related to operation of vehicle) | [20 empty] | 1646810
8905 | Sooner Power Plant | 2019-06-18 10:30 | Contractor was delivering a load of gravel to Sooner EVAP Pond and ran over suction hose to pump and two cones used to mark the hose. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Matthew Cox | 2019-07-01 08:30 | 2019-06-18 15:58 | 2019-06-18 15:58 | 2019-06-18 17:07 | 2019-07-02 10:30 | 2019-06-18 10:30 | 2019-06-21 11:49 |  |  | South end of road on EVAP Pond dam. |  |  | Chrysty Dorsey | Approved. | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Matthew Cox |  | On the morning of 6/18/2019 member met with Evan's Constructions at Sooner PP to have them deliver gravel to the EVAP Pond. Member instructed driver to follow him to the area they wish to have the gravel dumped. He informed the driver of a tight spot where pumps were placed on one side of the road and a guard rail on the other, and that he would park and come back and spot for him going in so he would not hit anything. Upon parking and exiting the vehicle member noticed the driver continuing on though the tight spot. Member tried to stop driver, but could not get his attention as he was looking in his mirror. Driver then ran over two of the cones used to mark the pump and hoses and the edge of the hose with his trailer. The hose is a suction hose and has wire inside to prevent it from collapsing under suction. When it was ran over it deformed some of the wires, but did not puncture the hose. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Special Services |  | Tommy Deaton | Matthew Cox |  | Kelly Casey | Reviewed with members expectations be clear to contractors and removal of hazards. | Kelly Casey |  | Low | [15 empty] | 16.06 Inadequate communication methods | Congested road and driver not waiting for spotter | 02. Failure to Warn | 1. Struck Against (Running or Bumping Into) | [68 empty] | Hose pinched on one side and bent the wire on the inside. Hose shows no sign of leaking. | 500 | Contractor | 3rd Party Property/Equipment | [20 empty] | 9583281
8906 | Metro Service Center | 2019-06-16 | On 6 /16/2019 during and circuit outage caused by a Cable failure on an underground feeder dip at Tulsa Substation circuit 3924; it was discovered the 3923T motor operated switch was in an unknown and abnormal state. The 3923T motor operated switch was found to be switch closed and Motor open and disengaged, the SCADA indication showed the switch to be in an open state. The correct status of this switch should have been switches open motor open and engaged. Due to this unknown configuration this caused an unnecessary outage on an adjacent circuit during a circuit outage. | Level 3 |  | FALSE | System Operational Incident |  | Lindle Coleman | Lead Assigned after discussion with operation leaders. Others to be assigned as needed based on Lead request to safety | 2019-06-21 14:35 | Power Delivery | Douglas Mack | 2019-08-20 08:16 | 2019-06-18 16:41 |  | 2019-07-29 06:49 | 2019-07-28 | 2019-06-18 16:26 | 2019-08-05 16:20 | 2019-08-06 14:36 | 2019-08-01 14:11 | DCC/ Tulsa Substation |  |  |  | Approve | T&D Ops |  | Level 3 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Jeffrey Uhls |  | Operational Incident Summary On Sunday, 6/16/2019 the 12.5kv Tulsa 3924 circuit locked out due to a fault on an underground cable between Riser 6972 and Riser 6973. At the same time the 12.5kv Tulsa 3923 circuit locked out. An abnormal circuit configuration at the substation was discovered that tied the 3924 and 3923 circuits together. The 3924T switch is a normally closed switch and the 3923T MOS switch is a normally open switch. Upon arrival to the substation a substation technician discovered switch 3923T was in the closed position with the motor mechanism disengaged in the open position. This abnormal condition tied the two circuits together through the transfer bus which resulted in both PCR 3923 and PCR 3924 tripping for the fault on the 3924 circuit. Chain of Events: • On Thursday, 6/13/2019 the exit feeder on the 12.5kv Tulsa 3923 circuit faulted, PCR 3923 locked out as a result. o Switching was conducted by a substation technician to isolate the faulted exist feeder on SWO M0966.  The 12.5kv Tulsa 3923 load was picked up on the 12.5kv Tulsa 3922 circuit by closing NO switch 7008.  The 3923RD and 3923L were opened and Danger Tagged. The 3923T MOS was verified opened, the motor mechanism disengaged, locked and Danger tagged. • On Friday, 6/14/2019 a North District line crew took a clearance from 3923L to 3923T to 3923RD to make repairs to the UG exit feeder. o The line crew was directed to remove the Danger Tags and place Hold Tags on the open boundaries and was then given a clearance to perform their work. o Repairs to the single faulted underground phase were completed, the line crew returned its clearance, and switching was directed to place the circuit back to normal on SWO M0966. • On Sunday, 6/16/2019 at approximately 9 pm there is a fault on the underground cable between Riser 6972 and Riser 6973 on the 3924 circuit. o Both the 3924 and the 3923 circuits locked out. o Bnk 1 had a transformer alarm - LTC 2 Beckwith Backup Control was in alarm. o The substation technician responding to the outage call discovered that the 3923T MOS switch blades were in the closed position while the motor mechanism was disengaged in the open position. • The substation technician informed the DCC operator of the abnormal state of switch 3923T and was directed to open the blades. o The switch blades on 3923T MOS were manually opened and the mechanism engaged placing it back in its normal state. • Switching was then conducted to close PCR 3923 and pick up the customer load on the circuit. • Bnk 1 LTC 2 Beckwith Control Panel was rest and placed back to its normal state of operation. • SWO M0981 was conducted to restore power to the customers on the 3924 circuit after the B/O underground cable section between Riser 6972 and Riser 6973 was isolated. | Cody Magby | Jeffrey Uhls |  | Metro Service Center | FALSE |  | FALSE | System Operations |  | Steven Genow | Douglas Mack |  | Dallas Rowley | I approve of this completed investigation along with all associated corrective actions. I appreciate all of the work and effort put forth and still to come in this learning opportunity! D. Rowley | Dallas Rowley | Lindle Coleman | High | [19 empty] | approved | reviewed and approve the cause and CAs cm
8907 | Seminole PP; EGX Gath/Trans | 2019-06-19 07:00 | High winds caused the intake crane to move. The crane pendant was broken and the hook caused damage to handrails on the circulating water pump motors. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Paul Schoelen | 2019-07-29 08:55 | 2019-06-19 13:15 | 2019-06-19 13:15 | 2019-07-08 10:36 | 2019-07-03 07:00 | 2019-06-19 07:00 | 2019-07-10 10:55 |  |  | Seminole PP intake structure |  |  | Chrysty Dorsey | Reviewed and approved | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Paul Schoelen |  | Plant electrician was working at the intake structure on the motor driven fire pump. He was using the crane to remove the motor cover. The member went to break and was then called away to work on SM2 turning gear motor. The member remained at the turning gear motor for the rest of his shift and did not return to the intake to finish the job. Overnight, storms moved through with 70 mph winds. The next morning the member came to work and noticed the crane had moved and damaged the handrails and equipment. During the interview the member stated he had worked at several locations throughout the day. He also stated that he had left his tools out at the intake jobsite overnight which is out of character for him. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | Maintenance |  | Robert Ensey | Paul Schoelen |  | Scott Lee | I approve this incident report. | Scott Lee |  | Low | [9 empty] | 10.03 Inadequate standards, specifications and/or design criteria | [6 empty] | The crane has never had a weather lock system installed. This system locks the crane when not in use to prevent it from moving in high winds. | 22. Inadequate or Improper Protective Equipment | 1. Struck Against (Running or Bumping Into) | [68 empty] | Handrails were bent and broken. Crane control pendant was broken. Motor filter bracket was bent. | 4000 | Robert Ensey | Fixed Equipment | [20 empty] | 9569065
8907 | Seminole PP; EGX Gath/Trans | 2019-06-19 07:00 | High winds caused the intake crane to move. The crane pendant was broken and the hook caused damage to handrails on the circulating water pump motors. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Paul Schoelen | 2019-07-29 08:55 | 2019-06-19 13:15 | 2019-06-19 13:15 | 2019-07-08 10:36 | 2019-07-03 07:00 | 2019-06-19 07:00 | 2019-07-10 10:55 |  |  | Seminole PP intake structure |  |  | Chrysty Dorsey | Reviewed and approved | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Paul Schoelen |  | Plant electrician was working at the intake structure on the motor driven fire pump. He was using the crane to remove the motor cover. The member went to break and was then called away to work on SM2 turning gear motor. The member remained at the turning gear motor for the rest of his shift and did not return to the intake to finish the job. Overnight, storms moved through with 70 mph winds. The next morning the member came to work and noticed the crane had moved and damaged the handrails and equipment. During the interview the member stated he had worked at several locations throughout the day. He also stated that he had left his tools out at the intake jobsite overnight which is out of character for him. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | Maintenance |  | Robert Ensey | Paul Schoelen |  | Scott Lee | I approve this incident report. | Scott Lee |  | Low |  |  | 3.03 Fatigue due to lack of rest | [13 empty] | Member failed to secure crane before leaving at end of shift. Current practice is to tie the crane off to the structure to prevent it from moving in high winds. | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) | [68 empty] | Handrails were bent and broken. Crane control pendant was broken. Motor filter bracket was bent. | 4000 | Robert Ensey | Fixed Equipment | [20 empty] | 9569065
8908 | Ft Smith Service Center | 2019-06-19 09:30 | This is a First Aid Report. Member was splicing overhead #4 service wire from the bucket. After completing the job, member felt discomfort in lower back. | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Sean Spicer | 2019-06-24 07:36 | 2019-06-19 13:53 | 2019-06-19 13:53 | 2019-06-20 11:32 | 2019-07-03 08:30 | 2019-06-19 13:33 |  |  |  | 9878 Hwy 64, Clarksville, Ar. |  |  | Hannah Everett | Member was evaluated the morning of 6/21/2019 and cleared for work. | T&D Ops |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | [5 empty] | FALSE | Ft Smith Service Center | FALSE |  | FALSE | Construction Services |  | Ronald Johnson | Sean Spicer |  |  |  | Charles Kolp |  | Low | [45 empty] | FALSE |  |  | 2016-02-22 | 1970-04-13 |  | 2019-06-19 07:00 | 0 | 0 |  | FALSE |  | Member was working from bucket, member was splicing #4 OH service. Member was using wooden handle crimpers. |  | FALSE | Ronald Johnson |  | First Aid | Ronald Johnson |  |  |  |  | Sprain/Strain |  | FALSE |  | Area Service Technician | Back |  |  | FALSE | Sean Spicer | FALSE |  | 6/19/2019 7:00:00 AM | 3 years | FALSE |  |  | Body position
8909 | Metro Service Center | 2019-06-19 09:00 | Company vehicle was struck by a bucket that fell off a private trailer. No injuries occurred. | Level 2 |  | FALSE | Property Damage |  |  |  |  | OGE Energy Corp | Alinor Wint | 2019-08-06 09:09 | 2019-06-20 14:32 | 2019-06-20 14:32 | 2019-07-10 16:01 | 2019-07-03 09:00 | 2019-06-20 14:17 | 2019-08-06 09:03 |  | 2019-07-17 10:18 | Exit 70 I-35 Pauls Valley, OK |  |  | William Young | Reviewed and approved. WCY 8-6-19 | Enterprise Services |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Terry Brown |  | Company vehicle was struck by a backhoe bucket that fell off a private trailer. Accident report from OHP is attached. |  |  |  | Metro Service Center | FALSE |  | FALSE | Real Estate |  | Jesse Perry | Alinor Wint |  | Vance Krebs | Approved , Vance Krebs 8/6/19 | Vance Krebs |  | Medium |  |  |  |  | 5.01 Lack of experience | [11 empty] | This is an incident that involved our member who wasn't at fault the answers below reflect that. | 22. Inadequate or Improper Protective Equipment | 2. Struck By (Hit By Moving Object) |  | Approved, Cody Vinyard | [66 empty] | Driver side cab, door and bed damaged | 4000 | Jesse Perry | Vehicle (not related to operation of vehicle) |  | F03-1349
8910 | River Valley | 2019-06-20 07:00 | Contract electrician was traveling back to the top floor of the sample tower. He noticed broken glass on the bottom floor. He investigated the source of the glass and found the top floor light globe was missing and was the source of the glass. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Michael Smith | 2019-08-23 15:17 | 2019-06-20 18:01 | 2019-06-20 18:01 | 2019-08-17 13:17 | 2019-07-04 07:00 | 2019-06-20 17:27 | 2019-08-23 13:56 |  |  | River Valley PP Fuel Supply Sample Tower |  |  | Anthony Gillespie | Corrective action should greatly reduce similar recurrence. | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Michael Smith |  | Light globe cracked and fell to the floor. The light globe cracked below the threaded area that attaches it to the housing. The broken pieces of glass fell to the ground. |  |  |  | River Valley | FALSE |  | TRUE | Fuel Supply |  | Michael Smith | Michael Smith |  | Timothy Chancellor | no additional comment. | Timothy Chancellor |  | Low | [14 empty] | 15.03 Inadequate inspection and/or monitoring |  | Manufacture defect in light globe broke. | 06. Using Defective Equipment | 2. Struck By (Hit By Moving Object)
8910 | River Valley | 2019-06-20 07:00 | Contract electrician was traveling back to the top floor of the sample tower. He noticed broken glass on the bottom floor. He investigated the source of the glass and found the top floor light globe was missing and was the source of the glass. | Level 1 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Michael Smith | 2019-08-23 15:17 | 2019-06-20 18:01 | 2019-06-20 18:01 | 2019-08-17 13:17 | 2019-07-04 07:00 | 2019-06-20 17:27 | 2019-08-23 13:56 |  |  | River Valley PP Fuel Supply Sample Tower |  |  | Anthony Gillespie | Corrective action should greatly reduce similar recurrence. | Power Supply |  | Level 1 | Property Damage |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Michael Smith |  | Light globe cracked and fell to the floor. The light globe cracked below the threaded area that attaches it to the housing. The broken pieces of glass fell to the ground. |  |  |  | River Valley | FALSE |  | TRUE | Fuel Supply |  | Michael Smith | Michael Smith |  | Timothy Chancellor | no additional comment. | Timothy Chancellor |  | Low | [14 empty] | 15.03 Inadequate inspection and/or monitoring |  | Manufacture defect in light globe broke. | 06. Using Defective Equipment | 2. Struck By (Hit By Moving Object)
8911 | Muskogee Power Plant | 2019-06-16 16:00 | Contractor felt something poking in the ankle. Reached down to rub his leg and discovered a wire fragment in his coveralls and in his leg. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Carol Rollins | 2019-08-26 14:01 | 2019-06-21 10:10 | 2019-06-21 10:10 | 2019-08-06 10:56 | 2019-06-30 16:00 | 2019-06-21 09:48 | 2019-08-16 06:50 |  | 2019-08-07 10:40 | Unit 4 cooling tower makeup piping building |  |  | Jesse Murray | Returning to Investigate after 7-17-19 Incident Call. Bob schedule a Call with MK SLT and My to Zachry Safety Leadership to discuss how they deemed this Non Worked Related. Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Carol Rollins |  | Zachry member was serving as a firewatch for pipe fitters while welding, grinding, and wire wheel use was going on when he felt something poking his ankle inside his boot. He struck it with his other foot. Then it began to sting. He then pulled his boot off and found a small piece of wire had punctured his ankle. Zachry member was taken to the local urgent care. Examined by Dr Shekiel who referred him to an orthopedic surgeon for removal. The ortho at Muskogee bone and joint performed a removal on 6/19/19. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | Engineering & Planning |  | Jerry Herriman | Carol Rollins |  | Jonathan Stogsdill | Reviewed. JHS | Jonathan Stogsdill |  | Medium | [12 empty] | 13.01 Inadequate assessment of needs and risks |  | 15.03 Inadequate inspection and/or monitoring |  | Possible defective wire wheel causing piece of wire to come loose and fall into boot where it worked its way up against skin and was accidentally kicked in upon initial reaction to it poking his skin and kicking at it with other foot. | 23. Defective Tools, Equipment or Materials | 2. Struck By (Hit By Moving Object) |  | Reviewed Bob Wright |  |  |  | Injury / Illness |  | Carol Rollins |  | wire stuck in leg | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Jerry Herriman | Zachry | Troy Herriman | Puncture |  | Ankle | Benjamin Pingel | Right | FALSE | [69 empty] | 9581896
8912 | River Valley | 2019-06-20 17:30 | Member felt light and dizzy. Member was taken to offsite emergency room for evaluation of conditions. | Level 2 |  | FALSE | Member Injury |  |  |  |  | OG&E Corp Services | Jesse Murray | 2019-07-22 13:36 | 2019-06-21 10:25 | 2019-06-21 10:25 | 2019-07-11 07:37 | 2019-07-04 17:30 | 2019-06-21 10:14 | 2019-07-22 12:36 |  | 2019-07-15 13:27 | River Valley Power Plant near the ID Fan. |  |  | Jerrod Moser | approved | Enterprise Services |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Jesse Murray |  | On 6-20-19 Tony G was observing emergency personnel responding to a fire at RV. Tony had been outside approx. 2 hours when he began to fell light headed and dizzy. He asked a fellow member to take him back to the plant to get some ac and water for a rest break. During Transport Tony became very dizzy, light headed and passed out for approx. 20 seconds. Plant personnel responded and got Tony to a stable state and at that point they decided to transport him to the local ER. ER found that Member was dehydrated. Did not treat the member but released him with no restrictions and no IV Fluids. Background. Tony had been on the Job for 9 days. Tony was on light duty and had been on light duty due to a personnel injury to his leg for some time prior. He was within a week of full release. Tony had been in AC environments for months now and had little to no physical activity in the recent months. This day Tony had coffee, diet coke, and one cup of water. After the event and investigation it is very clear Tony was dehydrated. We had Tony follow up with Doctor Estep as well to ensure he was ok and diagnose the condition. Estep confirmed he was dehydrated. Estep also gave him a full release. |  |  | FALSE | River Valley | FALSE |  | FALSE | Other |  | Timothy Chancellor | Jesse Murray |  | Jerrod Moser | approved | Jerrod Moser |  | Medium |  |  | 3.04 Fatigue due to sensory overload | [13 empty] | Member was on light duty prior to this incident due to personal injury. He was limited on activities and spent most time in air conditioned atmosphere's. He had been accustomed to this for 3 months because of his injury. He was not acclimated to working in the elements and did not hydrate properly all day. This caused the dizziness and dehydration. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | …. | [24 empty] | FALSE |  |  | 2019-06-10 | 1985-04-17 |  | 2019-06-20 07:00 | 0 | 0 | Sat down, took to AC building, Ice packs applied, and water/Gatorade intake. | FALSE |  | Member was not acclimated to being outside and did not intake enough fluids this day resulting in light head and dizzy feeling. |  | TRUE | Anthony Gillespie |  | First Aid | Anthony Gillespie | TRUE |  | Eastern Oklahoma Medical Center: Emergency Room |  | Dehydration |  | FALSE |  | Health and Safety Representative | Head |  |  | FALSE | Jesse Murray | FALSE |  | 6/20/2019 7:00:00 AM | 9 days | TRUE | FALSE | TRUE | Deydration | Member was standing and observing local fire department respond to a fire.
8913 | Horseshoe Lake Power Plant | 2019-06-21 08:30 | Grating fell into river pump basin while contractor was attempting to remove it preparing for work. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Michael Kennedy | 2019-09-05 10:23 | 2019-06-21 14:17 | 2019-06-21 14:17 | 2019-08-14 14:35 | 2019-07-05 08:30 | 2019-06-21 13:35 | 2019-08-29 07:25 |  |  | Horseshoe Lake PP River Pump Basin |  |  | Ashley Harris | Reviewed incident with Bill Young and Tanner Brady. The incident is being returned to the supervisor for additional information. We need the contractors incident investigation uploaded. Please attach any pictures that may have been taken. Please provide more specific information on the fall distance of the grating. Was a grating removal permit acquired? The pre job assessment is not adequate and should have driven a corrective action. Compare the pre job assessment to WSI pre job hazard assessment program. The type of event needs to be changed from "Fall from elevation to lower level" to Dropped object. The safety stand down needs to be specific on what it is covering and include a review of the WSI pre-job assessment. Mike I will give you a call. We added the WSI Pre Job Hazard Assessment Document. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Michael Kennedy |  | Contractor member acted on his own and admittedly that he should have waited on another member to help him. They had preformed their SWP and the member was tied off. He was supposed to just loosen screw anchors to prepare to lift the grating away. Not lift the grating away until another member was there to help. The contractor thought he could manage it himself but lost control of the grating. 6/21/2019 - HL River Pump Basin - Approximately 0820 W-S employee (Jeffrey Reed) attempted to remove an approximately 8’x3’ piece of metal grating by himself and it slipped out of his hands and fell into the basin. The metal grating fell about 10 feet. W-S Foreman (Eric Ledesma) contacted OG&E member Cory Puckett to inform him that the grating had fallen and that a come-along was needed to remove the grating. Cory arrived at the scene and asked what had happened. It was explained that Mr. Reed had lost control of the grating and it fell. Cory stopped work, pulled the entire crew together for a safety stand down and informed Dan Perry, Mike Kennedy & Jeff Baker. Mike Kennedy came to the scene of the incident met with members to ensure no one was injured and discussed the event leading up to the incident. Jeff Baker came to the scene and came up with a plan to get the grating out of the pump bay safely. Jeffrey was working alone. The foreman had only asked him to remove the securing bolts but he took it upon himself to try to move the grate alone. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Maintenance |  | Cory Puckett | Michael Kennedy |  | Robert Doupe | ` | Robert Doupe |  | Low |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction | 7.06 Improper attempt to save time or effort |  | 9.06 Inadequate work planning or programming | [7 empty] | Contractor acted alone and should have waited for help. | 36. Inadequate Preparation, Planning | 3. Fall from Elevation to Lower Level | [5 empty] | Property Damage |  | Michael Kennedy | [5 empty] | 3. Fall from Elevation to Lower Level | Cory Puckett | W-S Industrial Services, INC. | Jeffery Reed |  |  |  | Kyle Thornton | [71 empty] | 9584702
8913 | Horseshoe Lake Power Plant | 2019-06-21 08:30 | Grating fell into river pump basin while contractor was attempting to remove it preparing for work. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Michael Kennedy | 2019-09-05 10:23 | 2019-06-21 14:17 | 2019-06-21 14:17 | 2019-08-14 14:35 | 2019-07-05 08:30 | 2019-06-21 13:35 | 2019-08-29 07:25 |  |  | Horseshoe Lake PP River Pump Basin |  |  | Ashley Harris | Reviewed incident with Bill Young and Tanner Brady. The incident is being returned to the supervisor for additional information. We need the contractors incident investigation uploaded. Please attach any pictures that may have been taken. Please provide more specific information on the fall distance of the grating. Was a grating removal permit acquired? The pre job assessment is not adequate and should have driven a corrective action. Compare the pre job assessment to WSI pre job hazard assessment program. The type of event needs to be changed from "Fall from elevation to lower level" to Dropped object. The safety stand down needs to be specific on what it is covering and include a review of the WSI pre-job assessment. Mike I will give you a call. We added the WSI Pre Job Hazard Assessment Document. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Michael Kennedy |  | Contractor member acted on his own and admittedly that he should have waited on another member to help him. They had preformed their SWP and the member was tied off. He was supposed to just loosen screw anchors to prepare to lift the grating away. Not lift the grating away until another member was there to help. The contractor thought he could manage it himself but lost control of the grating. 6/21/2019 - HL River Pump Basin - Approximately 0820 W-S employee (Jeffrey Reed) attempted to remove an approximately 8’x3’ piece of metal grating by himself and it slipped out of his hands and fell into the basin. The metal grating fell about 10 feet. W-S Foreman (Eric Ledesma) contacted OG&E member Cory Puckett to inform him that the grating had fallen and that a come-along was needed to remove the grating. Cory arrived at the scene and asked what had happened. It was explained that Mr. Reed had lost control of the grating and it fell. Cory stopped work, pulled the entire crew together for a safety stand down and informed Dan Perry, Mike Kennedy & Jeff Baker. Mike Kennedy came to the scene of the incident met with members to ensure no one was injured and discussed the event leading up to the incident. Jeff Baker came to the scene and came up with a plan to get the grating out of the pump bay safely. Jeffrey was working alone. The foreman had only asked him to remove the securing bolts but he took it upon himself to try to move the grate alone. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Maintenance |  | Cory Puckett | Michael Kennedy |  | Robert Doupe | ` | Robert Doupe |  | Low | [6 empty] | 7.06 Improper attempt to save time or effort |  | 9.06 Inadequate work planning or programming | [7 empty] | Ergonomic stress of lifting the grating alone. | 17. Failure to Identify Hazard, Risk | 11. Overstress, Overpressure, Overexertion, Ergonomic | [5 empty] | Property Damage |  | Michael Kennedy | [5 empty] | 3. Fall from Elevation to Lower Level | Cory Puckett | W-S Industrial Services, INC. | Jeffery Reed |  |  |  | Kyle Thornton | [71 empty] | 9584702
8914 | River Valley | 2019-06-20 11:38 | The contractor pulled up to the gate and walked over to tell the guard that his crew was going to lunch. He returned to his pickup and could not see the gate, since he had pulled so close to it before exiting his pickup. When he went to drive forward, his vehicle bent the gate. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Melton Morris | 2019-08-12 14:26 | 2019-06-21 14:58 | 2019-06-21 14:58 | 2019-07-25 08:53 | 2019-07-04 11:38 | 2019-06-20 23:39 | 2019-07-29 15:04 |  |  | River Valley security outbound gate. |  |  | Anthony Gillespie | Discussion and execution of walk around / 360 expectations should greatly eliminate similar incidents. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Melton Morris |  | The contractor checked out with security to go to lunch, returned to his vehicle and went to drive out and the guard had not raised the gate. The contractor vehicle pushed against the gate and bent the arm. When straightening the arm was attempted, the arm broke. |  |  |  | River Valley | FALSE |  | FALSE | Other |  | Charles Dunn | Raymond Bowen |  | Timothy Chancellor | After discussion about incident, contractor was removed from the site due to lack of engagement in work at hand. | Timothy Chancellor |  | Low |  |  |  | 4.04 Routine, monotony, demand for uneventful vigilance | [12 empty] | The driver did not check the front of the vehicle prior to driving forward. | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) | [5 empty] | Vehicle |  | Melton Morris | [5 empty] | 1. Struck Against (Running or Bumping Into) | Charles Dunn | Boomer Environmental | Brennan Hoegger |  |  |  | Gary Martin |  |  |  |  | FALSE | [66 empty] | 2365003
8915 | River Valley | 2019-06-20 15:45 | At 1545 the outside operator reported a small oil fire below the 1B ID fan inboard bearing. The visible fire was put out with a blast from a dry powder fire extinguisher. Smoke was still observed from the insulation, so a local fire department was called to remove the insulation and put out any residual fire. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Melton Morris | 2019-08-07 14:05 | 2019-06-21 16:11 | 2019-06-21 16:11 | 2019-07-03 16:11 | 2019-07-04 15:45 | 2019-06-20 15:45 | 2019-07-29 15:01 |  | 2019-07-15 13:22 | 1B Boiler ID fan pedistal |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Melton Morris |  | During normal operations of the boiler, an alarm came in indicating a high bearing temperature on 1B ID fan. The CRO notified the outside operator of the temperature. The operator went to investigate the alarm and found a small fire under the bearing, he used a 20lb dry chemical fire extinguisher to extinguish the fire. After the fire was put out, smoke was still observed coming from under the insulation. A local fire department was called and they assisted in removing the skin, insulation and debris from the cavity under the bearing with no further incident. The debris appears to have accumulated over time and had oil contamination in it from the extended plant shut down. |  |  |  | River Valley | FALSE |  | TRUE | Operations |  | Marty Blount | Melton Morris |  | Timothy Chancellor | Agree with corrective actions. May also consider implementing 5S program. | Timothy Chancellor |  | Medium | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.4 Inadequate preventative cleaning or resurfacing |  |  |  |  | Failure to identify flammable/combustible material in a cavity below the ID fan bearing. | 27. Poor Housekeeping, Disorder | 9. Abnormal Operation
8915 | River Valley | 2019-06-20 15:45 | At 1545 the outside operator reported a small oil fire below the 1B ID fan inboard bearing. The visible fire was put out with a blast from a dry powder fire extinguisher. Smoke was still observed from the insulation, so a local fire department was called to remove the insulation and put out any residual fire. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Melton Morris | 2019-08-07 14:05 | 2019-06-21 16:11 | 2019-06-21 16:11 | 2019-07-03 16:11 | 2019-07-04 15:45 | 2019-06-20 15:45 | 2019-07-29 15:01 |  | 2019-07-15 13:22 | 1B Boiler ID fan pedistal |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Melton Morris |  | During normal operations of the boiler, an alarm came in indicating a high bearing temperature on 1B ID fan. The CRO notified the outside operator of the temperature. The operator went to investigate the alarm and found a small fire under the bearing, he used a 20lb dry chemical fire extinguisher to extinguish the fire. After the fire was put out, smoke was still observed coming from under the insulation. A local fire department was called and they assisted in removing the skin, insulation and debris from the cavity under the bearing with no further incident. The debris appears to have accumulated over time and had oil contamination in it from the extended plant shut down. |  |  |  | River Valley | FALSE |  | TRUE | Operations |  | Marty Blount | Melton Morris |  | Timothy Chancellor | Agree with corrective actions. May also consider implementing 5S program. | Timothy Chancellor |  | Medium | [9 empty] | 10.05 Inadequate assessment of operational readiness |  | 12.01.1 Inadequate preventative assessment of needs |  |  |  |  | Failure to identify flammable/combustible material in a cavity below the ID fan bearing. | 27. Poor Housekeeping, Disorder | 9. Abnormal Operation
8915 | River Valley | 2019-06-20 15:45 | At 1545 the outside operator reported a small oil fire below the 1B ID fan inboard bearing. The visible fire was put out with a blast from a dry powder fire extinguisher. Smoke was still observed from the insulation, so a local fire department was called to remove the insulation and put out any residual fire. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Melton Morris | 2019-08-07 14:05 | 2019-06-21 16:11 | 2019-06-21 16:11 | 2019-07-03 16:11 | 2019-07-04 15:45 | 2019-06-20 15:45 | 2019-07-29 15:01 |  | 2019-07-15 13:22 | 1B Boiler ID fan pedistal |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Melton Morris |  | During normal operations of the boiler, an alarm came in indicating a high bearing temperature on 1B ID fan. The CRO notified the outside operator of the temperature. The operator went to investigate the alarm and found a small fire under the bearing, he used a 20lb dry chemical fire extinguisher to extinguish the fire. After the fire was put out, smoke was still observed coming from under the insulation. A local fire department was called and they assisted in removing the skin, insulation and debris from the cavity under the bearing with no further incident. The debris appears to have accumulated over time and had oil contamination in it from the extended plant shut down. |  |  |  | River Valley | FALSE |  | TRUE | Operations |  | Marty Blount | Melton Morris |  | Timothy Chancellor | Agree with corrective actions. May also consider implementing 5S program. | Timothy Chancellor |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [8 empty] | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | Failure to identify the possibility of debris accumulation during extended inactivity. | 17. Failure to Identify Hazard, Risk | 9. Abnormal Operation
8916 | Mustang Power Plant | 2019-06-23 15:20 | Contractor fell off of second rung of ladder injuring shoulder while rigging engine for lift. Contractor was taken to Mercy Hospital. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Kevin Kain | 2019-07-24 13:00 | 2019-06-23 16:10 | 2019-06-23 16:10 | 2019-07-16 15:12 | 2019-07-07 15:20 | 2019-06-23 15:37 | 2019-07-18 13:34 |  | 2019-07-17 07:16 | South side of MT-06 |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Sanders |  | Siemens member was standing on the second rung of a 6' ladder installing a rear trunnion bearing on Unit 6's engine. The member was tightening the trunnion bearing retaining bolts with a 3/4" wrench, when the wrench slipped off of the bolt and caused the member to lose his balance on the ladder. The member fell to the ground landing on his left shoulder. The member was standing at an odd angle on the ladder which did not allow for 3-point contact. The ladder was placed parallel to the work surface due to it not fitting close enough to the work area in the perpendicular position. The position of the ladder allowed the member to stand backward on the ladder which contributed to the fall. *Siemens to send out company wide training on ladders *Siemens to update their SSOP on ladders. |  |  |  | Mustang Power Plant | FALSE |  | FALSE | Other |  | Kevin Kain | William Sanders |  | William Sanders | Siemens has taken the option of using impact type tools when tightening the trunnion bearing to their engineering department. We are researching platform style ladders that will be applicable for this work. | William Sanders |  | Medium | [12 empty] | 13.01 Inadequate assessment of needs and risks | 14.04 Inadequate monitoring of compliance |  |  | Contractor fell from ladder resulting in shoulder injury. | 11. Improper Position for Task | 3. Fall from Elevation to Lower Level |  | Met with Siemens Safety and they went over detailed incident description. Attached the portion that they would allow. |  |  |  | Injury / Illness |  | Kevin Kain |  | bruised | FALSE |  |  | 4. Fall on Same Level (Slip and Fall, Trip Over) | Kevin Kain | Siemens | Tim | Unknown |  | Shoulder | William Sanders |  | FALSE
8916 | Mustang Power Plant | 2019-06-23 15:20 | Contractor fell off of second rung of ladder injuring shoulder while rigging engine for lift. Contractor was taken to Mercy Hospital. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Kevin Kain | 2019-07-24 13:00 | 2019-06-23 16:10 | 2019-06-23 16:10 | 2019-07-16 15:12 | 2019-07-07 15:20 | 2019-06-23 15:37 | 2019-07-18 13:34 |  | 2019-07-17 07:16 | South side of MT-06 |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Sanders |  | Siemens member was standing on the second rung of a 6' ladder installing a rear trunnion bearing on Unit 6's engine. The member was tightening the trunnion bearing retaining bolts with a 3/4" wrench, when the wrench slipped off of the bolt and caused the member to lose his balance on the ladder. The member fell to the ground landing on his left shoulder. The member was standing at an odd angle on the ladder which did not allow for 3-point contact. The ladder was placed parallel to the work surface due to it not fitting close enough to the work area in the perpendicular position. The position of the ladder allowed the member to stand backward on the ladder which contributed to the fall. *Siemens to send out company wide training on ladders *Siemens to update their SSOP on ladders. |  |  |  | Mustang Power Plant | FALSE |  | FALSE | Other |  | Kevin Kain | William Sanders |  | William Sanders | Siemens has taken the option of using impact type tools when tightening the trunnion bearing to their engineering department. We are researching platform style ladders that will be applicable for this work. | William Sanders |  | Medium | [12 empty] | 13.01 Inadequate assessment of needs and risks | 14.04 Inadequate monitoring of compliance |  |  | Contractor fell from ladder resulting in shoulder injury. | 11. Improper Position for Task | 3. Fall from Elevation to Lower Level |  | Met with Siemens Safety and they went over detailed incident description. Attached the portion that they would allow. |  |  |  | Injury / Illness |  | Tanner Brady |  | Dislocated shoulder/fracture falling off ladder | FALSE |  |  | 3. Fall from Elevation to Lower Level | Kevin Kain | SIemens | TIm Klientop | Dislocation |  | Shoulder | William Sanders |  | TRUE | Personal Vehicle
8917 | Centennial Wind Farm | 2019-06-19 15:30 | Technician was descending the ladder and experienced an "immense" amount of pain in his ribcage from the climb assist lanyard pressing/cutting into his abdomen. He stopped on the ladder to detach the climb assist lanyard and the carabiner didn't close correctly allowing it to fall to the deck below when he let go of it. There was minor property damage and no injuries. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Scott Zigler | 2019-07-19 14:50 | 2019-06-24 09:34 | 2019-06-24 09:34 | 2019-06-24 10:40 | 2019-07-03 14:30 | 2019-06-24 08:58 | 2019-07-05 16:46 |  | 2019-07-05 10:54 | Centennial Wind Farm turbine 17, on the ladder between the yaw deck and the saddle deck. |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | TRUE |  | FALSE | FALSE | Scott Zigler |  | Technician was descending the ladder and experienced an "immense" amount of pain in his ribcage from the climb assist lanyard pressing/cutting into his abdomen. He stopped on the ladder to detach the climb assist lanyard and the carabiner didn't close correctly allowing it to fall to the deck below when he let go of it. |  |  |  | Centennial Wind Farm | FALSE |  | TRUE | Renewable Energy |  | Scott Zigler | Scott Zigler |  | Jason Thomas | Corrective actions acceptable. | Jason Thomas |  | Medium | [6 empty] | 7.07 Improper attempt to avoid discomfort | [5 empty] | 13.02 Inadequate human factors/ergonomics considerations |  |  |  | The Petzel harness that is used by this contractor had side "D" rings that are in an awkward position for use with our climb assist lanyard. This causes discomfort for the technicians. | 03. Failure to Secure | 3. Fall from Elevation to Lower Level | [5 empty] | Property Damage |  | Scott Zigler | [5 empty] | 3. Fall from Elevation to Lower Level | Scott Zigler | Skyclimber Renewables | Jeffrey White |  |  |  | Scott Zigler | [71 empty] | none
8917 | Centennial Wind Farm | 2019-06-19 15:30 | Technician was descending the ladder and experienced an "immense" amount of pain in his ribcage from the climb assist lanyard pressing/cutting into his abdomen. He stopped on the ladder to detach the climb assist lanyard and the carabiner didn't close correctly allowing it to fall to the deck below when he let go of it. There was minor property damage and no injuries. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Scott Zigler | 2019-07-19 14:50 | 2019-06-24 09:34 | 2019-06-24 09:34 | 2019-06-24 10:40 | 2019-07-03 14:30 | 2019-06-24 08:58 | 2019-07-05 16:46 |  | 2019-07-05 10:54 | Centennial Wind Farm turbine 17, on the ladder between the yaw deck and the saddle deck. |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | TRUE |  | FALSE | FALSE | Scott Zigler |  | Technician was descending the ladder and experienced an "immense" amount of pain in his ribcage from the climb assist lanyard pressing/cutting into his abdomen. He stopped on the ladder to detach the climb assist lanyard and the carabiner didn't close correctly allowing it to fall to the deck below when he let go of it. |  |  |  | Centennial Wind Farm | FALSE |  | TRUE | Renewable Energy |  | Scott Zigler | Scott Zigler |  | Jason Thomas | Corrective actions acceptable. | Jason Thomas |  | Medium | [6 empty] | 7.07 Improper attempt to avoid discomfort | [5 empty] | 13.04 Inadequate availability |  |  |  | The Petzel harness that is used by this contractor had side "D" rings that are in an awkward position for use with our climb assist lanyard. This causes discomfort for the technicians. | 03. Failure to Secure | 3. Fall from Elevation to Lower Level | [5 empty] | Property Damage |  | Scott Zigler | [5 empty] | 3. Fall from Elevation to Lower Level | Scott Zigler | Skyclimber Renewables | Jeffrey White |  |  |  | Scott Zigler | [71 empty] | none
8917 | Centennial Wind Farm | 2019-06-19 15:30 | Technician was descending the ladder and experienced an "immense" amount of pain in his ribcage from the climb assist lanyard pressing/cutting into his abdomen. He stopped on the ladder to detach the climb assist lanyard and the carabiner didn't close correctly allowing it to fall to the deck below when he let go of it. There was minor property damage and no injuries. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Scott Zigler | 2019-07-19 14:50 | 2019-06-24 09:34 | 2019-06-24 09:34 | 2019-06-24 10:40 | 2019-07-03 14:30 | 2019-06-24 08:58 | 2019-07-05 16:46 |  | 2019-07-05 10:54 | Centennial Wind Farm turbine 17, on the ladder between the yaw deck and the saddle deck. |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | TRUE | FALSE | TRUE |  | FALSE | FALSE | Scott Zigler |  | Technician was descending the ladder and experienced an "immense" amount of pain in his ribcage from the climb assist lanyard pressing/cutting into his abdomen. He stopped on the ladder to detach the climb assist lanyard and the carabiner didn't close correctly allowing it to fall to the deck below when he let go of it. |  |  |  | Centennial Wind Farm | FALSE |  | TRUE | Renewable Energy |  | Scott Zigler | Scott Zigler |  | Jason Thomas | Corrective actions acceptable. | Jason Thomas |  | Medium | [6 empty] | 7.07 Improper attempt to avoid discomfort | [5 empty] | 13.02 Inadequate human factors/ergonomics considerations |  |  |  | The Petzel harness that is used by this contractor had side "D" rings that are in an awkward position for use with our climb assist lanyard. This causes discomfort for the technicians. | 03. Failure to Secure | 3. Fall from Elevation to Lower Level | [5 empty] | Property Damage |  | Scott Zigler | [5 empty] | 3. Fall from Elevation to Lower Level | Scott Zigler | Skyclimber Renewables | Jeffrey White |  |  |  | Scott Zigler | [71 empty] | none
8917 | Centennial Wind Farm | 2019-06-19 15:30 | Technician was descending the ladder and experienced an "immense" amount of pain in his ribcage from the climb assist lanyard pressing/cutting into his abdomen. He stopped on the ladder to detach the climb assist lanyard and the carabiner didn't close correctly allowing it to fall to the deck below when he let go of it. There was minor property damage and no injuries. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Scott Zigler | 2019-07-19 14:50 | 2019-06-24 09:34 | 2019-06-24 09:34 | 2019-06-24 10:40 | 2019-07-03 14:30 | 2019-06-24 08:58 | 2019-07-05 16:46 |  | 2019-07-05 10:54 | Centennial Wind Farm turbine 17, on the ladder between the yaw deck and the saddle deck. |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | TRUE | FALSE | TRUE |  | FALSE | FALSE | Scott Zigler |  | Technician was descending the ladder and experienced an "immense" amount of pain in his ribcage from the climb assist lanyard pressing/cutting into his abdomen. He stopped on the ladder to detach the climb assist lanyard and the carabiner didn't close correctly allowing it to fall to the deck below when he let go of it. |  |  |  | Centennial Wind Farm | FALSE |  | TRUE | Renewable Energy |  | Scott Zigler | Scott Zigler |  | Jason Thomas | Corrective actions acceptable. | Jason Thomas |  | Medium | [6 empty] | 7.07 Improper attempt to avoid discomfort | [5 empty] | 13.04 Inadequate availability |  |  |  | The Petzel harness that is used by this contractor had side "D" rings that are in an awkward position for use with our climb assist lanyard. This causes discomfort for the technicians. | 03. Failure to Secure | 3. Fall from Elevation to Lower Level | [5 empty] | Property Damage |  | Scott Zigler | [5 empty] | 3. Fall from Elevation to Lower Level | Scott Zigler | Skyclimber Renewables | Jeffrey White |  |  |  | Scott Zigler | [71 empty] | none
8918 | McClain Power Plant | 2019-06-21 14:30 | Member was in a rental car heading to the airport. Stopped at Red light and awaiting to proceed. Felt a jolt and looked into rear view mirror. Member was rear ended. Member stepped out of car and immediately went to the rear of rental car. Inspected the rental car for damage. Identified a quarter size dent. The offending car was damaged on the front grill. Member approached the driver of the car. The driver remained in the car the entire time. Member called the police and reported the incident. | Level 2 |  | FALSE | Vehicle |  |  |  |  | Power Supply | Jeremy Loper | 2019-08-07 15:10 | 2019-06-25 08:45 | 2019-06-25 08:45 | 2019-07-26 09:06 | 2019-07-05 14:30 | 2019-06-25 08:31 | 2019-07-31 11:17 |  | 2019-07-30 14:45 | 7 street west & Albion Ave (St. Paul, MN). Stop Light intersection |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Jeremy Loper |  | Member was stop at a stop light. Member was struck by car behind. |  |  |  | McClain Power Plant | FALSE |  | FALSE | Maintenance |  | David Smith | Jeremy Loper |  | Jimmy Green | None | Jimmy Green |  | Medium |  | 2.06 Poor coordination | [14 empty] | Non member did not obey the traffic light nor did the non member stop. | 19. Failure to React, Correct | 2. Struck By (Hit By Moving Object) |  | I agree with investigation performed by JL. There should be no corrective actions as Member was stopped at light. TB 7/30/19 | [72 empty] | FALSE |  | St. Paul | Public Vehicle Struck OGE | OGE Vehicle Stopped/Parked | 2011-07-04 19:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
8919 | North Service Center | 2019-06-24 10:00 | This is a First Aid....While member was operating a extendo stick, he felt discomfort in his left leg. No medical attention was required, and member returned to work. | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Eric Engles | 2019-06-27 15:10 | 2019-06-25 14:40 | 2019-06-25 14:40 | 2019-06-25 14:45 | 2019-07-08 09:00 | 2019-06-25 14:32 |  |  |  | Guthrie High School.....200 Crooks Dr. |  |  | Luke Kennedy | Approved 6/25/19 | T&D Ops |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | [5 empty] | FALSE | North Service Center | FALSE |  | FALSE | PD Operations Services |  | Kelley Watson | Eric Engles |  |  |  | Steve Watkins |  | Low | [45 empty] | FALSE |  |  | 2007-05-29 | 1970-10-18 |  | 2019-06-24 07:00 | 0 | 0 |  | FALSE |  | Lifting extendo stick |  |  | Kelley Watson |  | First Aid | Kelley Watson |  |  |  |  | Sprain/Strain |  | FALSE |  | Area Service Technician | Groin |  |  |  | Eric Engles |  |  | 6/24/2019 7:00:00 AM |  | FALSE |  |  | Strain of stick
8920 | Sooner Power Plant | 2019-06-25 16:30 | OPC employee demolishing temporary construction facility water piping cut pipe on energized side of valve. | Level 1 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services | Richard Wood | 2019-07-15 08:44 | 2019-06-26 12:41 | 2019-06-26 12:41 | 2019-07-09 11:14 | 2019-07-09 16:30 | 2019-06-26 12:32 | 2019-07-11 11:36 |  |  | AQCS project construction trailers |  |  | Marcus Huddleston | No additional comments. MLH 7/15/19 | UTS |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Richard Wood |  | 190625 at approximately 1630 electricians were demolishing temporary utilities in the construction trailer area. They had previously been directed to cut a water line that was isolated east of the office area where they were also cutting and capping conduit below grade for final site demobilization. They continued with demo of conduit and cable at a second location and noticed a similar water line. They proceeded to cut the water line which was not isolated and in service. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | UTS - Capital Projects |  | Richard Wood | Richard Wood |  | Robert Weaver | I approve action 7034 | Robert Weaver |  | Low |  |  |  |  | 5.05 Misunderstood directions | [11 empty] | failure to evaluate change in work area | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) |  |  |  |  | SO AQCS | Property Damage |  | Richard Wood | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Richard Wood | OPC | Denise Deville |  |  |  | Richard Wood
8920 | Sooner Power Plant | 2019-06-25 16:30 | OPC employee demolishing temporary construction facility water piping cut pipe on energized side of valve. | Level 1 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services | Richard Wood | 2019-07-15 08:44 | 2019-06-26 12:41 | 2019-06-26 12:41 | 2019-07-09 11:14 | 2019-07-09 16:30 | 2019-06-26 12:32 | 2019-07-11 11:36 |  |  | AQCS project construction trailers |  |  | Marcus Huddleston | No additional comments. MLH 7/15/19 | UTS |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Richard Wood |  | 190625 at approximately 1630 electricians were demolishing temporary utilities in the construction trailer area. They had previously been directed to cut a water line that was isolated east of the office area where they were also cutting and capping conduit below grade for final site demobilization. They continued with demo of conduit and cable at a second location and noticed a similar water line. They proceeded to cut the water line which was not isolated and in service. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | UTS - Capital Projects |  | Richard Wood | Richard Wood |  | Robert Weaver | I approve action 7034 | Robert Weaver |  | Low |  |  |  |  | 5.05 Misunderstood directions | [11 empty] | failure to evaluate change in work area | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) |  |  |  |  | SO AQCS | Injury / Illness |  | Richard Wood | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Richard Wood | OPC | Denise Deville |  |  |  | Richard Wood
8920 | Sooner Power Plant | 2019-06-25 16:30 | OPC employee demolishing temporary construction facility water piping cut pipe on energized side of valve. | Level 1 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services | Richard Wood | 2019-07-15 08:44 | 2019-06-26 12:41 | 2019-06-26 12:41 | 2019-07-09 11:14 | 2019-07-09 16:30 | 2019-06-26 12:32 | 2019-07-11 11:36 |  |  | AQCS project construction trailers |  |  | Marcus Huddleston | No additional comments. MLH 7/15/19 | UTS |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Richard Wood |  | 190625 at approximately 1630 electricians were demolishing temporary utilities in the construction trailer area. They had previously been directed to cut a water line that was isolated east of the office area where they were also cutting and capping conduit below grade for final site demobilization. They continued with demo of conduit and cable at a second location and noticed a similar water line. They proceeded to cut the water line which was not isolated and in service. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | UTS - Capital Projects |  | Richard Wood | Richard Wood |  | Robert Weaver | I approve action 7034 | Robert Weaver |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | failure to evaluate change in work area | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) |  |  |  |  | SO AQCS | Property Damage |  | Richard Wood | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Richard Wood | OPC | Denise Deville |  |  |  | Richard Wood
8920 | Sooner Power Plant | 2019-06-25 16:30 | OPC employee demolishing temporary construction facility water piping cut pipe on energized side of valve. | Level 1 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services | Richard Wood | 2019-07-15 08:44 | 2019-06-26 12:41 | 2019-06-26 12:41 | 2019-07-09 11:14 | 2019-07-09 16:30 | 2019-06-26 12:32 | 2019-07-11 11:36 |  |  | AQCS project construction trailers |  |  | Marcus Huddleston | No additional comments. MLH 7/15/19 | UTS |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Richard Wood |  | 190625 at approximately 1630 electricians were demolishing temporary utilities in the construction trailer area. They had previously been directed to cut a water line that was isolated east of the office area where they were also cutting and capping conduit below grade for final site demobilization. They continued with demo of conduit and cable at a second location and noticed a similar water line. They proceeded to cut the water line which was not isolated and in service. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | UTS - Capital Projects |  | Richard Wood | Richard Wood |  | Robert Weaver | I approve action 7034 | Robert Weaver |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | failure to evaluate change in work area | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) |  |  |  |  | SO AQCS | Injury / Illness |  | Richard Wood | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Richard Wood | OPC | Denise Deville |  |  |  | Richard Wood
8921 | Mustang Power Plant | 2019-06-26 14:00 | Siemen's member was entering Unit 6 engine compartment using the bay door stairs and platform, when the grating shifted and fell through the steel structure. Siemen's member caught himself on the steel structure to prevent falling 3 feet to the ground. The grating was previously removed and reinstalled to allow the engine bay doors to open for engine removal. No injury occurred to Siemen's member. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | William Sanders | 2019-07-18 13:08 | 2019-06-26 14:48 | 2019-06-26 14:47 | 2019-07-16 15:09 | 2019-07-10 14:00 | 2019-06-26 14:28 | 2019-07-16 15:11 |  |  | Mustang Energy Center Unit 9 |  |  | Tanner Brady | Siemens incident is attached. CARs will resolve loose grating issue. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Sanders |  | Siemen's member was entering Unit 6 engine compartment using the bay door stairs and platform, when the grating shifted and fell through the steel structure. The grating had been removed and turned upside down to get the toe kick out of the way to allow the bay door to open. The toe kick is welded to the individual grating pieces, so the grating has to be flipped to point the toe kick down for clearance. Once the grating was flipped the Siemens member reinstalled to grating clips(4 of them) securing the grating to the structure. The Siemens member then stepped on the grating which caused it to shift. When the grating shifted, it loosened the clips and allowed the grating to fall through the structure 3 feet to the ground. Siemens member was able to catch himself on the steel supporting structure and didn't receive any injuries. It appears that when the grating was flipped upside down it was sitting awkwardly on the support structure due to the ribs on the walking surface of the grating. The ribs allowed the grating to shift when weight was applied which cause the clips to come loose. Siemens will complete their Near Miss Investigation and it will be attached to this report. The Siemens member suffered a bruised Knee and fore arm as well as a twisted ankle, no medical attention was needed. |  |  |  | Mustang Power Plant | FALSE |  | FALSE | Other |  | Charles Lilly | William Sanders |  | William Sanders | Siemens incident report is attached. | William Sanders |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [9 empty] | 15.03 Inadequate inspection and/or monitoring |  | The grating has a built in toe kick that will not allow the engine bay doors to open for engine change out. The grating had been taken up and flipped over to allow the doors to clear the toe kick. The top side of the grating is ribbed surface that allows the grating clips to securely hold the grating from shifting on the steel frame. The bottom side of the grating is a smooth steel surface that the grating clips have a hard time holding on to. While the grating was upside down, the grating clips allowed the grating to shift and fall through the steel support frame. | 15. Using Equipment Improperly | 3. Fall from Elevation to Lower Level | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | William Sanders | [5 empty] | 3. Fall from Elevation to Lower Level | Charles Lilly | Siemens | Steve Sweeney |  |  |  | William Sanders
8922 | Seminole PP; EGX Gath/Trans | 2019-06-26 02:30 | Will replacing Unit 3 down comer Valve, member notice a discomfort in his left eye. After job was completed member flush out eye and it seems to be better. Member will evaluate his condition. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Terry Bunch | 2019-07-08 09:19 | 2019-06-26 16:27 | 2019-06-26 16:27 | 2019-06-27 09:35 | 2019-07-10 02:30 | 2019-06-26 16:17 | 2019-06-27 10:59 |  |  | Seminole PP Unit 3 Boiler basement |  |  | Chrysty Dorsey | Reviewed | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Terry Bunch |  | Mechanic was in the process of welding in drain valve. During the process member felt something enter his left eye, he continues welding and upon finishing rinse out eye. Rinsing process seem to have remove the particle and no other first aid was needed. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | TRUE | Maintenance |  | Terry Bunch | Terry Bunch |  | Paul Schoelen | The member returned to work the next day with no further issues. | Paul Schoelen |  | Low | [11 empty] | 12.01.1 Inadequate preventative assessment of needs |  |  |  |  | Particles may fallen onto welding hood or face shield. | 33. Presence of Harmful Materials | 3. Fall from Elevation to Lower Level | [92 empty] | 9587374
8923 | River Valley | 2019-06-26 13:30 | While washing down for combustible dust, washdown member rose up from a crouched position and his forehead contacted corner of metal plate causing minor laceration to the forehead above his eyebrow. | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Supply | Timothy Chancellor | 2019-08-14 08:32 | 2019-06-27 15:22 | 2019-06-27 15:22 | 2019-07-29 14:49 | 2019-07-10 13:30 | 2019-06-27 15:03 |  |  |  | River Valley PP Dumper 1X Belt |  |  | Anthony Gillespie | Follow up with contract member is complete to stress importance of proper PPE usage and assigned corrective action should greatly eliminate incidents of this nature. | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | [5 empty] | FALSE | River Valley | FALSE |  | FALSE | Fuel Supply |  | Anthony Gillespie | Timothy Chancellor |  |  |  | Jeremiah Perryman |  | Low | [45 empty] | FALSE | [5 empty] | 2019-06-27 06:00 | 0 | 0 | Antiseptic wipe was used to clean cut and sterile dressing was applied to the cut. | FALSE |  | Member was bent over washing underneath belt in a crouched position. When he stood up, his head contacted a corner of a metal plate causing the laceration. |  | TRUE | Joshua Tackett |  | First Aid | Joshua Tackett | FALSE |  |  |  | Laceration |  | FALSE |  |  | Forehead |  | Left |  | Jeremiah Perryman |  |  | 6/27/2019 6:00:00 AM | 2 weeks | TRUE | FALSE | FALSE | Metal Plate. | Washing down 1X belt.
8924 | Metro Service Center | 2019-06-28 10:00 | Contractor struck down guy anchor while mowing turf. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Shawn Huff | 2019-07-23 12:39 | 2019-06-28 13:51 | 2019-06-28 13:51 | 2019-07-17 11:20 | 2019-07-12 10:00 | 2019-06-28 13:32 | 2019-07-17 16:04 |  | 2019-07-17 15:21 | Substation |  |  | William Young | Reviewed. Discussed with Jerrie and the possibility of putting hi-vis sleeves on guy wires. WCY | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Shawn Huff |  | From Chris King supervisor for Chemical Weed Control Arkansas. Hey Shawn, Just wanted to give a brief rundown of the incident at Panama sub on Friday morning 6/28/19. I happened to be on the mowing crew at the time, filling in for one of my guys, along with two contract workers, James Bradshaw and Jarrod Pryor. While mowing around a set of guy wires, James Bradshaw clipped the anchor with the mower deck, cutting the guy wire cable. No one was injured and no equipment was damaged, except for the anchor and cable. I actually saw it happen from about 75 feet away and immediately took photos and reported it to Pat Kidd. The location was wet and slick, and we were trying to mow as quickly as possible. James Bradshaw saw the guy wires, but just misjudged it. Plain and simple. I have attached some photos below. We marked the wire and anchor with orange cones and ribbon. Please let me know if there’s anything else we can do to help, besides taking our time and being more cautious. |  |  |  | Metro Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Shawn Huff |  |  |  | Reviewed incident. WIll forward to appropriate party for repair and collection of asset. Jarod |  |  | Medium |  |  |  |  | 5.06 Lack of situational awareness |  | 7.06 Improper attempt to save time or effort | [9 empty] | Mower struck down guy. | 04. Operating at Improper Speed | 1. Struck Against (Running or Bumping Into) |  | Chris - please include a corrective action (s). Perhaps it was a stand down where mowers were advised to slow down and be aware of their surroundings? J. Looney 7/16/19 - Approved, J. Looney |  |  |  | Property Damage |  | Shawn Huff | Struck down guy. Broke anchor |  |  |  |  | 2. Struck By (Hit By Moving Object) | Shawn Huff | Chemical Weed Control | James Bradshaw |  | Fixed Equipment | [6 empty] | FALSE | [66 empty] | 1111568
8925 | Muskogee Service Center | 2019-06-23 12:00 | When performing storm work, Small bucket truck got stuck. While being pulled out truck was damaged. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Delivery | Randell Gilbert | 2019-07-03 10:34 | 2019-07-02 13:13 | 2019-07-02 13:12 | 2019-07-02 14:15 | 2019-07-07 12:00 | 2019-06-23 12:15 | 2019-07-03 10:04 |  | 2019-07-02 14:24 | Old Hwy 69 north of Texanna Rd |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Randell Gilbert |  | Member completed storm work off of Old Hwy 69 north of Texanna Rd, on the side of the road. Member had positioned his truck nose first leaving one rear tire on the pavement to remove grounds that were installed. After completion member attempted to back his truck out with no success. The member began going forward and back at a short distance in order to gain momentum, this resulted in the truck sliding into the bottom of the ditch. Member called local member to assist. A public dump truck was nearby bringing gravel for transmission crews. The public dump truck pulled OGE truck from the rear, through tall grass. After being extracted from the ditch the OG&E vehicle was assessed for damage and was found that while being extracted the truck hit the corner of a concrete culvert that was in the tall grass. Members did not identify the concrete culvert before extracting the vehicle. Member then notified fleet and supervisor. |  |  |  | Muskogee Service Center | FALSE |  | FALSE | Construction Services |  | Joshua Cheney | Randell Gilbert |  | Michael Fox | I approve with the change of member did not call Brian McKinney. | Michael Fox |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [7 empty] | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | Member completed storm work off of Old Hwy 69 north of Texanna Rd, on the side of the road. Member had positioned his truck nose first leaving one tire on the pavement to remove grounds that were installed. After completion member attempted to back his truck out with no success. The member began going forward and back at a short distance in order to gain momentum, this resulted in the truck sliding into the bottom of the ditch. Member called local member to assit. A public dump truck was nearby bringing gravel for transmission crews. The public dump truck pulled OGE truck from the rear, through tall grass. After being extracted from the ditch the OG&E vehicle was assessed for damage and was found that while being extracted the truck hit the corner of a concrete culvert that was in the tall grass. Members did not identify the concrete culvert before extracting the vehicle. Member then notified fleet and supervisor. | 40. Weather Conditions | 1. Struck Against (Running or Bumping Into) |  | We should take the time to review Vehicle Extraction SOP.TDO.837 with our members. I approve. | [66 empty] | Steer rod and exhaust. | 9000 | Joshua Cheney | Vehicle (not related to operation of vehicle) |  | F08-499
8926 | River Valley | 2019-06-30 16:15 | The 1A boiler Primary Air fan 4160 volt motor junction box experienced an arc flash event during normal operation. The event blew 2 of the 3 doors off the box. The event resulted in the entire plant tripping through a sequence of events. | Level 2 |  | TRUE | Member Injury | Donnie Jones |  |  |  | Power Supply | Melton Morris | 2019-10-25 13:20 | 2019-07-02 16:12 | 2019-07-02 16:12 | 2019-10-16 14:38 | 2019-07-14 16:15 | 2019-07-01 15:16 | 2019-10-21 07:30 |  | 2019-10-18 08:24 | River Valley Unit 1, 1A boiler Primary Air Fan 4160 volt, motor junction box |  |  | Jesse Murray | I Approve. More Corrective Action are listed in RCA 2343. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Melton Morris |  | The 1A Primary Air (PA) fan had a "Y" connection of the 4160 volt cables fail while in service. This failure resulted in an arc flash incident. The incident was investigated by a cross functional team who completed a detailed RCA. The RCA # is 2340. Possible Solution Cause Controlled Install IR Windows on Terminal Boxes for use during PMs Failure of Cable to Lug Connection MI implementation - Critical Motor/Wiring/Switching – Utilize OGE MI for Outage PM inspection frequency Failure of Cable to Lug Connection Utilize lessons learned from MKPP PA fan lug failure - Intelex #008436 - Specifically, replacing all lug connections and following advice on type of lug to utilize as applicable Connection Overheating |  |  |  | River Valley | FALSE |  | TRUE | Operations |  | Bernard Terbieten Jr | Melton Morris |  | Timothy Chancellor | Thanks for the detail in the RCA. | Timothy Chancellor |  | Medium | [9 empty] | 10.03 Inadequate standards, specifications and/or design criteria | [6 empty] | The "Y" connection on the primary air fan failed while in service and resulted in an arc flash incident. | 23. Defective Tools, Equipment or Materials | 9. Abnormal Operation |  | Corrective actions identified should greatly reduce the possibility of recurrences. | [90 empty] | 9587667
8926 | River Valley | 2019-06-30 16:15 | The 1A boiler Primary Air fan 4160 volt motor junction box experienced an arc flash event during normal operation. The event blew 2 of the 3 doors off the box. The event resulted in the entire plant tripping through a sequence of events. | Level 2 |  | TRUE | Property Damage | Donnie Jones |  |  |  | Power Supply | Melton Morris | 2019-10-25 13:20 | 2019-07-02 16:12 | 2019-07-02 16:12 | 2019-10-16 14:38 | 2019-07-14 16:15 | 2019-07-01 15:16 | 2019-10-21 07:30 |  | 2019-10-18 08:24 | River Valley Unit 1, 1A boiler Primary Air Fan 4160 volt, motor junction box |  |  | Jesse Murray | I Approve. More Corrective Action are listed in RCA 2343. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Melton Morris |  | The 1A Primary Air (PA) fan had a "Y" connection of the 4160 volt cables fail while in service. This failure resulted in an arc flash incident. The incident was investigated by a cross functional team who completed a detailed RCA. The RCA # is 2340. Possible Solution Cause Controlled Install IR Windows on Terminal Boxes for use during PMs Failure of Cable to Lug Connection MI implementation - Critical Motor/Wiring/Switching – Utilize OGE MI for Outage PM inspection frequency Failure of Cable to Lug Connection Utilize lessons learned from MKPP PA fan lug failure - Intelex #008436 - Specifically, replacing all lug connections and following advice on type of lug to utilize as applicable Connection Overheating |  |  |  | River Valley | FALSE |  | TRUE | Operations |  | Bernard Terbieten Jr | Melton Morris |  | Timothy Chancellor | Thanks for the detail in the RCA. | Timothy Chancellor |  | Medium | [9 empty] | 10.03 Inadequate standards, specifications and/or design criteria | [6 empty] | The "Y" connection on the primary air fan failed while in service and resulted in an arc flash incident. | 23. Defective Tools, Equipment or Materials | 9. Abnormal Operation |  | Corrective actions identified should greatly reduce the possibility of recurrences. | [90 empty] | 9587667
8927 | Metro Service Center | 2019-07-02 10:30 | Switching error | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Delivery | John Legg | 2019-09-03 16:30 | 2019-07-03 09:02 | 2019-07-03 09:02 | 2019-08-14 07:57 | 2019-07-16 10:30 | 2019-07-03 08:57 | 2019-08-28 11:38 |  | 2019-08-19 07:37 | 12320 NW 10 OKC |  |  | William Young | Reviewed and approved. WCY 9-3-2019 | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | John Legg |  | On July 2nd, 2019, BGC had a switching incident in the west district. This incident occurred with a BGC employee, Brandon Chevialer, while he was performing the switch order, # DO0473. After performing the switching, a troubleshooter showed up and found that the switching had cause an outage. This resulted in finding that when he performed the switch order on #D00473 that he did not verify tags to the switch order number that were conflicting each other. He also did not notify the DCC. BGC policy is to always verify switch number and tags on every piece of equipment. Due to this incident and investigation by superintendent, Doug Dover, and Safety Director Aaron Vernon, that the switch error occurred by not verifying the tags. As a result, Brandon was terminated from his two week notice. Due to Doug and Aaron investigation, we believe the problem does not rely solely with the switchman because he did not have the correct information and mapping to know where the cables were going. Due to this incident, BCG has decided that they will not perform any switching order without more proper mapping, which included being able to see both ends of the loop and normal open. With this information we believe that we can prevent any other incidents from occurring. |  |  |  | Metro Service Center | FALSE |  | FALSE | Resource Planning & Coord |  | Joshua Robertson | John Legg |  | Nicole Rhodes | Reviewed. | Nicole Rhodes |  | Medium | [5 empty] | 6.02 Inadequate practice | [10 empty] | It was determined that when the employee performed the switching order #D00473 that he did not verify tags to the switch order number that were conflicting each other. He also did not notify the DCC. | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation |  | No additional comments. MLH 8/19/19 |  |  |  | Switching |  | John Legg | [5 empty] | 9. Abnormal Operation | Joshua Robertson | Brad Garrett COnstruction | Brandon Chevalier |  |  |  | John Legg
8928 | West Service Center | 2019-07-03 09:00 | Power Dolly tipped over while maneuvering through fence into the back yard. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Delivery | Joshua Robertson | 2019-07-22 13:53 | 2019-07-03 12:18 | 2019-07-03 12:18 | 2019-07-17 14:15 | 2019-07-17 09:00 | 2019-07-03 12:08 | 2019-07-22 13:15 |  | 2019-07-18 12:42 | 656 Hunters Hill Rd |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Joshua Robertson |  | On July 3, at 8 A.M a West line crew was beginning a back yard job at 656 Hunters Hill rd. They attempted to enter the back yard with the power dolly but the foreman decided it would be safer to try it from the next street over due to limited access in first yard. They moved to the second location and started to enter the back yard. They unloaded the power dolly and removed a panel of the fence so that they could gain access to the job site. Then they began laying out the mats and moving the power dolly toward the fence. Due to the narrow gap in the fence they had their tracks sucked in. When they approached the opening the ground was very sandy. This caused the mats to slip out from under the power dolly. As the mats slipped out the power dolly tipped over on its right side. The power dolly did sustain minor damages but no third party property was damaged. At this point they stopped work and contacted their field supervisor. The foreman also stated that they were on a 9% grade and the training they had just received on the power dolly indicated that it was safe up to a 20% grade. |  |  |  | West Service Center | FALSE |  | FALSE | Construction Services |  | Brandon Streber | Joshua Robertson |  | Terry Garrett | Working with Fleet to work with Manufacturer for a better mat. Should have an answer the week of 7/22. | Terry Garrett |  | Medium |  |  |  |  | 5.01 Lack of experience | 6.03 Infrequent performance | [10 empty] | soft ground, incline was too steep for tracks to be drawn in. | 18. Failure to Check, Monitor | 9. Abnormal Operation |  | I believe the corrective actions determined by the investigation will mitigate the hazards that caused this incident | [66 empty] | damage to bucket and side panel guard on boom of power dolly | 5000 | Brandon Streber | Industrial/Heavy Equipment |  | F24-0839
8928 | West Service Center | 2019-07-03 09:00 | Power Dolly tipped over while maneuvering through fence into the back yard. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Delivery | Joshua Robertson | 2019-07-22 13:53 | 2019-07-03 12:18 | 2019-07-03 12:18 | 2019-07-17 14:15 | 2019-07-17 09:00 | 2019-07-03 12:08 | 2019-07-22 13:15 |  | 2019-07-18 12:42 | 656 Hunters Hill Rd |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Joshua Robertson |  | On July 3, at 8 A.M a West line crew was beginning a back yard job at 656 Hunters Hill rd. They attempted to enter the back yard with the power dolly but the foreman decided it would be safer to try it from the next street over due to limited access in first yard. They moved to the second location and started to enter the back yard. They unloaded the power dolly and removed a panel of the fence so that they could gain access to the job site. Then they began laying out the mats and moving the power dolly toward the fence. Due to the narrow gap in the fence they had their tracks sucked in. When they approached the opening the ground was very sandy. This caused the mats to slip out from under the power dolly. As the mats slipped out the power dolly tipped over on its right side. The power dolly did sustain minor damages but no third party property was damaged. At this point they stopped work and contacted their field supervisor. The foreman also stated that they were on a 9% grade and the training they had just received on the power dolly indicated that it was safe up to a 20% grade. |  |  |  | West Service Center | FALSE |  | FALSE | Construction Services |  | Brandon Streber | Joshua Robertson |  | Terry Garrett | Working with Fleet to work with Manufacturer for a better mat. Should have an answer the week of 7/22. | Terry Garrett |  | Medium |  |  |  |  | 5.05 Misunderstood directions | 6.03 Infrequent performance | [10 empty] | soft ground, incline was too steep for tracks to be drawn in. | 18. Failure to Check, Monitor | 9. Abnormal Operation |  | I believe the corrective actions determined by the investigation will mitigate the hazards that caused this incident | [66 empty] | damage to bucket and side panel guard on boom of power dolly | 5000 | Brandon Streber | Industrial/Heavy Equipment |  | F24-0839
8929 | Muskogee Service Center | 2019-07-02 11:00 | After installing new load wires for customer members closed riser and noticed fault in meter. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Delivery | Michael Fox | 2019-07-22 14:53 | 2019-07-03 13:45 | 2019-07-03 13:45 | 2019-07-16 08:41 | 2019-07-16 11:00 | 2019-07-03 13:18 | 2019-07-22 14:08 |  | 2019-07-17 12:45 | 3500 Haskell Blvd East Gate Nursing Home |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Michael Fox |  | Customer was upgrading service and installing generator. Customer removed all load wires from transformer to building and replaced them with new 16 runs of 600 copper. Electrician marked all cables and landed them in their switch gear. OG&E crew lugged and landed load wires in transformer. Electrician didn't mark CT wires when they disconnected them before installing load wires. Ct wires were not color coated they were all black and laid on to spade were electrician thought they went. When OG&E energized B phase then C phase then A phase there was a fault at the meter. Opened up fuses and called Meter Tech to help correct CT wires. Once all CT wires were replaced closed fuses again and B phase blew back. OG&E crew removed load wires from transformer and Ohm out runs and found that had crossed two of the runs. |  |  |  | Muskogee Service Center | FALSE |  | TRUE | Construction Services |  | Gary Knupp | Michael Fox |  | Chad Inman | I agree with the corrective action above. We must continue to do our due diligence when working with multiple customers, contractors, and electricians. Checking continuity should become the norm, no more assumptions, we're past this, we're better than this, we are professionals. | Chad Inman |  | Medium | [14 empty] | 15.03 Inadequate inspection and/or monitoring |  | Customer was upgrading service and installing generator. Customer removed all load wires from transformer to building and replaced them with new 16 runs of 600 copper. Electrician marked all cables and landed them in their switch gear. OG&E crew lugged and landed load wires in transformer. Electrician didn't mark CT wires when they disconnected them before installing load wires. Ct wires were not color coated they were all black and laid on to spade were electrician thought they went. When OG&E energized B phase then C phase then A phase there was a fault at the meter. Opened up fuses and called Meter Tech to help correct CT wires. Once all CT wires were replaced closed fuses again and B phase blew back. OG&E crew removed load wires from transformer and Ohm out runs and found that had crossed two of the runs. | 18. Failure to Check, Monitor | 9. Abnormal Operation |  | Approved
8930 | Enid Service Center | 2019-07-03 14:00 | Lug nuts were not tightened on the passenger side steer tire after replacing steel wheels with the aluminum wheel. The vehicle has not been driven by an OG&E member since the wheel change out. | Level 2 |  | TRUE | Vehicle |  |  |  |  | Power Delivery | Mark Hamm | 2019-07-16 10:11 | 2019-07-03 14:24 | 2019-07-03 14:24 | 2019-07-08 11:27 | 2019-07-17 14:00 | 2019-07-03 14:15 | 2019-07-15 14:26 |  | 2019-07-15 14:08 | Enid Service Center |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Mark Hamm |  | Member was looking at the new wheels that were installed on trucks. At first glance the member noticed that the studs on the wheel were too short, but with further investigation it was determined that the lug nuts had not been tightened on the wheel. |  |  |  | Enid Service Center | FALSE |  | TRUE | Construction Services |  | Kellen Schmidt | Mark Hamm |  | Christopher Bristol | This was a good catch by our members. I appreciate that Fleet is partnering with us to ensure this doesn't happen again. | Christopher Bristol |  | Medium |  |  | 3.06 Exposure to temperature extremes | 4.04 Routine, monotony, demand for uneventful vigilance |  |  |  |  | 9.12 Inadequate performance measurement and evaluation |  |  |  | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | lug nuts were not tightened | 18. Failure to Check, Monitor | 12. Equipment Failure |  | good catch by following the 360 procedure.
8930 | Enid Service Center | 2019-07-03 14:00 | Lug nuts were not tightened on the passenger side steer tire after replacing steel wheels with the aluminum wheel. The vehicle has not been driven by an OG&E member since the wheel change out. | Level 2 |  | TRUE | Vehicle |  |  |  |  | Power Delivery | Mark Hamm | 2019-07-16 10:11 | 2019-07-03 14:24 | 2019-07-03 14:24 | 2019-07-08 11:27 | 2019-07-17 14:00 | 2019-07-03 14:15 | 2019-07-15 14:26 |  | 2019-07-15 14:08 | Enid Service Center |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Mark Hamm |  | Member was looking at the new wheels that were installed on trucks. At first glance the member noticed that the studs on the wheel were too short, but with further investigation it was determined that the lug nuts had not been tightened on the wheel. |  |  |  | Enid Service Center | FALSE |  | TRUE | Construction Services |  | Kellen Schmidt | Mark Hamm |  | Christopher Bristol | This was a good catch by our members. I appreciate that Fleet is partnering with us to ensure this doesn't happen again. | Christopher Bristol |  | Medium |  |  | 3.02 Fatigue due to task load or duration | 4.04 Routine, monotony, demand for uneventful vigilance |  |  |  |  | 9.12 Inadequate performance measurement and evaluation |  |  |  | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | lug nuts were not tightened | 18. Failure to Check, Monitor | 12. Equipment Failure |  | good catch by following the 360 procedure.
8931 | Muskogee Power Plant | 2019-07-03 11:00 | Contractor working to replace fire water header was on scaffold and placed hand on small copper city water line to stand up. This force cracked loose the nearest soldered joint resulting in a small leak. No injuries. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Benjamin Pingel | 2019-07-18 07:14 | 2019-07-03 15:03 | 2019-07-03 15:03 | 2019-07-03 16:12 | 2019-07-17 11:00 | 2019-07-03 11:30 | 2019-07-10 22:04 |  |  | Muskogee PP Unit 6 Turbine Generator Basement |  |  | Robert Wright | Approved Bob Wright | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Benjamin Pingel |  | Contractor was welding new piping for the fire header in 6 TG Basement near ceiling from a rolling scaffold. He was positioned laying on his back to access lower portion of weld. When he completed the weld he grabbed a 3/4" copper city water line to reposition on the scaffolding causing the 90* elbow on the water line to crack at the soldered joint. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | Engineering & Planning |  | Brent Case | Benjamin Pingel |  | Carol Rollins | discussed if the pipe had adequate support but concluded that it would not prevent the damage | Carol Rollins |  | Low | [14 empty] | 15.07 Use for wrong purpose |  | Contractor pulled part of body weight on copper water line to reposition on scaffold while lying on back. This resulted in the soldered joint breaking loose. | 15. Using Equipment Improperly | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Benjamin Pingel | Loose Soldered Joint in Small Copper City Water Line |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Brent Case | Zachry | Dan Worton |  | Fixed Equipment |  | Benjamin Pingel |  |  |  |  | FALSE | [66 empty] | 9583354
8932 | Muskogee Power Plant | 2019-07-02 18:30 | Contractor Member Descending scaffold stairs stepped on object and twisted ankle. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Jerry Knight | 2019-08-15 15:54 | 2019-07-03 16:05 | 2019-07-03 16:05 | 2019-08-09 11:50 | 2019-07-16 18:30 | 2019-07-03 15:57 | 2019-08-09 12:18 |  |  | Unit 6 Boiler Level 3 |  |  | Robert Wright | Approved Bob Wright | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Tiana Cradduck |  | Introduction: A step-on-object incident occurred inside the MK6 boiler level 3 on July 2, 2019 at approximately 14:30. The Zachry employee was traversing down scaffolding stairs when he stepped on a wedge shaped block of wood. The uneven surface caused his right ankle to roll towards the inside. He subsequently was given icing treatment and Tylenol as needed and continued regulary duties to assure full range of motion. Refer to photographs and drawings for details. Discussion: Interviews: Phone Interview July 10, 2019 07:55 – Contractor involved in incident stated that BEFORE his 4pm break, the wedge-shaped block of wood was not on the stairs so “someone must have dropped it” either during his break or sometime before he traversed down the scaffolding stairs. Juan said that those wedge shaped blocks are used inside the boiler regularly. He obviously did not expect the block to be present, and stated that it was “hard to see inside there”. He subsequently rolled his ankle to the inside, received first aid treatment, and was released back to work. Text Conversation July 10, 2019 08:45 – Contractor involved in incident provided me with photographs of the location with the wedge in its approximate location when the incident occurred. He said it was “absolutely possible” that someone could have dropped the wedge from above, which would make this a dropped object incident as well. Site and Incident Observations: The incident occurred on the boiler furnace scaffolding (Drawing 1). The contractor was completing issued discovery repairs on the furnace water wall tubes, he was at approximately the same elevation as the band of E wallblowers (Drawing 2). The contractor had completed his last water wall repair and was traversing down the furance scaffolding towards the “dance floor” above the coutant slopes (Drawing 2). As the contractor was traversing the furnace scaffolding, he went to step down a scaffold level and stepped on a wooden wedge block (Photographs 1 & 2). A photograph provided by the contractor shows scaffolding above the incident area (Photograph 3). |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | Power Supply Services |  | Jerry Knight | Tiana Cradduck |  | Patrick Coleman | Reviewed on 8/9/2019. | Patrick Coleman |  | Low | [8 empty] | 9.06 Inadequate work planning or programming |  |  | 12.01.3 Inadequate preventative adjustment/assembly |  | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  |  | A step-on-object incident occurred inside the MK6 boiler level 3 on July 2, 2019 at approximately 14:30. The Zachry employee was traversing down scaffolding stairs when he stepped on a wedge shaped block of wood. The uneven surface caused his right ankle to roll towards the inside. | 27. Poor Housekeeping, Disorder | 4. Fall on Same Level (Slip and Fall, Trip Over) | [5 empty] | Injury / Illness |  | Tiana Cradduck |  | sprain/strained ankle | FALSE |  |  | 4. Fall on Same Level (Slip and Fall, Trip Over) | Jerry Knight | Zachry | Juan Zuniga | Sprain/Strain |  | Ankle | Tiana Cradduck | Right | FALSE | [69 empty] | 18830407
8932 | Muskogee Power Plant | 2019-07-02 18:30 | Contractor Member Descending scaffold stairs stepped on object and twisted ankle. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Jerry Knight | 2019-08-15 15:54 | 2019-07-03 16:05 | 2019-07-03 16:05 | 2019-08-09 11:50 | 2019-07-16 18:30 | 2019-07-03 15:57 | 2019-08-09 12:18 |  |  | Unit 6 Boiler Level 3 |  |  | Robert Wright | Approved Bob Wright | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Tiana Cradduck |  | Introduction: A step-on-object incident occurred inside the MK6 boiler level 3 on July 2, 2019 at approximately 14:30. The Zachry employee was traversing down scaffolding stairs when he stepped on a wedge shaped block of wood. The uneven surface caused his right ankle to roll towards the inside. He subsequently was given icing treatment and Tylenol as needed and continued regulary duties to assure full range of motion. Refer to photographs and drawings for details. Discussion: Interviews: Phone Interview July 10, 2019 07:55 – Contractor involved in incident stated that BEFORE his 4pm break, the wedge-shaped block of wood was not on the stairs so “someone must have dropped it” either during his break or sometime before he traversed down the scaffolding stairs. Juan said that those wedge shaped blocks are used inside the boiler regularly. He obviously did not expect the block to be present, and stated that it was “hard to see inside there”. He subsequently rolled his ankle to the inside, received first aid treatment, and was released back to work. Text Conversation July 10, 2019 08:45 – Contractor involved in incident provided me with photographs of the location with the wedge in its approximate location when the incident occurred. He said it was “absolutely possible” that someone could have dropped the wedge from above, which would make this a dropped object incident as well. Site and Incident Observations: The incident occurred on the boiler furnace scaffolding (Drawing 1). The contractor was completing issued discovery repairs on the furnace water wall tubes, he was at approximately the same elevation as the band of E wallblowers (Drawing 2). The contractor had completed his last water wall repair and was traversing down the furance scaffolding towards the “dance floor” above the coutant slopes (Drawing 2). As the contractor was traversing the furnace scaffolding, he went to step down a scaffold level and stepped on a wooden wedge block (Photographs 1 & 2). A photograph provided by the contractor shows scaffolding above the incident area (Photograph 3). |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | Power Supply Services |  | Jerry Knight | Tiana Cradduck |  | Patrick Coleman | Reviewed on 8/9/2019. | Patrick Coleman |  | Low | [8 empty] | 9.06 Inadequate work planning or programming |  |  | 12.01.1 Inadequate preventative assessment of needs |  | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  |  | A step-on-object incident occurred inside the MK6 boiler level 3 on July 2, 2019 at approximately 14:30. The Zachry employee was traversing down scaffolding stairs when he stepped on a wedge shaped block of wood. The uneven surface caused his right ankle to roll towards the inside. | 27. Poor Housekeeping, Disorder | 4. Fall on Same Level (Slip and Fall, Trip Over) | [5 empty] | Injury / Illness |  | Tiana Cradduck |  | sprain/strained ankle | FALSE |  |  | 4. Fall on Same Level (Slip and Fall, Trip Over) | Jerry Knight | Zachry | Juan Zuniga | Sprain/Strain |  | Ankle | Tiana Cradduck | Right | FALSE | [69 empty] | 18830407
8933 | General Service Center | 2019-07-03 10:00 | Member was traveling north on I-35 when recap tire on left rear outside dual came apart. Tire damaged mud flap, fender, and exhaust stack on truck. | Level 2 |  | FALSE | Property Damage |  |  |  |  | OGE Energy Corp | Charles Shetley | 2019-07-23 11:22 | 2019-07-04 10:52 | 2019-07-04 10:52 | 2019-07-17 10:01 | 2019-07-17 10:00 | 2019-07-03 10:00 | 2019-07-17 11:48 |  | 2019-07-17 10:04 | Traveling north on I-35 near Hwy 412. |  |  | William Young | Reviewed and approved. WCY | Enterprise Services |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Charles Shetley |  | Member was driving F10-206 North on I-35 towards Hwy 412 when a recap on left rear outside duel lost the tread off the casing. When tire came apart the tread hit the fender and mud flap making one more revolution then letting go and hitting stack on the truck. DVIR was conducted and there was no deviation with the tire upon completion. Tires were gauge checked the day before and the day of the incident. All tires were inflated properly at the time of leaving yard. There was no load on the trailer at the time of the incident. |  |  |  | General Service Center | FALSE |  | FALSE | Supply Chain |  | Kyle Cline | Charles Shetley |  | George Wicks | Will reinforce team to check tire pressures as directed. | George Wicks |  | Medium | [13 empty] | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  |  | Member was traveling north on I-35 when recap tire on left rear outside dual came apart. Tire damaged mud flap, fender, and exhaust stack on truck. | 06. Using Defective Equipment | 12. Equipment Failure |  | Approved, Cody Vinyard. | [66 empty] | Damaged mud flap, fender, and exhaust stack. | 2000 | Kyle Cline | Industrial/Heavy Equipment |  | F10-206
8934 | Ada Service Center | 2019-07-03 11:30 | While performing storm work crew was positioning flatbed to remove material. While driving forward front passenger bumper made contact with fire hydrant that was camouflaged by tall grass. Driver walked out path prior to proceeding and used a spotter while positioning, but the hydrant was not detected (see attached pictures) | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Lyle Just | 2019-07-29 07:17 | 2019-07-08 11:39 | 2019-07-08 11:39 | 2019-07-08 12:00 | 2019-07-17 11:30 | 2019-07-03 11:31 | 2019-07-17 11:40 |  |  | 1/2 mile south of Hwy 19 West side of Indian Meridian in Pauls Valley |  |  | Terry Hackett | Reviewed/Approved | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Lyle Just |  | While performing storm work crew was positioning flatbed to remove material. While driving forward front passenger bumper made contact with fire hydrant that was camouflaged by tall grass. Driver walked out path prior to proceeding and used a spotter while positioning, but the hydrant was not detected (see attached pictures) |  |  |  | Ada Service Center | FALSE |  | FALSE | Construction Services |  | Todd Janda | Lyle Just |  | Chad Inman | Make sure that our members consistently stay engaged on the job site no matter what task they are performing, intentionality is key. An example of constant engagement in this case is understanding that utility right a ways are shared by all utilities and we must exhaust all efforts to locate these other utilities, even the ones that we know are not always located through the process of calling in locates. Live Safely; I protect myself and others from injury by constant engagement, always living safely. | Chad Inman |  | Low | [15 empty] | 16.03. Inadequate communication between different organizations | Hydrant is camouflaged by tall grass and not easily detectable. | 02. Failure to Warn | 1. Struck Against (Running or Bumping Into) | [74 empty] | TRUE |  | Pauls Valley | Struck Fixed Object | Drove Forward Into Object | 2007-12-16 18:00 |  | FALSE |  |  | Day Light |  |  | Grass |  | Clear
8937 | Sooner Power Plant | 2019-07-09 16:00 | Member was using a safety knife cutting blue mat material and ran knife across own finger. Small laceration to the top of his finger. Member had no gloves on. This is a first aid. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Supply | Trent Novotny | 2019-08-06 11:09 | 2019-07-09 17:00 | 2019-07-09 17:00 | 2019-07-20 18:34 | 2019-07-23 16:00 | 2019-07-09 16:34 | 2019-07-24 09:17 |  | 2019-07-22 07:26 | Sooner PP Unit 2 Level 3 Near BWCP |  |  | Jesse Murray | Approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Trent Novotny |  | As other members of the day crew was moving rigging on level 4 the member was prepping the area around 2C BWCP by putting blue matting down to prevent dropped objects. The member had gloves on but removed them to apply some duct tape on the ends of the mat to prevent a trip hazard. After applying the duct tape he noticed the mat was bulging around a foot of the scaffolding. He picked up an approved safety knife, held the mat with his right hand, and cut the mat with the self retracting blade. As the member was cutting the blue matting he inadvertently pulled the knife across the top of his right hand middle finger. Member stopped work and returned to the shop for first aid. The member then reported the first aid to his supervisor. Between taping the ends down and cutting the blue matting to fit around the feet of the scaffolding the member failed to put his gloves back on. A SWP was filled out for this job. "Wear gloves" was put on the SWP to mitigate sharp material. We discussed the need to wear gloves when performing a task such as this, but I wanted to know why he did not re-engage. Obviously disgusted with himself the member did not make any excuses for his actions. I suspect, even after being told "we are not in any hurry to get this done" that the member was putting undue pressure on himself to lead this job and get as much work done as possible before he handed the job to the night shift. We also discussed that there are 2 ends to that safety knife and he was fully aware that he should have used to cord cutter end which would not allow his finger to get close to the blade. Another thing we discussed was temperature in that area. Although not a cause, I do believe it contributed to the poor decision. The wet bulb temperature was around 110 degrees. There were fans in place to help mitigate this but they were mainly moving hot air. |  |  | FALSE | Sooner Power Plant | FALSE |  | FALSE | Maintenance |  | Randy Williams | Trent Novotny |  | Frank Brixey | Approved - Keith Brixey 7/24/2019 | Frank Brixey |  | Medium |  |  | 3.04 Fatigue due to sensory overload | [13 empty] | Member failed to utilize PPE to do the task | 07. Failing to Use PPE Properly | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 7/22/2019 | [24 empty] | FALSE |  |  | 2006-12-04 | 1964-11-18 |  | 2019-07-09 07:00 | 0 | 0 | Cleaned laceration and applied band-aid | FALSE |  | Member was prepping the work site by putting blue matting down to prevent dropped objects. As the member was using a safety knife he inadvertently ran the knife across the top of his finger and nail. |  | TRUE | Randy Williams |  | First Aid | Randy Williams |  |  |  |  | Laceration |  | FALSE |  | Plant Mechanic Senior | Finger |  | Right |  | Trent Novotny |  |  | 7/9/2019 7:00:00 AM | 13 | FALSE |  |  | Safety knife | Prepping the area for work on 2C BWCP | [24 empty] | 9587366
8937 | Sooner Power Plant | 2019-07-09 16:00 | Member was using a safety knife cutting blue mat material and ran knife across own finger. Small laceration to the top of his finger. Member had no gloves on. This is a first aid. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Supply | Trent Novotny | 2019-08-06 11:09 | 2019-07-09 17:00 | 2019-07-09 17:00 | 2019-07-20 18:34 | 2019-07-23 16:00 | 2019-07-09 16:34 | 2019-07-24 09:17 |  | 2019-07-22 07:26 | Sooner PP Unit 2 Level 3 Near BWCP |  |  | Jesse Murray | Approve. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Trent Novotny |  | As other members of the day crew was moving rigging on level 4 the member was prepping the area around 2C BWCP by putting blue matting down to prevent dropped objects. The member had gloves on but removed them to apply some duct tape on the ends of the mat to prevent a trip hazard. After applying the duct tape he noticed the mat was bulging around a foot of the scaffolding. He picked up an approved safety knife, held the mat with his right hand, and cut the mat with the self retracting blade. As the member was cutting the blue matting he inadvertently pulled the knife across the top of his right hand middle finger. Member stopped work and returned to the shop for first aid. The member then reported the first aid to his supervisor. Between taping the ends down and cutting the blue matting to fit around the feet of the scaffolding the member failed to put his gloves back on. A SWP was filled out for this job. "Wear gloves" was put on the SWP to mitigate sharp material. We discussed the need to wear gloves when performing a task such as this, but I wanted to know why he did not re-engage. Obviously disgusted with himself the member did not make any excuses for his actions. I suspect, even after being told "we are not in any hurry to get this done" that the member was putting undue pressure on himself to lead this job and get as much work done as possible before he handed the job to the night shift. We also discussed that there are 2 ends to that safety knife and he was fully aware that he should have used to cord cutter end which would not allow his finger to get close to the blade. Another thing we discussed was temperature in that area. Although not a cause, I do believe it contributed to the poor decision. The wet bulb temperature was around 110 degrees. There were fans in place to help mitigate this but they were mainly moving hot air. |  |  | FALSE | Sooner Power Plant | FALSE |  | FALSE | Maintenance |  | Randy Williams | Trent Novotny |  | Frank Brixey | Approved - Keith Brixey 7/24/2019 | Frank Brixey |  | Medium |  |  | 3.02 Fatigue due to task load or duration | [13 empty] | Member failed to utilize PPE to do the task | 07. Failing to Use PPE Properly | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell on 7/22/2019 | [24 empty] | FALSE |  |  | 2006-12-04 | 1964-11-18 |  | 2019-07-09 07:00 | 0 | 0 | Cleaned laceration and applied band-aid | FALSE |  | Member was prepping the work site by putting blue matting down to prevent dropped objects. As the member was using a safety knife he inadvertently ran the knife across the top of his finger and nail. |  | TRUE | Randy Williams |  | First Aid | Randy Williams |  |  |  |  | Laceration |  | FALSE |  | Plant Mechanic Senior | Finger |  | Right |  | Trent Novotny |  |  | 7/9/2019 7:00:00 AM | 13 | FALSE |  |  | Safety knife | Prepping the area for work on 2C BWCP | [24 empty] | 9587366
8938 | Ardmore Service Center | 2019-07-09 11:00 | Member experienced heat stress symptoms. Was taken to medical facility treated and released. | Level 3 |  | FALSE | Member Injury |  | Lindle Coleman | Discussed with Operation leaders | 2019-07-11 09:30 | Power Delivery | Carl Williams | 2019-08-02 08:10 | 2019-07-10 09:52 | 2019-07-10 09:51 | 2019-07-18 10:17 | 2019-07-23 11:00 | 2019-07-09 11:00 | 2019-07-22 14:02 | 2019-07-22 14:55 | 2019-07-18 13:14 | Mannsville Oklahoma 20th and Broadway ( Post Office) |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Carl Williams |  | The morning of Tuesday July 9th 2019, member was performing ground work (i.e. keeping two bucket operators supplied with tools and materials). The work reached a point where someone needed to climb the pole and assist with moving cables. The foreman was preparing to climb the pole when the member requested to perform the task. Foreman stated it was okay with him. When member reached the halfway mark of the pole he began to feel faint and climbed back to the ground. When he reached the ground he went to his knees and began vomiting. Foreman immediately put him in the truck and turned the air conditioner on, provided him water to drink, and put cool wet rags on his forehead and neck. Foreman assessed member and asked him if he needed an ambulance. Member stated he did not, so the foreman called a member at the Ardmore service center and had him come pick the member up and transport back to the service center. Fluids and a cool environment were continuously provided after the occurrence. Members took his blood pressure and heart rate and it was still elevated. At that time the determination was made to transport him to the ER for medical evaluation. Facts Ascertained: Member had been off on vacation for 6 days The Saturday and Sunday prior to returning to work, the member stated he had performed strenuous outdoor activities and the heat index was very high Member stated he drinks energy drinks daily but did not have one the date of the heat stress incident Member experienced minor heat stress symptoms the day before and did not notify Foreman Foreman did notice that member was not fully engaged the day before and upon talking to the member they concluded he was distracted due to things occurring outside of the workplace. Foreman instructed member to go home rest and come back to work in the morning fully engaged. The next day crew arrived at the work site at approximately 0800 heat stress symptoms occurred at approximately 1100 The heat index at 1100 was 93 degrees Fahrenheit Member stated he took several mini breaks from 0800-1100 Member stated he drank 1 12 ounce Gatorade and 2 12 ounce waters throughout the morning Member stated prior to climbing the pole he felt his heart racing, but wasn't sure what was wrong so he went to the cooler and drank another water and put one in his diddy bag to take up the pole with him. Member did not feel the necessity of notifying the crew members what he was experiencing Plenty of Gatorade and water was available Cooling towels where in the cooler Heat index, hydration, and breaks were all discussed during the tailboard | Terry Hackett | Carl Williams | FALSE | Ardmore Service Center | FALSE |  | FALSE | Construction Services |  | Kyle Pitman | Carl Williams |  | Chad Inman | I agree with the corrective actions listed above. We need to stress the importance for our leaders to be having the right discussions regarding our members safety and well being and our members need to be providing our leaders pertinent information regarding their health and well being. | Chad Inman | Lindle Coleman | High |  |  | 3.06 Exposure to temperature extremes |  | 5.06 Lack of situational awareness |  | 7.08 Improper attempt to gain attention | [9 empty] | Member performed strenuous outdoor physical activity the weekend prior to returning. Member drinks energy drink daily. 3.06 is referencing weekend temperatures and activities. | 20. Failure to Communicate, Coordinate | 11. Overstress, Overpressure, Overexertion, Ergonomic | Approved | Reviewed and approved TMH | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2018-11-19 | 1993-03-02 |  | 2019-07-09 07:00 | 0 | 0 | Moved to cool area Gave him fluids Cold wet rags on head and neck | FALSE |  | Heat Stress |  | TRUE | John McGehee |  | Recordable | John McGehee | TRUE |  |  |  | Heat Stroke/Exhaustion |  | TRUE |  | Distribution Lineman Apprentice | Unknown | All Other Illnesses | Multiple | TRUE | Kyle Pitman | TRUE | 2019 | 7/9/2019 7:00:00 AM | 8 months | TRUE | FALSE | TRUE | Heat | Member had been doing some ground work for the crew finish ground work put tools on stared up pole when he started feeling bad. | [24 empty] | 7959215
8938 | Ardmore Service Center | 2019-07-09 11:00 | Member experienced heat stress symptoms. Was taken to medical facility treated and released. | Level 3 |  | FALSE | Member Injury |  | Lindle Coleman | Discussed with Operation leaders | 2019-07-11 09:30 | Power Delivery | Carl Williams | 2019-08-02 08:10 | 2019-07-10 09:52 | 2019-07-10 09:51 | 2019-07-18 10:17 | 2019-07-23 11:00 | 2019-07-09 11:00 | 2019-07-22 14:02 | 2019-07-22 14:55 | 2019-07-18 13:14 | Mannsville Oklahoma 20th and Broadway ( Post Office) |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Carl Williams |  | The morning of Tuesday July 9th 2019, member was performing ground work (i.e. keeping two bucket operators supplied with tools and materials). The work reached a point where someone needed to climb the pole and assist with moving cables. The foreman was preparing to climb the pole when the member requested to perform the task. Foreman stated it was okay with him. When member reached the halfway mark of the pole he began to feel faint and climbed back to the ground. When he reached the ground he went to his knees and began vomiting. Foreman immediately put him in the truck and turned the air conditioner on, provided him water to drink, and put cool wet rags on his forehead and neck. Foreman assessed member and asked him if he needed an ambulance. Member stated he did not, so the foreman called a member at the Ardmore service center and had him come pick the member up and transport back to the service center. Fluids and a cool environment were continuously provided after the occurrence. Members took his blood pressure and heart rate and it was still elevated. At that time the determination was made to transport him to the ER for medical evaluation. Facts Ascertained: Member had been off on vacation for 6 days The Saturday and Sunday prior to returning to work, the member stated he had performed strenuous outdoor activities and the heat index was very high Member stated he drinks energy drinks daily but did not have one the date of the heat stress incident Member experienced minor heat stress symptoms the day before and did not notify Foreman Foreman did notice that member was not fully engaged the day before and upon talking to the member they concluded he was distracted due to things occurring outside of the workplace. Foreman instructed member to go home rest and come back to work in the morning fully engaged. The next day crew arrived at the work site at approximately 0800 heat stress symptoms occurred at approximately 1100 The heat index at 1100 was 93 degrees Fahrenheit Member stated he took several mini breaks from 0800-1100 Member stated he drank 1 12 ounce Gatorade and 2 12 ounce waters throughout the morning Member stated prior to climbing the pole he felt his heart racing, but wasn't sure what was wrong so he went to the cooler and drank another water and put one in his diddy bag to take up the pole with him. Member did not feel the necessity of notifying the crew members what he was experiencing Plenty of Gatorade and water was available Cooling towels where in the cooler Heat index, hydration, and breaks were all discussed during the tailboard | Terry Hackett | Carl Williams | FALSE | Ardmore Service Center | FALSE |  | FALSE | Construction Services |  | Kyle Pitman | Carl Williams |  | Chad Inman | I agree with the corrective actions listed above. We need to stress the importance for our leaders to be having the right discussions regarding our members safety and well being and our members need to be providing our leaders pertinent information regarding their health and well being. | Chad Inman | Lindle Coleman | High | [6 empty] | 7.08 Improper attempt to gain attention | [9 empty] | Member did not feel the need to notify crew of the symptoms he was experiencing. 07.08 Member was trying to "make a hand" and felt that he could perform the task without issue. | 19. Failure to React, Correct | 11. Overstress, Overpressure, Overexertion, Ergonomic | Approved | Reviewed and approved TMH | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2018-11-19 | 1993-03-02 |  | 2019-07-09 07:00 | 0 | 0 | Moved to cool area Gave him fluids Cold wet rags on head and neck | FALSE |  | Heat Stress |  | TRUE | John McGehee |  | Recordable | John McGehee | TRUE |  |  |  | Heat Stroke/Exhaustion |  | TRUE |  | Distribution Lineman Apprentice | Unknown | All Other Illnesses | Multiple | TRUE | Kyle Pitman | TRUE | 2019 | 7/9/2019 7:00:00 AM | 8 months | TRUE | FALSE | TRUE | Heat | Member had been doing some ground work for the crew finish ground work put tools on stared up pole when he started feeling bad. | [24 empty] | 7959215
8939 | Enid Service Center | 2019-07-09 08:30 | An OGE member was walking up to a Wright Tree Service (WTS) tree crew work site and distracted the foreman who walks into a barricaded work zone and is nearly struck by falling tree limb. | Level 1 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services | Grant Ehlen | 2019-07-15 10:27 | 2019-07-10 13:40 | 2019-07-10 13:40 | 2019-07-10 15:26 | 2019-07-23 08:30 | 2019-07-10 13:03 | 2019-07-11 14:08 |  |  | Enid, OK service area. |  |  | Jerrie Looney | Approved. J. Looney, 7/15/19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Grant Ehlen |  | The OGE North West District Staff Forester was conducting Safety and Quality ISNet audits in Enid, OK. The WTS crew foreman sees the forester walking up to the job site and walks through the crew's active "Drop Zone" area to get the crew's Job Briefing to present to the forester. As the foreman walked through the drop zone the other crew member was aloft in a bucket and dropped a small brushy limb, less than 1/2 inch in diameter and 3 feet long, and it slightly brushed the left shoulder and arm of the foreman as it fell to the ground. After talking to foreman and worker the conclusion is that both people were complacent in their focus on safety. The foreman failed to realize he was in a work zone as he walked across the work zone. He was focused on getting the job briefing and not focused on where he was. The worker aloft failed to stop and check where the foreman was in relation to the work zone before he dropped the brush to the ground. |  |  |  | Enid Service Center | FALSE |  | TRUE | PD - Resource Planning & Coord |  | Grant Ehlen | Christopher Martin |  | Christopher Martin | I agree with the near miss and we have discussed the situation. No further action needed. | Christopher Martin |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [10 empty] | 16.02 Inadequate vertical communication between supervisor and person | The OGE North West District Staff Forester was conducting Safety and Quality ISNet audits in Enid, OK. The WTS crew foreman sees the forester walking up to the job site and walks through the crew's active "Drop Zone" area to get the crew's Job Briefing to present to the forester. As the foreman walked through the drop zone the other crew member was aloft in a bucket and dropped a small brushy limb, less than 1/2 inch in diameter and 3 feet long, and it slightly brushed the left shoulder and arm of the foreman as it fell to the ground. | 16. Failure to Follow Procedure, Policy, Practice | 2. Struck By (Hit By Moving Object) | [5 empty] | Environmental |  | Grant Ehlen | [5 empty] | 2. Struck By (Hit By Moving Object) | Grant Ehlen | Wright Tree Service | Dean Flacher |  |  |  | Grant Ehlen
8940 | Seminole PP; EGX Gath/Trans | 2019-07-10 13:00 | While establishing the boundaries on a LOTO, the operators performing the tagging opened the breakers on the 2A FDF and 2B FDF recirc damper drives. Being unable to physically access the actual damper drives due to their elevated location the operators attempted to start the damper drives from the Control Room DCS. While performing the bump test on 2A FDF recirc damper they observed that the damper position responded to the open command indicating that the damper drive still had power. The operators notified the Shift Supervisor of the issue and the process of establishing the LOTO was stopped. | Level 1 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Gregory Fry | 2019-07-29 08:56 | 2019-07-10 17:11 | 2019-07-10 17:11 | 2019-07-11 15:59 | 2019-07-24 13:00 | 2019-07-10 13:30 | 2019-07-12 08:50 |  |  | Seminole Unit 2 Boiler MOV Breaker Panel |  |  | Chrysty Dorsey | Excellent job on the incident call. Reviewed and approved. | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Gregory Fry |  | After the establishing of the LOTO was stopped, plant electricians were notified of the situation and began troubleshooting the cause of the incident. The equipment involved in this incident was recently installed in the FDF upgrade project so the electrician went to the MOV panel which housed some of the breakers that supplied power to the new equipment. It was then determined by bump testing the 2A and 2B recirc dampers and also the 2A and 2B inlet dampers that the "A" side equipment wiring had been landed on the wrong breakers during installation. This incident was given a "Low" ranking due to the fact that the plant electrician stated that had a proper verification not been able to be achieved, he would have accessed the recirc damper drives with a man lift in order to gain access to the motor makeup box and verify the power locally. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | TRUE | Operations |  | Danny Huckleberry | Gregory Fry |  | Paul Schoelen | Review Complete | Paul Schoelen |  | Low | [9 empty] | 10.06 Inadequate or improper controls | [6 empty] | During construction, proper checkout of the involved equipment was not conducted or properly followed up during the conclusion of the project. | 09. Improper Placement | 9. Abnormal Operation | [92 empty] | 9587871
8940 | Seminole PP; EGX Gath/Trans | 2019-07-10 13:00 | While establishing the boundaries on a LOTO, the operators performing the tagging opened the breakers on the 2A FDF and 2B FDF recirc damper drives. Being unable to physically access the actual damper drives due to their elevated location the operators attempted to start the damper drives from the Control Room DCS. While performing the bump test on 2A FDF recirc damper they observed that the damper position responded to the open command indicating that the damper drive still had power. The operators notified the Shift Supervisor of the issue and the process of establishing the LOTO was stopped. | Level 1 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Gregory Fry | 2019-07-29 08:56 | 2019-07-10 17:11 | 2019-07-10 17:11 | 2019-07-11 15:59 | 2019-07-24 13:00 | 2019-07-10 13:30 | 2019-07-12 08:50 |  |  | Seminole Unit 2 Boiler MOV Breaker Panel |  |  | Chrysty Dorsey | Excellent job on the incident call. Reviewed and approved. | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Gregory Fry |  | After the establishing of the LOTO was stopped, plant electricians were notified of the situation and began troubleshooting the cause of the incident. The equipment involved in this incident was recently installed in the FDF upgrade project so the electrician went to the MOV panel which housed some of the breakers that supplied power to the new equipment. It was then determined by bump testing the 2A and 2B recirc dampers and also the 2A and 2B inlet dampers that the "A" side equipment wiring had been landed on the wrong breakers during installation. This incident was given a "Low" ranking due to the fact that the plant electrician stated that had a proper verification not been able to be achieved, he would have accessed the recirc damper drives with a man lift in order to gain access to the motor makeup box and verify the power locally. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | TRUE | Operations |  | Danny Huckleberry | Gregory Fry |  | Paul Schoelen | Review Complete | Paul Schoelen |  | Low | [9 empty] | 10.07 Inadequate monitoring of initial operation | [6 empty] | During construction, proper checkout of the involved equipment was not conducted or properly followed up during the conclusion of the project. | 09. Improper Placement | 9. Abnormal Operation | [92 empty] | 9587871
8940 | Seminole PP; EGX Gath/Trans | 2019-07-10 13:00 | While establishing the boundaries on a LOTO, the operators performing the tagging opened the breakers on the 2A FDF and 2B FDF recirc damper drives. Being unable to physically access the actual damper drives due to their elevated location the operators attempted to start the damper drives from the Control Room DCS. While performing the bump test on 2A FDF recirc damper they observed that the damper position responded to the open command indicating that the damper drive still had power. The operators notified the Shift Supervisor of the issue and the process of establishing the LOTO was stopped. | Level 1 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Gregory Fry | 2019-07-29 08:56 | 2019-07-10 17:11 | 2019-07-10 17:11 | 2019-07-11 15:59 | 2019-07-24 13:00 | 2019-07-10 13:30 | 2019-07-12 08:50 |  |  | Seminole Unit 2 Boiler MOV Breaker Panel |  |  | Chrysty Dorsey | Excellent job on the incident call. Reviewed and approved. | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Gregory Fry |  | After the establishing of the LOTO was stopped, plant electricians were notified of the situation and began troubleshooting the cause of the incident. The equipment involved in this incident was recently installed in the FDF upgrade project so the electrician went to the MOV panel which housed some of the breakers that supplied power to the new equipment. It was then determined by bump testing the 2A and 2B recirc dampers and also the 2A and 2B inlet dampers that the "A" side equipment wiring had been landed on the wrong breakers during installation. This incident was given a "Low" ranking due to the fact that the plant electrician stated that had a proper verification not been able to be achieved, he would have accessed the recirc damper drives with a man lift in order to gain access to the motor makeup box and verify the power locally. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | TRUE | Operations |  | Danny Huckleberry | Gregory Fry |  | Paul Schoelen | Review Complete | Paul Schoelen |  | Low | [9 empty] | 10.03 Inadequate standards, specifications and/or design criteria | [6 empty] | During construction, proper checkout of the involved equipment was not conducted or properly followed up during the conclusion of the project. | 09. Improper Placement | 9. Abnormal Operation | [92 empty] | 9587871
8940 | Seminole PP; EGX Gath/Trans | 2019-07-10 13:00 | While establishing the boundaries on a LOTO, the operators performing the tagging opened the breakers on the 2A FDF and 2B FDF recirc damper drives. Being unable to physically access the actual damper drives due to their elevated location the operators attempted to start the damper drives from the Control Room DCS. While performing the bump test on 2A FDF recirc damper they observed that the damper position responded to the open command indicating that the damper drive still had power. The operators notified the Shift Supervisor of the issue and the process of establishing the LOTO was stopped. | Level 1 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Gregory Fry | 2019-07-29 08:56 | 2019-07-10 17:11 | 2019-07-10 17:11 | 2019-07-11 15:59 | 2019-07-24 13:00 | 2019-07-10 13:30 | 2019-07-12 08:50 |  |  | Seminole Unit 2 Boiler MOV Breaker Panel |  |  | Chrysty Dorsey | Excellent job on the incident call. Reviewed and approved. | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Gregory Fry |  | After the establishing of the LOTO was stopped, plant electricians were notified of the situation and began troubleshooting the cause of the incident. The equipment involved in this incident was recently installed in the FDF upgrade project so the electrician went to the MOV panel which housed some of the breakers that supplied power to the new equipment. It was then determined by bump testing the 2A and 2B recirc dampers and also the 2A and 2B inlet dampers that the "A" side equipment wiring had been landed on the wrong breakers during installation. This incident was given a "Low" ranking due to the fact that the plant electrician stated that had a proper verification not been able to be achieved, he would have accessed the recirc damper drives with a man lift in order to gain access to the motor makeup box and verify the power locally. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | TRUE | Operations |  | Danny Huckleberry | Gregory Fry |  | Paul Schoelen | Review Complete | Paul Schoelen |  | Low | [9 empty] | 10.04 Inadequate monitoring of construction | [6 empty] | During construction, proper checkout of the involved equipment was not conducted or properly followed up during the conclusion of the project. | 09. Improper Placement | 9. Abnormal Operation | [92 empty] | 9587871
8940 | Seminole PP; EGX Gath/Trans | 2019-07-10 13:00 | While establishing the boundaries on a LOTO, the operators performing the tagging opened the breakers on the 2A FDF and 2B FDF recirc damper drives. Being unable to physically access the actual damper drives due to their elevated location the operators attempted to start the damper drives from the Control Room DCS. While performing the bump test on 2A FDF recirc damper they observed that the damper position responded to the open command indicating that the damper drive still had power. The operators notified the Shift Supervisor of the issue and the process of establishing the LOTO was stopped. | Level 1 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Gregory Fry | 2019-07-29 08:56 | 2019-07-10 17:11 | 2019-07-10 17:11 | 2019-07-11 15:59 | 2019-07-24 13:00 | 2019-07-10 13:30 | 2019-07-12 08:50 |  |  | Seminole Unit 2 Boiler MOV Breaker Panel |  |  | Chrysty Dorsey | Excellent job on the incident call. Reviewed and approved. | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Gregory Fry |  | After the establishing of the LOTO was stopped, plant electricians were notified of the situation and began troubleshooting the cause of the incident. The equipment involved in this incident was recently installed in the FDF upgrade project so the electrician went to the MOV panel which housed some of the breakers that supplied power to the new equipment. It was then determined by bump testing the 2A and 2B recirc dampers and also the 2A and 2B inlet dampers that the "A" side equipment wiring had been landed on the wrong breakers during installation. This incident was given a "Low" ranking due to the fact that the plant electrician stated that had a proper verification not been able to be achieved, he would have accessed the recirc damper drives with a man lift in order to gain access to the motor makeup box and verify the power locally. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | TRUE | Operations |  | Danny Huckleberry | Gregory Fry |  | Paul Schoelen | Review Complete | Paul Schoelen |  | Low | [9 empty] | 10.05 Inadequate assessment of operational readiness | [6 empty] | During construction, proper checkout of the involved equipment was not conducted or properly followed up during the conclusion of the project. | 09. Improper Placement | 9. Abnormal Operation | [92 empty] | 9587871
8940 | Seminole PP; EGX Gath/Trans | 2019-07-10 13:00 | While establishing the boundaries on a LOTO, the operators performing the tagging opened the breakers on the 2A FDF and 2B FDF recirc damper drives. Being unable to physically access the actual damper drives due to their elevated location the operators attempted to start the damper drives from the Control Room DCS. While performing the bump test on 2A FDF recirc damper they observed that the damper position responded to the open command indicating that the damper drive still had power. The operators notified the Shift Supervisor of the issue and the process of establishing the LOTO was stopped. | Level 1 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Gregory Fry | 2019-07-29 08:56 | 2019-07-10 17:11 | 2019-07-10 17:11 | 2019-07-11 15:59 | 2019-07-24 13:00 | 2019-07-10 13:30 | 2019-07-12 08:50 |  |  | Seminole Unit 2 Boiler MOV Breaker Panel |  |  | Chrysty Dorsey | Excellent job on the incident call. Reviewed and approved. | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Gregory Fry |  | After the establishing of the LOTO was stopped, plant electricians were notified of the situation and began troubleshooting the cause of the incident. The equipment involved in this incident was recently installed in the FDF upgrade project so the electrician went to the MOV panel which housed some of the breakers that supplied power to the new equipment. It was then determined by bump testing the 2A and 2B recirc dampers and also the 2A and 2B inlet dampers that the "A" side equipment wiring had been landed on the wrong breakers during installation. This incident was given a "Low" ranking due to the fact that the plant electrician stated that had a proper verification not been able to be achieved, he would have accessed the recirc damper drives with a man lift in order to gain access to the motor makeup box and verify the power locally. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | TRUE | Operations |  | Danny Huckleberry | Gregory Fry |  | Paul Schoelen | Review Complete | Paul Schoelen |  | Low | [9 empty] | 10.08 Inadequate evaluation of changes | [6 empty] | During construction, proper checkout of the involved equipment was not conducted or properly followed up during the conclusion of the project. | 09. Improper Placement | 9. Abnormal Operation | [92 empty] | 9587871
8941 | South District Service Center | 2019-07-10 09:00 | The crew were on pulling in to dump woodchips and ran into a parked truck causing dents and scratches. | Level 1 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Christopher Martin | 2019-07-24 10:05 | 2019-07-11 13:25 | 2019-07-11 13:25 | 2019-07-23 16:03 | 2019-07-24 09:00 | 2019-07-11 13:19 | 2019-07-23 16:11 |  |  | Private residents yard in Norman |  |  | Jerrie Looney | Approved. J. Looney 7/24/19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Christopher Martin |  | The Crew arrived at the property to unload woodchips. The crew foreperson contacted the customer for the unloading spot and then proceeded to drive onto the customer's property through their driveway. While turning around in the driveway the driver drove past a parked 1995 F-150. He continued on taking a sharp right turn not realizing the position of the rear of his vehicle in relation to the parked vehicle. While making the turn the trucks tailgate made contact with the left rear side of the customer's parked vehicle causing scratches and dents to the vehicle. |  |  |  | South District Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Brian Hall | Christopher Martin |  | Christopher Martin | I agree with the corrective actions discussed and we will be following up to make sure they are holding the driver's training they stated they would. | Christopher Martin |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [8 empty] | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  | 16.01 Inadequate horizontal communication between peers | The Crew arrived at the property to unload woodchips. The crew foreperson contacted the customer for the unloading spot and then proceeded to drive onto the customer's property through their driveway. While turning around in the driveway the driver drove past a parked 1995 F-150. He continued on taking a sharp right turn not realizing the position of the rear of his vehicle in relation to the parked vehicle. While making the turn the trucks tailgate made contact with the left rear side of the customer's parked vehicle causing scratches and dents to the vehicle. | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) | [5 empty] | Vehicle |  | Christopher Martin | Dents and scratches on vehicle side |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Brian Hall | Asplundh | Sheldon Rider |  | Vehicle (not related to vehicle's operation) |  | Christopher Martin |  |  |  |  | FALSE
8941 | South District Service Center | 2019-07-10 09:00 | The crew were on pulling in to dump woodchips and ran into a parked truck causing dents and scratches. | Level 1 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Christopher Martin | 2019-07-24 10:05 | 2019-07-11 13:25 | 2019-07-11 13:25 | 2019-07-23 16:03 | 2019-07-24 09:00 | 2019-07-11 13:19 | 2019-07-23 16:11 |  |  | Private residents yard in Norman |  |  | Jerrie Looney | Approved. J. Looney 7/24/19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Christopher Martin |  | The Crew arrived at the property to unload woodchips. The crew foreperson contacted the customer for the unloading spot and then proceeded to drive onto the customer's property through their driveway. While turning around in the driveway the driver drove past a parked 1995 F-150. He continued on taking a sharp right turn not realizing the position of the rear of his vehicle in relation to the parked vehicle. While making the turn the trucks tailgate made contact with the left rear side of the customer's parked vehicle causing scratches and dents to the vehicle. |  |  |  | South District Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Brian Hall | Christopher Martin |  | Christopher Martin | I agree with the corrective actions discussed and we will be following up to make sure they are holding the driver's training they stated they would. | Christopher Martin |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [8 empty] | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  | 16.01 Inadequate horizontal communication between peers | The Crew arrived at the property to unload woodchips. The crew foreperson contacted the customer for the unloading spot and then proceeded to drive onto the customer's property through their driveway. While turning around in the driveway the driver drove past a parked 1995 F-150. He continued on taking a sharp right turn not realizing the position of the rear of his vehicle in relation to the parked vehicle. While making the turn the trucks tailgate made contact with the left rear side of the customer's parked vehicle causing scratches and dents to the vehicle. | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Christopher Martin | Dents and scratches on vehicle side |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Brian Hall | Asplundh | Sheldon Rider |  | Vehicle (not related to vehicle's operation) |  | Christopher Martin |  |  |  |  | FALSE
8942 | Metro Service Center | 2019-03-26 14:30 | Member was operating an electrical pipe threading tool, threading 1 1/2 inch pipe. The tool caught hold of the pipe and the handle contacted member's knee and took him to the ground. Members knee was sore the next day, he does not wish to seek any medical attention at this time. OGE nurse was notified of the event. The member was still experiencing pain 3 months after the incident occurred. The decision was made to get evaluation done by OGE doctor. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Kenny La Ferney | 2019-07-15 08:15 | 2019-07-11 14:46 | 2019-07-11 14:46 | 2019-07-11 15:29 | 2019-04-09 14:30 | 2019-07-11 10:47 | 2019-07-15 07:04 |  | 2019-07-11 15:34 | Salt Creek Substation, Coalgate OK |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Kenny La Ferney |  | Member was threading conduit with a had operated threading tool. The tool struck the member in his right knee which caused his some discomfort but he continued working not thinking he had any injury. Once it was reported we discussed rather he needed to see a doctor. He did not feel it was necessary to see a doctor and went on to work for next three months. It was still giving him some trouble so the decision was made to have the knee evaluated by OGE doctor. After evaluation they determined he had some damage to the knee. After reviewing the tool choice the decision was made to purchase support brackets to prevent this from reoccurring. |  |  | TRUE | Metro Service Center | FALSE |  | FALSE | Construction Services | 8785 | Nicholas Dean | Kenny La Ferney |  | Gary Lassley | After reviewing the tool choice the decision was made to purchase support brackets to prevent this from reoccurring. Kenny La Ferney has completed this task. Kenny has also communicated the new work procedure to all of the other Substation Construction Crews. | Gary Lassley |  | Medium | [12 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | The tool was being operated properly but without the added support bracket. The support bracket prevents the tool from slipping or contacting the user. | 21. Inadequate Guards or Barriers | 2. Struck By (Hit By Moving Object) |  | Reviewed and approve corrective actions. cm | [24 empty] | FALSE |  | Days away from Work (H) | 2007-01-02 | 1981-03-10 |  | 2019-03-26 07:00 | 11 | 169 |  | FALSE |  | Member was struck by the pipe threading tool |  |  | Nicholas Dean |  | Recordable | Nicholas Dean |  |  |  |  | Internal Injuries |  | TRUE |  | Substation Construction Technician | Knee | Injury | Right | TRUE | David Rogers | TRUE | 2019 | 3/26/2019 7:00:00 AM | 12 | FALSE |  |  | pipe threading tool | Threading conduit with Rigid pipe threading tool | [24 empty] | 1646182
8943 | Horseshoe Lake Power Plant | 2019-07-11 13:30 | Siemens welder was tack welding on the LP upper half shell and felt discomfort in his eye during the morning that became progressively worse. Around 11:00 he looked in a mirror and noticed a foreign object in his eye. He then notified his supervisor and Workcare was called. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Daniel Perry | 2019-07-30 10:13 | 2019-07-12 12:16 | 2019-07-12 12:16 | 2019-07-24 19:11 | 2019-07-25 13:30 | 2019-07-12 11:58 | 2019-07-24 19:13 |  |  | Horseshoe Lake Unit 7 Basement. |  |  | Ashley Harris | Approved, Ashley Harris- July 30,2019 | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Daniel Perry |  | Today 7/11/19 TS had a welder, Darrell Kirkpatrick, at Horseshoe Lake that was welding overhead on the LP cover tack welding seal screws. The upper half was on cribbing and he was TIG welding overhead. He had prescription safety glasses on along with a welding hood. The hood was raised and lowered as the work went along. During the morning the welder began to notice some discomfort in his eye. As the morning went along it became progressively worse until around 11:00 local time he went and looked in a mirror. The welder noticed a foreign object in the eye and site TS lead was notified and WorkCare was called. The contractor did not use any eyewash stations at the facility. An appointment at a local clinic was made for 1:30 local time. The contractor drove himself to the clinic. The doctor had to numb his eye and a metal flake was extracted. The welder was prescribed drops and released. Welder had a follow up the next day and returned to work with no restrictions. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Maintenance |  | Daniel Perry | Daniel Perry |  | Daniel Perry | I have reviewed this investigation and I approve. | Daniel Perry |  | Low | [12 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | Contract member failed to adequately protect from foreign debris entering his eye while working. | 07. Failing to Use PPE Properly | 2. Struck By (Hit By Moving Object) | [5 empty] | Injury / Illness |  | Daniel Perry |  | Foreign material in eye. | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Daniel Perry | Siemens | Darrell Kirkpatrick | Foreign Body |  | Eye | Daniel Perry | Front | FALSE | [69 empty] | 9581777
8944 | Northeast District Service Cen | 2019-07-15 08:30 | While performing pole top rescue, rescue dummy fell striking member | Level 3 |  | FALSE | Member Injury |  | Lindle Coleman | Reviewed with operations | 2019-07-16 10:22 | Power Delivery | Randell Gilbert | 2019-08-20 08:15 | 2019-07-15 14:12 | 2019-07-15 14:12 | 2019-07-29 11:52 | 2019-07-29 07:30 | 2019-07-15 14:05 | 2019-08-02 08:56 | 2019-08-05 09:07 | 2019-07-29 12:26 | Kellyville Service Center Pole Yard |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Randell Gilbert |  | The morning started by watching the training video and covering the importance of a successful rescue. The team moved to the North end of the Pole yard where there are several poles set up for training. The group held a Tailboard and completed Vimocity stretches. Several ¼" P-line ropes were cut to length. The bucket was set up to maneuver manikin into place around the pole through cross arm braces. The member climbed up the pole and successfully performed the rescue. While the manikin was on the ground after the rescue the Intern made one bowline knot on the manikin for the next rescue. The member who had performed the rescue, remained at the top of the pole to assist in helping the bucket hang the manikin. The bucket remained holding the manikin, so the member could descend and maneuver past the manikin. The member started his descent and about 10ft from the ground the member in the bucket unhooked from the manikin. The member on the pole took a few more steps and then was struck by the falling manikin. The Northside rope of the manikin’s belt came untied swinging the manikin toward the Southside of the pole and the weight of the manikin caused the other knot in the rope to come untied resulting in the manikin falling and striking the member. The member was struck in the head and back, knocking off his hardhat and safety glasses causing him to cut out of the pole then striking the pole with his left cheek. Several members rushed to his aid. The injured member immediately asked for an ambulance and stated he was in a lot of pain in his neck and back area. Several members on the ground assisted in unbuckling his safety while supporting his neck and carefully laid him down to the ground. His supervisor, called 911 at 8:30 am and directed another member to drive to the front gate and wait on the ambulance and guide them to the location. The ambulance arrived at 8:44 am and transported the member to the hospital. Facts Ascertained: -Members discussed during tailboard to climb down southeast side of the pole to reduce amount of gaffs marks on one side of the pole -This was the first pole top rescue training of the day, with 21 members on site -The manikin was hung on the eastside of the pole -Both knots on P line did come untied (NOTE: There were no knots found on the rope or on the belt) - Intern tied one knot and the investigation team was not able to determine who tied the other -Quarter inch rope measured at 24" & 22" -Intern made one tie (the side that was cut) to the Northside of the rope and it was not inspected by other members prior to lifting -Both members, in the bucket and on the pole, training is up-to date -Intern was on his second internship (First with OGE as of 7-08-19) | Michael Eckart | Randell Gilbert | FALSE | Northeast District Service Cen | FALSE |  | FALSE | Construction Services |  | Randell Gilbert | Michael Fox |  | Chad Inman | I approve the Corrective Actions. Thank you for the time and commitment that the investigation team put into this. I'm also appreciative of the decision to move forward with the correct tool for this application. | Chad Inman | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.11 Inadequate matching of individual qualifications and job/task requirements |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Failed to inspect and verify condition of knot made by Intern 5.01: Interns are sent to us to learn and gain field experience. It is our responsibility to check and monitor their work 9.11: Intern should not have been allowed to secure belt to manikin without adequate verification 14.01.4: We currently do not have documented work practices for how to secure the manikin to the pole | 18. Failure to Check, Monitor | 2. Struck By (Hit By Moving Object) | approved | I approve. | [24 empty] | FALSE |  | Days away from Work (H) | 2007-04-23 | 1984-02-18 |  | 2019-07-15 07:00 | 6 | 77 |  | FALSE |  | While descending pole after performing pole top rescue, dummy fell striking member. |  |  | Dwayne Fox |  | Recordable | Dwayne Fox | TRUE |  |  |  | Contusion |  | TRUE |  | Lineman | Back | Injury |  | TRUE | Donald Melson | TRUE | 2019 | 7/15/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | Rescue dummy
8944 | Northeast District Service Cen | 2019-07-15 08:30 | While performing pole top rescue, rescue dummy fell striking member | Level 3 |  | FALSE | Member Injury |  | Lindle Coleman | Reviewed with operations | 2019-07-16 10:22 | Power Delivery | Randell Gilbert | 2019-08-20 08:15 | 2019-07-15 14:12 | 2019-07-15 14:12 | 2019-07-29 11:52 | 2019-07-29 07:30 | 2019-07-15 14:05 | 2019-08-02 08:56 | 2019-08-05 09:07 | 2019-07-29 12:26 | Kellyville Service Center Pole Yard |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Randell Gilbert |  | The morning started by watching the training video and covering the importance of a successful rescue. The team moved to the North end of the Pole yard where there are several poles set up for training. The group held a Tailboard and completed Vimocity stretches. Several ¼" P-line ropes were cut to length. The bucket was set up to maneuver manikin into place around the pole through cross arm braces. The member climbed up the pole and successfully performed the rescue. While the manikin was on the ground after the rescue the Intern made one bowline knot on the manikin for the next rescue. The member who had performed the rescue, remained at the top of the pole to assist in helping the bucket hang the manikin. The bucket remained holding the manikin, so the member could descend and maneuver past the manikin. The member started his descent and about 10ft from the ground the member in the bucket unhooked from the manikin. The member on the pole took a few more steps and then was struck by the falling manikin. The Northside rope of the manikin’s belt came untied swinging the manikin toward the Southside of the pole and the weight of the manikin caused the other knot in the rope to come untied resulting in the manikin falling and striking the member. The member was struck in the head and back, knocking off his hardhat and safety glasses causing him to cut out of the pole then striking the pole with his left cheek. Several members rushed to his aid. The injured member immediately asked for an ambulance and stated he was in a lot of pain in his neck and back area. Several members on the ground assisted in unbuckling his safety while supporting his neck and carefully laid him down to the ground. His supervisor, called 911 at 8:30 am and directed another member to drive to the front gate and wait on the ambulance and guide them to the location. The ambulance arrived at 8:44 am and transported the member to the hospital. Facts Ascertained: -Members discussed during tailboard to climb down southeast side of the pole to reduce amount of gaffs marks on one side of the pole -This was the first pole top rescue training of the day, with 21 members on site -The manikin was hung on the eastside of the pole -Both knots on P line did come untied (NOTE: There were no knots found on the rope or on the belt) - Intern tied one knot and the investigation team was not able to determine who tied the other -Quarter inch rope measured at 24" & 22" -Intern made one tie (the side that was cut) to the Northside of the rope and it was not inspected by other members prior to lifting -Both members, in the bucket and on the pole, training is up-to date -Intern was on his second internship (First with OGE as of 7-08-19) | Michael Eckart | Randell Gilbert | FALSE | Northeast District Service Cen | FALSE |  | FALSE | Construction Services |  | Randell Gilbert | Michael Fox |  | Chad Inman | I approve the Corrective Actions. Thank you for the time and commitment that the investigation team put into this. I'm also appreciative of the decision to move forward with the correct tool for this application. | Chad Inman | Lindle Coleman | High | [8 empty] | 9.09 Inadequate identification and evaluation of loss exposures |  |  |  | 13.01 Inadequate assessment of needs and risks |  |  |  | P line/ rope is not engineered and designed for pole top rescue 9.09 & 13.01: Prior to this occurrence all T&D Locations performed pole top rescue using knots to secure the manikin to the pole. The need to use equipment designed for this task was not identified. | 22. Inadequate or Improper Protective Equipment | 2. Struck By (Hit By Moving Object) | approved | I approve. | [24 empty] | FALSE |  | Days away from Work (H) | 2007-04-23 | 1984-02-18 |  | 2019-07-15 07:00 | 6 | 77 |  | FALSE |  | While descending pole after performing pole top rescue, dummy fell striking member. |  |  | Dwayne Fox |  | Recordable | Dwayne Fox | TRUE |  |  |  | Contusion |  | TRUE |  | Lineman | Back | Injury |  | TRUE | Donald Melson | TRUE | 2019 | 7/15/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | Rescue dummy
8944 | Northeast District Service Cen | 2019-07-15 08:30 | While performing pole top rescue, rescue dummy fell striking member | Level 3 |  | FALSE | Member Injury |  | Lindle Coleman | Reviewed with operations | 2019-07-16 10:22 | Power Delivery | Randell Gilbert | 2019-08-20 08:15 | 2019-07-15 14:12 | 2019-07-15 14:12 | 2019-07-29 11:52 | 2019-07-29 07:30 | 2019-07-15 14:05 | 2019-08-02 08:56 | 2019-08-05 09:07 | 2019-07-29 12:26 | Kellyville Service Center Pole Yard |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Randell Gilbert |  | The morning started by watching the training video and covering the importance of a successful rescue. The team moved to the North end of the Pole yard where there are several poles set up for training. The group held a Tailboard and completed Vimocity stretches. Several ¼" P-line ropes were cut to length. The bucket was set up to maneuver manikin into place around the pole through cross arm braces. The member climbed up the pole and successfully performed the rescue. While the manikin was on the ground after the rescue the Intern made one bowline knot on the manikin for the next rescue. The member who had performed the rescue, remained at the top of the pole to assist in helping the bucket hang the manikin. The bucket remained holding the manikin, so the member could descend and maneuver past the manikin. The member started his descent and about 10ft from the ground the member in the bucket unhooked from the manikin. The member on the pole took a few more steps and then was struck by the falling manikin. The Northside rope of the manikin’s belt came untied swinging the manikin toward the Southside of the pole and the weight of the manikin caused the other knot in the rope to come untied resulting in the manikin falling and striking the member. The member was struck in the head and back, knocking off his hardhat and safety glasses causing him to cut out of the pole then striking the pole with his left cheek. Several members rushed to his aid. The injured member immediately asked for an ambulance and stated he was in a lot of pain in his neck and back area. Several members on the ground assisted in unbuckling his safety while supporting his neck and carefully laid him down to the ground. His supervisor, called 911 at 8:30 am and directed another member to drive to the front gate and wait on the ambulance and guide them to the location. The ambulance arrived at 8:44 am and transported the member to the hospital. Facts Ascertained: -Members discussed during tailboard to climb down southeast side of the pole to reduce amount of gaffs marks on one side of the pole -This was the first pole top rescue training of the day, with 21 members on site -The manikin was hung on the eastside of the pole -Both knots on P line did come untied (NOTE: There were no knots found on the rope or on the belt) - Intern tied one knot and the investigation team was not able to determine who tied the other -Quarter inch rope measured at 24" & 22" -Intern made one tie (the side that was cut) to the Northside of the rope and it was not inspected by other members prior to lifting -Both members, in the bucket and on the pole, training is up-to date -Intern was on his second internship (First with OGE as of 7-08-19) | Michael Eckart | Randell Gilbert | FALSE | Northeast District Service Cen | FALSE |  | FALSE | Construction Services |  | Randell Gilbert | Michael Fox |  | Chad Inman | I approve the Corrective Actions. Thank you for the time and commitment that the investigation team put into this. I'm also appreciative of the decision to move forward with the correct tool for this application. | Chad Inman | Lindle Coleman | High | [7 empty] | 8.1.2 Improper conduct that is condoned: Unintentional | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | There currently are no documented work practices for how to secure the manikin or where to climb in regards to the orientation of the manikin. 8.1.2: The risk of depending only on knots and the orientation of the climber has been unintentionally accepted across T&D 9.04 & 14.01.4: Our current procedure does not adequately address/mitigate the risk mentioned above | 02. Failure to Warn | 2. Struck By (Hit By Moving Object) | approved | I approve. | [24 empty] | FALSE |  | Days away from Work (H) | 2007-04-23 | 1984-02-18 |  | 2019-07-15 07:00 | 6 | 77 |  | FALSE |  | While descending pole after performing pole top rescue, dummy fell striking member. |  |  | Dwayne Fox |  | Recordable | Dwayne Fox | TRUE |  |  |  | Contusion |  | TRUE |  | Lineman | Back | Injury |  | TRUE | Donald Melson | TRUE | 2019 | 7/15/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | Rescue dummy
8944 | Northeast District Service Cen | 2019-07-15 08:30 | While performing pole top rescue, rescue dummy fell striking member | Level 3 |  | FALSE | Member Injury |  | Lindle Coleman | Reviewed with operations | 2019-07-16 10:22 | Power Delivery | Randell Gilbert | 2019-08-20 08:15 | 2019-07-15 14:12 | 2019-07-15 14:12 | 2019-07-29 11:52 | 2019-07-29 07:30 | 2019-07-15 14:05 | 2019-08-02 08:56 | 2019-08-05 09:07 | 2019-07-29 12:26 | Kellyville Service Center Pole Yard |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Randell Gilbert |  | The morning started by watching the training video and covering the importance of a successful rescue. The team moved to the North end of the Pole yard where there are several poles set up for training. The group held a Tailboard and completed Vimocity stretches. Several ¼" P-line ropes were cut to length. The bucket was set up to maneuver manikin into place around the pole through cross arm braces. The member climbed up the pole and successfully performed the rescue. While the manikin was on the ground after the rescue the Intern made one bowline knot on the manikin for the next rescue. The member who had performed the rescue, remained at the top of the pole to assist in helping the bucket hang the manikin. The bucket remained holding the manikin, so the member could descend and maneuver past the manikin. The member started his descent and about 10ft from the ground the member in the bucket unhooked from the manikin. The member on the pole took a few more steps and then was struck by the falling manikin. The Northside rope of the manikin’s belt came untied swinging the manikin toward the Southside of the pole and the weight of the manikin caused the other knot in the rope to come untied resulting in the manikin falling and striking the member. The member was struck in the head and back, knocking off his hardhat and safety glasses causing him to cut out of the pole then striking the pole with his left cheek. Several members rushed to his aid. The injured member immediately asked for an ambulance and stated he was in a lot of pain in his neck and back area. Several members on the ground assisted in unbuckling his safety while supporting his neck and carefully laid him down to the ground. His supervisor, called 911 at 8:30 am and directed another member to drive to the front gate and wait on the ambulance and guide them to the location. The ambulance arrived at 8:44 am and transported the member to the hospital. Facts Ascertained: -Members discussed during tailboard to climb down southeast side of the pole to reduce amount of gaffs marks on one side of the pole -This was the first pole top rescue training of the day, with 21 members on site -The manikin was hung on the eastside of the pole -Both knots on P line did come untied (NOTE: There were no knots found on the rope or on the belt) - Intern tied one knot and the investigation team was not able to determine who tied the other -Quarter inch rope measured at 24" & 22" -Intern made one tie (the side that was cut) to the Northside of the rope and it was not inspected by other members prior to lifting -Both members, in the bucket and on the pole, training is up-to date -Intern was on his second internship (First with OGE as of 7-08-19) | Michael Eckart | Randell Gilbert | FALSE | Northeast District Service Cen | FALSE |  | FALSE | Construction Services |  | Randell Gilbert | Michael Fox |  | Chad Inman | I approve the Corrective Actions. Thank you for the time and commitment that the investigation team put into this. I'm also appreciative of the decision to move forward with the correct tool for this application. | Chad Inman | Lindle Coleman | High | [7 empty] | 8.1.2 Improper conduct that is condoned: Unintentional | 9.09 Inadequate identification and evaluation of loss exposures |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | There currently are no documented work practices for how to secure the manikin or where to climb in regards to the orientation of the manikin. 8.1.2: The risk of depending only on knots and the orientation of the climber has been unintentionally accepted across T&D 9.04 & 14.01.4: Our current procedure does not adequately address/mitigate the risk mentioned above | 02. Failure to Warn | 2. Struck By (Hit By Moving Object) | approved | I approve. | [24 empty] | FALSE |  | Days away from Work (H) | 2007-04-23 | 1984-02-18 |  | 2019-07-15 07:00 | 6 | 77 |  | FALSE |  | While descending pole after performing pole top rescue, dummy fell striking member. |  |  | Dwayne Fox |  | Recordable | Dwayne Fox | TRUE |  |  |  | Contusion |  | TRUE |  | Lineman | Back | Injury |  | TRUE | Donald Melson | TRUE | 2019 | 7/15/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | Rescue dummy
8944 | Northeast District Service Cen | 2019-07-15 08:30 | While performing pole top rescue, rescue dummy fell striking member | Level 3 |  | FALSE | Member Injury |  | Lindle Coleman | Reviewed with operations | 2019-07-16 10:22 | Power Delivery | Randell Gilbert | 2019-08-20 08:15 | 2019-07-15 14:12 | 2019-07-15 14:12 | 2019-07-29 11:52 | 2019-07-29 07:30 | 2019-07-15 14:05 | 2019-08-02 08:56 | 2019-08-05 09:07 | 2019-07-29 12:26 | Kellyville Service Center Pole Yard |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Randell Gilbert |  | The morning started by watching the training video and covering the importance of a successful rescue. The team moved to the North end of the Pole yard where there are several poles set up for training. The group held a Tailboard and completed Vimocity stretches. Several ¼" P-line ropes were cut to length. The bucket was set up to maneuver manikin into place around the pole through cross arm braces. The member climbed up the pole and successfully performed the rescue. While the manikin was on the ground after the rescue the Intern made one bowline knot on the manikin for the next rescue. The member who had performed the rescue, remained at the top of the pole to assist in helping the bucket hang the manikin. The bucket remained holding the manikin, so the member could descend and maneuver past the manikin. The member started his descent and about 10ft from the ground the member in the bucket unhooked from the manikin. The member on the pole took a few more steps and then was struck by the falling manikin. The Northside rope of the manikin’s belt came untied swinging the manikin toward the Southside of the pole and the weight of the manikin caused the other knot in the rope to come untied resulting in the manikin falling and striking the member. The member was struck in the head and back, knocking off his hardhat and safety glasses causing him to cut out of the pole then striking the pole with his left cheek. Several members rushed to his aid. The injured member immediately asked for an ambulance and stated he was in a lot of pain in his neck and back area. Several members on the ground assisted in unbuckling his safety while supporting his neck and carefully laid him down to the ground. His supervisor, called 911 at 8:30 am and directed another member to drive to the front gate and wait on the ambulance and guide them to the location. The ambulance arrived at 8:44 am and transported the member to the hospital. Facts Ascertained: -Members discussed during tailboard to climb down southeast side of the pole to reduce amount of gaffs marks on one side of the pole -This was the first pole top rescue training of the day, with 21 members on site -The manikin was hung on the eastside of the pole -Both knots on P line did come untied (NOTE: There were no knots found on the rope or on the belt) - Intern tied one knot and the investigation team was not able to determine who tied the other -Quarter inch rope measured at 24" & 22" -Intern made one tie (the side that was cut) to the Northside of the rope and it was not inspected by other members prior to lifting -Both members, in the bucket and on the pole, training is up-to date -Intern was on his second internship (First with OGE as of 7-08-19) | Terry Hackett | Randell Gilbert | FALSE | Northeast District Service Cen | FALSE |  | FALSE | Construction Services |  | Randell Gilbert | Michael Fox |  | Chad Inman | I approve the Corrective Actions. Thank you for the time and commitment that the investigation team put into this. I'm also appreciative of the decision to move forward with the correct tool for this application. | Chad Inman | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.11 Inadequate matching of individual qualifications and job/task requirements |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Failed to inspect and verify condition of knot made by Intern 5.01: Interns are sent to us to learn and gain field experience. It is our responsibility to check and monitor their work 9.11: Intern should not have been allowed to secure belt to manikin without adequate verification 14.01.4: We currently do not have documented work practices for how to secure the manikin to the pole | 18. Failure to Check, Monitor | 2. Struck By (Hit By Moving Object) | approved | I approve. | [24 empty] | FALSE |  | Days away from Work (H) | 2007-04-23 | 1984-02-18 |  | 2019-07-15 07:00 | 6 | 77 |  | FALSE |  | While descending pole after performing pole top rescue, dummy fell striking member. |  |  | Dwayne Fox |  | Recordable | Dwayne Fox | TRUE |  |  |  | Contusion |  | TRUE |  | Lineman | Back | Injury |  | TRUE | Donald Melson | TRUE | 2019 | 7/15/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | Rescue dummy
8944 | Northeast District Service Cen | 2019-07-15 08:30 | While performing pole top rescue, rescue dummy fell striking member | Level 3 |  | FALSE | Member Injury |  | Lindle Coleman | Reviewed with operations | 2019-07-16 10:22 | Power Delivery | Randell Gilbert | 2019-08-20 08:15 | 2019-07-15 14:12 | 2019-07-15 14:12 | 2019-07-29 11:52 | 2019-07-29 07:30 | 2019-07-15 14:05 | 2019-08-02 08:56 | 2019-08-05 09:07 | 2019-07-29 12:26 | Kellyville Service Center Pole Yard |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Randell Gilbert |  | The morning started by watching the training video and covering the importance of a successful rescue. The team moved to the North end of the Pole yard where there are several poles set up for training. The group held a Tailboard and completed Vimocity stretches. Several ¼" P-line ropes were cut to length. The bucket was set up to maneuver manikin into place around the pole through cross arm braces. The member climbed up the pole and successfully performed the rescue. While the manikin was on the ground after the rescue the Intern made one bowline knot on the manikin for the next rescue. The member who had performed the rescue, remained at the top of the pole to assist in helping the bucket hang the manikin. The bucket remained holding the manikin, so the member could descend and maneuver past the manikin. The member started his descent and about 10ft from the ground the member in the bucket unhooked from the manikin. The member on the pole took a few more steps and then was struck by the falling manikin. The Northside rope of the manikin’s belt came untied swinging the manikin toward the Southside of the pole and the weight of the manikin caused the other knot in the rope to come untied resulting in the manikin falling and striking the member. The member was struck in the head and back, knocking off his hardhat and safety glasses causing him to cut out of the pole then striking the pole with his left cheek. Several members rushed to his aid. The injured member immediately asked for an ambulance and stated he was in a lot of pain in his neck and back area. Several members on the ground assisted in unbuckling his safety while supporting his neck and carefully laid him down to the ground. His supervisor, called 911 at 8:30 am and directed another member to drive to the front gate and wait on the ambulance and guide them to the location. The ambulance arrived at 8:44 am and transported the member to the hospital. Facts Ascertained: -Members discussed during tailboard to climb down southeast side of the pole to reduce amount of gaffs marks on one side of the pole -This was the first pole top rescue training of the day, with 21 members on site -The manikin was hung on the eastside of the pole -Both knots on P line did come untied (NOTE: There were no knots found on the rope or on the belt) - Intern tied one knot and the investigation team was not able to determine who tied the other -Quarter inch rope measured at 24" & 22" -Intern made one tie (the side that was cut) to the Northside of the rope and it was not inspected by other members prior to lifting -Both members, in the bucket and on the pole, training is up-to date -Intern was on his second internship (First with OGE as of 7-08-19) | Terry Hackett | Randell Gilbert | FALSE | Northeast District Service Cen | FALSE |  | FALSE | Construction Services |  | Randell Gilbert | Michael Fox |  | Chad Inman | I approve the Corrective Actions. Thank you for the time and commitment that the investigation team put into this. I'm also appreciative of the decision to move forward with the correct tool for this application. | Chad Inman | Lindle Coleman | High | [8 empty] | 9.09 Inadequate identification and evaluation of loss exposures |  |  |  | 13.01 Inadequate assessment of needs and risks |  |  |  | P line/ rope is not engineered and designed for pole top rescue 9.09 & 13.01: Prior to this occurrence all T&D Locations performed pole top rescue using knots to secure the manikin to the pole. The need to use equipment designed for this task was not identified. | 22. Inadequate or Improper Protective Equipment | 2. Struck By (Hit By Moving Object) | approved | I approve. | [24 empty] | FALSE |  | Days away from Work (H) | 2007-04-23 | 1984-02-18 |  | 2019-07-15 07:00 | 6 | 77 |  | FALSE |  | While descending pole after performing pole top rescue, dummy fell striking member. |  |  | Dwayne Fox |  | Recordable | Dwayne Fox | TRUE |  |  |  | Contusion |  | TRUE |  | Lineman | Back | Injury |  | TRUE | Donald Melson | TRUE | 2019 | 7/15/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | Rescue dummy
8944 | Northeast District Service Cen | 2019-07-15 08:30 | While performing pole top rescue, rescue dummy fell striking member | Level 3 |  | FALSE | Member Injury |  | Lindle Coleman | Reviewed with operations | 2019-07-16 10:22 | Power Delivery | Randell Gilbert | 2019-08-20 08:15 | 2019-07-15 14:12 | 2019-07-15 14:12 | 2019-07-29 11:52 | 2019-07-29 07:30 | 2019-07-15 14:05 | 2019-08-02 08:56 | 2019-08-05 09:07 | 2019-07-29 12:26 | Kellyville Service Center Pole Yard |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Randell Gilbert |  | The morning started by watching the training video and covering the importance of a successful rescue. The team moved to the North end of the Pole yard where there are several poles set up for training. The group held a Tailboard and completed Vimocity stretches. Several ¼" P-line ropes were cut to length. The bucket was set up to maneuver manikin into place around the pole through cross arm braces. The member climbed up the pole and successfully performed the rescue. While the manikin was on the ground after the rescue the Intern made one bowline knot on the manikin for the next rescue. The member who had performed the rescue, remained at the top of the pole to assist in helping the bucket hang the manikin. The bucket remained holding the manikin, so the member could descend and maneuver past the manikin. The member started his descent and about 10ft from the ground the member in the bucket unhooked from the manikin. The member on the pole took a few more steps and then was struck by the falling manikin. The Northside rope of the manikin’s belt came untied swinging the manikin toward the Southside of the pole and the weight of the manikin caused the other knot in the rope to come untied resulting in the manikin falling and striking the member. The member was struck in the head and back, knocking off his hardhat and safety glasses causing him to cut out of the pole then striking the pole with his left cheek. Several members rushed to his aid. The injured member immediately asked for an ambulance and stated he was in a lot of pain in his neck and back area. Several members on the ground assisted in unbuckling his safety while supporting his neck and carefully laid him down to the ground. His supervisor, called 911 at 8:30 am and directed another member to drive to the front gate and wait on the ambulance and guide them to the location. The ambulance arrived at 8:44 am and transported the member to the hospital. Facts Ascertained: -Members discussed during tailboard to climb down southeast side of the pole to reduce amount of gaffs marks on one side of the pole -This was the first pole top rescue training of the day, with 21 members on site -The manikin was hung on the eastside of the pole -Both knots on P line did come untied (NOTE: There were no knots found on the rope or on the belt) - Intern tied one knot and the investigation team was not able to determine who tied the other -Quarter inch rope measured at 24" & 22" -Intern made one tie (the side that was cut) to the Northside of the rope and it was not inspected by other members prior to lifting -Both members, in the bucket and on the pole, training is up-to date -Intern was on his second internship (First with OGE as of 7-08-19) | Terry Hackett | Randell Gilbert | FALSE | Northeast District Service Cen | FALSE |  | FALSE | Construction Services |  | Randell Gilbert | Michael Fox |  | Chad Inman | I approve the Corrective Actions. Thank you for the time and commitment that the investigation team put into this. I'm also appreciative of the decision to move forward with the correct tool for this application. | Chad Inman | Lindle Coleman | High | [7 empty] | 8.1.2 Improper conduct that is condoned: Unintentional | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | There currently are no documented work practices for how to secure the manikin or where to climb in regards to the orientation of the manikin. 8.1.2: The risk of depending only on knots and the orientation of the climber has been unintentionally accepted across T&D 9.04 & 14.01.4: Our current procedure does not adequately address/mitigate the risk mentioned above | 02. Failure to Warn | 2. Struck By (Hit By Moving Object) | approved | I approve. | [24 empty] | FALSE |  | Days away from Work (H) | 2007-04-23 | 1984-02-18 |  | 2019-07-15 07:00 | 6 | 77 |  | FALSE |  | While descending pole after performing pole top rescue, dummy fell striking member. |  |  | Dwayne Fox |  | Recordable | Dwayne Fox | TRUE |  |  |  | Contusion |  | TRUE |  | Lineman | Back | Injury |  | TRUE | Donald Melson | TRUE | 2019 | 7/15/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | Rescue dummy
8944 | Northeast District Service Cen | 2019-07-15 08:30 | While performing pole top rescue, rescue dummy fell striking member | Level 3 |  | FALSE | Member Injury |  | Lindle Coleman | Reviewed with operations | 2019-07-16 10:22 | Power Delivery | Randell Gilbert | 2019-08-20 08:15 | 2019-07-15 14:12 | 2019-07-15 14:12 | 2019-07-29 11:52 | 2019-07-29 07:30 | 2019-07-15 14:05 | 2019-08-02 08:56 | 2019-08-05 09:07 | 2019-07-29 12:26 | Kellyville Service Center Pole Yard |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Randell Gilbert |  | The morning started by watching the training video and covering the importance of a successful rescue. The team moved to the North end of the Pole yard where there are several poles set up for training. The group held a Tailboard and completed Vimocity stretches. Several ¼" P-line ropes were cut to length. The bucket was set up to maneuver manikin into place around the pole through cross arm braces. The member climbed up the pole and successfully performed the rescue. While the manikin was on the ground after the rescue the Intern made one bowline knot on the manikin for the next rescue. The member who had performed the rescue, remained at the top of the pole to assist in helping the bucket hang the manikin. The bucket remained holding the manikin, so the member could descend and maneuver past the manikin. The member started his descent and about 10ft from the ground the member in the bucket unhooked from the manikin. The member on the pole took a few more steps and then was struck by the falling manikin. The Northside rope of the manikin’s belt came untied swinging the manikin toward the Southside of the pole and the weight of the manikin caused the other knot in the rope to come untied resulting in the manikin falling and striking the member. The member was struck in the head and back, knocking off his hardhat and safety glasses causing him to cut out of the pole then striking the pole with his left cheek. Several members rushed to his aid. The injured member immediately asked for an ambulance and stated he was in a lot of pain in his neck and back area. Several members on the ground assisted in unbuckling his safety while supporting his neck and carefully laid him down to the ground. His supervisor, called 911 at 8:30 am and directed another member to drive to the front gate and wait on the ambulance and guide them to the location. The ambulance arrived at 8:44 am and transported the member to the hospital. Facts Ascertained: -Members discussed during tailboard to climb down southeast side of the pole to reduce amount of gaffs marks on one side of the pole -This was the first pole top rescue training of the day, with 21 members on site -The manikin was hung on the eastside of the pole -Both knots on P line did come untied (NOTE: There were no knots found on the rope or on the belt) - Intern tied one knot and the investigation team was not able to determine who tied the other -Quarter inch rope measured at 24" & 22" -Intern made one tie (the side that was cut) to the Northside of the rope and it was not inspected by other members prior to lifting -Both members, in the bucket and on the pole, training is up-to date -Intern was on his second internship (First with OGE as of 7-08-19) | Terry Hackett | Randell Gilbert | FALSE | Northeast District Service Cen | FALSE |  | FALSE | Construction Services |  | Randell Gilbert | Michael Fox |  | Chad Inman | I approve the Corrective Actions. Thank you for the time and commitment that the investigation team put into this. I'm also appreciative of the decision to move forward with the correct tool for this application. | Chad Inman | Lindle Coleman | High | [7 empty] | 8.1.2 Improper conduct that is condoned: Unintentional | 9.09 Inadequate identification and evaluation of loss exposures |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | There currently are no documented work practices for how to secure the manikin or where to climb in regards to the orientation of the manikin. 8.1.2: The risk of depending only on knots and the orientation of the climber has been unintentionally accepted across T&D 9.04 & 14.01.4: Our current procedure does not adequately address/mitigate the risk mentioned above | 02. Failure to Warn | 2. Struck By (Hit By Moving Object) | approved | I approve. | [24 empty] | FALSE |  | Days away from Work (H) | 2007-04-23 | 1984-02-18 |  | 2019-07-15 07:00 | 6 | 77 |  | FALSE |  | While descending pole after performing pole top rescue, dummy fell striking member. |  |  | Dwayne Fox |  | Recordable | Dwayne Fox | TRUE |  |  |  | Contusion |  | TRUE |  | Lineman | Back | Injury |  | TRUE | Donald Melson | TRUE | 2019 | 7/15/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | Rescue dummy
8944 | Northeast District Service Cen | 2019-07-15 08:30 | While performing pole top rescue, rescue dummy fell striking member | Level 3 |  | FALSE | Member Injury |  | Lindle Coleman | Reviewed with operations | 2019-07-16 10:22 | Power Delivery | Randell Gilbert | 2019-08-20 08:15 | 2019-07-15 14:12 | 2019-07-15 14:12 | 2019-07-29 11:52 | 2019-07-29 07:30 | 2019-07-15 14:05 | 2019-08-02 08:56 | 2019-08-05 09:07 | 2019-07-29 12:26 | Kellyville Service Center Pole Yard |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Randell Gilbert |  | The morning started by watching the training video and covering the importance of a successful rescue. The team moved to the North end of the Pole yard where there are several poles set up for training. The group held a Tailboard and completed Vimocity stretches. Several ¼" P-line ropes were cut to length. The bucket was set up to maneuver manikin into place around the pole through cross arm braces. The member climbed up the pole and successfully performed the rescue. While the manikin was on the ground after the rescue the Intern made one bowline knot on the manikin for the next rescue. The member who had performed the rescue, remained at the top of the pole to assist in helping the bucket hang the manikin. The bucket remained holding the manikin, so the member could descend and maneuver past the manikin. The member started his descent and about 10ft from the ground the member in the bucket unhooked from the manikin. The member on the pole took a few more steps and then was struck by the falling manikin. The Northside rope of the manikin’s belt came untied swinging the manikin toward the Southside of the pole and the weight of the manikin caused the other knot in the rope to come untied resulting in the manikin falling and striking the member. The member was struck in the head and back, knocking off his hardhat and safety glasses causing him to cut out of the pole then striking the pole with his left cheek. Several members rushed to his aid. The injured member immediately asked for an ambulance and stated he was in a lot of pain in his neck and back area. Several members on the ground assisted in unbuckling his safety while supporting his neck and carefully laid him down to the ground. His supervisor, called 911 at 8:30 am and directed another member to drive to the front gate and wait on the ambulance and guide them to the location. The ambulance arrived at 8:44 am and transported the member to the hospital. Facts Ascertained: -Members discussed during tailboard to climb down southeast side of the pole to reduce amount of gaffs marks on one side of the pole -This was the first pole top rescue training of the day, with 21 members on site -The manikin was hung on the eastside of the pole -Both knots on P line did come untied (NOTE: There were no knots found on the rope or on the belt) - Intern tied one knot and the investigation team was not able to determine who tied the other -Quarter inch rope measured at 24" & 22" -Intern made one tie (the side that was cut) to the Northside of the rope and it was not inspected by other members prior to lifting -Both members, in the bucket and on the pole, training is up-to date -Intern was on his second internship (First with OGE as of 7-08-19) | Hannah Everett | Randell Gilbert | FALSE | Northeast District Service Cen | FALSE |  | FALSE | Construction Services |  | Randell Gilbert | Michael Fox |  | Chad Inman | I approve the Corrective Actions. Thank you for the time and commitment that the investigation team put into this. I'm also appreciative of the decision to move forward with the correct tool for this application. | Chad Inman | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.11 Inadequate matching of individual qualifications and job/task requirements |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Failed to inspect and verify condition of knot made by Intern 5.01: Interns are sent to us to learn and gain field experience. It is our responsibility to check and monitor their work 9.11: Intern should not have been allowed to secure belt to manikin without adequate verification 14.01.4: We currently do not have documented work practices for how to secure the manikin to the pole | 18. Failure to Check, Monitor | 2. Struck By (Hit By Moving Object) | approved | I approve. | [24 empty] | FALSE |  | Days away from Work (H) | 2007-04-23 | 1984-02-18 |  | 2019-07-15 07:00 | 6 | 77 |  | FALSE |  | While descending pole after performing pole top rescue, dummy fell striking member. |  |  | Dwayne Fox |  | Recordable | Dwayne Fox | TRUE |  |  |  | Contusion |  | TRUE |  | Lineman | Back | Injury |  | TRUE | Donald Melson | TRUE | 2019 | 7/15/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | Rescue dummy
8944 | Northeast District Service Cen | 2019-07-15 08:30 | While performing pole top rescue, rescue dummy fell striking member | Level 3 |  | FALSE | Member Injury |  | Lindle Coleman | Reviewed with operations | 2019-07-16 10:22 | Power Delivery | Randell Gilbert | 2019-08-20 08:15 | 2019-07-15 14:12 | 2019-07-15 14:12 | 2019-07-29 11:52 | 2019-07-29 07:30 | 2019-07-15 14:05 | 2019-08-02 08:56 | 2019-08-05 09:07 | 2019-07-29 12:26 | Kellyville Service Center Pole Yard |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Randell Gilbert |  | The morning started by watching the training video and covering the importance of a successful rescue. The team moved to the North end of the Pole yard where there are several poles set up for training. The group held a Tailboard and completed Vimocity stretches. Several ¼" P-line ropes were cut to length. The bucket was set up to maneuver manikin into place around the pole through cross arm braces. The member climbed up the pole and successfully performed the rescue. While the manikin was on the ground after the rescue the Intern made one bowline knot on the manikin for the next rescue. The member who had performed the rescue, remained at the top of the pole to assist in helping the bucket hang the manikin. The bucket remained holding the manikin, so the member could descend and maneuver past the manikin. The member started his descent and about 10ft from the ground the member in the bucket unhooked from the manikin. The member on the pole took a few more steps and then was struck by the falling manikin. The Northside rope of the manikin’s belt came untied swinging the manikin toward the Southside of the pole and the weight of the manikin caused the other knot in the rope to come untied resulting in the manikin falling and striking the member. The member was struck in the head and back, knocking off his hardhat and safety glasses causing him to cut out of the pole then striking the pole with his left cheek. Several members rushed to his aid. The injured member immediately asked for an ambulance and stated he was in a lot of pain in his neck and back area. Several members on the ground assisted in unbuckling his safety while supporting his neck and carefully laid him down to the ground. His supervisor, called 911 at 8:30 am and directed another member to drive to the front gate and wait on the ambulance and guide them to the location. The ambulance arrived at 8:44 am and transported the member to the hospital. Facts Ascertained: -Members discussed during tailboard to climb down southeast side of the pole to reduce amount of gaffs marks on one side of the pole -This was the first pole top rescue training of the day, with 21 members on site -The manikin was hung on the eastside of the pole -Both knots on P line did come untied (NOTE: There were no knots found on the rope or on the belt) - Intern tied one knot and the investigation team was not able to determine who tied the other -Quarter inch rope measured at 24" & 22" -Intern made one tie (the side that was cut) to the Northside of the rope and it was not inspected by other members prior to lifting -Both members, in the bucket and on the pole, training is up-to date -Intern was on his second internship (First with OGE as of 7-08-19) | Hannah Everett | Randell Gilbert | FALSE | Northeast District Service Cen | FALSE |  | FALSE | Construction Services |  | Randell Gilbert | Michael Fox |  | Chad Inman | I approve the Corrective Actions. Thank you for the time and commitment that the investigation team put into this. I'm also appreciative of the decision to move forward with the correct tool for this application. | Chad Inman | Lindle Coleman | High | [8 empty] | 9.09 Inadequate identification and evaluation of loss exposures |  |  |  | 13.01 Inadequate assessment of needs and risks |  |  |  | P line/ rope is not engineered and designed for pole top rescue 9.09 & 13.01: Prior to this occurrence all T&D Locations performed pole top rescue using knots to secure the manikin to the pole. The need to use equipment designed for this task was not identified. | 22. Inadequate or Improper Protective Equipment | 2. Struck By (Hit By Moving Object) | approved | I approve. | [24 empty] | FALSE |  | Days away from Work (H) | 2007-04-23 | 1984-02-18 |  | 2019-07-15 07:00 | 6 | 77 |  | FALSE |  | While descending pole after performing pole top rescue, dummy fell striking member. |  |  | Dwayne Fox |  | Recordable | Dwayne Fox | TRUE |  |  |  | Contusion |  | TRUE |  | Lineman | Back | Injury |  | TRUE | Donald Melson | TRUE | 2019 | 7/15/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | Rescue dummy
8944 | Northeast District Service Cen | 2019-07-15 08:30 | While performing pole top rescue, rescue dummy fell striking member | Level 3 |  | FALSE | Member Injury |  | Lindle Coleman | Reviewed with operations | 2019-07-16 10:22 | Power Delivery | Randell Gilbert | 2019-08-20 08:15 | 2019-07-15 14:12 | 2019-07-15 14:12 | 2019-07-29 11:52 | 2019-07-29 07:30 | 2019-07-15 14:05 | 2019-08-02 08:56 | 2019-08-05 09:07 | 2019-07-29 12:26 | Kellyville Service Center Pole Yard |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Randell Gilbert |  | The morning started by watching the training video and covering the importance of a successful rescue. The team moved to the North end of the Pole yard where there are several poles set up for training. The group held a Tailboard and completed Vimocity stretches. Several ¼" P-line ropes were cut to length. The bucket was set up to maneuver manikin into place around the pole through cross arm braces. The member climbed up the pole and successfully performed the rescue. While the manikin was on the ground after the rescue the Intern made one bowline knot on the manikin for the next rescue. The member who had performed the rescue, remained at the top of the pole to assist in helping the bucket hang the manikin. The bucket remained holding the manikin, so the member could descend and maneuver past the manikin. The member started his descent and about 10ft from the ground the member in the bucket unhooked from the manikin. The member on the pole took a few more steps and then was struck by the falling manikin. The Northside rope of the manikin’s belt came untied swinging the manikin toward the Southside of the pole and the weight of the manikin caused the other knot in the rope to come untied resulting in the manikin falling and striking the member. The member was struck in the head and back, knocking off his hardhat and safety glasses causing him to cut out of the pole then striking the pole with his left cheek. Several members rushed to his aid. The injured member immediately asked for an ambulance and stated he was in a lot of pain in his neck and back area. Several members on the ground assisted in unbuckling his safety while supporting his neck and carefully laid him down to the ground. His supervisor, called 911 at 8:30 am and directed another member to drive to the front gate and wait on the ambulance and guide them to the location. The ambulance arrived at 8:44 am and transported the member to the hospital. Facts Ascertained: -Members discussed during tailboard to climb down southeast side of the pole to reduce amount of gaffs marks on one side of the pole -This was the first pole top rescue training of the day, with 21 members on site -The manikin was hung on the eastside of the pole -Both knots on P line did come untied (NOTE: There were no knots found on the rope or on the belt) - Intern tied one knot and the investigation team was not able to determine who tied the other -Quarter inch rope measured at 24" & 22" -Intern made one tie (the side that was cut) to the Northside of the rope and it was not inspected by other members prior to lifting -Both members, in the bucket and on the pole, training is up-to date -Intern was on his second internship (First with OGE as of 7-08-19) | Hannah Everett | Randell Gilbert | FALSE | Northeast District Service Cen | FALSE |  | FALSE | Construction Services |  | Randell Gilbert | Michael Fox |  | Chad Inman | I approve the Corrective Actions. Thank you for the time and commitment that the investigation team put into this. I'm also appreciative of the decision to move forward with the correct tool for this application. | Chad Inman | Lindle Coleman | High | [7 empty] | 8.1.2 Improper conduct that is condoned: Unintentional | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | There currently are no documented work practices for how to secure the manikin or where to climb in regards to the orientation of the manikin. 8.1.2: The risk of depending only on knots and the orientation of the climber has been unintentionally accepted across T&D 9.04 & 14.01.4: Our current procedure does not adequately address/mitigate the risk mentioned above | 02. Failure to Warn | 2. Struck By (Hit By Moving Object) | approved | I approve. | [24 empty] | FALSE |  | Days away from Work (H) | 2007-04-23 | 1984-02-18 |  | 2019-07-15 07:00 | 6 | 77 |  | FALSE |  | While descending pole after performing pole top rescue, dummy fell striking member. |  |  | Dwayne Fox |  | Recordable | Dwayne Fox | TRUE |  |  |  | Contusion |  | TRUE |  | Lineman | Back | Injury |  | TRUE | Donald Melson | TRUE | 2019 | 7/15/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | Rescue dummy
8944 | Northeast District Service Cen | 2019-07-15 08:30 | While performing pole top rescue, rescue dummy fell striking member | Level 3 |  | FALSE | Member Injury |  | Lindle Coleman | Reviewed with operations | 2019-07-16 10:22 | Power Delivery | Randell Gilbert | 2019-08-20 08:15 | 2019-07-15 14:12 | 2019-07-15 14:12 | 2019-07-29 11:52 | 2019-07-29 07:30 | 2019-07-15 14:05 | 2019-08-02 08:56 | 2019-08-05 09:07 | 2019-07-29 12:26 | Kellyville Service Center Pole Yard |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Randell Gilbert |  | The morning started by watching the training video and covering the importance of a successful rescue. The team moved to the North end of the Pole yard where there are several poles set up for training. The group held a Tailboard and completed Vimocity stretches. Several ¼" P-line ropes were cut to length. The bucket was set up to maneuver manikin into place around the pole through cross arm braces. The member climbed up the pole and successfully performed the rescue. While the manikin was on the ground after the rescue the Intern made one bowline knot on the manikin for the next rescue. The member who had performed the rescue, remained at the top of the pole to assist in helping the bucket hang the manikin. The bucket remained holding the manikin, so the member could descend and maneuver past the manikin. The member started his descent and about 10ft from the ground the member in the bucket unhooked from the manikin. The member on the pole took a few more steps and then was struck by the falling manikin. The Northside rope of the manikin’s belt came untied swinging the manikin toward the Southside of the pole and the weight of the manikin caused the other knot in the rope to come untied resulting in the manikin falling and striking the member. The member was struck in the head and back, knocking off his hardhat and safety glasses causing him to cut out of the pole then striking the pole with his left cheek. Several members rushed to his aid. The injured member immediately asked for an ambulance and stated he was in a lot of pain in his neck and back area. Several members on the ground assisted in unbuckling his safety while supporting his neck and carefully laid him down to the ground. His supervisor, called 911 at 8:30 am and directed another member to drive to the front gate and wait on the ambulance and guide them to the location. The ambulance arrived at 8:44 am and transported the member to the hospital. Facts Ascertained: -Members discussed during tailboard to climb down southeast side of the pole to reduce amount of gaffs marks on one side of the pole -This was the first pole top rescue training of the day, with 21 members on site -The manikin was hung on the eastside of the pole -Both knots on P line did come untied (NOTE: There were no knots found on the rope or on the belt) - Intern tied one knot and the investigation team was not able to determine who tied the other -Quarter inch rope measured at 24" & 22" -Intern made one tie (the side that was cut) to the Northside of the rope and it was not inspected by other members prior to lifting -Both members, in the bucket and on the pole, training is up-to date -Intern was on his second internship (First with OGE as of 7-08-19) | Hannah Everett | Randell Gilbert | FALSE | Northeast District Service Cen | FALSE |  | FALSE | Construction Services |  | Randell Gilbert | Michael Fox |  | Chad Inman | I approve the Corrective Actions. Thank you for the time and commitment that the investigation team put into this. I'm also appreciative of the decision to move forward with the correct tool for this application. | Chad Inman | Lindle Coleman | High | [7 empty] | 8.1.2 Improper conduct that is condoned: Unintentional | 9.09 Inadequate identification and evaluation of loss exposures |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | There currently are no documented work practices for how to secure the manikin or where to climb in regards to the orientation of the manikin. 8.1.2: The risk of depending only on knots and the orientation of the climber has been unintentionally accepted across T&D 9.04 & 14.01.4: Our current procedure does not adequately address/mitigate the risk mentioned above | 02. Failure to Warn | 2. Struck By (Hit By Moving Object) | approved | I approve. | [24 empty] | FALSE |  | Days away from Work (H) | 2007-04-23 | 1984-02-18 |  | 2019-07-15 07:00 | 6 | 77 |  | FALSE |  | While descending pole after performing pole top rescue, dummy fell striking member. |  |  | Dwayne Fox |  | Recordable | Dwayne Fox | TRUE |  |  |  | Contusion |  | TRUE |  | Lineman | Back | Injury |  | TRUE | Donald Melson | TRUE | 2019 | 7/15/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | Rescue dummy
8946 | Metro Service Center | 2019-07-17 09:00 | Member backed company vehicle into company member's personal vehicle while performing volunteer work at Carney Public Schools. | Level 2 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Kenny La Ferney | 2019-08-09 10:48 | 2019-07-17 11:01 | 2019-07-17 11:01 | 2019-08-07 12:14 | 2019-07-31 09:00 | 2019-07-17 10:53 | 2019-08-09 10:27 |  | 2019-08-07 12:58 | Carney Ok Public Schools |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Kenny La Ferney |  | Members were pulling up to do volunteer service at Carney Public schools. One of the crew members came from his home to the jobsite and was in his personal vehicle. Member was trying to get the bucket truck into position to perform work. He had an intern backing him and was watching the backer for signals. As he was backing up he struck the members personal vehicle with passenger side, rear bumper of the bucket truck. The spotter never gave him signal to stop or turn. He stated he did not see the personal vehicle was why he did not stop the driver. Intern has been working at OGE for approximately 8 weeks, this is his second internship. The personal vehicle was parked too close to the jobsite and the spotter failed to give adequate signals to prevent an incident. Member driving the truck was focused on the spotter and failed to check mirrors, evaluate obstructions in his route, or communicate with the spotter in regards to where he was going. Backer went through the parking and vehicle situational awareness WBT on 3/21/2019 (this course covers 360 and the correct way to be a spotter). Backer stated he surveyed the area directly around the truck prior to the backing process, but was not aware of where the driver was backing to and did not identify the personal vehicle that was approximately 50' away. |  |  |  | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Tommy Nichols | Jimmy Combs |  | Gary Lassley | I have a few unanswered questions regarding this incident. (1) Do Interns receive backing training prior to their internship at OGE? Was he familiar with our backing procedure and hand signals? (2) How did the Intern miss the personal vehicle? Did he survey the area for potential obstruction prior to backing? | Gary Lassley |  | Medium | [6 empty] | 7.13 Inadequate reinforcement of proper behavior | [9 empty] | driver did not communicate the route he was going to back with the spotter. | 02. Failure to Warn | 1. Struck Against (Running or Bumping Into) |  | Reviewed. OGE should consider integrating backing technology (cameras/beepers/etc...) into our fleet vehicles that are currently not equipped. | [72 empty] | TRUE |  | Carney | OGE Vehicle Struck Other Vehicle | Backing Related | 2015-08-16 19:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
8946 | Metro Service Center | 2019-07-17 09:00 | Member backed company vehicle into company member's personal vehicle while performing volunteer work at Carney Public Schools. | Level 2 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Kenny La Ferney | 2019-08-09 10:48 | 2019-07-17 11:01 | 2019-07-17 11:01 | 2019-08-07 12:14 | 2019-07-31 09:00 | 2019-07-17 10:53 | 2019-08-09 10:27 |  | 2019-08-07 12:58 | Carney Ok Public Schools |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Kenny La Ferney |  | Members were pulling up to do volunteer service at Carney Public schools. One of the crew members came from his home to the jobsite and was in his personal vehicle. Member was trying to get the bucket truck into position to perform work. He had an intern backing him and was watching the backer for signals. As he was backing up he struck the members personal vehicle with passenger side, rear bumper of the bucket truck. The spotter never gave him signal to stop or turn. He stated he did not see the personal vehicle was why he did not stop the driver. Intern has been working at OGE for approximately 8 weeks, this is his second internship. The personal vehicle was parked too close to the jobsite and the spotter failed to give adequate signals to prevent an incident. Member driving the truck was focused on the spotter and failed to check mirrors, evaluate obstructions in his route, or communicate with the spotter in regards to where he was going. Backer went through the parking and vehicle situational awareness WBT on 3/21/2019 (this course covers 360 and the correct way to be a spotter). Backer stated he surveyed the area directly around the truck prior to the backing process, but was not aware of where the driver was backing to and did not identify the personal vehicle that was approximately 50' away. |  |  |  | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Tommy Nichols | Jimmy Combs |  | Gary Lassley | I have a few unanswered questions regarding this incident. (1) Do Interns receive backing training prior to their internship at OGE? Was he familiar with our backing procedure and hand signals? (2) How did the Intern miss the personal vehicle? Did he survey the area for potential obstruction prior to backing? | Gary Lassley |  | Medium |  | 2.07 Slow reaction time |  |  | 5.01 Lack of experience | [10 empty] | 16.01 Inadequate horizontal communication between peers | Spotter failed to perform task efficiently and member driving was not aware of all his surroundings. | 02. Failure to Warn | 1. Struck Against (Running or Bumping Into) |  | Reviewed. OGE should consider integrating backing technology (cameras/beepers/etc...) into our fleet vehicles that are currently not equipped. | [72 empty] | TRUE |  | Carney | OGE Vehicle Struck Other Vehicle | Backing Related | 2015-08-16 19:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
8946 | Metro Service Center | 2019-07-17 09:00 | Member backed company vehicle into company member's personal vehicle while performing volunteer work at Carney Public Schools. | Level 2 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Kenny La Ferney | 2019-08-09 10:48 | 2019-07-17 11:01 | 2019-07-17 11:01 | 2019-08-07 12:14 | 2019-07-31 09:00 | 2019-07-17 10:53 | 2019-08-09 10:27 |  | 2019-08-07 12:58 | Carney Ok Public Schools |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Kenny La Ferney |  | Members were pulling up to do volunteer service at Carney Public schools. One of the crew members came from his home to the jobsite and was in his personal vehicle. Member was trying to get the bucket truck into position to perform work. He had an intern backing him and was watching the backer for signals. As he was backing up he struck the members personal vehicle with passenger side, rear bumper of the bucket truck. The spotter never gave him signal to stop or turn. He stated he did not see the personal vehicle was why he did not stop the driver. Intern has been working at OGE for approximately 8 weeks, this is his second internship. The personal vehicle was parked too close to the jobsite and the spotter failed to give adequate signals to prevent an incident. Member driving the truck was focused on the spotter and failed to check mirrors, evaluate obstructions in his route, or communicate with the spotter in regards to where he was going. Backer went through the parking and vehicle situational awareness WBT on 3/21/2019 (this course covers 360 and the correct way to be a spotter). Backer stated he surveyed the area directly around the truck prior to the backing process, but was not aware of where the driver was backing to and did not identify the personal vehicle that was approximately 50' away. |  |  |  | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Tommy Nichols | Jimmy Combs |  | Gary Lassley | I have a few unanswered questions regarding this incident. (1) Do Interns receive backing training prior to their internship at OGE? Was he familiar with our backing procedure and hand signals? (2) How did the Intern miss the personal vehicle? Did he survey the area for potential obstruction prior to backing? | Gary Lassley |  | Medium |  | 2.07 Slow reaction time |  |  | 5.06 Lack of situational awareness | [10 empty] | 16.01 Inadequate horizontal communication between peers | Spotter failed to perform task efficiently and member driving was not aware of all his surroundings. | 02. Failure to Warn | 1. Struck Against (Running or Bumping Into) |  | Reviewed. OGE should consider integrating backing technology (cameras/beepers/etc...) into our fleet vehicles that are currently not equipped. | [72 empty] | TRUE |  | Carney | OGE Vehicle Struck Other Vehicle | Backing Related | 2015-08-16 19:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
8946 | Metro Service Center | 2019-07-17 09:00 | Member backed company vehicle into company member's personal vehicle while performing volunteer work at Carney Public Schools. | Level 2 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Kenny La Ferney | 2019-08-09 10:48 | 2019-07-17 11:01 | 2019-07-17 11:01 | 2019-08-07 12:14 | 2019-07-31 09:00 | 2019-07-17 10:53 | 2019-08-09 10:27 |  | 2019-08-07 12:58 | Carney Ok Public Schools |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Kenny La Ferney |  | Members were pulling up to do volunteer service at Carney Public schools. One of the crew members came from his home to the jobsite and was in his personal vehicle. Member was trying to get the bucket truck into position to perform work. He had an intern backing him and was watching the backer for signals. As he was backing up he struck the members personal vehicle with passenger side, rear bumper of the bucket truck. The spotter never gave him signal to stop or turn. He stated he did not see the personal vehicle was why he did not stop the driver. Intern has been working at OGE for approximately 8 weeks, this is his second internship. The personal vehicle was parked too close to the jobsite and the spotter failed to give adequate signals to prevent an incident. Member driving the truck was focused on the spotter and failed to check mirrors, evaluate obstructions in his route, or communicate with the spotter in regards to where he was going. Backer went through the parking and vehicle situational awareness WBT on 3/21/2019 (this course covers 360 and the correct way to be a spotter). Backer stated he surveyed the area directly around the truck prior to the backing process, but was not aware of where the driver was backing to and did not identify the personal vehicle that was approximately 50' away. |  |  |  | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Tommy Nichols | Jimmy Combs |  | Gary Lassley | I have a few unanswered questions regarding this incident. (1) Do Interns receive backing training prior to their internship at OGE? Was he familiar with our backing procedure and hand signals? (2) How did the Intern miss the personal vehicle? Did he survey the area for potential obstruction prior to backing? | Gary Lassley |  | Medium |  | 2.01 Fears and phobias |  |  | 5.01 Lack of experience | [10 empty] | 16.01 Inadequate horizontal communication between peers | Spotter failed to perform task efficiently and member driving was not aware of all his surroundings. | 02. Failure to Warn | 1. Struck Against (Running or Bumping Into) |  | Reviewed. OGE should consider integrating backing technology (cameras/beepers/etc...) into our fleet vehicles that are currently not equipped. | [72 empty] | TRUE |  | Carney | OGE Vehicle Struck Other Vehicle | Backing Related | 2015-08-16 19:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
8946 | Metro Service Center | 2019-07-17 09:00 | Member backed company vehicle into company member's personal vehicle while performing volunteer work at Carney Public Schools. | Level 2 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Kenny La Ferney | 2019-08-09 10:48 | 2019-07-17 11:01 | 2019-07-17 11:01 | 2019-08-07 12:14 | 2019-07-31 09:00 | 2019-07-17 10:53 | 2019-08-09 10:27 |  | 2019-08-07 12:58 | Carney Ok Public Schools |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Kenny La Ferney |  | Members were pulling up to do volunteer service at Carney Public schools. One of the crew members came from his home to the jobsite and was in his personal vehicle. Member was trying to get the bucket truck into position to perform work. He had an intern backing him and was watching the backer for signals. As he was backing up he struck the members personal vehicle with passenger side, rear bumper of the bucket truck. The spotter never gave him signal to stop or turn. He stated he did not see the personal vehicle was why he did not stop the driver. Intern has been working at OGE for approximately 8 weeks, this is his second internship. The personal vehicle was parked too close to the jobsite and the spotter failed to give adequate signals to prevent an incident. Member driving the truck was focused on the spotter and failed to check mirrors, evaluate obstructions in his route, or communicate with the spotter in regards to where he was going. Backer went through the parking and vehicle situational awareness WBT on 3/21/2019 (this course covers 360 and the correct way to be a spotter). Backer stated he surveyed the area directly around the truck prior to the backing process, but was not aware of where the driver was backing to and did not identify the personal vehicle that was approximately 50' away. |  |  |  | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Tommy Nichols | Jimmy Combs |  | Gary Lassley | I have a few unanswered questions regarding this incident. (1) Do Interns receive backing training prior to their internship at OGE? Was he familiar with our backing procedure and hand signals? (2) How did the Intern miss the personal vehicle? Did he survey the area for potential obstruction prior to backing? | Gary Lassley |  | Medium |  | 2.01 Fears and phobias |  |  | 5.06 Lack of situational awareness | [10 empty] | 16.01 Inadequate horizontal communication between peers | Spotter failed to perform task efficiently and member driving was not aware of all his surroundings. | 02. Failure to Warn | 1. Struck Against (Running or Bumping Into) |  | Reviewed. OGE should consider integrating backing technology (cameras/beepers/etc...) into our fleet vehicles that are currently not equipped. | [72 empty] | TRUE |  | Carney | OGE Vehicle Struck Other Vehicle | Backing Related | 2015-08-16 19:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
8947 | Metro Service Center | 2019-07-18 09:00 | Tree trimmer dropped limb on gas meter, causing a small crack and gas leak. | Level 1 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Richard Norton | 2019-08-30 11:46 | 2019-07-18 14:43 | 2019-07-18 14:43 | 2019-07-22 13:49 | 2019-08-01 09:00 | 2019-07-18 14:29 | 2019-08-28 11:36 |  |  | 2507 Kirby Dr., Ada, OK |  |  | Jerrie Looney | Approved, J. Looney 8.30.19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Richard Norton |  | On Thursday July 18th, 2019, trimmer Carlos Rosado was trimming a tree in the front yard of a residence located at 2507 East Kirby Drive in Ada, OK. The crew completed a walk through and job briefing prior to beginning work. After approximately 10 minutes of trimming, the groundsman Elmer Melendez, began to notice an odor of gas. Melendez then called an “all stop”, notified his General Foreman, and began to investigate where the smell was coming from. Melendez uncovered a gas meter surrounded by brush that was directly in the drop zone. The brush surrounding the meter was leftover from the recent storm work. The damage caused was a small crack on the top of the gas meter. Once the General Foreman arrived on the scene he then notified the Davey Pre-Planner, who contacted Center Point Gas Company. Center Point arrived on scene and quickly made repairs. |  |  |  | Metro Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Richard Norton |  |  | Nicole Rhodes | Reviewed. |  |  | Low |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction | [10 empty] | On Thursday July 18th, 2019, trimmer Carlos Rosado was trimming a tree in the front yard of a residence located at 2507 East Kirby Drive in Ada, OK. The crew completed a walk through and job briefing prior to beginning work. After approximately 10 minutes of trimming, the groundsman Elmer Melendez, began to notice an odor of gas. Melendez then called an “all stop”, notified his General Foreman, and began to investigate where the smell was coming from. Melendez uncovered a gas meter surrounded by brush that was directly in the drop zone. The brush surrounding the meter was leftover from the recent storm work. The damage caused was a small crack on the top of the gas meter. Once the General Foreman arrived on the scene he then notified the Davey Pre-Planner, who contacted Center Point Gas Company. Center Point arrived on scene and quickly made repairs. | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Richard Norton | Dropped limb on gas meter |  |  |  |  | 2. Struck By (Hit By Moving Object) | Richard Norton | West Tree | Carlos Rosado |  | 3rd Party Property/Equipment | [6 empty] | FALSE
8947 | Metro Service Center | 2019-07-18 09:00 | Tree trimmer dropped limb on gas meter, causing a small crack and gas leak. | Level 1 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Richard Norton | 2019-08-30 11:46 | 2019-07-18 14:43 | 2019-07-18 14:43 | 2019-07-22 13:49 | 2019-08-01 09:00 | 2019-07-18 14:29 | 2019-08-28 11:36 |  |  | 2507 Kirby Dr., Ada, OK |  |  | Jerrie Looney | Approved, J. Looney 8.30.19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Richard Norton |  | On Thursday July 18th, 2019, trimmer Carlos Rosado was trimming a tree in the front yard of a residence located at 2507 East Kirby Drive in Ada, OK. The crew completed a walk through and job briefing prior to beginning work. After approximately 10 minutes of trimming, the groundsman Elmer Melendez, began to notice an odor of gas. Melendez then called an “all stop”, notified his General Foreman, and began to investigate where the smell was coming from. Melendez uncovered a gas meter surrounded by brush that was directly in the drop zone. The brush surrounding the meter was leftover from the recent storm work. The damage caused was a small crack on the top of the gas meter. Once the General Foreman arrived on the scene he then notified the Davey Pre-Planner, who contacted Center Point Gas Company. Center Point arrived on scene and quickly made repairs. |  |  |  | Metro Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Richard Norton |  |  | Nicole Rhodes | Reviewed. |  |  | Low |  |  |  |  | 5.06 Lack of situational awareness | 6.01 Inadequate initial instruction | [10 empty] | On Thursday July 18th, 2019, trimmer Carlos Rosado was trimming a tree in the front yard of a residence located at 2507 East Kirby Drive in Ada, OK. The crew completed a walk through and job briefing prior to beginning work. After approximately 10 minutes of trimming, the groundsman Elmer Melendez, began to notice an odor of gas. Melendez then called an “all stop”, notified his General Foreman, and began to investigate where the smell was coming from. Melendez uncovered a gas meter surrounded by brush that was directly in the drop zone. The brush surrounding the meter was leftover from the recent storm work. The damage caused was a small crack on the top of the gas meter. Once the General Foreman arrived on the scene he then notified the Davey Pre-Planner, who contacted Center Point Gas Company. Center Point arrived on scene and quickly made repairs. | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Richard Norton | Dropped limb on gas meter |  |  |  |  | 2. Struck By (Hit By Moving Object) | Richard Norton | West Tree | Carlos Rosado |  | 3rd Party Property/Equipment | [6 empty] | FALSE
8948 | Metro Service Center | 2019-07-18 08:30 | Member was rear ended. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Travis Sallee | 2019-07-30 13:16 | 2019-07-19 08:14 | 2019-07-19 08:14 | 2019-07-19 08:18 | 2019-08-01 08:30 | 2019-07-19 08:06 |  |  |  | OKC on SW 44th street at the railroad tracks |  |  | Brent Perdue | approved | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | [6 empty] | Metro Service Center | FALSE |  | FALSE | PD Operations Services |  | Maximilian Koller | Travis Sallee |  |  |  | Jeffrey Gleim |  | Low | [93 empty] | FALSE |  | OKC | Public Vehicle Struck OGE | OGE Vehicle Stopped/Parked | 2017-08-13 19:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
8948 | Metro Service Center | 2019-07-18 08:30 | Member was rear ended. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Travis Sallee | 2019-07-30 13:16 | 2019-07-19 08:14 | 2019-07-19 08:14 | 2019-07-19 08:18 | 2019-08-01 08:30 | 2019-07-19 08:06 |  |  |  | OKC on SW 44th street at the railroad tracks |  |  | Brent Perdue | approved | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | [6 empty] | Metro Service Center | FALSE |  | FALSE | PD Operations Services |  | Maximilian Koller | Travis Sallee |  |  |  | Jeffrey Gleim |  | Low | [93 empty] | FALSE |  | OKC | Public Vehicle Struck OGE | OGE Vehicle Stopped/Parked | 2017-08-13 19:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
8949 | Redbud Plant | 2019-07-19 21:00 | At time 2049 on the 19th of July a smoke alarm was received in the control room indicating that smoke was present in the Server Room Building. Auxiliary Operator investigated and reported white smoke in the Server Room. Fire Department called as a precautionary measure. White smoke had cleared when Fire Department arrived, FD conducted thermal imaging check with no hot spots found. No injuries. | Level 2 |  | FALSE | Property Damage | Donnie Jones |  |  |  | Power Supply | Anthony Gatto | 2019-08-16 12:21 | 2019-07-19 21:56 | 2019-07-19 21:56 | 2019-07-26 10:03 | 2019-08-02 21:00 | 2019-07-19 21:44 | 2019-07-30 07:31 |  | 2019-07-29 15:05 | Redbud Power Plant Server Room Building |  |  | Jesse Murray | I Approve. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Anthony Gatto |  | On 7/19/19 at 2049 the Control Room fire panel alarmed indicating smoke detected in the Server Room. At 2050 the Auxiliary Operator reported white smoke in the Server Room and the Control Room Operator contacted 911 and the Luther Fire Department was dispatched to the plant. At 2100 Luther Fire Department was on scene. At 2121 the Fire Department reported no signs of fire found and they conducted thermal imaging and found no hot spots in the Server Room. Both A/C units secured after smoke was detected in the Server Room and we were unable to restart either A/C unit. Facilities member (Brent Miller) arrived at the plant to troubleshoot the A/C units. One of the units was found to have a burnt fan motor and was tagged out, the other unit was reset and A/C was restored to the Server Room. On 7/24/19 the fan motor was replaced and the unit was restored to service. These two A/C units have been in place since the plant was built (2002) and were slated to be replaced this year. In light of this incident Facilities has accelerated replacement. Both A/C units should arrive within two weeks. |  |  |  | Redbud Plant | FALSE |  | FALSE | Operations |  | Anthony Gatto | Anthony Gatto |  | Robert Doupe | RDD Aprove | Robert Doupe |  | Medium | [11 empty] | 12.01.1 Inadequate preventative assessment of needs |  |  |  |  | A/C units were nearing the end of expected service life. this caused a degradation in fan motor winding insulation and ultimate failure. | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure |  | I have reviewed this incident and what G and Tom have added I approve. | [66 empty] | A/C unit fan motor burnt. | 1300 | Anthony Gatto | Fire | Timothy VanDeren | [19 empty] | Facilities W/O generated
8949 | Redbud Plant | 2019-07-19 21:00 | At time 2049 on the 19th of July a smoke alarm was received in the control room indicating that smoke was present in the Server Room Building. Auxiliary Operator investigated and reported white smoke in the Server Room. Fire Department called as a precautionary measure. White smoke had cleared when Fire Department arrived, FD conducted thermal imaging check with no hot spots found. No injuries. | Level 2 |  | FALSE | Property Damage | Donnie Jones |  |  |  | Power Supply | Anthony Gatto | 2019-08-16 12:21 | 2019-07-19 21:56 | 2019-07-19 21:56 | 2019-07-26 10:03 | 2019-08-02 21:00 | 2019-07-19 21:44 | 2019-07-30 07:31 |  | 2019-07-29 15:05 | Redbud Power Plant Server Room Building |  |  | Jesse Murray | I Approve. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Anthony Gatto |  | On 7/19/19 at 2049 the Control Room fire panel alarmed indicating smoke detected in the Server Room. At 2050 the Auxiliary Operator reported white smoke in the Server Room and the Control Room Operator contacted 911 and the Luther Fire Department was dispatched to the plant. At 2100 Luther Fire Department was on scene. At 2121 the Fire Department reported no signs of fire found and they conducted thermal imaging and found no hot spots in the Server Room. Both A/C units secured after smoke was detected in the Server Room and we were unable to restart either A/C unit. Facilities member (Brent Miller) arrived at the plant to troubleshoot the A/C units. One of the units was found to have a burnt fan motor and was tagged out, the other unit was reset and A/C was restored to the Server Room. On 7/24/19 the fan motor was replaced and the unit was restored to service. These two A/C units have been in place since the plant was built (2002) and were slated to be replaced this year. In light of this incident Facilities has accelerated replacement. Both A/C units should arrive within two weeks. |  |  |  | Redbud Plant | FALSE |  | FALSE | Operations |  | Anthony Gatto | Anthony Gatto |  | Robert Doupe | RDD Aprove | Robert Doupe |  | Medium | [11 empty] | 12.01.1 Inadequate preventative assessment of needs |  |  |  |  | A/C units were nearing the end of expected service life. this caused a degradation in fan motor winding insulation and ultimate failure. | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure |  | I have reviewed this incident and what G and Tom have added I approve. | [66 empty] | A/C unit fan motor burnt. | 1300 | Anthony Gatto | Fire | Jason James | [19 empty] | Facilities W/O generated
8950 | River Valley | 2019-07-21 02:30 | Stack opacity elevated alarming the CRO that there was an issue in 2B bag house. The fire was contained inside the module and hopper and no fire was ever observed. The fire fighters extinguished the fire by injecting water into the hopper without going inside the module. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Melton Morris | 2019-10-25 13:23 | 2019-07-22 09:14 | 2019-07-22 09:14 | 2019-10-16 15:46 | 2019-08-04 02:30 | 2019-07-21 02:30 | 2019-10-21 07:29 |  | 2019-10-18 08:17 | River Valley 2B boiler bag house module 12 |  |  | Jesse Murray | Approved. More CA's are assigned in the RCA for this event. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Melton Morris |  | 2B boiler bag house compartment Module 12 had ash build up in the hopper to the point it contacted the filter bags. Approximately 5 feet of ash built up onto the bags. The ash became hot enough to melt the Teflon off the bags and catch the Teflon on fire and then the cloth material of the bags. |  |  |  | River Valley | FALSE |  | FALSE | Operations |  | Charles Hill | Melton Morris |  | Timothy Chancellor | Good job on a through RCA. | Timothy Chancellor |  | Medium | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  | 15.03 Inadequate inspection and/or monitoring |  | INSPECT ALL BAGHOUSE HOPPERS FOR CRACKS/OPENINGS TO ATMOSPHERE. VERIFY OPERATION OF ALL VIBRATORS AND HEATERS | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure |  | Corrective actions identified should greatly reduce possibility of recurrence. | [66 empty] | 1A Module 4 bridged over and had ash suspended above the ash hopper gate. | 40000 | Melton Morris | Process Interruption | [20 empty] | 9588396
8950 | River Valley | 2019-07-21 02:30 | Stack opacity elevated alarming the CRO that there was an issue in 2B bag house. The fire was contained inside the module and hopper and no fire was ever observed. The fire fighters extinguished the fire by injecting water into the hopper without going inside the module. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Melton Morris | 2019-10-25 13:23 | 2019-07-22 09:14 | 2019-07-22 09:14 | 2019-10-16 15:46 | 2019-08-04 02:30 | 2019-07-21 02:30 | 2019-10-21 07:29 |  | 2019-10-18 08:17 | River Valley 2B boiler bag house module 12 |  |  | Jesse Murray | Approved. More CA's are assigned in the RCA for this event. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Melton Morris |  | 2B boiler bag house compartment Module 12 had ash build up in the hopper to the point it contacted the filter bags. Approximately 5 feet of ash built up onto the bags. The ash became hot enough to melt the Teflon off the bags and catch the Teflon on fire and then the cloth material of the bags. |  |  |  | River Valley | FALSE |  | FALSE | Operations |  | Charles Hill | Melton Morris |  | Timothy Chancellor | Good job on a through RCA. | Timothy Chancellor |  | Medium | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  | 15.03 Inadequate inspection and/or monitoring |  | INSPECT ALL BAGHOUSE HOPPERS FOR CRACKS/OPENINGS TO ATMOSPHERE. VERIFY OPERATION OF ALL VIBRATORS AND HEATERS | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure |  | Corrective actions identified should greatly reduce possibility of recurrence. | [66 empty] | 1B Module 11 bridged over and had ash suspended above the ash hopper gate. | 40000 | Melton Morris | Process Interruption | [20 empty] | 9588396
8950 | River Valley | 2019-07-21 02:30 | Stack opacity elevated alarming the CRO that there was an issue in 2B bag house. The fire was contained inside the module and hopper and no fire was ever observed. The fire fighters extinguished the fire by injecting water into the hopper without going inside the module. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Melton Morris | 2019-10-25 13:23 | 2019-07-22 09:14 | 2019-07-22 09:14 | 2019-10-16 15:46 | 2019-08-04 02:30 | 2019-07-21 02:30 | 2019-10-21 07:29 |  | 2019-10-18 08:17 | River Valley 2B boiler bag house module 12 |  |  | Jesse Murray | Approved. More CA's are assigned in the RCA for this event. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Melton Morris |  | 2B boiler bag house compartment Module 12 had ash build up in the hopper to the point it contacted the filter bags. Approximately 5 feet of ash built up onto the bags. The ash became hot enough to melt the Teflon off the bags and catch the Teflon on fire and then the cloth material of the bags. |  |  |  | River Valley | FALSE |  | FALSE | Operations |  | Charles Hill | Melton Morris |  | Timothy Chancellor | Good job on a through RCA. | Timothy Chancellor |  | Medium | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  | 15.03 Inadequate inspection and/or monitoring |  | INSPECT ALL BAGHOUSE HOPPERS FOR CRACKS/OPENINGS TO ATMOSPHERE. VERIFY OPERATION OF ALL VIBRATORS AND HEATERS | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure |  | Corrective actions identified should greatly reduce possibility of recurrence. | [66 empty] | 2A Module 2 bridged over and had ash suspended above the ash hopper gate. | 40000 | George Haney | Process Interruption | [20 empty] | 9588396
8950 | River Valley | 2019-07-21 02:30 | Stack opacity elevated alarming the CRO that there was an issue in 2B bag house. The fire was contained inside the module and hopper and no fire was ever observed. The fire fighters extinguished the fire by injecting water into the hopper without going inside the module. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Melton Morris | 2019-10-25 13:23 | 2019-07-22 09:14 | 2019-07-22 09:14 | 2019-10-16 15:46 | 2019-08-04 02:30 | 2019-07-21 02:30 | 2019-10-21 07:29 |  | 2019-10-18 08:17 | River Valley 2B boiler bag house module 12 |  |  | Jesse Murray | Approved. More CA's are assigned in the RCA for this event. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Melton Morris |  | 2B boiler bag house compartment Module 12 had ash build up in the hopper to the point it contacted the filter bags. Approximately 5 feet of ash built up onto the bags. The ash became hot enough to melt the Teflon off the bags and catch the Teflon on fire and then the cloth material of the bags. |  |  |  | River Valley | FALSE |  | FALSE | Operations |  | Charles Hill | Melton Morris |  | Timothy Chancellor | Good job on a through RCA. | Timothy Chancellor |  | Medium | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  | 15.03 Inadequate inspection and/or monitoring |  | INSPECT ALL BAGHOUSE HOPPERS FOR CRACKS/OPENINGS TO ATMOSPHERE. VERIFY OPERATION OF ALL VIBRATORS AND HEATERS | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure |  | Corrective actions identified should greatly reduce possibility of recurrence. | [66 empty] | Bags and cages damaged beyond use in Module 12 of 2B baghouse. The bags are burned and the cages are bent and damaged from the fire. | 50000 | Charles Hill | Fire |  | 2B bag house module 12 | [18 empty] | 9588396
8950 | River Valley | 2019-07-21 02:30 | Stack opacity elevated alarming the CRO that there was an issue in 2B bag house. The fire was contained inside the module and hopper and no fire was ever observed. The fire fighters extinguished the fire by injecting water into the hopper without going inside the module. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Melton Morris | 2019-10-25 13:23 | 2019-07-22 09:14 | 2019-07-22 09:14 | 2019-10-16 15:46 | 2019-08-04 02:30 | 2019-07-21 02:30 | 2019-10-21 07:29 |  | 2019-10-18 08:17 | River Valley 2B boiler bag house module 12 |  |  | Jesse Murray | Approved. More CA's are assigned in the RCA for this event. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Melton Morris |  | 2B boiler bag house compartment Module 12 had ash build up in the hopper to the point it contacted the filter bags. Approximately 5 feet of ash built up onto the bags. The ash became hot enough to melt the Teflon off the bags and catch the Teflon on fire and then the cloth material of the bags. |  |  |  | River Valley | FALSE |  | FALSE | Operations |  | Charles Hill | Melton Morris |  | Timothy Chancellor | Good job on a through RCA. | Timothy Chancellor |  | Medium | [11 empty] | 12.01.1 Inadequate preventative assessment of needs |  |  |  |  | 2B boiler bag house compartment Module 12 had ash build up in the hopper to the point it contacted the filter bags. Approximately 5 feet of ash built up onto the bags. The ash became hot enough to melt the Teflon off the bags and catch the Teflon on fire and then the cloth material of the bags. | 23. Defective Tools, Equipment or Materials | 9. Abnormal Operation |  | Corrective actions identified should greatly reduce possibility of recurrence. | [66 empty] | 1A Module 4 bridged over and had ash suspended above the ash hopper gate. | 40000 | Melton Morris | Process Interruption | [20 empty] | 9588396
8950 | River Valley | 2019-07-21 02:30 | Stack opacity elevated alarming the CRO that there was an issue in 2B bag house. The fire was contained inside the module and hopper and no fire was ever observed. The fire fighters extinguished the fire by injecting water into the hopper without going inside the module. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Melton Morris | 2019-10-25 13:23 | 2019-07-22 09:14 | 2019-07-22 09:14 | 2019-10-16 15:46 | 2019-08-04 02:30 | 2019-07-21 02:30 | 2019-10-21 07:29 |  | 2019-10-18 08:17 | River Valley 2B boiler bag house module 12 |  |  | Jesse Murray | Approved. More CA's are assigned in the RCA for this event. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Melton Morris |  | 2B boiler bag house compartment Module 12 had ash build up in the hopper to the point it contacted the filter bags. Approximately 5 feet of ash built up onto the bags. The ash became hot enough to melt the Teflon off the bags and catch the Teflon on fire and then the cloth material of the bags. |  |  |  | River Valley | FALSE |  | FALSE | Operations |  | Charles Hill | Melton Morris |  | Timothy Chancellor | Good job on a through RCA. | Timothy Chancellor |  | Medium | [11 empty] | 12.01.1 Inadequate preventative assessment of needs |  |  |  |  | 2B boiler bag house compartment Module 12 had ash build up in the hopper to the point it contacted the filter bags. Approximately 5 feet of ash built up onto the bags. The ash became hot enough to melt the Teflon off the bags and catch the Teflon on fire and then the cloth material of the bags. | 23. Defective Tools, Equipment or Materials | 9. Abnormal Operation |  | Corrective actions identified should greatly reduce possibility of recurrence. | [66 empty] | 1B Module 11 bridged over and had ash suspended above the ash hopper gate. | 40000 | Melton Morris | Process Interruption | [20 empty] | 9588396
8950 | River Valley | 2019-07-21 02:30 | Stack opacity elevated alarming the CRO that there was an issue in 2B bag house. The fire was contained inside the module and hopper and no fire was ever observed. The fire fighters extinguished the fire by injecting water into the hopper without going inside the module. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Melton Morris | 2019-10-25 13:23 | 2019-07-22 09:14 | 2019-07-22 09:14 | 2019-10-16 15:46 | 2019-08-04 02:30 | 2019-07-21 02:30 | 2019-10-21 07:29 |  | 2019-10-18 08:17 | River Valley 2B boiler bag house module 12 |  |  | Jesse Murray | Approved. More CA's are assigned in the RCA for this event. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Melton Morris |  | 2B boiler bag house compartment Module 12 had ash build up in the hopper to the point it contacted the filter bags. Approximately 5 feet of ash built up onto the bags. The ash became hot enough to melt the Teflon off the bags and catch the Teflon on fire and then the cloth material of the bags. |  |  |  | River Valley | FALSE |  | FALSE | Operations |  | Charles Hill | Melton Morris |  | Timothy Chancellor | Good job on a through RCA. | Timothy Chancellor |  | Medium | [11 empty] | 12.01.1 Inadequate preventative assessment of needs |  |  |  |  | 2B boiler bag house compartment Module 12 had ash build up in the hopper to the point it contacted the filter bags. Approximately 5 feet of ash built up onto the bags. The ash became hot enough to melt the Teflon off the bags and catch the Teflon on fire and then the cloth material of the bags. | 23. Defective Tools, Equipment or Materials | 9. Abnormal Operation |  | Corrective actions identified should greatly reduce possibility of recurrence. | [66 empty] | 2A Module 2 bridged over and had ash suspended above the ash hopper gate. | 40000 | George Haney | Process Interruption | [20 empty] | 9588396
8950 | River Valley | 2019-07-21 02:30 | Stack opacity elevated alarming the CRO that there was an issue in 2B bag house. The fire was contained inside the module and hopper and no fire was ever observed. The fire fighters extinguished the fire by injecting water into the hopper without going inside the module. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Melton Morris | 2019-10-25 13:23 | 2019-07-22 09:14 | 2019-07-22 09:14 | 2019-10-16 15:46 | 2019-08-04 02:30 | 2019-07-21 02:30 | 2019-10-21 07:29 |  | 2019-10-18 08:17 | River Valley 2B boiler bag house module 12 |  |  | Jesse Murray | Approved. More CA's are assigned in the RCA for this event. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Melton Morris |  | 2B boiler bag house compartment Module 12 had ash build up in the hopper to the point it contacted the filter bags. Approximately 5 feet of ash built up onto the bags. The ash became hot enough to melt the Teflon off the bags and catch the Teflon on fire and then the cloth material of the bags. |  |  |  | River Valley | FALSE |  | FALSE | Operations |  | Charles Hill | Melton Morris |  | Timothy Chancellor | Good job on a through RCA. | Timothy Chancellor |  | Medium | [11 empty] | 12.01.1 Inadequate preventative assessment of needs |  |  |  |  | 2B boiler bag house compartment Module 12 had ash build up in the hopper to the point it contacted the filter bags. Approximately 5 feet of ash built up onto the bags. The ash became hot enough to melt the Teflon off the bags and catch the Teflon on fire and then the cloth material of the bags. | 23. Defective Tools, Equipment or Materials | 9. Abnormal Operation |  | Corrective actions identified should greatly reduce possibility of recurrence. | [66 empty] | Bags and cages damaged beyond use in Module 12 of 2B baghouse. The bags are burned and the cages are bent and damaged from the fire. | 50000 | Charles Hill | Fire |  | 2B bag house module 12 | [18 empty] | 9588396
8950 | River Valley | 2019-07-21 02:30 | Stack opacity elevated alarming the CRO that there was an issue in 2B bag house. The fire was contained inside the module and hopper and no fire was ever observed. The fire fighters extinguished the fire by injecting water into the hopper without going inside the module. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Melton Morris | 2019-10-25 13:23 | 2019-07-22 09:14 | 2019-07-22 09:14 | 2019-10-16 15:46 | 2019-08-04 02:30 | 2019-07-21 02:30 | 2019-10-21 07:29 |  | 2019-10-18 08:17 | River Valley 2B boiler bag house module 12 |  |  | Jesse Murray | Approved. More CA's are assigned in the RCA for this event. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Melton Morris |  | 2B boiler bag house compartment Module 12 had ash build up in the hopper to the point it contacted the filter bags. Approximately 5 feet of ash built up onto the bags. The ash became hot enough to melt the Teflon off the bags and catch the Teflon on fire and then the cloth material of the bags. |  |  |  | River Valley | FALSE |  | FALSE | Operations |  | Charles Hill | Melton Morris |  | Timothy Chancellor | Good job on a through RCA. | Timothy Chancellor |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.02 Inadequate practice | [10 empty] | ADD AIRLOCK FUNCTION CHECK TO OPERATOR ROUNDS TO ENSURE PROPER OPERATION OF AIRLOCKS AT ALL TIMES | 18. Failure to Check, Monitor | 9. Abnormal Operation |  | Corrective actions identified should greatly reduce possibility of recurrence. | [66 empty] | 1A Module 4 bridged over and had ash suspended above the ash hopper gate. | 40000 | Melton Morris | Process Interruption | [20 empty] | 9588396
8950 | River Valley | 2019-07-21 02:30 | Stack opacity elevated alarming the CRO that there was an issue in 2B bag house. The fire was contained inside the module and hopper and no fire was ever observed. The fire fighters extinguished the fire by injecting water into the hopper without going inside the module. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Melton Morris | 2019-10-25 13:23 | 2019-07-22 09:14 | 2019-07-22 09:14 | 2019-10-16 15:46 | 2019-08-04 02:30 | 2019-07-21 02:30 | 2019-10-21 07:29 |  | 2019-10-18 08:17 | River Valley 2B boiler bag house module 12 |  |  | Jesse Murray | Approved. More CA's are assigned in the RCA for this event. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Melton Morris |  | 2B boiler bag house compartment Module 12 had ash build up in the hopper to the point it contacted the filter bags. Approximately 5 feet of ash built up onto the bags. The ash became hot enough to melt the Teflon off the bags and catch the Teflon on fire and then the cloth material of the bags. |  |  |  | River Valley | FALSE |  | FALSE | Operations |  | Charles Hill | Melton Morris |  | Timothy Chancellor | Good job on a through RCA. | Timothy Chancellor |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.02 Inadequate practice | [10 empty] | ADD AIRLOCK FUNCTION CHECK TO OPERATOR ROUNDS TO ENSURE PROPER OPERATION OF AIRLOCKS AT ALL TIMES | 18. Failure to Check, Monitor | 9. Abnormal Operation |  | Corrective actions identified should greatly reduce possibility of recurrence. | [66 empty] | 1B Module 11 bridged over and had ash suspended above the ash hopper gate. | 40000 | Melton Morris | Process Interruption | [20 empty] | 9588396
8950 | River Valley | 2019-07-21 02:30 | Stack opacity elevated alarming the CRO that there was an issue in 2B bag house. The fire was contained inside the module and hopper and no fire was ever observed. The fire fighters extinguished the fire by injecting water into the hopper without going inside the module. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Melton Morris | 2019-10-25 13:23 | 2019-07-22 09:14 | 2019-07-22 09:14 | 2019-10-16 15:46 | 2019-08-04 02:30 | 2019-07-21 02:30 | 2019-10-21 07:29 |  | 2019-10-18 08:17 | River Valley 2B boiler bag house module 12 |  |  | Jesse Murray | Approved. More CA's are assigned in the RCA for this event. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Melton Morris |  | 2B boiler bag house compartment Module 12 had ash build up in the hopper to the point it contacted the filter bags. Approximately 5 feet of ash built up onto the bags. The ash became hot enough to melt the Teflon off the bags and catch the Teflon on fire and then the cloth material of the bags. |  |  |  | River Valley | FALSE |  | FALSE | Operations |  | Charles Hill | Melton Morris |  | Timothy Chancellor | Good job on a through RCA. | Timothy Chancellor |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.02 Inadequate practice | [10 empty] | ADD AIRLOCK FUNCTION CHECK TO OPERATOR ROUNDS TO ENSURE PROPER OPERATION OF AIRLOCKS AT ALL TIMES | 18. Failure to Check, Monitor | 9. Abnormal Operation |  | Corrective actions identified should greatly reduce possibility of recurrence. | [66 empty] | 2A Module 2 bridged over and had ash suspended above the ash hopper gate. | 40000 | George Haney | Process Interruption | [20 empty] | 9588396
8950 | River Valley | 2019-07-21 02:30 | Stack opacity elevated alarming the CRO that there was an issue in 2B bag house. The fire was contained inside the module and hopper and no fire was ever observed. The fire fighters extinguished the fire by injecting water into the hopper without going inside the module. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Melton Morris | 2019-10-25 13:23 | 2019-07-22 09:14 | 2019-07-22 09:14 | 2019-10-16 15:46 | 2019-08-04 02:30 | 2019-07-21 02:30 | 2019-10-21 07:29 |  | 2019-10-18 08:17 | River Valley 2B boiler bag house module 12 |  |  | Jesse Murray | Approved. More CA's are assigned in the RCA for this event. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Melton Morris |  | 2B boiler bag house compartment Module 12 had ash build up in the hopper to the point it contacted the filter bags. Approximately 5 feet of ash built up onto the bags. The ash became hot enough to melt the Teflon off the bags and catch the Teflon on fire and then the cloth material of the bags. |  |  |  | River Valley | FALSE |  | FALSE | Operations |  | Charles Hill | Melton Morris |  | Timothy Chancellor | Good job on a through RCA. | Timothy Chancellor |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.02 Inadequate practice | [10 empty] | ADD AIRLOCK FUNCTION CHECK TO OPERATOR ROUNDS TO ENSURE PROPER OPERATION OF AIRLOCKS AT ALL TIMES | 18. Failure to Check, Monitor | 9. Abnormal Operation |  | Corrective actions identified should greatly reduce possibility of recurrence. | [66 empty] | Bags and cages damaged beyond use in Module 12 of 2B baghouse. The bags are burned and the cages are bent and damaged from the fire. | 50000 | Charles Hill | Fire |  | 2B bag house module 12 | [18 empty] | 9588396
8950 | River Valley | 2019-07-21 02:30 | Stack opacity elevated alarming the CRO that there was an issue in 2B bag house. The fire was contained inside the module and hopper and no fire was ever observed. The fire fighters extinguished the fire by injecting water into the hopper without going inside the module. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Melton Morris | 2019-10-25 13:23 | 2019-07-22 09:14 | 2019-07-22 09:14 | 2019-10-16 15:46 | 2019-08-04 02:30 | 2019-07-21 02:30 | 2019-10-21 07:29 |  | 2019-10-18 08:17 | River Valley 2B boiler bag house module 12 |  |  | Jesse Murray | Approved. More CA's are assigned in the RCA for this event. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Melton Morris |  | 2B boiler bag house compartment Module 12 had ash build up in the hopper to the point it contacted the filter bags. Approximately 5 feet of ash built up onto the bags. The ash became hot enough to melt the Teflon off the bags and catch the Teflon on fire and then the cloth material of the bags. |  |  |  | River Valley | FALSE |  | FALSE | Operations |  | Charles Hill | Melton Morris |  | Timothy Chancellor | Good job on a through RCA. | Timothy Chancellor |  | Medium | [11 empty] | 12.01.3 Inadequate preventative adjustment/assembly |  |  |  |  | PURCHASE SPARE ASH LEVEL PROBES AND DEVELOP A PM PROCESS OF INSTALLING CALIBRATED PROBES AT PREDETERMINED SERVICE INTERVAL ON ALL BAGHOUSE MODULES | 18. Failure to Check, Monitor | 12. Equipment Failure |  | Corrective actions identified should greatly reduce possibility of recurrence. | [66 empty] | 1A Module 4 bridged over and had ash suspended above the ash hopper gate. | 40000 | Melton Morris | Process Interruption | [20 empty] | 9588396
8950 | River Valley | 2019-07-21 02:30 | Stack opacity elevated alarming the CRO that there was an issue in 2B bag house. The fire was contained inside the module and hopper and no fire was ever observed. The fire fighters extinguished the fire by injecting water into the hopper without going inside the module. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Melton Morris | 2019-10-25 13:23 | 2019-07-22 09:14 | 2019-07-22 09:14 | 2019-10-16 15:46 | 2019-08-04 02:30 | 2019-07-21 02:30 | 2019-10-21 07:29 |  | 2019-10-18 08:17 | River Valley 2B boiler bag house module 12 |  |  | Jesse Murray | Approved. More CA's are assigned in the RCA for this event. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Melton Morris |  | 2B boiler bag house compartment Module 12 had ash build up in the hopper to the point it contacted the filter bags. Approximately 5 feet of ash built up onto the bags. The ash became hot enough to melt the Teflon off the bags and catch the Teflon on fire and then the cloth material of the bags. |  |  |  | River Valley | FALSE |  | FALSE | Operations |  | Charles Hill | Melton Morris |  | Timothy Chancellor | Good job on a through RCA. | Timothy Chancellor |  | Medium | [11 empty] | 12.01.3 Inadequate preventative adjustment/assembly |  |  |  |  | PURCHASE SPARE ASH LEVEL PROBES AND DEVELOP A PM PROCESS OF INSTALLING CALIBRATED PROBES AT PREDETERMINED SERVICE INTERVAL ON ALL BAGHOUSE MODULES | 18. Failure to Check, Monitor | 12. Equipment Failure |  | Corrective actions identified should greatly reduce possibility of recurrence. | [66 empty] | 1B Module 11 bridged over and had ash suspended above the ash hopper gate. | 40000 | Melton Morris | Process Interruption | [20 empty] | 9588396
8950 | River Valley | 2019-07-21 02:30 | Stack opacity elevated alarming the CRO that there was an issue in 2B bag house. The fire was contained inside the module and hopper and no fire was ever observed. The fire fighters extinguished the fire by injecting water into the hopper without going inside the module. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Melton Morris | 2019-10-25 13:23 | 2019-07-22 09:14 | 2019-07-22 09:14 | 2019-10-16 15:46 | 2019-08-04 02:30 | 2019-07-21 02:30 | 2019-10-21 07:29 |  | 2019-10-18 08:17 | River Valley 2B boiler bag house module 12 |  |  | Jesse Murray | Approved. More CA's are assigned in the RCA for this event. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Melton Morris |  | 2B boiler bag house compartment Module 12 had ash build up in the hopper to the point it contacted the filter bags. Approximately 5 feet of ash built up onto the bags. The ash became hot enough to melt the Teflon off the bags and catch the Teflon on fire and then the cloth material of the bags. |  |  |  | River Valley | FALSE |  | FALSE | Operations |  | Charles Hill | Melton Morris |  | Timothy Chancellor | Good job on a through RCA. | Timothy Chancellor |  | Medium | [11 empty] | 12.01.3 Inadequate preventative adjustment/assembly |  |  |  |  | PURCHASE SPARE ASH LEVEL PROBES AND DEVELOP A PM PROCESS OF INSTALLING CALIBRATED PROBES AT PREDETERMINED SERVICE INTERVAL ON ALL BAGHOUSE MODULES | 18. Failure to Check, Monitor | 12. Equipment Failure |  | Corrective actions identified should greatly reduce possibility of recurrence. | [66 empty] | 2A Module 2 bridged over and had ash suspended above the ash hopper gate. | 40000 | George Haney | Process Interruption | [20 empty] | 9588396
8950 | River Valley | 2019-07-21 02:30 | Stack opacity elevated alarming the CRO that there was an issue in 2B bag house. The fire was contained inside the module and hopper and no fire was ever observed. The fire fighters extinguished the fire by injecting water into the hopper without going inside the module. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Melton Morris | 2019-10-25 13:23 | 2019-07-22 09:14 | 2019-07-22 09:14 | 2019-10-16 15:46 | 2019-08-04 02:30 | 2019-07-21 02:30 | 2019-10-21 07:29 |  | 2019-10-18 08:17 | River Valley 2B boiler bag house module 12 |  |  | Jesse Murray | Approved. More CA's are assigned in the RCA for this event. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Melton Morris |  | 2B boiler bag house compartment Module 12 had ash build up in the hopper to the point it contacted the filter bags. Approximately 5 feet of ash built up onto the bags. The ash became hot enough to melt the Teflon off the bags and catch the Teflon on fire and then the cloth material of the bags. |  |  |  | River Valley | FALSE |  | FALSE | Operations |  | Charles Hill | Melton Morris |  | Timothy Chancellor | Good job on a through RCA. | Timothy Chancellor |  | Medium | [11 empty] | 12.01.3 Inadequate preventative adjustment/assembly |  |  |  |  | PURCHASE SPARE ASH LEVEL PROBES AND DEVELOP A PM PROCESS OF INSTALLING CALIBRATED PROBES AT PREDETERMINED SERVICE INTERVAL ON ALL BAGHOUSE MODULES | 18. Failure to Check, Monitor | 12. Equipment Failure |  | Corrective actions identified should greatly reduce possibility of recurrence. | [66 empty] | Bags and cages damaged beyond use in Module 12 of 2B baghouse. The bags are burned and the cages are bent and damaged from the fire. | 50000 | Charles Hill | Fire |  | 2B bag house module 12 | [18 empty] | 9588396
8951 | Ardmore Service Center | 2019-07-20 19:30 | Vehicle struck overhead awning. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Carl Williams | 2019-08-12 07:49 | 2019-07-22 10:46 | 2019-07-22 10:46 | 2019-08-02 07:14 | 2019-08-03 19:30 | 2019-07-22 10:35 | 2019-08-05 14:06 |  |  | Ardmore Oklahoma |  |  | Terry Hackett | The company has experienced multiple incidents where our vehicles have struck overhead awnings. Policy, expectations, and awareness are crucial to minimize occurrence. | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Carl Williams |  | Member parked in large parking lot behind restaurant. Upon exiting the parking lot member noticed cars had parked along a small pipe fence (bumper to bumper), which did not leave much room between the drive through and the parked vehicles. This was the only exit route. Member waited approximately 25 minutes for vehicles to leave, but later found out these were employee vehicles. Member cautiously proceeded forward observing the awning and vehicles on the right side to ensure he did not strike them. Member thought got out of his vehicle twice and thought he was in a position where he could clear the awning and the vehicles, but struck the awning approximately 3" from the edge with the boom of the service truck. |  |  |  | Ardmore Service Center | FALSE |  | FALSE | Construction Services |  | Robert Beardslee | Carl Williams |  | Kenneth McKinzie | Changed Corrective actions to be completed by Bobby Beardslee. Train members on Hazard identification and mitigation. Share lessons learned with Southern area | Kenneth McKinzie |  | Low |  |  |  | 4.05 Extreme concentration/perception demands |  |  | 7.06 Improper attempt to save time or effort | [9 empty] | The hazard of striking the awning was identified, but the proper controls were not identified (i.e. spotter or have vehicles move) | 11. Improper Position for Task | 1. Struck Against (Running or Bumping Into) | [74 empty] | TRUE |  | Ardmore | Struck Fixed Object | Drove Forward Into Object | 1995-01-08 18:00 |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Clear
8952 | North Service Center | 2019-07-22 15:00 | Davey Tree climber almost overheated | Level 2 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services | Grant Ehlen | 2019-07-27 12:27 | 2019-07-22 15:33 | 2019-07-22 15:33 | 2019-07-22 16:01 | 2019-08-05 15:00 | 2019-07-22 15:00 | 2019-07-23 16:13 |  | 2019-07-22 16:45 | NW OKC job site |  |  | William Young | Reviewed and approved. WCY 7/27/2019 | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Grant Ehlen |  | I observed a climber in a tree on a very hot afternoon. He was sitting wiping his forehead repeatedly. I kept watching him for a few more minutes. He continued sitting but not working. I asked the contract GF if he thought something might be wrong. The GF asked the worker if he felt ok. The worker didn't respond immediately so the GF asked him to come down and rest. The worker finally came down and got a cool cloth to put on his neck. |  |  |  | North Service Center | FALSE |  | TRUE | PD - Resource Planning & Coord |  | Grant Ehlen | Christopher Martin |  | Christopher Martin | I agree with the corrective actions discussed. No further action needed. | Christopher Martin |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [10 empty] | 16.02 Inadequate vertical communication between supervisor and person | high heat | 40. Weather Conditions | 11. Overstress, Overpressure, Overexertion, Ergonomic |  | Approved. J. Looney 7/22/19 |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Grant Ehlen | [5 empty] | 11. Overstress, Overpressure, Overexertion, Ergonomic | Grant Ehlen | Davey Tree Surgery | Employee A |  |  |  | Christopher Martin
8953 | Muskogee Power Plant | 2019-07-23 15:30 | J.A.M Delivery drivers fill hose came off of the truck spraying Diesel outside the containment area. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Scott Stidham | 2019-08-16 12:12 | 2019-07-23 16:56 | 2019-07-23 16:56 | 2019-07-25 17:00 | 2019-08-06 15:30 | 2019-07-23 16:47 | 2019-08-05 09:13 |  | 2019-07-26 14:19 | Diesel tank north of Maintenance shop |  |  | Jesse Murray | Approve. Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Scott Stidham |  | Diesel delivery driver was offloading into the tanks north of the maintenance shop. The driver was a newer driver and had never offloaded into this tank, when he hooked up his hoses to the truck he did not secure the couplings with any type of locking device. During the Offloading process one of the hoses came loose spraying diesel onto the truck ground and an OGE truck parked nearby. The driver did not have a OGE personnel present during the offloading process. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Other |  | William Edwards | Scott Stidham |  |  | Reviewed, and agree. SPC |  |  | Medium |  |  |  | 4.04 Routine, monotony, demand for uneventful vigilance | 5.01 Lack of experience | [11 empty] | Driver I failed to secure his fill hose to the tanker. He was aware that he had straps on his hose and stated that they don't always use them. | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation |  | reviewed Bob Wright |  |  |  | Injury / Illness |  | Scott Stidham | [5 empty] | 9. Abnormal Operation | William Edwards | J.A.M | James |  |  |  | Robert Wright
8953 | Muskogee Power Plant | 2019-07-23 15:30 | J.A.M Delivery drivers fill hose came off of the truck spraying Diesel outside the containment area. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Scott Stidham | 2019-08-16 12:12 | 2019-07-23 16:56 | 2019-07-23 16:56 | 2019-07-25 17:00 | 2019-08-06 15:30 | 2019-07-23 16:47 | 2019-08-05 09:13 |  | 2019-07-26 14:19 | Diesel tank north of Maintenance shop |  |  | Jesse Murray | Approve. Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Scott Stidham |  | Diesel delivery driver was offloading into the tanks north of the maintenance shop. The driver was a newer driver and had never offloaded into this tank, when he hooked up his hoses to the truck he did not secure the couplings with any type of locking device. During the Offloading process one of the hoses came loose spraying diesel onto the truck ground and an OGE truck parked nearby. The driver did not have a OGE personnel present during the offloading process. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Other |  | William Edwards | Scott Stidham |  |  | Reviewed, and agree. SPC |  |  | Medium | [8 empty] | 9.02 Unclear or conflicting assignment of responsibility | [7 empty] | Plant contact failed to inform Operations or Chemist that a delivery of fuel was onsite and needed offloading. | 20. Failure to Communicate, Coordinate | 9. Abnormal Operation |  | reviewed Bob Wright |  |  |  | Injury / Illness |  | Scott Stidham | [5 empty] | 9. Abnormal Operation | William Edwards | J.A.M | James |  |  |  | Robert Wright
8953 | Muskogee Power Plant | 2019-07-23 15:30 | J.A.M Delivery drivers fill hose came off of the truck spraying Diesel outside the containment area. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Scott Stidham | 2019-08-16 12:12 | 2019-07-23 16:56 | 2019-07-23 16:56 | 2019-07-25 17:00 | 2019-08-06 15:30 | 2019-07-23 16:47 | 2019-08-05 09:13 |  | 2019-07-26 14:19 | Diesel tank north of Maintenance shop |  |  | Jesse Murray | Approve. Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Scott Stidham |  | Diesel delivery driver was offloading into the tanks north of the maintenance shop. The driver was a newer driver and had never offloaded into this tank, when he hooked up his hoses to the truck he did not secure the couplings with any type of locking device. During the Offloading process one of the hoses came loose spraying diesel onto the truck ground and an OGE truck parked nearby. The driver did not have a OGE personnel present during the offloading process. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Other |  | William Edwards | Scott Stidham |  |  | Reviewed, and agree. SPC |  |  | Medium | [8 empty] | 9.04 Giving inadequate policy, procedure, practices or guidelines | [7 empty] | Plant contact failed to inform Operations or Chemist that a delivery of fuel was onsite and needed offloading. | 20. Failure to Communicate, Coordinate | 9. Abnormal Operation |  | reviewed Bob Wright |  |  |  | Injury / Illness |  | Scott Stidham | [5 empty] | 9. Abnormal Operation | William Edwards | J.A.M | James |  |  |  | Robert Wright
8953 | Muskogee Power Plant | 2019-07-23 15:30 | J.A.M Delivery drivers fill hose came off of the truck spraying Diesel outside the containment area. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Scott Stidham | 2019-08-16 12:12 | 2019-07-23 16:56 | 2019-07-23 16:56 | 2019-07-25 17:00 | 2019-08-06 15:30 | 2019-07-23 16:47 | 2019-08-05 09:13 |  | 2019-07-26 14:19 | Diesel tank north of Maintenance shop |  |  | Jesse Murray | Approve. Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Scott Stidham |  | Diesel delivery driver was offloading into the tanks north of the maintenance shop. The driver was a newer driver and had never offloaded into this tank, when he hooked up his hoses to the truck he did not secure the couplings with any type of locking device. During the Offloading process one of the hoses came loose spraying diesel onto the truck ground and an OGE truck parked nearby. The driver did not have a OGE personnel present during the offloading process. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Other |  | William Edwards | Scott Stidham |  |  | Reviewed, and agree. SPC |  |  | Medium | [8 empty] | 9.04 Giving inadequate policy, procedure, practices or guidelines | [7 empty] | SOP.PS.073 and OI.MK.102 both misidentify the role of Plant Chemist or Operator as being responsible for being present before chemical unloading and to serve as the plant representative/contact per the document instructions. This should state that an Operator or Chemist should be present before offloading chemicals. Per definition in both docs Unloading is the process of moving totes or barrels and Offloading is the act of transferring bulk chemical from containers. OI.MK.102 also does not include a list of all bulk chemicals maintained at the plant as required by the SOP | 34. Inadequate Instructions, Procedures | 9. Abnormal Operation |  | reviewed Bob Wright |  |  |  | Injury / Illness |  | Scott Stidham | [5 empty] | 9. Abnormal Operation | William Edwards | J.A.M | James |  |  |  | Robert Wright
8954 | River Valley | 2019-07-23 11:00 | While erecting scaffolding under the 2B Bag House, contractor was observed working 7' off the ground with no fall protection. Fall protection harness/ connecting device was being worn, but not utilized. | Level 3 |  | TRUE | Contractor | Donnie Jones | Jesse Murray | Assigned per Andy | 2019-08-07 07:07 | Power Supply | Gary Martin | 2019-10-21 07:33 | 2019-07-24 15:29 | 2019-07-24 15:29 | 2019-08-29 13:09 | 2019-08-06 10:00 | 2019-07-23 14:53 | 2019-09-18 06:51 | 2019-10-09 15:27 | 2019-08-30 08:39 | 2B bag house mod 12 Scaffolding to manway. |  |  | Donnie Jones | I concur with your corrective actions, thank you. | Power Supply |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Melton Morris |  | While erecting scaffolding under the 2B Bag House, contractor was observed working 7' off the ground with no fall protection. Fall protection harness/ connecting device was being worn, but not utilized. Individual was terminated from the contract company and is not allowed back on site. Individual was trained on fall protection and was the lead scaffold builder at Seminole plant. Individual had been trained on fall protection. | Gary Martin | Melton Morris |  | River Valley | FALSE |  | TRUE | Other |  | Anthony Gillespie | Gary Martin |  | Timothy Chancellor | Actions appropriate for the situation. | Timothy Chancellor | Jesse Murray | High | [6 empty] | 7.06 Improper attempt to save time or effort | [9 empty] | While erecting scaffolding under the 2B Bag House, contractor was observed working 7' off the ground with no fall protection. Fall protection harness/ connecting device was being worn, but not utilized. | 07. Failing to Use PPE Properly | 3. Fall from Elevation to Lower Level | Approved. Jesse Murray | Appropriate actions taken due to nature of incident. |  |  |  | Injury / Illness |  | Gary Martin | [5 empty] | 3. Fall from Elevation to Lower Level | Anthony Gillespie | EAI | Gilberto Salinas |  |  |  | Gary Martin
8955 | River Valley | 2019-07-23 13:00 | A clamp was attached to a leg loosely and while attempting to attach another one the first clamp came loose and fell app 18 feet to the ground. No one was struck with the clamp and barricade was in place. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Gary Martin | 2019-08-26 08:25 | 2019-07-24 15:45 | 2019-07-24 15:45 | 2019-08-16 14:38 | 2019-08-06 13:00 | 2019-07-24 15:33 | 2019-08-23 13:51 |  |  | 2B bag house mod 12 scaffolding to manway. |  |  | Anthony Gillespie | Coordination with contractors that stresses expectation for proper securement should reduce likelihood of recurrence. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Gary Martin |  | A clamp was attached to a leg loosely and while attempting to attach another one the first clamp came loose and fell app 18 feet to the ground. No one was struck with the clamp and barricade was in place. The job was stopped and supervision was notified of incident.Physical barricades were in place and the clamp fell within the barricaded zone. Clamp weight is app. 2 LB. This was the second incident that day for this individual. Individual was terminated from employment by contractor supervision. A clamp was attached to a leg loosely and while attempting to attach another one the first clamp came loose and fell app 18 feet to the ground. No one was struck with the clamp and barricade was in place. A clamp was attached to a leg loosely and while attempting to attach another one the first clamp came loose and fell app 18 feet to the ground. No one was struck with the clamp and barricade was in place. |  |  |  | River Valley | FALSE |  | TRUE | Other |  | Anthony Gillespie | Gary Martin |  | Timothy Chancellor | no further comments. action to address with scaffolding contractor is appropriate. | Timothy Chancellor |  | Low | [13 empty] | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  |  | Failure to secure clamp to crossmember. | 03. Failure to Secure | 3. Fall from Elevation to Lower Level | [5 empty] | Injury / Illness |  | Gary Martin | [5 empty] | 3. Fall from Elevation to Lower Level | Anthony Gillespie | EAI | Gilbert Salinas |  |  |  | Gary Martin | [71 empty] | 9588396
8956 | Seminole PP; EGX Gath/Trans | 2019-07-25 10:30 | Contractor was loading a bundle rack of 5ft scaffold poles onto truck. The bundles stack on top of each other by the 4 legs. While setting bundle down onto the other bundle, one leg did not line up, causing the bundle to fall forward off the truck. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Terry Bunch | 2019-09-17 10:47 | 2019-07-25 13:27 | 2019-07-25 13:27 | 2019-08-23 10:19 | 2019-08-08 10:30 | 2019-07-25 13:15 | 2019-08-29 09:07 |  | 2019-08-23 10:52 | Temporary Scaffold storage area for outage. South of Unit 1. |  |  | Jesse Murray | Approved. Jesse Murray 9-17-19 | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Terry Bunch |  | While loading racks of scaffolding the forklift operator and spotter failed to see that the racks were not line up, causing the load to fall on truck bed and ground. EAI does not have formal training on being a spotter. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | TRUE | Other |  | Timothy Coffey | Terry Bunch |  | Paul Schoelen | Review Complete | Paul Schoelen |  | Medium |  |  |  | 4.04 Routine, monotony, demand for uneventful vigilance | [9 empty] | 14.01.2 Inadequate development of standards: coordination with process design |  |  | Individuals were in to be of a hurry and not focus on the task at hand. | 16. Failure to Follow Procedure, Policy, Practice | 3. Fall from Elevation to Lower Level |  | See comments for reason being returned. Update: Reviewed. |  |  |  | Vehicle |  | Terry Bunch | [5 empty] | 9. Abnormal Operation | Terry Bunch | ENVIRONMENTAL ACTION INC | Raul Castillo |  |  |  | Terry Bunch
8957 | Seminole PP; EGX Gath/Trans | 2019-07-18 | Contractor PPRS installed balance weights at exciter coupling while turning gear was engaged. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Justin Stahl | 2019-08-28 08:00 | 2019-07-25 15:23 | 2019-07-25 15:23 | 2019-08-07 15:40 | 2019-08-01 | 2019-07-25 15:14 | 2019-08-09 13:15 |  | 2019-08-09 13:56 | Turbine Deck SM01 Exciter Coupling |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Justin Stahl |  | LOTO was hung on EH pumps and one simple LOTO ready to be hung for the main turbine turning gear for the balance shot on #9 bearing. The PPRS workers signed on the EH LOTO. PPRS was looking for weights and having to make some so the turbine was left on turning gear until they were ready. PPRS Lead was in and out of the control room checking on the PPRS members and was told not to install weights until the simple LOTO was in place on the turning gear. PPRS returned to the control room ready to sign off the LOTO’s saying the weights were in place. Member had PPRS show him what they did. The coupling in the exciter is exposed where PPRS had access to put the shot in while still on turning gear and PPRS tightened it as it went around and would wait for it to come back around to tighten it some more. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | Operations |  | Danny Huckleberry | Justin Stahl |  | Scott Lee | I approve this investigation report. | Scott Lee |  | Medium |  |  |  |  | 5.05 Misunderstood directions | [10 empty] | 16.03. Inadequate communication between different organizations | Contractor not adhering to instructions from Operating Authority. | 16. Failure to Follow Procedure, Policy, Practice | 5. Caught In (Pinch and Nip Points) |  | See WorkFlow Comments for reason being returned. |  |  |  | Clearance / LOTO |  | Justin Stahl | [5 empty] | 5. Caught In (Pinch and Nip Points) | Danny Huckleberry | PPRS | Byron Hester |  |  |  | Justin Stahl | [71 empty] | 9584993
8958 | Muskogee Service Center | 2019-07-25 11:30 | This is a First Aid. Member felt nauseous due to heat and came down from the bucket. | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Brian McKinney | 2019-07-29 13:27 | 2019-07-25 15:23 | 2019-07-25 15:23 | 2019-07-29 09:29 | 2019-08-08 10:30 | 2019-07-25 15:08 |  |  |  | 900 west Gentry Checotah |  |  | Hannah Everett | Approved | T&D Ops |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE |  |  | Member was working a three phase primary pole in bucket when he experience temporary heat exhaustion while he was wearing his gloves and sleeves. Member came down from the bucket and the crew began to cool him off with water and removing his FR shirt. Member came back to the plant and continued to drink water along with the hydration popsicles. Member is feeling better by 2:30 pm. |  |  | FALSE | Muskogee Service Center | FALSE |  | FALSE | Construction Services |  |  | Brian McKinney |  |  |  | Michael Fox |  | Low | [45 empty] | FALSE |  |  | 2015-03-03 | 1991-01-18 |  | 2019-07-25 07:00 | 0 | 0 |  | FALSE |  | Member was in the bucket wearing his gloves and sleeves while working on a three phase primary pole. |  | FALSE | Cody Duke |  | First Aid | Cody Duke |  |  |  |  | Heat Stroke/Exhaustion |  | FALSE |  | Lineman | Head |  |  | FALSE | Brian McKinney | FALSE |  | 7/25/2019 7:00:00 AM |  | FALSE |  |  | Heat exhaustion | [25 empty] | 7383995
8959 | Horseshoe Lake Power Plant | 2019-07-25 14:00 | while backfilling eroded ditch at the Enable gas yard contractor broke make-up water line from #7 and 8 deep wells. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-08-29 08:06 | 2019-07-26 06:12 | 2019-07-26 06:12 | 2019-08-27 15:48 | 2019-08-08 14:00 | 2019-07-25 14:00 | 2019-08-28 09:58 |  | 2019-08-27 15:51 | Horseshoe Lake @ Enable drive on west side of plant property |  |  | Jesse Murray | I am returning due to comments from 8/21/19 incident call. Please modify the corrective actions to address the immediate and basic cause selected. The corrective actions should alight with the root cause. Lets make sure the corrective actions prevent the root cause from happening again. Jesse Murray 8/21/19 Approved. 8/29/19 | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Plant requested contractor repair erosion damage from spring flooding at the Enable gas yard road tie in to plant road. Erosion had uncovered approximately 4 feet of a 6" fiberglass water line that comes from #7 and #8 deep wells to the plant. Repair process was to backfill exposed line with sand from the river settling basin and install a piece of HDPE left from another project and utilize it for a culvert and cover with crusher run rock. While spreading the sand with an excavator contractor had spread 2 dump truck loads and was using his bucket to pack when water started flowing from backfill. He contacted his plant contact immediately and contact notified control room to help isolate water. During repair, line was identified as containing ACM and insulators were contacted to cut and dispose of crushed line. When repair was uncovered the old piping was damaged from pressure of bucket when contractor was compacting sand around piping. The plant has had some previous leaks that were the result of ground pressure and its brittleness causes it to break. The contractor was onsite for another project that was wrapping up and the plant asked if they could assist in repair of erosion with some left over rock from that project to repair this damage. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | No comment, approved. | Brian Huckabay |  | Medium |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.11 Inadequate matching of individual qualifications and job/task requirements | [7 empty] | Failure to Identify line and risk exposure prior to contractors beginning work. | 17. Failure to Identify Hazard, Risk | 7. Caught Between or Under (Crushed or Amputated) |  | Reviewed. Reviewed again and after corrected immediate and basic causes with additional corrective actions added, I approve. |  |  |  | Property Damage |  | Kelly Casey | broken water line |  |  |  |  | 12. Equipment Failure | Kelly Casey | Duncan and Sons | Bobby Claig |  | Utility Strike |  | Kelly Casey |  |  |  |  | FALSE | [66 empty] | 615604
8959 | Horseshoe Lake Power Plant | 2019-07-25 14:00 | while backfilling eroded ditch at the Enable gas yard contractor broke make-up water line from #7 and 8 deep wells. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-08-29 08:06 | 2019-07-26 06:12 | 2019-07-26 06:12 | 2019-08-27 15:48 | 2019-08-08 14:00 | 2019-07-25 14:00 | 2019-08-28 09:58 |  | 2019-08-27 15:51 | Horseshoe Lake @ Enable drive on west side of plant property |  |  | Jesse Murray | I am returning due to comments from 8/21/19 incident call. Please modify the corrective actions to address the immediate and basic cause selected. The corrective actions should alight with the root cause. Lets make sure the corrective actions prevent the root cause from happening again. Jesse Murray 8/21/19 Approved. 8/29/19 | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Plant requested contractor repair erosion damage from spring flooding at the Enable gas yard road tie in to plant road. Erosion had uncovered approximately 4 feet of a 6" fiberglass water line that comes from #7 and #8 deep wells to the plant. Repair process was to backfill exposed line with sand from the river settling basin and install a piece of HDPE left from another project and utilize it for a culvert and cover with crusher run rock. While spreading the sand with an excavator contractor had spread 2 dump truck loads and was using his bucket to pack when water started flowing from backfill. He contacted his plant contact immediately and contact notified control room to help isolate water. During repair, line was identified as containing ACM and insulators were contacted to cut and dispose of crushed line. When repair was uncovered the old piping was damaged from pressure of bucket when contractor was compacting sand around piping. The plant has had some previous leaks that were the result of ground pressure and its brittleness causes it to break. The contractor was onsite for another project that was wrapping up and the plant asked if they could assist in repair of erosion with some left over rock from that project to repair this damage. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | No comment, approved. | Brian Huckabay |  | Medium |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | [7 empty] | Failure to Identify line and risk exposure prior to contractors beginning work. | 17. Failure to Identify Hazard, Risk | 7. Caught Between or Under (Crushed or Amputated) |  | Reviewed. Reviewed again and after corrected immediate and basic causes with additional corrective actions added, I approve. |  |  |  | Property Damage |  | Kelly Casey | broken water line |  |  |  |  | 12. Equipment Failure | Kelly Casey | Duncan and Sons | Bobby Claig |  | Utility Strike |  | Kelly Casey |  |  |  |  | FALSE | [66 empty] | 615604
8959 | Horseshoe Lake Power Plant | 2019-07-25 14:00 | while backfilling eroded ditch at the Enable gas yard contractor broke make-up water line from #7 and 8 deep wells. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-08-29 08:06 | 2019-07-26 06:12 | 2019-07-26 06:12 | 2019-08-27 15:48 | 2019-08-08 14:00 | 2019-07-25 14:00 | 2019-08-28 09:58 |  | 2019-08-27 15:51 | Horseshoe Lake @ Enable drive on west side of plant property |  |  | Jesse Murray | I am returning due to comments from 8/21/19 incident call. Please modify the corrective actions to address the immediate and basic cause selected. The corrective actions should alight with the root cause. Lets make sure the corrective actions prevent the root cause from happening again. Jesse Murray 8/21/19 Approved. 8/29/19 | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Plant requested contractor repair erosion damage from spring flooding at the Enable gas yard road tie in to plant road. Erosion had uncovered approximately 4 feet of a 6" fiberglass water line that comes from #7 and #8 deep wells to the plant. Repair process was to backfill exposed line with sand from the river settling basin and install a piece of HDPE left from another project and utilize it for a culvert and cover with crusher run rock. While spreading the sand with an excavator contractor had spread 2 dump truck loads and was using his bucket to pack when water started flowing from backfill. He contacted his plant contact immediately and contact notified control room to help isolate water. During repair, line was identified as containing ACM and insulators were contacted to cut and dispose of crushed line. When repair was uncovered the old piping was damaged from pressure of bucket when contractor was compacting sand around piping. The plant has had some previous leaks that were the result of ground pressure and its brittleness causes it to break. The contractor was onsite for another project that was wrapping up and the plant asked if they could assist in repair of erosion with some left over rock from that project to repair this damage. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | No comment, approved. | Brian Huckabay |  | Medium |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.06 Inadequate work planning or programming | [7 empty] | Failure to Identify line and risk exposure prior to contractors beginning work. | 17. Failure to Identify Hazard, Risk | 7. Caught Between or Under (Crushed or Amputated) |  | Reviewed. Reviewed again and after corrected immediate and basic causes with additional corrective actions added, I approve. |  |  |  | Property Damage |  | Kelly Casey | broken water line |  |  |  |  | 12. Equipment Failure | Kelly Casey | Duncan and Sons | Bobby Claig |  | Utility Strike |  | Kelly Casey |  |  |  |  | FALSE | [66 empty] | 615604
8959 | Horseshoe Lake Power Plant | 2019-07-25 14:00 | while backfilling eroded ditch at the Enable gas yard contractor broke make-up water line from #7 and 8 deep wells. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-08-29 08:06 | 2019-07-26 06:12 | 2019-07-26 06:12 | 2019-08-27 15:48 | 2019-08-08 14:00 | 2019-07-25 14:00 | 2019-08-28 09:58 |  | 2019-08-27 15:51 | Horseshoe Lake @ Enable drive on west side of plant property |  |  | Jesse Murray | I am returning due to comments from 8/21/19 incident call. Please modify the corrective actions to address the immediate and basic cause selected. The corrective actions should alight with the root cause. Lets make sure the corrective actions prevent the root cause from happening again. Jesse Murray 8/21/19 Approved. 8/29/19 | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Plant requested contractor repair erosion damage from spring flooding at the Enable gas yard road tie in to plant road. Erosion had uncovered approximately 4 feet of a 6" fiberglass water line that comes from #7 and #8 deep wells to the plant. Repair process was to backfill exposed line with sand from the river settling basin and install a piece of HDPE left from another project and utilize it for a culvert and cover with crusher run rock. While spreading the sand with an excavator contractor had spread 2 dump truck loads and was using his bucket to pack when water started flowing from backfill. He contacted his plant contact immediately and contact notified control room to help isolate water. During repair, line was identified as containing ACM and insulators were contacted to cut and dispose of crushed line. When repair was uncovered the old piping was damaged from pressure of bucket when contractor was compacting sand around piping. The plant has had some previous leaks that were the result of ground pressure and its brittleness causes it to break. The contractor was onsite for another project that was wrapping up and the plant asked if they could assist in repair of erosion with some left over rock from that project to repair this damage. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | No comment, approved. | Brian Huckabay |  | Medium |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.11 Inadequate matching of individual qualifications and job/task requirements | [7 empty] | Failure to Identify line and risk exposure prior to contractors beginning work. | 17. Failure to Identify Hazard, Risk | 7. Caught Between or Under (Crushed or Amputated) |  | Reviewed. Reviewed again and after corrected immediate and basic causes with additional corrective actions added, I approve. |  |  |  | Property Damage |  | Kelly Casey | broken water line |  |  |  |  | 12. Equipment Failure | Kelly Casey | Duncan and Sons | Bobby Claig |  | Utility Strike |  | Kelly Casey |  |  |  |  | FALSE | [66 empty] | 615604
8959 | Horseshoe Lake Power Plant | 2019-07-25 14:00 | while backfilling eroded ditch at the Enable gas yard contractor broke make-up water line from #7 and 8 deep wells. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-08-29 08:06 | 2019-07-26 06:12 | 2019-07-26 06:12 | 2019-08-27 15:48 | 2019-08-08 14:00 | 2019-07-25 14:00 | 2019-08-28 09:58 |  | 2019-08-27 15:51 | Horseshoe Lake @ Enable drive on west side of plant property |  |  | Jesse Murray | I am returning due to comments from 8/21/19 incident call. Please modify the corrective actions to address the immediate and basic cause selected. The corrective actions should alight with the root cause. Lets make sure the corrective actions prevent the root cause from happening again. Jesse Murray 8/21/19 Approved. 8/29/19 | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Plant requested contractor repair erosion damage from spring flooding at the Enable gas yard road tie in to plant road. Erosion had uncovered approximately 4 feet of a 6" fiberglass water line that comes from #7 and #8 deep wells to the plant. Repair process was to backfill exposed line with sand from the river settling basin and install a piece of HDPE left from another project and utilize it for a culvert and cover with crusher run rock. While spreading the sand with an excavator contractor had spread 2 dump truck loads and was using his bucket to pack when water started flowing from backfill. He contacted his plant contact immediately and contact notified control room to help isolate water. During repair, line was identified as containing ACM and insulators were contacted to cut and dispose of crushed line. When repair was uncovered the old piping was damaged from pressure of bucket when contractor was compacting sand around piping. The plant has had some previous leaks that were the result of ground pressure and its brittleness causes it to break. The contractor was onsite for another project that was wrapping up and the plant asked if they could assist in repair of erosion with some left over rock from that project to repair this damage. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | No comment, approved. | Brian Huckabay |  | Medium |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | [7 empty] | Failure to Identify line and risk exposure prior to contractors beginning work. | 17. Failure to Identify Hazard, Risk | 7. Caught Between or Under (Crushed or Amputated) |  | Reviewed. Reviewed again and after corrected immediate and basic causes with additional corrective actions added, I approve. |  |  |  | Property Damage |  | Kelly Casey | broken water line |  |  |  |  | 12. Equipment Failure | Kelly Casey | Duncan and Sons | Bobby Claig |  | Utility Strike |  | Kelly Casey |  |  |  |  | FALSE | [66 empty] | 615604