8959 | Horseshoe Lake Power Plant | 2019-07-25 14:00 | while backfilling eroded ditch at the Enable gas yard contractor broke make-up water line from #7 and 8 deep wells. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-08-29 08:06 | 2019-07-26 06:12 | 2019-07-26 06:12 | 2019-08-27 15:48 | 2019-08-08 14:00 | 2019-07-25 14:00 | 2019-08-28 09:58 |  | 2019-08-27 15:51 | Horseshoe Lake @ Enable drive on west side of plant property |  |  | Jesse Murray | I am returning due to comments from 8/21/19 incident call. Please modify the corrective actions to address the immediate and basic cause selected. The corrective actions should alight with the root cause. Lets make sure the corrective actions prevent the root cause from happening again. Jesse Murray 8/21/19 Approved. 8/29/19 | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Plant requested contractor repair erosion damage from spring flooding at the Enable gas yard road tie in to plant road. Erosion had uncovered approximately 4 feet of a 6" fiberglass water line that comes from #7 and #8 deep wells to the plant. Repair process was to backfill exposed line with sand from the river settling basin and install a piece of HDPE left from another project and utilize it for a culvert and cover with crusher run rock. While spreading the sand with an excavator contractor had spread 2 dump truck loads and was using his bucket to pack when water started flowing from backfill. He contacted his plant contact immediately and contact notified control room to help isolate water. During repair, line was identified as containing ACM and insulators were contacted to cut and dispose of crushed line. When repair was uncovered the old piping was damaged from pressure of bucket when contractor was compacting sand around piping. The plant has had some previous leaks that were the result of ground pressure and its brittleness causes it to break. The contractor was onsite for another project that was wrapping up and the plant asked if they could assist in repair of erosion with some left over rock from that project to repair this damage. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | No comment, approved. | Brian Huckabay |  | Medium |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming | [7 empty] | Failure to Identify line and risk exposure prior to contractors beginning work. | 17. Failure to Identify Hazard, Risk | 7. Caught Between or Under (Crushed or Amputated) |  | Reviewed. Reviewed again and after corrected immediate and basic causes with additional corrective actions added, I approve. |  |  |  | Property Damage |  | Kelly Casey | broken water line |  |  |  |  | 12. Equipment Failure | Kelly Casey | Duncan and Sons | Bobby Claig |  | Utility Strike |  | Kelly Casey |  |  |  |  | FALSE | [66 empty] | 615604
8959 | Horseshoe Lake Power Plant | 2019-07-25 14:00 | while backfilling eroded ditch at the Enable gas yard contractor broke make-up water line from #7 and 8 deep wells. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-08-29 08:06 | 2019-07-26 06:12 | 2019-07-26 06:12 | 2019-08-27 15:48 | 2019-08-08 14:00 | 2019-07-25 14:00 | 2019-08-28 09:58 |  | 2019-08-27 15:51 | Horseshoe Lake @ Enable drive on west side of plant property |  |  | Jesse Murray | I am returning due to comments from 8/21/19 incident call. Please modify the corrective actions to address the immediate and basic cause selected. The corrective actions should alight with the root cause. Lets make sure the corrective actions prevent the root cause from happening again. Jesse Murray 8/21/19 Approved. 8/29/19 | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Plant requested contractor repair erosion damage from spring flooding at the Enable gas yard road tie in to plant road. Erosion had uncovered approximately 4 feet of a 6" fiberglass water line that comes from #7 and #8 deep wells to the plant. Repair process was to backfill exposed line with sand from the river settling basin and install a piece of HDPE left from another project and utilize it for a culvert and cover with crusher run rock. While spreading the sand with an excavator contractor had spread 2 dump truck loads and was using his bucket to pack when water started flowing from backfill. He contacted his plant contact immediately and contact notified control room to help isolate water. During repair, line was identified as containing ACM and insulators were contacted to cut and dispose of crushed line. When repair was uncovered the old piping was damaged from pressure of bucket when contractor was compacting sand around piping. The plant has had some previous leaks that were the result of ground pressure and its brittleness causes it to break. The contractor was onsite for another project that was wrapping up and the plant asked if they could assist in repair of erosion with some left over rock from that project to repair this damage. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | No comment, approved. | Brian Huckabay |  | Medium |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | [6 empty] | 16.04 Inadequate communication between work groups | Failure to coordinate / instruct contractor for risk mitigation. | 20. Failure to Communicate, Coordinate | 7. Caught Between or Under (Crushed or Amputated) |  | Reviewed. Reviewed again and after corrected immediate and basic causes with additional corrective actions added, I approve. |  |  |  | Property Damage |  | Kelly Casey | broken water line |  |  |  |  | 12. Equipment Failure | Kelly Casey | Duncan and Sons | Bobby Claig |  | Utility Strike |  | Kelly Casey |  |  |  |  | FALSE | [66 empty] | 615604
8959 | Horseshoe Lake Power Plant | 2019-07-25 14:00 | while backfilling eroded ditch at the Enable gas yard contractor broke make-up water line from #7 and 8 deep wells. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-08-29 08:06 | 2019-07-26 06:12 | 2019-07-26 06:12 | 2019-08-27 15:48 | 2019-08-08 14:00 | 2019-07-25 14:00 | 2019-08-28 09:58 |  | 2019-08-27 15:51 | Horseshoe Lake @ Enable drive on west side of plant property |  |  | Jesse Murray | I am returning due to comments from 8/21/19 incident call. Please modify the corrective actions to address the immediate and basic cause selected. The corrective actions should alight with the root cause. Lets make sure the corrective actions prevent the root cause from happening again. Jesse Murray 8/21/19 Approved. 8/29/19 | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Plant requested contractor repair erosion damage from spring flooding at the Enable gas yard road tie in to plant road. Erosion had uncovered approximately 4 feet of a 6" fiberglass water line that comes from #7 and #8 deep wells to the plant. Repair process was to backfill exposed line with sand from the river settling basin and install a piece of HDPE left from another project and utilize it for a culvert and cover with crusher run rock. While spreading the sand with an excavator contractor had spread 2 dump truck loads and was using his bucket to pack when water started flowing from backfill. He contacted his plant contact immediately and contact notified control room to help isolate water. During repair, line was identified as containing ACM and insulators were contacted to cut and dispose of crushed line. When repair was uncovered the old piping was damaged from pressure of bucket when contractor was compacting sand around piping. The plant has had some previous leaks that were the result of ground pressure and its brittleness causes it to break. The contractor was onsite for another project that was wrapping up and the plant asked if they could assist in repair of erosion with some left over rock from that project to repair this damage. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | No comment, approved. | Brian Huckabay |  | Medium |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | [6 empty] | 16.03. Inadequate communication between different organizations | Failure to coordinate / instruct contractor for risk mitigation. | 20. Failure to Communicate, Coordinate | 7. Caught Between or Under (Crushed or Amputated) |  | Reviewed. Reviewed again and after corrected immediate and basic causes with additional corrective actions added, I approve. |  |  |  | Property Damage |  | Kelly Casey | broken water line |  |  |  |  | 12. Equipment Failure | Kelly Casey | Duncan and Sons | Bobby Claig |  | Utility Strike |  | Kelly Casey |  |  |  |  | FALSE | [66 empty] | 615604
8959 | Horseshoe Lake Power Plant | 2019-07-25 14:00 | while backfilling eroded ditch at the Enable gas yard contractor broke make-up water line from #7 and 8 deep wells. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-08-29 08:06 | 2019-07-26 06:12 | 2019-07-26 06:12 | 2019-08-27 15:48 | 2019-08-08 14:00 | 2019-07-25 14:00 | 2019-08-28 09:58 |  | 2019-08-27 15:51 | Horseshoe Lake @ Enable drive on west side of plant property |  |  | Jesse Murray | I am returning due to comments from 8/21/19 incident call. Please modify the corrective actions to address the immediate and basic cause selected. The corrective actions should alight with the root cause. Lets make sure the corrective actions prevent the root cause from happening again. Jesse Murray 8/21/19 Approved. 8/29/19 | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Plant requested contractor repair erosion damage from spring flooding at the Enable gas yard road tie in to plant road. Erosion had uncovered approximately 4 feet of a 6" fiberglass water line that comes from #7 and #8 deep wells to the plant. Repair process was to backfill exposed line with sand from the river settling basin and install a piece of HDPE left from another project and utilize it for a culvert and cover with crusher run rock. While spreading the sand with an excavator contractor had spread 2 dump truck loads and was using his bucket to pack when water started flowing from backfill. He contacted his plant contact immediately and contact notified control room to help isolate water. During repair, line was identified as containing ACM and insulators were contacted to cut and dispose of crushed line. When repair was uncovered the old piping was damaged from pressure of bucket when contractor was compacting sand around piping. The plant has had some previous leaks that were the result of ground pressure and its brittleness causes it to break. The contractor was onsite for another project that was wrapping up and the plant asked if they could assist in repair of erosion with some left over rock from that project to repair this damage. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | No comment, approved. | Brian Huckabay |  | Medium |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.10 Lack of supervisory/management job knowledge | [6 empty] | 16.04 Inadequate communication between work groups | Failure to coordinate / instruct contractor for risk mitigation. | 20. Failure to Communicate, Coordinate | 7. Caught Between or Under (Crushed or Amputated) |  | Reviewed. Reviewed again and after corrected immediate and basic causes with additional corrective actions added, I approve. |  |  |  | Property Damage |  | Kelly Casey | broken water line |  |  |  |  | 12. Equipment Failure | Kelly Casey | Duncan and Sons | Bobby Claig |  | Utility Strike |  | Kelly Casey |  |  |  |  | FALSE | [66 empty] | 615604
8959 | Horseshoe Lake Power Plant | 2019-07-25 14:00 | while backfilling eroded ditch at the Enable gas yard contractor broke make-up water line from #7 and 8 deep wells. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-08-29 08:06 | 2019-07-26 06:12 | 2019-07-26 06:12 | 2019-08-27 15:48 | 2019-08-08 14:00 | 2019-07-25 14:00 | 2019-08-28 09:58 |  | 2019-08-27 15:51 | Horseshoe Lake @ Enable drive on west side of plant property |  |  | Jesse Murray | I am returning due to comments from 8/21/19 incident call. Please modify the corrective actions to address the immediate and basic cause selected. The corrective actions should alight with the root cause. Lets make sure the corrective actions prevent the root cause from happening again. Jesse Murray 8/21/19 Approved. 8/29/19 | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Plant requested contractor repair erosion damage from spring flooding at the Enable gas yard road tie in to plant road. Erosion had uncovered approximately 4 feet of a 6" fiberglass water line that comes from #7 and #8 deep wells to the plant. Repair process was to backfill exposed line with sand from the river settling basin and install a piece of HDPE left from another project and utilize it for a culvert and cover with crusher run rock. While spreading the sand with an excavator contractor had spread 2 dump truck loads and was using his bucket to pack when water started flowing from backfill. He contacted his plant contact immediately and contact notified control room to help isolate water. During repair, line was identified as containing ACM and insulators were contacted to cut and dispose of crushed line. When repair was uncovered the old piping was damaged from pressure of bucket when contractor was compacting sand around piping. The plant has had some previous leaks that were the result of ground pressure and its brittleness causes it to break. The contractor was onsite for another project that was wrapping up and the plant asked if they could assist in repair of erosion with some left over rock from that project to repair this damage. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | No comment, approved. | Brian Huckabay |  | Medium |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.10 Lack of supervisory/management job knowledge | [6 empty] | 16.03. Inadequate communication between different organizations | Failure to coordinate / instruct contractor for risk mitigation. | 20. Failure to Communicate, Coordinate | 7. Caught Between or Under (Crushed or Amputated) |  | Reviewed. Reviewed again and after corrected immediate and basic causes with additional corrective actions added, I approve. |  |  |  | Property Damage |  | Kelly Casey | broken water line |  |  |  |  | 12. Equipment Failure | Kelly Casey | Duncan and Sons | Bobby Claig |  | Utility Strike |  | Kelly Casey |  |  |  |  | FALSE | [66 empty] | 615604
8960 | River Valley | 2019-07-25 15:00 | Contractor wash washing ash and debris out of the ash hopper below Mod 12 on 2B boiler. The contractor got ash inside his glove, which resulted in a chemical burn on his right hand and forearm from the lime stone that is present in the ash. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Melton Morris | 2019-09-22 08:18 | 2019-07-26 15:17 | 2019-07-26 15:17 | 2019-08-30 09:11 | 2019-08-08 15:00 | 2019-07-26 10:00 | 2019-09-18 06:55 |  |  | 2B Boiler Bag House module 12 |  |  | Anthony Gillespie | Corrective actions listed should eliminate future incidents of a similar nature. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Melton Morris |  | Contractor wash washing ash and debris out of the ash hopper below Mod 12 on 2B boiler. The contractor got ash inside his glove, which resulted in a chemical burn on his right hand and forearm from the lime stone that is present in the ash. |  |  |  | River Valley | FALSE |  | FALSE | Maintenance |  | Tony Smith | Michael Smith |  | Timothy Chancellor | Hazards associated with ash also covered in site job orientation checksheet. | Timothy Chancellor |  | Low |  |  |  |  | 5.01 Lack of experience | [11 empty] | Contractor wash washing ash and debris out of the ash hopper below Mod 12 on 2B boiler. The contractor got ash inside his glove, which resulted in a chemical burn on his right hand and forearm from the lime stone that is present in the ash. | 07. Failing to Use PPE Properly | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Melton Morris | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Tony Smith | W-S Companies | Jacob Norton |  |  |  | Tony Smith
8962 | South District Service Center | 2019-07-29 10:30 | While opening door to get gloves, wind caught door springing it open and causing the door to warp. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Delivery | Gary Parks | 2019-08-14 15:12 | 2019-07-29 12:56 | 2019-07-29 12:56 | 2019-08-08 14:57 | 2019-08-12 10:30 | 2019-07-29 12:50 | 2019-08-12 14:18 |  |  | 2209 S. Santa Fe Ave. Oklahoma City, Oklahoma |  |  | Luke Kennedy | Approved 08/14/2019 | T&D Ops |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Gary Parks |  | On July 29, 2019 South Crew was setting up a job site at 2209 S Santa Fe ave OKC, Oklahoma. Justin Taylor returned to the truck after it had been set up to retrieve his work gloves. As he opened the door the wind caught it and sprung the hinges to the point where the door would not shut properly. At this point he contacted his supervisor and secured the door so that he could safely make his way back to the service center. |  |  |  | South District Service Center | FALSE |  | FALSE | Construction Services |  | Justin Taylor | Gary Parks |  | Terry Garrett | I agree with corrective action | Terry Garrett |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | wind catching door | 40. Weather Conditions | 2. Struck By (Hit By Moving Object) | [68 empty] | dent in door and sprung hinges. | 500 |  | Vehicle (not related to operation of vehicle) |  | F10-282
8963 | Sooner Power Plant | 2019-07-29 | Member parked company truck on road shoulder outside machine shop, between planning offices and water house. Member left vehicle to coordinate with subcontractors for several hours. Upon returning to the truck, member noticed a dent in the driver's rear fender. | Level 2 |  | FALSE | Vehicle |  |  |  |  | Power Supply | Tyler Fischer | 2019-08-28 08:01 | 2019-07-29 14:20 | 2019-07-29 14:20 | 2019-08-12 10:43 | 2019-08-12 | 2019-07-29 13:59 | 2019-08-26 08:13 |  | 2019-08-13 16:02 | Sooner PP Outside Machine Shop |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Tyler Fischer |  | Member reported a dent in the driver's side bed of his assigned truck, behind the rear tire. Member did not remember seeing it that morning during his inspections of the truck prior to parking it in front of the Sooner Plant water treatment building, between the building and the planning office building. Member parked the truck, and met with contractors to execute the morning's work. Upon returning a few hours later, member noticed the dent, and reported the incident. Further investigation of plant video feeds yielded no results on the occurrence of the incident, and was unavailable to establish if the truck came into the plant with the dent. No further witnesses came forward to present knowledge of the event. Due to lack of evidence and witnesses, the result of the investigation is inconclusive. Member and assistant had an opportunity to pop the dent out, and most of the damage is gone. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Engineering & Planning |  | Tead Haga | Tyler Fischer |  | Donald Wyckoff | I have reviewed the incident and approve. Donald Wyckoff 8/26/19. | Donald Wyckoff |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Event cause identified as a lack of situational awareness, by either the member assigned to the truck, for not noticing the dent, or the person that caused the dent. | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) |  | Approved by Brady Sowell on 8/13 | [72 empty] | FALSE |  | Red Rock | Other | Unknown | 2009-08-16 19:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | John Legg | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.01 Lack of experience | 6.01 Inadequate initial instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.2 Inadequate development of standards: coordination with process design |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | John Legg | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.01 Lack of experience | 6.01 Inadequate initial instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.3 Inadequate development of standards: employee involvement |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | John Legg | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.01 Lack of experience | 6.01 Inadequate initial instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | John Legg | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.01 Lack of experience | 6.01 Inadequate initial instruction |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.01.2 Inadequate development of standards: coordination with process design |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | John Legg | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.01 Lack of experience | 6.01 Inadequate initial instruction |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.01.3 Inadequate development of standards: employee involvement |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | John Legg | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.01 Lack of experience | 6.01 Inadequate initial instruction |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | John Legg | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.01 Lack of experience | 6.01 Inadequate initial instruction |  |  | 9.10 Lack of supervisory/management job knowledge |  |  |  |  | 14.01.2 Inadequate development of standards: coordination with process design |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | John Legg | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.01 Lack of experience | 6.01 Inadequate initial instruction |  |  | 9.10 Lack of supervisory/management job knowledge |  |  |  |  | 14.01.3 Inadequate development of standards: employee involvement |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | John Legg | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.01 Lack of experience | 6.01 Inadequate initial instruction |  |  | 9.10 Lack of supervisory/management job knowledge |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | John Legg | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.03 Inadequate initial training | 6.01 Inadequate initial instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.2 Inadequate development of standards: coordination with process design |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | John Legg | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.03 Inadequate initial training | 6.01 Inadequate initial instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.3 Inadequate development of standards: employee involvement |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | John Legg | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.03 Inadequate initial training | 6.01 Inadequate initial instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | John Legg | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.03 Inadequate initial training | 6.01 Inadequate initial instruction |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.01.2 Inadequate development of standards: coordination with process design |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | John Legg | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.03 Inadequate initial training | 6.01 Inadequate initial instruction |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.01.3 Inadequate development of standards: employee involvement |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | John Legg | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.03 Inadequate initial training | 6.01 Inadequate initial instruction |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | John Legg | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.03 Inadequate initial training | 6.01 Inadequate initial instruction |  |  | 9.10 Lack of supervisory/management job knowledge |  |  |  |  | 14.01.2 Inadequate development of standards: coordination with process design |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | John Legg | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.03 Inadequate initial training | 6.01 Inadequate initial instruction |  |  | 9.10 Lack of supervisory/management job knowledge |  |  |  |  | 14.01.3 Inadequate development of standards: employee involvement |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | John Legg | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.03 Inadequate initial training | 6.01 Inadequate initial instruction |  |  | 9.10 Lack of supervisory/management job knowledge |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | John Legg | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.06 Lack of situational awareness | 6.01 Inadequate initial instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.2 Inadequate development of standards: coordination with process design |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | John Legg | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.06 Lack of situational awareness | 6.01 Inadequate initial instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.3 Inadequate development of standards: employee involvement |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | John Legg | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.06 Lack of situational awareness | 6.01 Inadequate initial instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | John Legg | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.06 Lack of situational awareness | 6.01 Inadequate initial instruction |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.01.2 Inadequate development of standards: coordination with process design |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | John Legg | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.06 Lack of situational awareness | 6.01 Inadequate initial instruction |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.01.3 Inadequate development of standards: employee involvement |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | John Legg | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.06 Lack of situational awareness | 6.01 Inadequate initial instruction |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | John Legg | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.06 Lack of situational awareness | 6.01 Inadequate initial instruction |  |  | 9.10 Lack of supervisory/management job knowledge |  |  |  |  | 14.01.2 Inadequate development of standards: coordination with process design |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | John Legg | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.06 Lack of situational awareness | 6.01 Inadequate initial instruction |  |  | 9.10 Lack of supervisory/management job knowledge |  |  |  |  | 14.01.3 Inadequate development of standards: employee involvement |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | John Legg | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.06 Lack of situational awareness | 6.01 Inadequate initial instruction |  |  | 9.10 Lack of supervisory/management job knowledge |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | Marcus Huddleston | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.01 Lack of experience | 6.01 Inadequate initial instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.2 Inadequate development of standards: coordination with process design |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | Marcus Huddleston | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.01 Lack of experience | 6.01 Inadequate initial instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.3 Inadequate development of standards: employee involvement |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | Marcus Huddleston | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.01 Lack of experience | 6.01 Inadequate initial instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | Marcus Huddleston | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.01 Lack of experience | 6.01 Inadequate initial instruction |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.01.2 Inadequate development of standards: coordination with process design |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | Marcus Huddleston | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.01 Lack of experience | 6.01 Inadequate initial instruction |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.01.3 Inadequate development of standards: employee involvement |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | Marcus Huddleston | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.01 Lack of experience | 6.01 Inadequate initial instruction |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | Marcus Huddleston | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.01 Lack of experience | 6.01 Inadequate initial instruction |  |  | 9.10 Lack of supervisory/management job knowledge |  |  |  |  | 14.01.2 Inadequate development of standards: coordination with process design |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | Marcus Huddleston | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.01 Lack of experience | 6.01 Inadequate initial instruction |  |  | 9.10 Lack of supervisory/management job knowledge |  |  |  |  | 14.01.3 Inadequate development of standards: employee involvement |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | Marcus Huddleston | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.01 Lack of experience | 6.01 Inadequate initial instruction |  |  | 9.10 Lack of supervisory/management job knowledge |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | Marcus Huddleston | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.03 Inadequate initial training | 6.01 Inadequate initial instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.2 Inadequate development of standards: coordination with process design |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | Marcus Huddleston | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.03 Inadequate initial training | 6.01 Inadequate initial instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.3 Inadequate development of standards: employee involvement |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | Marcus Huddleston | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.03 Inadequate initial training | 6.01 Inadequate initial instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | Marcus Huddleston | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.03 Inadequate initial training | 6.01 Inadequate initial instruction |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.01.2 Inadequate development of standards: coordination with process design |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | Marcus Huddleston | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.03 Inadequate initial training | 6.01 Inadequate initial instruction |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.01.3 Inadequate development of standards: employee involvement |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | Marcus Huddleston | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.03 Inadequate initial training | 6.01 Inadequate initial instruction |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | Marcus Huddleston | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.03 Inadequate initial training | 6.01 Inadequate initial instruction |  |  | 9.10 Lack of supervisory/management job knowledge |  |  |  |  | 14.01.2 Inadequate development of standards: coordination with process design |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | Marcus Huddleston | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.03 Inadequate initial training | 6.01 Inadequate initial instruction |  |  | 9.10 Lack of supervisory/management job knowledge |  |  |  |  | 14.01.3 Inadequate development of standards: employee involvement |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | Marcus Huddleston | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.03 Inadequate initial training | 6.01 Inadequate initial instruction |  |  | 9.10 Lack of supervisory/management job knowledge |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | Marcus Huddleston | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.06 Lack of situational awareness | 6.01 Inadequate initial instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.2 Inadequate development of standards: coordination with process design |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | Marcus Huddleston | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.06 Lack of situational awareness | 6.01 Inadequate initial instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.3 Inadequate development of standards: employee involvement |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | Marcus Huddleston | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.06 Lack of situational awareness | 6.01 Inadequate initial instruction |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | Marcus Huddleston | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.06 Lack of situational awareness | 6.01 Inadequate initial instruction |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.01.2 Inadequate development of standards: coordination with process design |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | Marcus Huddleston | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.06 Lack of situational awareness | 6.01 Inadequate initial instruction |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.01.3 Inadequate development of standards: employee involvement |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | Marcus Huddleston | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.06 Lack of situational awareness | 6.01 Inadequate initial instruction |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | Marcus Huddleston | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.06 Lack of situational awareness | 6.01 Inadequate initial instruction |  |  | 9.10 Lack of supervisory/management job knowledge |  |  |  |  | 14.01.2 Inadequate development of standards: coordination with process design |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | Marcus Huddleston | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.06 Lack of situational awareness | 6.01 Inadequate initial instruction |  |  | 9.10 Lack of supervisory/management job knowledge |  |  |  |  | 14.01.3 Inadequate development of standards: employee involvement |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8964 | Metro Service Center | 2019-07-29 12:30 | The employee climbed a pole to fix the light, leaned into the arm of a 9500 HPS light and it shocked him. We are still unsure of what followed but the employee did fall 4-5 feet before his safety caught him. I am not sure if this knocked him unconscious or not. The employee does not have any burn marks on him at all. He is at the hospital and is awake and alert. expected to be released. The foreman returned to the job to check the light arm and found that it did have voltage on it. | Level 4 |  | FALSE | Contractor |  | Jerrod Moser | This investigation is being directed by Jennifer Castillo internal counsel. | 2019-07-30 10:57 | Power Delivery | John Legg | 2019-09-16 07:29 | 2019-07-29 15:51 | 2019-07-29 15:51 | 2019-09-05 14:38 | 2019-08-30 | 2019-07-29 15:45 | 2019-09-13 08:19 |  |  | Crew was working on WO 7958738 WL 32. This is a Grid Mod job and they was doing go backs |  |  | Jerrod Moser | Approved | T&D Ops |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On July 29 at approximately 12:30 p.m. a Fusion lineman working a go-back ticket experienced an electrical contact related to an incorrectly wired security light photo control. Per crew interviews, the lineman encountered a minor electrical shock as he ascended the pole. He asked for and was provided a pair of gloves and continued to work. Sometime later (interview time estimates varied from 15 to 45 minutes) he received a second contact resulting in a loss of conscious. Weather conditions at the time leading up to the incident involved light rain and drizzle. It is believed that the second electrical shock resulted form contact with the light arm that was energized or from contact with a Fargo on the back side of the pole. Their were difficulties with execution of the rescue. When the injured was lowered to the ground he was not breathing and CPR was initiated and maintained until EMS arrived. EMS took over CPR and transported the injured to the hospital. The incident findings revealed issues with job planning, communication, tailboards, crew qualifications, training, procedures and PPE. | Marcus Huddleston | William Young |  | Metro Service Center | TRUE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  |  | Reviewed | Nicole Rhodes |  | Very High |  |  |  |  | 5.06 Lack of situational awareness | 6.01 Inadequate initial instruction |  |  | 9.10 Lack of supervisory/management job knowledge |  |  |  |  | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | Contractor came in contact with energized conductor. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | John Legg |  | contact | FALSE |  |  | 12. Equipment Failure | John Legg | Fusion Industries | unkown | Burn: Electrical |  | Arm | John Legg | Right | TRUE | Company Vehicle | [68 empty] | 7958738
8965 | McClain Power Plant | 2019-07-28 12:00 | The 5" flexible metal hose connecting the PM3 fuel gas valve to PM3 fuel distribution manifold failed. A high hazardous gas level alarm came in indicating LEL was greater than 10%. Gas turbine controls closed the PM3 fuel gas valve and tripped the unit. No fire, no explosion and no member injury occurred. | Level 2 |  | FALSE | System Operational Incident |  |  |  |  | Power Supply | Jimmy Green | 2019-08-07 14:13 | 2019-07-30 10:53 |  | 2019-07-30 15:57 | 2019-09-08 12:00 | 2019-07-30 10:29 | 2019-08-01 07:49 |  | 2019-07-31 10:39 | McClain Power Plant, GT2 turbine enclosure |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Jimmy Green |  | Gas Turbine controls removed GT2 from service on 7/28/19 about 12:08 PM. During the GT2 event, a fuel gas supply pressure regulation problem occurred which removed GT1 and the steam turbine from service. Operators contacted maintenance to troubleshoot the GT2 failure. Maintenance suspected a fuel leak on the PM3 fuel gas system. Once the fuel gas system was restored GT1 and the Steam turbine were returned to service on 7/28/19 about 14:50. Visual inspection from GT2 turbine compartment doors could not identify obvious leaks on the PM3 fuel distribution system. Approximately 16:00 the unit started the spin cool process. About 22:00 the unit was cool enough to enter. The unit was LOTOd and a confined space entry permit was issued to allow visual inspection and ultrasonic inspection. About 23:30 the failed hose was discovered by visual observation. The part# from the failed hose was obtained. There were no hoses in SAP inventory. The GE CPM (contract performance manager) was contacted on 7/29/19 about 00:30 and asked to check his onsite inventory and GE supply system. There were no hoses in the GE supply system and none in the GE on site inventory. At this point it was decided to wait till the morning and start contacting other GE resources for spare hoses. 7/29/19 11:00 a plant in LA was located that had a spare hose. A hotshot was called and arranged for pickup and delivery to McClain. Expected delivery 7/30/19 07:00 7/30/19 06:30 - Hose arrived on site. Maintenance installed and then cranked the unit to check for leaks. No leaks. 7/30/10 10:30 - GT2 was started and returned to service. Failed hose appeared to have cracked at the end that was welded to the elbow. The hose did appear to have some dents in the outer armor but it is difficult to tell whether these were pre-existing or occurred during the hose failure. |  |  |  | McClain Power Plant | FALSE |  | FALSE | Operations |  | Jimmy Green | Tony Shook |  | Tony Shook | We may or may not perform an RCA on this failure. Nolan is working with PSS to determine the actual need for an RCA in this matter. | Tony Shook |  | Medium |  |  |  |  | 5.01 Lack of experience |  |  |  |  | 10.03 Inadequate standards, specifications and/or design criteria |  | 12.01.1 Inadequate preventative assessment of needs |  |  | 15.03 Inadequate inspection and/or monitoring |  | Flexible Metal Hose failed. Looks like the interior pressure part of the hose developed a crack that progressed to total circumferential failure. | 18. Failure to Check, Monitor | 12. Equipment Failure |  | Reviewed on 7/31/19 and approve. | [90 empty] | 9588618
8965 | McClain Power Plant | 2019-07-28 12:00 | The 5" flexible metal hose connecting the PM3 fuel gas valve to PM3 fuel distribution manifold failed. A high hazardous gas level alarm came in indicating LEL was greater than 10%. Gas turbine controls closed the PM3 fuel gas valve and tripped the unit. No fire, no explosion and no member injury occurred. | Level 2 |  | FALSE | System Operational Incident |  |  |  |  | Power Supply | Jimmy Green | 2019-08-07 14:13 | 2019-07-30 10:53 |  | 2019-07-30 15:57 | 2019-09-08 12:00 | 2019-07-30 10:29 | 2019-08-01 07:49 |  | 2019-07-31 10:39 | McClain Power Plant, GT2 turbine enclosure |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Jimmy Green |  | Gas Turbine controls removed GT2 from service on 7/28/19 about 12:08 PM. During the GT2 event, a fuel gas supply pressure regulation problem occurred which removed GT1 and the steam turbine from service. Operators contacted maintenance to troubleshoot the GT2 failure. Maintenance suspected a fuel leak on the PM3 fuel gas system. Once the fuel gas system was restored GT1 and the Steam turbine were returned to service on 7/28/19 about 14:50. Visual inspection from GT2 turbine compartment doors could not identify obvious leaks on the PM3 fuel distribution system. Approximately 16:00 the unit started the spin cool process. About 22:00 the unit was cool enough to enter. The unit was LOTOd and a confined space entry permit was issued to allow visual inspection and ultrasonic inspection. About 23:30 the failed hose was discovered by visual observation. The part# from the failed hose was obtained. There were no hoses in SAP inventory. The GE CPM (contract performance manager) was contacted on 7/29/19 about 00:30 and asked to check his onsite inventory and GE supply system. There were no hoses in the GE supply system and none in the GE on site inventory. At this point it was decided to wait till the morning and start contacting other GE resources for spare hoses. 7/29/19 11:00 a plant in LA was located that had a spare hose. A hotshot was called and arranged for pickup and delivery to McClain. Expected delivery 7/30/19 07:00 7/30/19 06:30 - Hose arrived on site. Maintenance installed and then cranked the unit to check for leaks. No leaks. 7/30/10 10:30 - GT2 was started and returned to service. Failed hose appeared to have cracked at the end that was welded to the elbow. The hose did appear to have some dents in the outer armor but it is difficult to tell whether these were pre-existing or occurred during the hose failure. |  |  |  | McClain Power Plant | FALSE |  | FALSE | Operations |  | Jimmy Green | Tony Shook |  | Tony Shook | We may or may not perform an RCA on this failure. Nolan is working with PSS to determine the actual need for an RCA in this matter. | Tony Shook |  | Medium |  |  |  |  | 5.01 Lack of experience |  |  |  |  | 10.03 Inadequate standards, specifications and/or design criteria |  | 12.01.1 Inadequate preventative assessment of needs |  |  | 15.02 Improper extension of service life |  | Flexible Metal Hose failed. Looks like the interior pressure part of the hose developed a crack that progressed to total circumferential failure. | 18. Failure to Check, Monitor | 12. Equipment Failure |  | Reviewed on 7/31/19 and approve. | [90 empty] | 9588618
8966 | Centennial Wind Farm | 2019-07-30 09:00 | Skyclimber Renewables technician was backing up service truck and struck the building, damaging the metal siding. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Scott Zigler | 2019-08-19 07:33 | 2019-07-30 11:57 | 2019-07-30 11:57 | 2019-08-13 13:41 | 2019-08-13 09:00 | 2019-07-30 11:20 | 2019-08-13 14:15 |  |  | Centennial Wind Farm North side of O&M building. |  |  | Marcus Huddleston | No additional comments. MLH 8/19/19 | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Scott Zigler |  | Sub contractor was in contractors vehicle, backing into parking spot on north side of O&M building. The contractor struck the corrugated metal siding with the rear bumper of the truck. No spotter was being utilized. The subcontractor claimed to have been using backup camera and mirror but claimed the backup camera froze up. The camera was tested after the incident and found to be in working condition. Backup alarm sensor on the vehicle were not working. Contractor stated the alarms hadn't worked in some time. Subcontractor was unaware the vehicle had sensors. This incident is still in review and awaiting contractors report. Further information will be added when available. |  |  |  | Centennial Wind Farm | FALSE |  | FALSE | Renewable Energy |  | Scott Zigler | Scott Zigler |  | Jason Thomas | The truck involved in the incident is at another site. Truck is due to be in service next week 8/22/2019. S. Zigler is to verify operation of back up sensors (if equipped) and functionality of back up camera. | Jason Thomas |  | Low |  | 2.07 Slow reaction time |  |  | 5.06 Lack of situational awareness | [7 empty] | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | Driver of vehicle relied on his backup camera instead of utilizing his mirrors at all times. | 15. Using Equipment Improperly | 1. Struck Against (Running or Bumping Into) | [5 empty] | Vehicle |  | Scott Zigler | Damage to metal siding on North side of O&M building |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Scott Zigler | Sky Climber Renewables | Charles Peschka |  | Structural |  | Scott Zigler |  |  |  |  | FALSE | [42 empty] | Tin siding on O&M building is caved in approximately 8' wide by 6" deep | 2000 | Charles Peschka | Structural |  | V74-719 Vestas Fleet Vehicle
8966 | Centennial Wind Farm | 2019-07-30 09:00 | Skyclimber Renewables technician was backing up service truck and struck the building, damaging the metal siding. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Scott Zigler | 2019-08-19 07:33 | 2019-07-30 11:57 | 2019-07-30 11:57 | 2019-08-13 13:41 | 2019-08-13 09:00 | 2019-07-30 11:20 | 2019-08-13 14:15 |  |  | Centennial Wind Farm North side of O&M building. |  |  | Marcus Huddleston | No additional comments. MLH 8/19/19 | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Scott Zigler |  | Sub contractor was in contractors vehicle, backing into parking spot on north side of O&M building. The contractor struck the corrugated metal siding with the rear bumper of the truck. No spotter was being utilized. The subcontractor claimed to have been using backup camera and mirror but claimed the backup camera froze up. The camera was tested after the incident and found to be in working condition. Backup alarm sensor on the vehicle were not working. Contractor stated the alarms hadn't worked in some time. Subcontractor was unaware the vehicle had sensors. This incident is still in review and awaiting contractors report. Further information will be added when available. |  |  |  | Centennial Wind Farm | FALSE |  | FALSE | Renewable Energy |  | Scott Zigler | Scott Zigler |  | Jason Thomas | The truck involved in the incident is at another site. Truck is due to be in service next week 8/22/2019. S. Zigler is to verify operation of back up sensors (if equipped) and functionality of back up camera. | Jason Thomas |  | Low |  | 2.07 Slow reaction time |  |  | 5.06 Lack of situational awareness | [7 empty] | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | Driver of vehicle relied on his backup camera instead of utilizing his mirrors at all times. | 15. Using Equipment Improperly | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Scott Zigler | Damage to metal siding on North side of O&M building |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Scott Zigler | Sky Climber Renewables | Charles Peschka |  | Structural |  | Scott Zigler |  |  |  |  | FALSE | [42 empty] | Tin siding on O&M building is caved in approximately 8' wide by 6" deep | 2000 | Charles Peschka | Structural |  | V74-719 Vestas Fleet Vehicle
8967 | Corporate Headquarters Bldg | 2019-07-26 14:00 | Pulled into the front parking lot to stop and enter time. When leaving member backed into ballard near the gate keypad. No damage to the vehicle. The ballard was rusted out at the base and fell over. Member repaired ballard. | Level 1 |  | FALSE | Vehicle |  |  |  |  | OG&E Corp Services | Les Waller | 2019-08-23 15:52 | 2019-08-01 14:01 | 2019-08-01 14:01 | 2019-08-21 12:41 | 2019-08-09 13:00 | 2019-08-01 13:45 | 2019-08-23 11:30 |  |  | Old East Service Center on Post Road. |  |  | Jerrie Looney | J. Looney, 8.23.19 | UTS |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Les Waller |  | Member pulled into the old service center to enter time for the day. Member did not exit the vehicle. After completing the time entry the member backed out to leave. While backing the member struck the card reader. The member did not do a 360 prior to backing out. The member did not see the card reader. This was a common routine for the member. |  |  |  | Corporate Headquarters Bldg | FALSE |  | FALSE | UTS - Envir. & Process Chem |  | Richard Fuller | Les Waller |  | Robert Benham | I concur with the corrective action. | Robert Benham |  | Low |  | 2.02 Emotional disturbance |  |  |  | 6.02 Inadequate practice |  | 8.2.2 Improper conduct that is not condoned: Unintentional | [8 empty] | Member did not perform a 360 prior to backing and did not see the card reader while backing. | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) | [74 empty] | TRUE |  | Midwest City | Struck Fixed Object | Backing Related | 2017-03-20 |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Clear
8968 | Muskogee Power Plant | 2019-08-02 13:30 | "B" phase insulator on the 101 line to the 161kv reserve sub failed... While later inspecting the site it was found that the insulator blew apart sending some pieces of ceramic up to 30 yards away. | Level 1 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Zackary Thompson | 2019-09-11 09:12 | 2019-08-04 10:02 | 2019-08-04 10:02 | 2019-09-01 12:09 | 2019-08-16 13:30 | 2019-08-04 09:44 | 2019-09-03 17:38 |  |  | Muskogee PP 101 line to 161kv reserve sub. Pole located east of 6 crusher house switch gear and north of Unit 6 reclaim |  |  | Robert Wright | Approved Bob Wright | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Zackary Thompson |  | "B" phase insulator on the 101 line to the 161kv reserve sub failed... While later inspecting the site it was found that the insulator blew apart sending some pieces of ceramic up to 30 yards away. The pole that the insulator was attached to is located east of 6 Crusher Switch Gear and north of conveyor 17/18 enclosure. It is very rare for anyone to be in this area. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Zackary Thompson | Zackary Thompson |  |  | Please add some pics and a bit more information about the area and the risk involved. |  |  | Low | [14 empty] | 15.03 Inadequate inspection and/or monitoring |  | "B" phase insulator on the 101 line to the 161kv reserve sub failed | 18. Failure to Check, Monitor | 12. Equipment Failure
8969 | Metro Service Center | 2019-08-02 08:30 | Fork lift struck overhead door controller | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Delivery | Darryl Splawn | 2019-08-15 10:04 | 2019-08-05 08:11 | 2019-08-05 08:11 | 2019-08-14 11:44 | 2019-08-16 08:30 | 2019-08-05 08:04 | 2019-08-14 15:22 |  | 2019-08-14 15:11 | Metro Meter Shop Entrance |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Darryl Splawn |  | The member was attempting to leave the metro meter shop in a fork lift. He opened the garage door by leaning out and pushing the open button while still seated on the forklift. After the door started to open, the member turned to position the forklift for going down the ramp. While turning the forklift contacted the garage door controller, causing damage to the controller. |  |  |  | Metro Service Center | FALSE |  | FALSE | PD Operations Services |  | Stephen Wooten | Darryl Splawn |  | Steve Watkins | Approved | Steve Watkins |  | Medium | [6 empty] | 7.06 Improper attempt to save time or effort | [9 empty] | Fork lift struck fixed object | 11. Improper Position for Task | 1. Struck Against (Running or Bumping Into) |  | good investigation on this incident with good corrective actions. | [66 empty] | Damaged Overhead Door Controller | 500 | Stephen Wooten | Fixed Equipment
8970 | Durant Service Center | 2019-08-01 14:30 | While placing new light poles in new addition. Hit primary wire while digging pole hole with auger. Primary was miss located. | Level 2 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Lyle Just | 2019-09-20 13:16 | 2019-08-05 11:05 |  | 2019-09-17 19:23 | 2019-09-12 14:30 | 2019-08-05 10:55 | 2019-09-20 12:12 |  | 2019-09-19 10:30 | Goddard St. & Poplar St. Caddo OK. |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Lyle Just |  | While digging in new lights hit primary cable. The cable was 32 inches off the mark on the back side of the ped. It was 22 inches to the edge of the auger hole. They were digging the hole with an 18 inch auger. Primary wire was 34" from the locate marks |  |  |  | Durant Service Center | FALSE |  | FALSE | Construction Services |  | Shad Barnett | Lyle Just |  | Chad Inman | I agree with the corrective action listed. This is a great example of not allowing ourselves to become completely reliant on our utility locates, we must perform our due diligence. | Chad Inman |  | Medium | [15 empty] | 16.08 Incorrect instructions | Cable was mislocated | 02. Failure to Warn | 1. Struck Against (Running or Bumping Into) |  | Reviewed. Locate company would not own responsibility. Operations manager and safety manager gave instruction to close incident, due to efficiency and lack of added value. | [90 empty] | 7383592
8971 | Metro Service Center | 2019-07-30 18:30 | (Potential conductor overload) On 7/29/19 the DCC executed an Order for switching M0888, potentially over loading conductor which may have contributed to conductor burning down on 7/30/19. This switching was requested to kill out a section of line on the Midway 29 so Transmission crews could drill a pear hole for a self-supporting transmission structure. DCC moved approximately 90amps of load from the Midway 29 to the Green Pasture 24. | Level 1 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Douglas Mack | 2019-09-16 08:34 | 2019-08-05 12:23 |  | 2019-09-13 18:33 | 2019-09-10 18:30 | 2019-08-05 11:24 | 2019-09-14 11:07 |  |  | Metro DCC |  |  | Cody Magby | very thorough investigation. cm | T&D Ops |  | Level 1 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Douglas Mack |  | Summary Potential Conductor Overload Monday, July 29, 2019 the DCC executed an order for Switching M-0888, potentially over loading conductor which may have contributed to conductor burning down Monday evening, July 29, 2019. The switching was requested to de-energize a section of line on Midway 852229 for Transmission crew to drill a pier hole for a self-supporting transmission structure. DCC moved 32.43% (approximately 90amps) of load from Midway 852229 to Green Pastures 845824. Timeline Monday, June 3, 2019 Request for Equipment 19-06-03090657 Job # 1646840 Requested by: Project Coordinator Boundaries of Line or Equipment Request: Midway 12.5kv Circuit 852229 from 600amp Switch 11622 ABC Phase to cut gaps North side of Lateral 18913 C Phase. Work to be done: De-Energize line for 10 days to drill and set self-supporting Transmission poles. DCC Operator 1, noted outage on 11 transformer stations to cut gaps North of Lateral 18913 DCC Operator 1 trended Midway 852229 circuit and highest peaks for the last month at 235Amp’s. Also, showed peaks on Green Pastures 845824 on ABC Phases dated for 6/3/2019 at 3:00pm Switching Order M-0888 signed by three DCC Operators Wednesday, July 15, 2019 at 12:33pm Line Foreman 1 advised DCC Operator 2, he drove the line out and needed to make changes to switching order he was also notified they will not perform switching until Monday, July 29, 2019 and will return switching order to normal on Thursday, August 1, 2019. DCC Operator 2 placed switching order in the Book and updated the dates for switching to be performed. Monday, July 29, 2019 at 7:49am Line Foreman 1 advised DCC Operator 3; he is ready to start Switching Order M-0888 that is scheduled. Power Quality Tech 1 will be assisting concerning the Regulators. Monday, July 29, 2019 at 7:56am Power Quality Tech 2 called into DCC requesting Switching Order M-0888 to help out Line Foreman 1 as well. Monday, July 29, 2019 at 8:58am DCC Operator 3 issued and directed switching order M-0888 to Power Quality Tech 1, Line Foreman 1 and Power Quality Tech 2 Monday, July 29, 2019 at 11:28am Switching Order M-0888 completed Monday, July 29, 2019 from 11:28a-6:32pm Per Revenue Protection Investigator, there were no low voltage events in Silver Springs prior to outage at 6:32pm on Green Pastures 5824 Monday, July 29, 2019 at 6:32pm Received outages in OMS (Outage Management System) until DCC Dispatcher 1, analyzed outage and opened Recloser 3198 located Choctaw RD & NE 75 in Arcadia on Green Pastures 845824 PD-07292019-00687 Monday, July 29, 2019 at 6:36pm DCC Dispatcher 1 dispatched Troubleshooter 1, accepted outage at 6:36pm. Monday, July 29, 2019 @ 6:39pm Customer Service sent a police/fire call (350 ticket) in Harrah, stated transformer blown, line down and grass fire. Monday, July 29, 2019 @ 7:04pm Transmission Operator 1 advised DCC Operator 2, Control Operator at Horseshoe he had an alternate station power alarm showing to be fed from Midway 2229. Transmission Operator 1 asked DCC Operator 2 if he has any problems on the feeder ? (Midway 2229) DCC Operator 2 advised he shows nothing on Midway 2229. Transmission Operator 1 does he thinks there is anything downstream that Control 1 can see. DCC Operator 2 transferred Transmission Operator 1 to Control 1. Monday, July 29, 2019 @ 7:06pm Transmission Operator 1, Senior System Operator advised he has an alarm at Horseshoe Lake Power Plant. It is loss of alternate station power. Showing alternate Station Power is fed from Midway 2229 circuit. DCC Dispatcher 1 advised he saw a ticket come in on Midway 2229 as soon as another outages came in on Green Pastures 5824 …there is a line down per police/ fire ticket that came in at 6:40pm. Transmission Operator 1, advised his alarm came in at 6:33pm. DCC Dispatcher 1, advised he had Trouble man in route and is showing178 customers offline. Transmission Operator 1 advised to have DCC contact him at 8166 when power is restored. Monday, July 29, 2019 @ 8:28pm Troubleshooter 1 advised to dispatch Linecrew will a roll of # 4 primary and some sleeves. There is broke #4 primary in 3 or 4 different spots. Not sure what caused it because there are no poles down. DCC Dispatcher 1 advised he thinks it was overloaded. Monday, July 29, 2019 @ 8:33pm Transmission Operator 1 wanted to know approximate ETR because he is still getting alarms from Horseshoe Lake Plant. DCC Operator 4, advised it may be a couple of hours. Monday, July 29, 2019 @ 8:33pm DCC Dispatcher 1 dispatched Line Foreman 2, to make repairs. Line Foreman 2 advised they will be at 24 hours at 1:00am Monday, July 29, 2019 @ 8:41pm Transmission Operator 1 conferenced call DCC Operator 4 in Control 2 and Operation Foreman at the Horseshoe Lake Plant, advised they are experiencing trouble with a feed to their deep wells that provide water to their units and also to their system lake make up and blow down. He wanted to know how long the outage will take so he can formulate a plan. Monday, July 29, 2019 @ 8:45pm DCC Dispatcher 1 called Transmission Operator 1 to advise the Troubleman found #4 primary line down and Linecrew is in route. Transmission Operator 1 asked for an ETR, DCC Dispatcher 1 gave Transmission Operator 1, Line Foreman 2’s contact information to get approximate ETR. Monday, July 29, 2019 @ 8:45pm DCC Operator 4 called Line Foreman 2 asking for an ETR. Line Foreman 2 informed him it will take an hour to get onsite and maybe approximately 2 hours to make repairs. Monday, July 29, 2019 @ 8:48pm DCC Dispatcher 1 called Troubleshooter 1 advised Control 2 is needing a switchman because the Horseshoe Lake Plant was losing their water supply. Monday, July 29, 2019 @ 8:50pm DCC Operator 4 called Troubleshooter 1 informed him that he needed a switchman to perform switching to pick up the water well for the Horseshoe Lake Plant. Monday, July 29, 2019 @ 9:30pm Troubleshooter 1 advised DCC Operator 4 he found a Switch Danger Tagged and grounded. Troubleshooter 1 advised the Danger Tagged stated do not operate. DCC Operator 4 agreed there are jumpers lifted south of the Switch and that is why the Switch is grounded and the maps had not been updated. Monday, July 29, 2019 @ 9:32pm DCC Operator 4 called Transmission Operator 1 and stated he cannot pick up the wells at Horseshoe Lake Plant. There are jumpers lifted south of the Switch and there no way to back feed because of the Highway Project. The ETR will be approximately 11:30pm Monday, July 29, 2019 @ 9:44pm Technical Support Rep., asked what the ETR was for the Harrah outage? He advised on the customer’s account is saying 9:57pm. DCC Dispatcher 1 advised OMS is showing 10:57pm and will adjust it to 11:57pm. Monday, July 29, 2019 @ 9:56pm DCC Supervisor, called in and spoke with DCC Dispatcher 1 to find out the cause of the outage on Green Pastures. DCC Dispatcher 1 advised there is #4 primary line down in three different places. DCC Supervisor asked if the wire was down due to load? It will not do any good if the linecrew makes repairs it will potentially burn down again if the Green Pastures circuit is overloaded. Also, the DCC Supervisor advised the Dispatcher to check with DCC Operator 4 to see if there are any options, he can get the load off Green Pastures. Monday, July 29, 2019 @ 10:02pm DCC Supervisor, spoke with DCC Operator 4 asking what the options are to restore Green Pastures. DCC Operator 4 advised he attempted to perform switching to get the Horseshoe Lake Plant water pumps back online because they are losing their water supply but switching was done (M-0888), jumpers lifted and grounds in place south of the Switch. Tuesday, July 30, 2019 @ 12:19am DCC Operator 4 called Line Foreman 2 asking for an ETR update Horseshoe Lake Plant is making inquiries. Line Foreman 2 advised they are pulling their first set of grounds approximate time is 30 minutes. Tuesday, July 30, 2019 @ 12:20am DCC Operator 4 advised Transmission Operator 1 the line crew are pulling their ground and ETR to should 30 minutes. Tuesday, July 30, 2019 @ 12:40am DCC Dispatcher 2, gave Line Foreman 2 permission to close Recloser 3198 Tuesday, July 30, 2019 @ 12:46am Line Foreman 2 advised A Phase did not hold and there is a fire. Line Foreman 2 added they are at 24 hours and 15 minutes and is requesting to send another Linecrew to relieve him and his crew. Tuesday, July 30, 2019 @ 12:53am DCC Dispatcher 2 dispatched Linecrew Foreman, Line Foreman 3, truck 530 to relieve Line Foreman 2 and his crew. Tuesday, July 30, 2019 @ 02:08am DCC Operator 4 advised Transmission Operator 1 that Line Foreman 2 attempted to close Recloser 3198 - it burnt down some more wire. Line Foreman 2 timed out and, Line Foreman 3 heading from Shawnee will be onsite in 20 minutes. Tuesday, July 30, 2019 @ 04:44am Transmission Operator 1 advised he will be leaving soon and to contact his relief in the TCC when circuit is restored because this is their alternate feed to Horseshoe Lake Plant. Tuesday, July 30, 2019 @ 6:50am DCC Operator 4 advised Senior System Operator, Transmission Operator 2 in Transmission Control Center (TCC) repairs made and power restored at 6:50am. Senior Operator, DCC Operator 4 wrote handwritten switching to restore outage on Recloser 3198 in Sections due to cold load pickup on Green Pastures 5824 Overall Outage: 12 hours 52 Minutes Other Relevant Information: -What voltages do meter view show on the affected area from 1130 on 7/29 to 0700 7/30? NOTE: Meter view data is populated day after and is not a tool in use by the DCC for day to day situational awareness. Charts below shows the average hourly voltage for meters and what percentage of customers are below a certain voltage value. -How much load do we think was actually on the #4 that burned down? Use TLM or escalation tools from planning. Distribution planning did a study using the switching order and locations where the line burned down: Approx. 100-120 amps per phase on the burned down conductor was shown on the study. #4 ACSR is rated for 140 amps. It is not clear how closely the model reflects real world conditions particularly when the voltages were as far from normal as indicated by meter measurements. It is possible that the line was not overloaded for its normal condition and use, but perhaps weak points existed (mechanical damage from previous fault events or improperly installed jumpers, splices etc.) that caused it to fail at an amperage that was less than expected. Regardless, the voltage data following the switching event shows that this operating condition was not desirable. DMS system shows reasonably well how much load was transferred to green pastures both in SCADA telemetry and power flow, but because Green Pastures is non-scada, we do not have a good estimate of what load was on the Green Pastures circuit during the event. Distribution planning pulled data sources together manually that we do not currently have in DMS to provide this estimate. -Did OMS receive any customer calls complaining of low voltage? No customer calls for low voltage were received. -What is the definition of a meter event for low voltage (duration, magnitude etc.) in silver springs? what is the definition of a meter event for low voltage? a. For the I210+c meters (NEW METERS ARE PROGRAMMED) i. SAG = 8% voltage less than the nominal voltage for a minimum of 1 second – No AMM Alarm – PQ read only ii. SWELL = 6% voltage greater than nominal voltage for a minimum of 1 second– No AMM Alarm – PQ read only iii. Under Voltage Alert is 10% voltage less than the nominal voltage for 15 minutes or more – this is the same as a CA 000400 = Low Potential on I210+c this alert comes in from AMM iv. Over Voltage Alert is 8% voltage more than the nominal voltage for 15 minutes or more – this comes in from AMM as I210C over Voltage Diagnostic 7 Set b. For the KV2c Meters (NEW METERS ARE PROGRAMMED) i. SAG = 8% voltage less than the nominal voltage for a minimum of 4 cycles – No AMM Alarm – PQ read only ii. SWELL = 6% voltage greater than nominal voltage for a minimum of 4 cycles - No AMM Alarm – PQ read only iii. Under Voltage Alert is 10% voltage less than the nominal voltage for 15 minutes or more – this alert comes in from AMM iv. Over Voltage Alert is 8% voltage more than the nominal voltage for 15 minutes or more – this alert comes in from AMM v. c. For the I210+c meters (METERS WERE ORIGINALLY PROGRAMMED) i. SAG = 10% voltage less than the nominal voltage for a minimum of 1 second – No AMM Alarm – PQ read only ii. SWELL = 10% voltage greater than nominal voltage for a minimum of 1 second– No AMM Alarm – PQ read only iii. Under Voltage Alert is 15% voltage less than the nominal voltage for 3 seconds more – this is the same as a CA 000400 = Low Potential on I210+c this alert comes in from AMM iv. Over Voltage Alert is 10% voltage more than the nominal voltage for 3 seconds more – this comes in from AMM as I210C over Voltage Diagnostic 7 Set d. For the KV2c Meters (METERS WERE ORIGINALLY PROGRAMMED) i. SAG = 10% voltage less than the nominal voltage for a minimum of 4 cycles – No AMM Alarm – PQ read only ii. SWELL = 10% voltage greater than nominal voltage for a minimum of 4 cycles - No AMM Alarm – PQ read only iii. Under Voltage Alert is 10% voltage less than the nominal voltage for 10 seconds or more – this alert comes in from AMM iv. Over Voltage Alert is 10% voltage more than the nominal voltage for 10 seconds or more - this alert comes in from AMM NOTE: The alerts received are read with normal data reads. They do not come in near realtime. It appears that the voltages were not low enough prior to the burn down to reliably trigger meter events if they are mostly programmed at +/-10% from nominal. -Is anything done with a low voltage meter event when it is received? Not on a consistent basis in any OG&E workgroup. Occasional use for data anomalies. There are some others in the company looking at voltages from other points of view such as revenue protection. -Do we know where the alternate station power transformers are for our substations? Is this clearly noted? From SP&C: No known list that is quickly referenceable exists. What if any notes were recorded regarding the temperature at which the original switching was planned? No known notes existed. Were there warnings that the switching may not be possible in hotter temperature conditions? No warnings were noted What guidelines exist to direct operators to re-analyze switching in light of new weather conditions or date changes? All switching orders should be reanalyze before execution. NOTE: Current training and available tools to the operators limit the extent to which an operator can have the situational awareness required to annunciate the problems associated with this switching. Did we recheck any load measurements between original date and actual date of execution? NO Were the recorded loads at Green Pastures the current AD readings in the field or was that from history? Field readings Do the operators even have access to the AD reading history any longer? Yes, we view thru DAA What communication was passed between Control 1 and Control 2 verbally? It appears that Control 2 may have known that simply reclosing recloser 3198 was not going to resolve the problem/outage due to overload problems, but control 1 directed the closing of 3198, resulting in another burndown. Phone calls seem to indicate good communication between control 1 and 2 originally, but the information regarding the overload and cold pickup appears to have been lost at shift change and line crew rotation. |  |  |  | Metro Service Center | FALSE |  | FALSE | System Operations |  | Rachel Davis | Douglas Mack |  | Darrell Fuller | Please review | Darrell Fuller |  | Low |  |  |  |  | 5.01 Lack of experience | [8 empty] | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  | 16.05 Inadequate communication between shifts | conductor overload | 18. Failure to Check, Monitor | 9. Abnormal Operation
8971 | Metro Service Center | 2019-07-30 18:30 | (Potential conductor overload) On 7/29/19 the DCC executed an Order for switching M0888, potentially over loading conductor which may have contributed to conductor burning down on 7/30/19. This switching was requested to kill out a section of line on the Midway 29 so Transmission crews could drill a pear hole for a self-supporting transmission structure. DCC moved approximately 90amps of load from the Midway 29 to the Green Pasture 24. | Level 1 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Douglas Mack | 2019-09-16 08:34 | 2019-08-05 12:23 |  | 2019-09-13 18:33 | 2019-09-10 18:30 | 2019-08-05 11:24 | 2019-09-14 11:07 |  |  | Metro DCC |  |  | Cody Magby | very thorough investigation. cm | T&D Ops |  | Level 1 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Douglas Mack |  | Summary Potential Conductor Overload Monday, July 29, 2019 the DCC executed an order for Switching M-0888, potentially over loading conductor which may have contributed to conductor burning down Monday evening, July 29, 2019. The switching was requested to de-energize a section of line on Midway 852229 for Transmission crew to drill a pier hole for a self-supporting transmission structure. DCC moved 32.43% (approximately 90amps) of load from Midway 852229 to Green Pastures 845824. Timeline Monday, June 3, 2019 Request for Equipment 19-06-03090657 Job # 1646840 Requested by: Project Coordinator Boundaries of Line or Equipment Request: Midway 12.5kv Circuit 852229 from 600amp Switch 11622 ABC Phase to cut gaps North side of Lateral 18913 C Phase. Work to be done: De-Energize line for 10 days to drill and set self-supporting Transmission poles. DCC Operator 1, noted outage on 11 transformer stations to cut gaps North of Lateral 18913 DCC Operator 1 trended Midway 852229 circuit and highest peaks for the last month at 235Amp’s. Also, showed peaks on Green Pastures 845824 on ABC Phases dated for 6/3/2019 at 3:00pm Switching Order M-0888 signed by three DCC Operators Wednesday, July 15, 2019 at 12:33pm Line Foreman 1 advised DCC Operator 2, he drove the line out and needed to make changes to switching order he was also notified they will not perform switching until Monday, July 29, 2019 and will return switching order to normal on Thursday, August 1, 2019. DCC Operator 2 placed switching order in the Book and updated the dates for switching to be performed. Monday, July 29, 2019 at 7:49am Line Foreman 1 advised DCC Operator 3; he is ready to start Switching Order M-0888 that is scheduled. Power Quality Tech 1 will be assisting concerning the Regulators. Monday, July 29, 2019 at 7:56am Power Quality Tech 2 called into DCC requesting Switching Order M-0888 to help out Line Foreman 1 as well. Monday, July 29, 2019 at 8:58am DCC Operator 3 issued and directed switching order M-0888 to Power Quality Tech 1, Line Foreman 1 and Power Quality Tech 2 Monday, July 29, 2019 at 11:28am Switching Order M-0888 completed Monday, July 29, 2019 from 11:28a-6:32pm Per Revenue Protection Investigator, there were no low voltage events in Silver Springs prior to outage at 6:32pm on Green Pastures 5824 Monday, July 29, 2019 at 6:32pm Received outages in OMS (Outage Management System) until DCC Dispatcher 1, analyzed outage and opened Recloser 3198 located Choctaw RD & NE 75 in Arcadia on Green Pastures 845824 PD-07292019-00687 Monday, July 29, 2019 at 6:36pm DCC Dispatcher 1 dispatched Troubleshooter 1, accepted outage at 6:36pm. Monday, July 29, 2019 @ 6:39pm Customer Service sent a police/fire call (350 ticket) in Harrah, stated transformer blown, line down and grass fire. Monday, July 29, 2019 @ 7:04pm Transmission Operator 1 advised DCC Operator 2, Control Operator at Horseshoe he had an alternate station power alarm showing to be fed from Midway 2229. Transmission Operator 1 asked DCC Operator 2 if he has any problems on the feeder ? (Midway 2229) DCC Operator 2 advised he shows nothing on Midway 2229. Transmission Operator 1 does he thinks there is anything downstream that Control 1 can see. DCC Operator 2 transferred Transmission Operator 1 to Control 1. Monday, July 29, 2019 @ 7:06pm Transmission Operator 1, Senior System Operator advised he has an alarm at Horseshoe Lake Power Plant. It is loss of alternate station power. Showing alternate Station Power is fed from Midway 2229 circuit. DCC Dispatcher 1 advised he saw a ticket come in on Midway 2229 as soon as another outages came in on Green Pastures 5824 …there is a line down per police/ fire ticket that came in at 6:40pm. Transmission Operator 1, advised his alarm came in at 6:33pm. DCC Dispatcher 1, advised he had Trouble man in route and is showing178 customers offline. Transmission Operator 1 advised to have DCC contact him at 8166 when power is restored. Monday, July 29, 2019 @ 8:28pm Troubleshooter 1 advised to dispatch Linecrew will a roll of # 4 primary and some sleeves. There is broke #4 primary in 3 or 4 different spots. Not sure what caused it because there are no poles down. DCC Dispatcher 1 advised he thinks it was overloaded. Monday, July 29, 2019 @ 8:33pm Transmission Operator 1 wanted to know approximate ETR because he is still getting alarms from Horseshoe Lake Plant. DCC Operator 4, advised it may be a couple of hours. Monday, July 29, 2019 @ 8:33pm DCC Dispatcher 1 dispatched Line Foreman 2, to make repairs. Line Foreman 2 advised they will be at 24 hours at 1:00am Monday, July 29, 2019 @ 8:41pm Transmission Operator 1 conferenced call DCC Operator 4 in Control 2 and Operation Foreman at the Horseshoe Lake Plant, advised they are experiencing trouble with a feed to their deep wells that provide water to their units and also to their system lake make up and blow down. He wanted to know how long the outage will take so he can formulate a plan. Monday, July 29, 2019 @ 8:45pm DCC Dispatcher 1 called Transmission Operator 1 to advise the Troubleman found #4 primary line down and Linecrew is in route. Transmission Operator 1 asked for an ETR, DCC Dispatcher 1 gave Transmission Operator 1, Line Foreman 2’s contact information to get approximate ETR. Monday, July 29, 2019 @ 8:45pm DCC Operator 4 called Line Foreman 2 asking for an ETR. Line Foreman 2 informed him it will take an hour to get onsite and maybe approximately 2 hours to make repairs. Monday, July 29, 2019 @ 8:48pm DCC Dispatcher 1 called Troubleshooter 1 advised Control 2 is needing a switchman because the Horseshoe Lake Plant was losing their water supply. Monday, July 29, 2019 @ 8:50pm DCC Operator 4 called Troubleshooter 1 informed him that he needed a switchman to perform switching to pick up the water well for the Horseshoe Lake Plant. Monday, July 29, 2019 @ 9:30pm Troubleshooter 1 advised DCC Operator 4 he found a Switch Danger Tagged and grounded. Troubleshooter 1 advised the Danger Tagged stated do not operate. DCC Operator 4 agreed there are jumpers lifted south of the Switch and that is why the Switch is grounded and the maps had not been updated. Monday, July 29, 2019 @ 9:32pm DCC Operator 4 called Transmission Operator 1 and stated he cannot pick up the wells at Horseshoe Lake Plant. There are jumpers lifted south of the Switch and there no way to back feed because of the Highway Project. The ETR will be approximately 11:30pm Monday, July 29, 2019 @ 9:44pm Technical Support Rep., asked what the ETR was for the Harrah outage? He advised on the customer’s account is saying 9:57pm. DCC Dispatcher 1 advised OMS is showing 10:57pm and will adjust it to 11:57pm. Monday, July 29, 2019 @ 9:56pm DCC Supervisor, called in and spoke with DCC Dispatcher 1 to find out the cause of the outage on Green Pastures. DCC Dispatcher 1 advised there is #4 primary line down in three different places. DCC Supervisor asked if the wire was down due to load? It will not do any good if the linecrew makes repairs it will potentially burn down again if the Green Pastures circuit is overloaded. Also, the DCC Supervisor advised the Dispatcher to check with DCC Operator 4 to see if there are any options, he can get the load off Green Pastures. Monday, July 29, 2019 @ 10:02pm DCC Supervisor, spoke with DCC Operator 4 asking what the options are to restore Green Pastures. DCC Operator 4 advised he attempted to perform switching to get the Horseshoe Lake Plant water pumps back online because they are losing their water supply but switching was done (M-0888), jumpers lifted and grounds in place south of the Switch. Tuesday, July 30, 2019 @ 12:19am DCC Operator 4 called Line Foreman 2 asking for an ETR update Horseshoe Lake Plant is making inquiries. Line Foreman 2 advised they are pulling their first set of grounds approximate time is 30 minutes. Tuesday, July 30, 2019 @ 12:20am DCC Operator 4 advised Transmission Operator 1 the line crew are pulling their ground and ETR to should 30 minutes. Tuesday, July 30, 2019 @ 12:40am DCC Dispatcher 2, gave Line Foreman 2 permission to close Recloser 3198 Tuesday, July 30, 2019 @ 12:46am Line Foreman 2 advised A Phase did not hold and there is a fire. Line Foreman 2 added they are at 24 hours and 15 minutes and is requesting to send another Linecrew to relieve him and his crew. Tuesday, July 30, 2019 @ 12:53am DCC Dispatcher 2 dispatched Linecrew Foreman, Line Foreman 3, truck 530 to relieve Line Foreman 2 and his crew. Tuesday, July 30, 2019 @ 02:08am DCC Operator 4 advised Transmission Operator 1 that Line Foreman 2 attempted to close Recloser 3198 - it burnt down some more wire. Line Foreman 2 timed out and, Line Foreman 3 heading from Shawnee will be onsite in 20 minutes. Tuesday, July 30, 2019 @ 04:44am Transmission Operator 1 advised he will be leaving soon and to contact his relief in the TCC when circuit is restored because this is their alternate feed to Horseshoe Lake Plant. Tuesday, July 30, 2019 @ 6:50am DCC Operator 4 advised Senior System Operator, Transmission Operator 2 in Transmission Control Center (TCC) repairs made and power restored at 6:50am. Senior Operator, DCC Operator 4 wrote handwritten switching to restore outage on Recloser 3198 in Sections due to cold load pickup on Green Pastures 5824 Overall Outage: 12 hours 52 Minutes Other Relevant Information: -What voltages do meter view show on the affected area from 1130 on 7/29 to 0700 7/30? NOTE: Meter view data is populated day after and is not a tool in use by the DCC for day to day situational awareness. Charts below shows the average hourly voltage for meters and what percentage of customers are below a certain voltage value. -How much load do we think was actually on the #4 that burned down? Use TLM or escalation tools from planning. Distribution planning did a study using the switching order and locations where the line burned down: Approx. 100-120 amps per phase on the burned down conductor was shown on the study. #4 ACSR is rated for 140 amps. It is not clear how closely the model reflects real world conditions particularly when the voltages were as far from normal as indicated by meter measurements. It is possible that the line was not overloaded for its normal condition and use, but perhaps weak points existed (mechanical damage from previous fault events or improperly installed jumpers, splices etc.) that caused it to fail at an amperage that was less than expected. Regardless, the voltage data following the switching event shows that this operating condition was not desirable. DMS system shows reasonably well how much load was transferred to green pastures both in SCADA telemetry and power flow, but because Green Pastures is non-scada, we do not have a good estimate of what load was on the Green Pastures circuit during the event. Distribution planning pulled data sources together manually that we do not currently have in DMS to provide this estimate. -Did OMS receive any customer calls complaining of low voltage? No customer calls for low voltage were received. -What is the definition of a meter event for low voltage (duration, magnitude etc.) in silver springs? what is the definition of a meter event for low voltage? a. For the I210+c meters (NEW METERS ARE PROGRAMMED) i. SAG = 8% voltage less than the nominal voltage for a minimum of 1 second – No AMM Alarm – PQ read only ii. SWELL = 6% voltage greater than nominal voltage for a minimum of 1 second– No AMM Alarm – PQ read only iii. Under Voltage Alert is 10% voltage less than the nominal voltage for 15 minutes or more – this is the same as a CA 000400 = Low Potential on I210+c this alert comes in from AMM iv. Over Voltage Alert is 8% voltage more than the nominal voltage for 15 minutes or more – this comes in from AMM as I210C over Voltage Diagnostic 7 Set b. For the KV2c Meters (NEW METERS ARE PROGRAMMED) i. SAG = 8% voltage less than the nominal voltage for a minimum of 4 cycles – No AMM Alarm – PQ read only ii. SWELL = 6% voltage greater than nominal voltage for a minimum of 4 cycles - No AMM Alarm – PQ read only iii. Under Voltage Alert is 10% voltage less than the nominal voltage for 15 minutes or more – this alert comes in from AMM iv. Over Voltage Alert is 8% voltage more than the nominal voltage for 15 minutes or more – this alert comes in from AMM v. c. For the I210+c meters (METERS WERE ORIGINALLY PROGRAMMED) i. SAG = 10% voltage less than the nominal voltage for a minimum of 1 second – No AMM Alarm – PQ read only ii. SWELL = 10% voltage greater than nominal voltage for a minimum of 1 second– No AMM Alarm – PQ read only iii. Under Voltage Alert is 15% voltage less than the nominal voltage for 3 seconds more – this is the same as a CA 000400 = Low Potential on I210+c this alert comes in from AMM iv. Over Voltage Alert is 10% voltage more than the nominal voltage for 3 seconds more – this comes in from AMM as I210C over Voltage Diagnostic 7 Set d. For the KV2c Meters (METERS WERE ORIGINALLY PROGRAMMED) i. SAG = 10% voltage less than the nominal voltage for a minimum of 4 cycles – No AMM Alarm – PQ read only ii. SWELL = 10% voltage greater than nominal voltage for a minimum of 4 cycles - No AMM Alarm – PQ read only iii. Under Voltage Alert is 10% voltage less than the nominal voltage for 10 seconds or more – this alert comes in from AMM iv. Over Voltage Alert is 10% voltage more than the nominal voltage for 10 seconds or more - this alert comes in from AMM NOTE: The alerts received are read with normal data reads. They do not come in near realtime. It appears that the voltages were not low enough prior to the burn down to reliably trigger meter events if they are mostly programmed at +/-10% from nominal. -Is anything done with a low voltage meter event when it is received? Not on a consistent basis in any OG&E workgroup. Occasional use for data anomalies. There are some others in the company looking at voltages from other points of view such as revenue protection. -Do we know where the alternate station power transformers are for our substations? Is this clearly noted? From SP&C: No known list that is quickly referenceable exists. What if any notes were recorded regarding the temperature at which the original switching was planned? No known notes existed. Were there warnings that the switching may not be possible in hotter temperature conditions? No warnings were noted What guidelines exist to direct operators to re-analyze switching in light of new weather conditions or date changes? All switching orders should be reanalyze before execution. NOTE: Current training and available tools to the operators limit the extent to which an operator can have the situational awareness required to annunciate the problems associated with this switching. Did we recheck any load measurements between original date and actual date of execution? NO Were the recorded loads at Green Pastures the current AD readings in the field or was that from history? Field readings Do the operators even have access to the AD reading history any longer? Yes, we view thru DAA What communication was passed between Control 1 and Control 2 verbally? It appears that Control 2 may have known that simply reclosing recloser 3198 was not going to resolve the problem/outage due to overload problems, but control 1 directed the closing of 3198, resulting in another burndown. Phone calls seem to indicate good communication between control 1 and 2 originally, but the information regarding the overload and cold pickup appears to have been lost at shift change and line crew rotation. |  |  |  | Metro Service Center | FALSE |  | FALSE | System Operations |  | Rachel Davis | Douglas Mack |  | Darrell Fuller | Please review | Darrell Fuller |  | Low |  |  |  |  | 5.03 Inadequate initial training | [8 empty] | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  | 16.05 Inadequate communication between shifts | conductor overload | 18. Failure to Check, Monitor | 9. Abnormal Operation
8971 | Metro Service Center | 2019-07-30 18:30 | (Potential conductor overload) On 7/29/19 the DCC executed an Order for switching M0888, potentially over loading conductor which may have contributed to conductor burning down on 7/30/19. This switching was requested to kill out a section of line on the Midway 29 so Transmission crews could drill a pear hole for a self-supporting transmission structure. DCC moved approximately 90amps of load from the Midway 29 to the Green Pasture 24. | Level 1 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Douglas Mack | 2019-09-16 08:34 | 2019-08-05 12:23 |  | 2019-09-13 18:33 | 2019-09-10 18:30 | 2019-08-05 11:24 | 2019-09-14 11:07 |  |  | Metro DCC |  |  | Cody Magby | very thorough investigation. cm | T&D Ops |  | Level 1 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Douglas Mack |  | Summary Potential Conductor Overload Monday, July 29, 2019 the DCC executed an order for Switching M-0888, potentially over loading conductor which may have contributed to conductor burning down Monday evening, July 29, 2019. The switching was requested to de-energize a section of line on Midway 852229 for Transmission crew to drill a pier hole for a self-supporting transmission structure. DCC moved 32.43% (approximately 90amps) of load from Midway 852229 to Green Pastures 845824. Timeline Monday, June 3, 2019 Request for Equipment 19-06-03090657 Job # 1646840 Requested by: Project Coordinator Boundaries of Line or Equipment Request: Midway 12.5kv Circuit 852229 from 600amp Switch 11622 ABC Phase to cut gaps North side of Lateral 18913 C Phase. Work to be done: De-Energize line for 10 days to drill and set self-supporting Transmission poles. DCC Operator 1, noted outage on 11 transformer stations to cut gaps North of Lateral 18913 DCC Operator 1 trended Midway 852229 circuit and highest peaks for the last month at 235Amp’s. Also, showed peaks on Green Pastures 845824 on ABC Phases dated for 6/3/2019 at 3:00pm Switching Order M-0888 signed by three DCC Operators Wednesday, July 15, 2019 at 12:33pm Line Foreman 1 advised DCC Operator 2, he drove the line out and needed to make changes to switching order he was also notified they will not perform switching until Monday, July 29, 2019 and will return switching order to normal on Thursday, August 1, 2019. DCC Operator 2 placed switching order in the Book and updated the dates for switching to be performed. Monday, July 29, 2019 at 7:49am Line Foreman 1 advised DCC Operator 3; he is ready to start Switching Order M-0888 that is scheduled. Power Quality Tech 1 will be assisting concerning the Regulators. Monday, July 29, 2019 at 7:56am Power Quality Tech 2 called into DCC requesting Switching Order M-0888 to help out Line Foreman 1 as well. Monday, July 29, 2019 at 8:58am DCC Operator 3 issued and directed switching order M-0888 to Power Quality Tech 1, Line Foreman 1 and Power Quality Tech 2 Monday, July 29, 2019 at 11:28am Switching Order M-0888 completed Monday, July 29, 2019 from 11:28a-6:32pm Per Revenue Protection Investigator, there were no low voltage events in Silver Springs prior to outage at 6:32pm on Green Pastures 5824 Monday, July 29, 2019 at 6:32pm Received outages in OMS (Outage Management System) until DCC Dispatcher 1, analyzed outage and opened Recloser 3198 located Choctaw RD & NE 75 in Arcadia on Green Pastures 845824 PD-07292019-00687 Monday, July 29, 2019 at 6:36pm DCC Dispatcher 1 dispatched Troubleshooter 1, accepted outage at 6:36pm. Monday, July 29, 2019 @ 6:39pm Customer Service sent a police/fire call (350 ticket) in Harrah, stated transformer blown, line down and grass fire. Monday, July 29, 2019 @ 7:04pm Transmission Operator 1 advised DCC Operator 2, Control Operator at Horseshoe he had an alternate station power alarm showing to be fed from Midway 2229. Transmission Operator 1 asked DCC Operator 2 if he has any problems on the feeder ? (Midway 2229) DCC Operator 2 advised he shows nothing on Midway 2229. Transmission Operator 1 does he thinks there is anything downstream that Control 1 can see. DCC Operator 2 transferred Transmission Operator 1 to Control 1. Monday, July 29, 2019 @ 7:06pm Transmission Operator 1, Senior System Operator advised he has an alarm at Horseshoe Lake Power Plant. It is loss of alternate station power. Showing alternate Station Power is fed from Midway 2229 circuit. DCC Dispatcher 1 advised he saw a ticket come in on Midway 2229 as soon as another outages came in on Green Pastures 5824 …there is a line down per police/ fire ticket that came in at 6:40pm. Transmission Operator 1, advised his alarm came in at 6:33pm. DCC Dispatcher 1, advised he had Trouble man in route and is showing178 customers offline. Transmission Operator 1 advised to have DCC contact him at 8166 when power is restored. Monday, July 29, 2019 @ 8:28pm Troubleshooter 1 advised to dispatch Linecrew will a roll of # 4 primary and some sleeves. There is broke #4 primary in 3 or 4 different spots. Not sure what caused it because there are no poles down. DCC Dispatcher 1 advised he thinks it was overloaded. Monday, July 29, 2019 @ 8:33pm Transmission Operator 1 wanted to know approximate ETR because he is still getting alarms from Horseshoe Lake Plant. DCC Operator 4, advised it may be a couple of hours. Monday, July 29, 2019 @ 8:33pm DCC Dispatcher 1 dispatched Line Foreman 2, to make repairs. Line Foreman 2 advised they will be at 24 hours at 1:00am Monday, July 29, 2019 @ 8:41pm Transmission Operator 1 conferenced call DCC Operator 4 in Control 2 and Operation Foreman at the Horseshoe Lake Plant, advised they are experiencing trouble with a feed to their deep wells that provide water to their units and also to their system lake make up and blow down. He wanted to know how long the outage will take so he can formulate a plan. Monday, July 29, 2019 @ 8:45pm DCC Dispatcher 1 called Transmission Operator 1 to advise the Troubleman found #4 primary line down and Linecrew is in route. Transmission Operator 1 asked for an ETR, DCC Dispatcher 1 gave Transmission Operator 1, Line Foreman 2’s contact information to get approximate ETR. Monday, July 29, 2019 @ 8:45pm DCC Operator 4 called Line Foreman 2 asking for an ETR. Line Foreman 2 informed him it will take an hour to get onsite and maybe approximately 2 hours to make repairs. Monday, July 29, 2019 @ 8:48pm DCC Dispatcher 1 called Troubleshooter 1 advised Control 2 is needing a switchman because the Horseshoe Lake Plant was losing their water supply. Monday, July 29, 2019 @ 8:50pm DCC Operator 4 called Troubleshooter 1 informed him that he needed a switchman to perform switching to pick up the water well for the Horseshoe Lake Plant. Monday, July 29, 2019 @ 9:30pm Troubleshooter 1 advised DCC Operator 4 he found a Switch Danger Tagged and grounded. Troubleshooter 1 advised the Danger Tagged stated do not operate. DCC Operator 4 agreed there are jumpers lifted south of the Switch and that is why the Switch is grounded and the maps had not been updated. Monday, July 29, 2019 @ 9:32pm DCC Operator 4 called Transmission Operator 1 and stated he cannot pick up the wells at Horseshoe Lake Plant. There are jumpers lifted south of the Switch and there no way to back feed because of the Highway Project. The ETR will be approximately 11:30pm Monday, July 29, 2019 @ 9:44pm Technical Support Rep., asked what the ETR was for the Harrah outage? He advised on the customer’s account is saying 9:57pm. DCC Dispatcher 1 advised OMS is showing 10:57pm and will adjust it to 11:57pm. Monday, July 29, 2019 @ 9:56pm DCC Supervisor, called in and spoke with DCC Dispatcher 1 to find out the cause of the outage on Green Pastures. DCC Dispatcher 1 advised there is #4 primary line down in three different places. DCC Supervisor asked if the wire was down due to load? It will not do any good if the linecrew makes repairs it will potentially burn down again if the Green Pastures circuit is overloaded. Also, the DCC Supervisor advised the Dispatcher to check with DCC Operator 4 to see if there are any options, he can get the load off Green Pastures. Monday, July 29, 2019 @ 10:02pm DCC Supervisor, spoke with DCC Operator 4 asking what the options are to restore Green Pastures. DCC Operator 4 advised he attempted to perform switching to get the Horseshoe Lake Plant water pumps back online because they are losing their water supply but switching was done (M-0888), jumpers lifted and grounds in place south of the Switch. Tuesday, July 30, 2019 @ 12:19am DCC Operator 4 called Line Foreman 2 asking for an ETR update Horseshoe Lake Plant is making inquiries. Line Foreman 2 advised they are pulling their first set of grounds approximate time is 30 minutes. Tuesday, July 30, 2019 @ 12:20am DCC Operator 4 advised Transmission Operator 1 the line crew are pulling their ground and ETR to should 30 minutes. Tuesday, July 30, 2019 @ 12:40am DCC Dispatcher 2, gave Line Foreman 2 permission to close Recloser 3198 Tuesday, July 30, 2019 @ 12:46am Line Foreman 2 advised A Phase did not hold and there is a fire. Line Foreman 2 added they are at 24 hours and 15 minutes and is requesting to send another Linecrew to relieve him and his crew. Tuesday, July 30, 2019 @ 12:53am DCC Dispatcher 2 dispatched Linecrew Foreman, Line Foreman 3, truck 530 to relieve Line Foreman 2 and his crew. Tuesday, July 30, 2019 @ 02:08am DCC Operator 4 advised Transmission Operator 1 that Line Foreman 2 attempted to close Recloser 3198 - it burnt down some more wire. Line Foreman 2 timed out and, Line Foreman 3 heading from Shawnee will be onsite in 20 minutes. Tuesday, July 30, 2019 @ 04:44am Transmission Operator 1 advised he will be leaving soon and to contact his relief in the TCC when circuit is restored because this is their alternate feed to Horseshoe Lake Plant. Tuesday, July 30, 2019 @ 6:50am DCC Operator 4 advised Senior System Operator, Transmission Operator 2 in Transmission Control Center (TCC) repairs made and power restored at 6:50am. Senior Operator, DCC Operator 4 wrote handwritten switching to restore outage on Recloser 3198 in Sections due to cold load pickup on Green Pastures 5824 Overall Outage: 12 hours 52 Minutes Other Relevant Information: -What voltages do meter view show on the affected area from 1130 on 7/29 to 0700 7/30? NOTE: Meter view data is populated day after and is not a tool in use by the DCC for day to day situational awareness. Charts below shows the average hourly voltage for meters and what percentage of customers are below a certain voltage value. -How much load do we think was actually on the #4 that burned down? Use TLM or escalation tools from planning. Distribution planning did a study using the switching order and locations where the line burned down: Approx. 100-120 amps per phase on the burned down conductor was shown on the study. #4 ACSR is rated for 140 amps. It is not clear how closely the model reflects real world conditions particularly when the voltages were as far from normal as indicated by meter measurements. It is possible that the line was not overloaded for its normal condition and use, but perhaps weak points existed (mechanical damage from previous fault events or improperly installed jumpers, splices etc.) that caused it to fail at an amperage that was less than expected. Regardless, the voltage data following the switching event shows that this operating condition was not desirable. DMS system shows reasonably well how much load was transferred to green pastures both in SCADA telemetry and power flow, but because Green Pastures is non-scada, we do not have a good estimate of what load was on the Green Pastures circuit during the event. Distribution planning pulled data sources together manually that we do not currently have in DMS to provide this estimate. -Did OMS receive any customer calls complaining of low voltage? No customer calls for low voltage were received. -What is the definition of a meter event for low voltage (duration, magnitude etc.) in silver springs? what is the definition of a meter event for low voltage? a. For the I210+c meters (NEW METERS ARE PROGRAMMED) i. SAG = 8% voltage less than the nominal voltage for a minimum of 1 second – No AMM Alarm – PQ read only ii. SWELL = 6% voltage greater than nominal voltage for a minimum of 1 second– No AMM Alarm – PQ read only iii. Under Voltage Alert is 10% voltage less than the nominal voltage for 15 minutes or more – this is the same as a CA 000400 = Low Potential on I210+c this alert comes in from AMM iv. Over Voltage Alert is 8% voltage more than the nominal voltage for 15 minutes or more – this comes in from AMM as I210C over Voltage Diagnostic 7 Set b. For the KV2c Meters (NEW METERS ARE PROGRAMMED) i. SAG = 8% voltage less than the nominal voltage for a minimum of 4 cycles – No AMM Alarm – PQ read only ii. SWELL = 6% voltage greater than nominal voltage for a minimum of 4 cycles - No AMM Alarm – PQ read only iii. Under Voltage Alert is 10% voltage less than the nominal voltage for 15 minutes or more – this alert comes in from AMM iv. Over Voltage Alert is 8% voltage more than the nominal voltage for 15 minutes or more – this alert comes in from AMM v. c. For the I210+c meters (METERS WERE ORIGINALLY PROGRAMMED) i. SAG = 10% voltage less than the nominal voltage for a minimum of 1 second – No AMM Alarm – PQ read only ii. SWELL = 10% voltage greater than nominal voltage for a minimum of 1 second– No AMM Alarm – PQ read only iii. Under Voltage Alert is 15% voltage less than the nominal voltage for 3 seconds more – this is the same as a CA 000400 = Low Potential on I210+c this alert comes in from AMM iv. Over Voltage Alert is 10% voltage more than the nominal voltage for 3 seconds more – this comes in from AMM as I210C over Voltage Diagnostic 7 Set d. For the KV2c Meters (METERS WERE ORIGINALLY PROGRAMMED) i. SAG = 10% voltage less than the nominal voltage for a minimum of 4 cycles – No AMM Alarm – PQ read only ii. SWELL = 10% voltage greater than nominal voltage for a minimum of 4 cycles - No AMM Alarm – PQ read only iii. Under Voltage Alert is 10% voltage less than the nominal voltage for 10 seconds or more – this alert comes in from AMM iv. Over Voltage Alert is 10% voltage more than the nominal voltage for 10 seconds or more - this alert comes in from AMM NOTE: The alerts received are read with normal data reads. They do not come in near realtime. It appears that the voltages were not low enough prior to the burn down to reliably trigger meter events if they are mostly programmed at +/-10% from nominal. -Is anything done with a low voltage meter event when it is received? Not on a consistent basis in any OG&E workgroup. Occasional use for data anomalies. There are some others in the company looking at voltages from other points of view such as revenue protection. -Do we know where the alternate station power transformers are for our substations? Is this clearly noted? From SP&C: No known list that is quickly referenceable exists. What if any notes were recorded regarding the temperature at which the original switching was planned? No known notes existed. Were there warnings that the switching may not be possible in hotter temperature conditions? No warnings were noted What guidelines exist to direct operators to re-analyze switching in light of new weather conditions or date changes? All switching orders should be reanalyze before execution. NOTE: Current training and available tools to the operators limit the extent to which an operator can have the situational awareness required to annunciate the problems associated with this switching. Did we recheck any load measurements between original date and actual date of execution? NO Were the recorded loads at Green Pastures the current AD readings in the field or was that from history? Field readings Do the operators even have access to the AD reading history any longer? Yes, we view thru DAA What communication was passed between Control 1 and Control 2 verbally? It appears that Control 2 may have known that simply reclosing recloser 3198 was not going to resolve the problem/outage due to overload problems, but control 1 directed the closing of 3198, resulting in another burndown. Phone calls seem to indicate good communication between control 1 and 2 originally, but the information regarding the overload and cold pickup appears to have been lost at shift change and line crew rotation. |  |  |  | Metro Service Center | FALSE |  | FALSE | System Operations |  | Rachel Davis | Douglas Mack |  | Darrell Fuller | Please review | Darrell Fuller |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [8 empty] | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  | 16.05 Inadequate communication between shifts | conductor overload | 18. Failure to Check, Monitor | 9. Abnormal Operation
8971 | Metro Service Center | 2019-07-30 18:30 | (Potential conductor overload) On 7/29/19 the DCC executed an Order for switching M0888, potentially over loading conductor which may have contributed to conductor burning down on 7/30/19. This switching was requested to kill out a section of line on the Midway 29 so Transmission crews could drill a pear hole for a self-supporting transmission structure. DCC moved approximately 90amps of load from the Midway 29 to the Green Pasture 24. | Level 1 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Douglas Mack | 2019-09-16 08:34 | 2019-08-05 12:23 |  | 2019-09-13 18:33 | 2019-09-10 18:30 | 2019-08-05 11:24 | 2019-09-14 11:07 |  |  | Metro DCC |  |  | Cody Magby | very thorough investigation. cm | T&D Ops |  | Level 1 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Douglas Mack |  | Summary Potential Conductor Overload Monday, July 29, 2019 the DCC executed an order for Switching M-0888, potentially over loading conductor which may have contributed to conductor burning down Monday evening, July 29, 2019. The switching was requested to de-energize a section of line on Midway 852229 for Transmission crew to drill a pier hole for a self-supporting transmission structure. DCC moved 32.43% (approximately 90amps) of load from Midway 852229 to Green Pastures 845824. Timeline Monday, June 3, 2019 Request for Equipment 19-06-03090657 Job # 1646840 Requested by: Project Coordinator Boundaries of Line or Equipment Request: Midway 12.5kv Circuit 852229 from 600amp Switch 11622 ABC Phase to cut gaps North side of Lateral 18913 C Phase. Work to be done: De-Energize line for 10 days to drill and set self-supporting Transmission poles. DCC Operator 1, noted outage on 11 transformer stations to cut gaps North of Lateral 18913 DCC Operator 1 trended Midway 852229 circuit and highest peaks for the last month at 235Amp’s. Also, showed peaks on Green Pastures 845824 on ABC Phases dated for 6/3/2019 at 3:00pm Switching Order M-0888 signed by three DCC Operators Wednesday, July 15, 2019 at 12:33pm Line Foreman 1 advised DCC Operator 2, he drove the line out and needed to make changes to switching order he was also notified they will not perform switching until Monday, July 29, 2019 and will return switching order to normal on Thursday, August 1, 2019. DCC Operator 2 placed switching order in the Book and updated the dates for switching to be performed. Monday, July 29, 2019 at 7:49am Line Foreman 1 advised DCC Operator 3; he is ready to start Switching Order M-0888 that is scheduled. Power Quality Tech 1 will be assisting concerning the Regulators. Monday, July 29, 2019 at 7:56am Power Quality Tech 2 called into DCC requesting Switching Order M-0888 to help out Line Foreman 1 as well. Monday, July 29, 2019 at 8:58am DCC Operator 3 issued and directed switching order M-0888 to Power Quality Tech 1, Line Foreman 1 and Power Quality Tech 2 Monday, July 29, 2019 at 11:28am Switching Order M-0888 completed Monday, July 29, 2019 from 11:28a-6:32pm Per Revenue Protection Investigator, there were no low voltage events in Silver Springs prior to outage at 6:32pm on Green Pastures 5824 Monday, July 29, 2019 at 6:32pm Received outages in OMS (Outage Management System) until DCC Dispatcher 1, analyzed outage and opened Recloser 3198 located Choctaw RD & NE 75 in Arcadia on Green Pastures 845824 PD-07292019-00687 Monday, July 29, 2019 at 6:36pm DCC Dispatcher 1 dispatched Troubleshooter 1, accepted outage at 6:36pm. Monday, July 29, 2019 @ 6:39pm Customer Service sent a police/fire call (350 ticket) in Harrah, stated transformer blown, line down and grass fire. Monday, July 29, 2019 @ 7:04pm Transmission Operator 1 advised DCC Operator 2, Control Operator at Horseshoe he had an alternate station power alarm showing to be fed from Midway 2229. Transmission Operator 1 asked DCC Operator 2 if he has any problems on the feeder ? (Midway 2229) DCC Operator 2 advised he shows nothing on Midway 2229. Transmission Operator 1 does he thinks there is anything downstream that Control 1 can see. DCC Operator 2 transferred Transmission Operator 1 to Control 1. Monday, July 29, 2019 @ 7:06pm Transmission Operator 1, Senior System Operator advised he has an alarm at Horseshoe Lake Power Plant. It is loss of alternate station power. Showing alternate Station Power is fed from Midway 2229 circuit. DCC Dispatcher 1 advised he saw a ticket come in on Midway 2229 as soon as another outages came in on Green Pastures 5824 …there is a line down per police/ fire ticket that came in at 6:40pm. Transmission Operator 1, advised his alarm came in at 6:33pm. DCC Dispatcher 1, advised he had Trouble man in route and is showing178 customers offline. Transmission Operator 1 advised to have DCC contact him at 8166 when power is restored. Monday, July 29, 2019 @ 8:28pm Troubleshooter 1 advised to dispatch Linecrew will a roll of # 4 primary and some sleeves. There is broke #4 primary in 3 or 4 different spots. Not sure what caused it because there are no poles down. DCC Dispatcher 1 advised he thinks it was overloaded. Monday, July 29, 2019 @ 8:33pm Transmission Operator 1 wanted to know approximate ETR because he is still getting alarms from Horseshoe Lake Plant. DCC Operator 4, advised it may be a couple of hours. Monday, July 29, 2019 @ 8:33pm DCC Dispatcher 1 dispatched Line Foreman 2, to make repairs. Line Foreman 2 advised they will be at 24 hours at 1:00am Monday, July 29, 2019 @ 8:41pm Transmission Operator 1 conferenced call DCC Operator 4 in Control 2 and Operation Foreman at the Horseshoe Lake Plant, advised they are experiencing trouble with a feed to their deep wells that provide water to their units and also to their system lake make up and blow down. He wanted to know how long the outage will take so he can formulate a plan. Monday, July 29, 2019 @ 8:45pm DCC Dispatcher 1 called Transmission Operator 1 to advise the Troubleman found #4 primary line down and Linecrew is in route. Transmission Operator 1 asked for an ETR, DCC Dispatcher 1 gave Transmission Operator 1, Line Foreman 2’s contact information to get approximate ETR. Monday, July 29, 2019 @ 8:45pm DCC Operator 4 called Line Foreman 2 asking for an ETR. Line Foreman 2 informed him it will take an hour to get onsite and maybe approximately 2 hours to make repairs. Monday, July 29, 2019 @ 8:48pm DCC Dispatcher 1 called Troubleshooter 1 advised Control 2 is needing a switchman because the Horseshoe Lake Plant was losing their water supply. Monday, July 29, 2019 @ 8:50pm DCC Operator 4 called Troubleshooter 1 informed him that he needed a switchman to perform switching to pick up the water well for the Horseshoe Lake Plant. Monday, July 29, 2019 @ 9:30pm Troubleshooter 1 advised DCC Operator 4 he found a Switch Danger Tagged and grounded. Troubleshooter 1 advised the Danger Tagged stated do not operate. DCC Operator 4 agreed there are jumpers lifted south of the Switch and that is why the Switch is grounded and the maps had not been updated. Monday, July 29, 2019 @ 9:32pm DCC Operator 4 called Transmission Operator 1 and stated he cannot pick up the wells at Horseshoe Lake Plant. There are jumpers lifted south of the Switch and there no way to back feed because of the Highway Project. The ETR will be approximately 11:30pm Monday, July 29, 2019 @ 9:44pm Technical Support Rep., asked what the ETR was for the Harrah outage? He advised on the customer’s account is saying 9:57pm. DCC Dispatcher 1 advised OMS is showing 10:57pm and will adjust it to 11:57pm. Monday, July 29, 2019 @ 9:56pm DCC Supervisor, called in and spoke with DCC Dispatcher 1 to find out the cause of the outage on Green Pastures. DCC Dispatcher 1 advised there is #4 primary line down in three different places. DCC Supervisor asked if the wire was down due to load? It will not do any good if the linecrew makes repairs it will potentially burn down again if the Green Pastures circuit is overloaded. Also, the DCC Supervisor advised the Dispatcher to check with DCC Operator 4 to see if there are any options, he can get the load off Green Pastures. Monday, July 29, 2019 @ 10:02pm DCC Supervisor, spoke with DCC Operator 4 asking what the options are to restore Green Pastures. DCC Operator 4 advised he attempted to perform switching to get the Horseshoe Lake Plant water pumps back online because they are losing their water supply but switching was done (M-0888), jumpers lifted and grounds in place south of the Switch. Tuesday, July 30, 2019 @ 12:19am DCC Operator 4 called Line Foreman 2 asking for an ETR update Horseshoe Lake Plant is making inquiries. Line Foreman 2 advised they are pulling their first set of grounds approximate time is 30 minutes. Tuesday, July 30, 2019 @ 12:20am DCC Operator 4 advised Transmission Operator 1 the line crew are pulling their ground and ETR to should 30 minutes. Tuesday, July 30, 2019 @ 12:40am DCC Dispatcher 2, gave Line Foreman 2 permission to close Recloser 3198 Tuesday, July 30, 2019 @ 12:46am Line Foreman 2 advised A Phase did not hold and there is a fire. Line Foreman 2 added they are at 24 hours and 15 minutes and is requesting to send another Linecrew to relieve him and his crew. Tuesday, July 30, 2019 @ 12:53am DCC Dispatcher 2 dispatched Linecrew Foreman, Line Foreman 3, truck 530 to relieve Line Foreman 2 and his crew. Tuesday, July 30, 2019 @ 02:08am DCC Operator 4 advised Transmission Operator 1 that Line Foreman 2 attempted to close Recloser 3198 - it burnt down some more wire. Line Foreman 2 timed out and, Line Foreman 3 heading from Shawnee will be onsite in 20 minutes. Tuesday, July 30, 2019 @ 04:44am Transmission Operator 1 advised he will be leaving soon and to contact his relief in the TCC when circuit is restored because this is their alternate feed to Horseshoe Lake Plant. Tuesday, July 30, 2019 @ 6:50am DCC Operator 4 advised Senior System Operator, Transmission Operator 2 in Transmission Control Center (TCC) repairs made and power restored at 6:50am. Senior Operator, DCC Operator 4 wrote handwritten switching to restore outage on Recloser 3198 in Sections due to cold load pickup on Green Pastures 5824 Overall Outage: 12 hours 52 Minutes Other Relevant Information: -What voltages do meter view show on the affected area from 1130 on 7/29 to 0700 7/30? NOTE: Meter view data is populated day after and is not a tool in use by the DCC for day to day situational awareness. Charts below shows the average hourly voltage for meters and what percentage of customers are below a certain voltage value. -How much load do we think was actually on the #4 that burned down? Use TLM or escalation tools from planning. Distribution planning did a study using the switching order and locations where the line burned down: Approx. 100-120 amps per phase on the burned down conductor was shown on the study. #4 ACSR is rated for 140 amps. It is not clear how closely the model reflects real world conditions particularly when the voltages were as far from normal as indicated by meter measurements. It is possible that the line was not overloaded for its normal condition and use, but perhaps weak points existed (mechanical damage from previous fault events or improperly installed jumpers, splices etc.) that caused it to fail at an amperage that was less than expected. Regardless, the voltage data following the switching event shows that this operating condition was not desirable. DMS system shows reasonably well how much load was transferred to green pastures both in SCADA telemetry and power flow, but because Green Pastures is non-scada, we do not have a good estimate of what load was on the Green Pastures circuit during the event. Distribution planning pulled data sources together manually that we do not currently have in DMS to provide this estimate. -Did OMS receive any customer calls complaining of low voltage? No customer calls for low voltage were received. -What is the definition of a meter event for low voltage (duration, magnitude etc.) in silver springs? what is the definition of a meter event for low voltage? a. For the I210+c meters (NEW METERS ARE PROGRAMMED) i. SAG = 8% voltage less than the nominal voltage for a minimum of 1 second – No AMM Alarm – PQ read only ii. SWELL = 6% voltage greater than nominal voltage for a minimum of 1 second– No AMM Alarm – PQ read only iii. Under Voltage Alert is 10% voltage less than the nominal voltage for 15 minutes or more – this is the same as a CA 000400 = Low Potential on I210+c this alert comes in from AMM iv. Over Voltage Alert is 8% voltage more than the nominal voltage for 15 minutes or more – this comes in from AMM as I210C over Voltage Diagnostic 7 Set b. For the KV2c Meters (NEW METERS ARE PROGRAMMED) i. SAG = 8% voltage less than the nominal voltage for a minimum of 4 cycles – No AMM Alarm – PQ read only ii. SWELL = 6% voltage greater than nominal voltage for a minimum of 4 cycles - No AMM Alarm – PQ read only iii. Under Voltage Alert is 10% voltage less than the nominal voltage for 15 minutes or more – this alert comes in from AMM iv. Over Voltage Alert is 8% voltage more than the nominal voltage for 15 minutes or more – this alert comes in from AMM v. c. For the I210+c meters (METERS WERE ORIGINALLY PROGRAMMED) i. SAG = 10% voltage less than the nominal voltage for a minimum of 1 second – No AMM Alarm – PQ read only ii. SWELL = 10% voltage greater than nominal voltage for a minimum of 1 second– No AMM Alarm – PQ read only iii. Under Voltage Alert is 15% voltage less than the nominal voltage for 3 seconds more – this is the same as a CA 000400 = Low Potential on I210+c this alert comes in from AMM iv. Over Voltage Alert is 10% voltage more than the nominal voltage for 3 seconds more – this comes in from AMM as I210C over Voltage Diagnostic 7 Set d. For the KV2c Meters (METERS WERE ORIGINALLY PROGRAMMED) i. SAG = 10% voltage less than the nominal voltage for a minimum of 4 cycles – No AMM Alarm – PQ read only ii. SWELL = 10% voltage greater than nominal voltage for a minimum of 4 cycles - No AMM Alarm – PQ read only iii. Under Voltage Alert is 10% voltage less than the nominal voltage for 10 seconds or more – this alert comes in from AMM iv. Over Voltage Alert is 10% voltage more than the nominal voltage for 10 seconds or more - this alert comes in from AMM NOTE: The alerts received are read with normal data reads. They do not come in near realtime. It appears that the voltages were not low enough prior to the burn down to reliably trigger meter events if they are mostly programmed at +/-10% from nominal. -Is anything done with a low voltage meter event when it is received? Not on a consistent basis in any OG&E workgroup. Occasional use for data anomalies. There are some others in the company looking at voltages from other points of view such as revenue protection. -Do we know where the alternate station power transformers are for our substations? Is this clearly noted? From SP&C: No known list that is quickly referenceable exists. What if any notes were recorded regarding the temperature at which the original switching was planned? No known notes existed. Were there warnings that the switching may not be possible in hotter temperature conditions? No warnings were noted What guidelines exist to direct operators to re-analyze switching in light of new weather conditions or date changes? All switching orders should be reanalyze before execution. NOTE: Current training and available tools to the operators limit the extent to which an operator can have the situational awareness required to annunciate the problems associated with this switching. Did we recheck any load measurements between original date and actual date of execution? NO Were the recorded loads at Green Pastures the current AD readings in the field or was that from history? Field readings Do the operators even have access to the AD reading history any longer? Yes, we view thru DAA What communication was passed between Control 1 and Control 2 verbally? It appears that Control 2 may have known that simply reclosing recloser 3198 was not going to resolve the problem/outage due to overload problems, but control 1 directed the closing of 3198, resulting in another burndown. Phone calls seem to indicate good communication between control 1 and 2 originally, but the information regarding the overload and cold pickup appears to have been lost at shift change and line crew rotation. |  |  |  | Metro Service Center | FALSE |  | FALSE | System Operations |  | Rachel Davis | Douglas Mack |  | Darrell Fuller | Please review | Darrell Fuller |  | Low |  |  |  |  | 5.01 Lack of experience | 6.05 Inadequate review instruction | [10 empty] | Overloaded conductor | 08. Improper Loading | 12. Equipment Failure
8971 | Metro Service Center | 2019-07-30 18:30 | (Potential conductor overload) On 7/29/19 the DCC executed an Order for switching M0888, potentially over loading conductor which may have contributed to conductor burning down on 7/30/19. This switching was requested to kill out a section of line on the Midway 29 so Transmission crews could drill a pear hole for a self-supporting transmission structure. DCC moved approximately 90amps of load from the Midway 29 to the Green Pasture 24. | Level 1 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Douglas Mack | 2019-09-16 08:34 | 2019-08-05 12:23 |  | 2019-09-13 18:33 | 2019-09-10 18:30 | 2019-08-05 11:24 | 2019-09-14 11:07 |  |  | Metro DCC |  |  | Cody Magby | very thorough investigation. cm | T&D Ops |  | Level 1 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Douglas Mack |  | Summary Potential Conductor Overload Monday, July 29, 2019 the DCC executed an order for Switching M-0888, potentially over loading conductor which may have contributed to conductor burning down Monday evening, July 29, 2019. The switching was requested to de-energize a section of line on Midway 852229 for Transmission crew to drill a pier hole for a self-supporting transmission structure. DCC moved 32.43% (approximately 90amps) of load from Midway 852229 to Green Pastures 845824. Timeline Monday, June 3, 2019 Request for Equipment 19-06-03090657 Job # 1646840 Requested by: Project Coordinator Boundaries of Line or Equipment Request: Midway 12.5kv Circuit 852229 from 600amp Switch 11622 ABC Phase to cut gaps North side of Lateral 18913 C Phase. Work to be done: De-Energize line for 10 days to drill and set self-supporting Transmission poles. DCC Operator 1, noted outage on 11 transformer stations to cut gaps North of Lateral 18913 DCC Operator 1 trended Midway 852229 circuit and highest peaks for the last month at 235Amp’s. Also, showed peaks on Green Pastures 845824 on ABC Phases dated for 6/3/2019 at 3:00pm Switching Order M-0888 signed by three DCC Operators Wednesday, July 15, 2019 at 12:33pm Line Foreman 1 advised DCC Operator 2, he drove the line out and needed to make changes to switching order he was also notified they will not perform switching until Monday, July 29, 2019 and will return switching order to normal on Thursday, August 1, 2019. DCC Operator 2 placed switching order in the Book and updated the dates for switching to be performed. Monday, July 29, 2019 at 7:49am Line Foreman 1 advised DCC Operator 3; he is ready to start Switching Order M-0888 that is scheduled. Power Quality Tech 1 will be assisting concerning the Regulators. Monday, July 29, 2019 at 7:56am Power Quality Tech 2 called into DCC requesting Switching Order M-0888 to help out Line Foreman 1 as well. Monday, July 29, 2019 at 8:58am DCC Operator 3 issued and directed switching order M-0888 to Power Quality Tech 1, Line Foreman 1 and Power Quality Tech 2 Monday, July 29, 2019 at 11:28am Switching Order M-0888 completed Monday, July 29, 2019 from 11:28a-6:32pm Per Revenue Protection Investigator, there were no low voltage events in Silver Springs prior to outage at 6:32pm on Green Pastures 5824 Monday, July 29, 2019 at 6:32pm Received outages in OMS (Outage Management System) until DCC Dispatcher 1, analyzed outage and opened Recloser 3198 located Choctaw RD & NE 75 in Arcadia on Green Pastures 845824 PD-07292019-00687 Monday, July 29, 2019 at 6:36pm DCC Dispatcher 1 dispatched Troubleshooter 1, accepted outage at 6:36pm. Monday, July 29, 2019 @ 6:39pm Customer Service sent a police/fire call (350 ticket) in Harrah, stated transformer blown, line down and grass fire. Monday, July 29, 2019 @ 7:04pm Transmission Operator 1 advised DCC Operator 2, Control Operator at Horseshoe he had an alternate station power alarm showing to be fed from Midway 2229. Transmission Operator 1 asked DCC Operator 2 if he has any problems on the feeder ? (Midway 2229) DCC Operator 2 advised he shows nothing on Midway 2229. Transmission Operator 1 does he thinks there is anything downstream that Control 1 can see. DCC Operator 2 transferred Transmission Operator 1 to Control 1. Monday, July 29, 2019 @ 7:06pm Transmission Operator 1, Senior System Operator advised he has an alarm at Horseshoe Lake Power Plant. It is loss of alternate station power. Showing alternate Station Power is fed from Midway 2229 circuit. DCC Dispatcher 1 advised he saw a ticket come in on Midway 2229 as soon as another outages came in on Green Pastures 5824 …there is a line down per police/ fire ticket that came in at 6:40pm. Transmission Operator 1, advised his alarm came in at 6:33pm. DCC Dispatcher 1, advised he had Trouble man in route and is showing178 customers offline. Transmission Operator 1 advised to have DCC contact him at 8166 when power is restored. Monday, July 29, 2019 @ 8:28pm Troubleshooter 1 advised to dispatch Linecrew will a roll of # 4 primary and some sleeves. There is broke #4 primary in 3 or 4 different spots. Not sure what caused it because there are no poles down. DCC Dispatcher 1 advised he thinks it was overloaded. Monday, July 29, 2019 @ 8:33pm Transmission Operator 1 wanted to know approximate ETR because he is still getting alarms from Horseshoe Lake Plant. DCC Operator 4, advised it may be a couple of hours. Monday, July 29, 2019 @ 8:33pm DCC Dispatcher 1 dispatched Line Foreman 2, to make repairs. Line Foreman 2 advised they will be at 24 hours at 1:00am Monday, July 29, 2019 @ 8:41pm Transmission Operator 1 conferenced call DCC Operator 4 in Control 2 and Operation Foreman at the Horseshoe Lake Plant, advised they are experiencing trouble with a feed to their deep wells that provide water to their units and also to their system lake make up and blow down. He wanted to know how long the outage will take so he can formulate a plan. Monday, July 29, 2019 @ 8:45pm DCC Dispatcher 1 called Transmission Operator 1 to advise the Troubleman found #4 primary line down and Linecrew is in route. Transmission Operator 1 asked for an ETR, DCC Dispatcher 1 gave Transmission Operator 1, Line Foreman 2’s contact information to get approximate ETR. Monday, July 29, 2019 @ 8:45pm DCC Operator 4 called Line Foreman 2 asking for an ETR. Line Foreman 2 informed him it will take an hour to get onsite and maybe approximately 2 hours to make repairs. Monday, July 29, 2019 @ 8:48pm DCC Dispatcher 1 called Troubleshooter 1 advised Control 2 is needing a switchman because the Horseshoe Lake Plant was losing their water supply. Monday, July 29, 2019 @ 8:50pm DCC Operator 4 called Troubleshooter 1 informed him that he needed a switchman to perform switching to pick up the water well for the Horseshoe Lake Plant. Monday, July 29, 2019 @ 9:30pm Troubleshooter 1 advised DCC Operator 4 he found a Switch Danger Tagged and grounded. Troubleshooter 1 advised the Danger Tagged stated do not operate. DCC Operator 4 agreed there are jumpers lifted south of the Switch and that is why the Switch is grounded and the maps had not been updated. Monday, July 29, 2019 @ 9:32pm DCC Operator 4 called Transmission Operator 1 and stated he cannot pick up the wells at Horseshoe Lake Plant. There are jumpers lifted south of the Switch and there no way to back feed because of the Highway Project. The ETR will be approximately 11:30pm Monday, July 29, 2019 @ 9:44pm Technical Support Rep., asked what the ETR was for the Harrah outage? He advised on the customer’s account is saying 9:57pm. DCC Dispatcher 1 advised OMS is showing 10:57pm and will adjust it to 11:57pm. Monday, July 29, 2019 @ 9:56pm DCC Supervisor, called in and spoke with DCC Dispatcher 1 to find out the cause of the outage on Green Pastures. DCC Dispatcher 1 advised there is #4 primary line down in three different places. DCC Supervisor asked if the wire was down due to load? It will not do any good if the linecrew makes repairs it will potentially burn down again if the Green Pastures circuit is overloaded. Also, the DCC Supervisor advised the Dispatcher to check with DCC Operator 4 to see if there are any options, he can get the load off Green Pastures. Monday, July 29, 2019 @ 10:02pm DCC Supervisor, spoke with DCC Operator 4 asking what the options are to restore Green Pastures. DCC Operator 4 advised he attempted to perform switching to get the Horseshoe Lake Plant water pumps back online because they are losing their water supply but switching was done (M-0888), jumpers lifted and grounds in place south of the Switch. Tuesday, July 30, 2019 @ 12:19am DCC Operator 4 called Line Foreman 2 asking for an ETR update Horseshoe Lake Plant is making inquiries. Line Foreman 2 advised they are pulling their first set of grounds approximate time is 30 minutes. Tuesday, July 30, 2019 @ 12:20am DCC Operator 4 advised Transmission Operator 1 the line crew are pulling their ground and ETR to should 30 minutes. Tuesday, July 30, 2019 @ 12:40am DCC Dispatcher 2, gave Line Foreman 2 permission to close Recloser 3198 Tuesday, July 30, 2019 @ 12:46am Line Foreman 2 advised A Phase did not hold and there is a fire. Line Foreman 2 added they are at 24 hours and 15 minutes and is requesting to send another Linecrew to relieve him and his crew. Tuesday, July 30, 2019 @ 12:53am DCC Dispatcher 2 dispatched Linecrew Foreman, Line Foreman 3, truck 530 to relieve Line Foreman 2 and his crew. Tuesday, July 30, 2019 @ 02:08am DCC Operator 4 advised Transmission Operator 1 that Line Foreman 2 attempted to close Recloser 3198 - it burnt down some more wire. Line Foreman 2 timed out and, Line Foreman 3 heading from Shawnee will be onsite in 20 minutes. Tuesday, July 30, 2019 @ 04:44am Transmission Operator 1 advised he will be leaving soon and to contact his relief in the TCC when circuit is restored because this is their alternate feed to Horseshoe Lake Plant. Tuesday, July 30, 2019 @ 6:50am DCC Operator 4 advised Senior System Operator, Transmission Operator 2 in Transmission Control Center (TCC) repairs made and power restored at 6:50am. Senior Operator, DCC Operator 4 wrote handwritten switching to restore outage on Recloser 3198 in Sections due to cold load pickup on Green Pastures 5824 Overall Outage: 12 hours 52 Minutes Other Relevant Information: -What voltages do meter view show on the affected area from 1130 on 7/29 to 0700 7/30? NOTE: Meter view data is populated day after and is not a tool in use by the DCC for day to day situational awareness. Charts below shows the average hourly voltage for meters and what percentage of customers are below a certain voltage value. -How much load do we think was actually on the #4 that burned down? Use TLM or escalation tools from planning. Distribution planning did a study using the switching order and locations where the line burned down: Approx. 100-120 amps per phase on the burned down conductor was shown on the study. #4 ACSR is rated for 140 amps. It is not clear how closely the model reflects real world conditions particularly when the voltages were as far from normal as indicated by meter measurements. It is possible that the line was not overloaded for its normal condition and use, but perhaps weak points existed (mechanical damage from previous fault events or improperly installed jumpers, splices etc.) that caused it to fail at an amperage that was less than expected. Regardless, the voltage data following the switching event shows that this operating condition was not desirable. DMS system shows reasonably well how much load was transferred to green pastures both in SCADA telemetry and power flow, but because Green Pastures is non-scada, we do not have a good estimate of what load was on the Green Pastures circuit during the event. Distribution planning pulled data sources together manually that we do not currently have in DMS to provide this estimate. -Did OMS receive any customer calls complaining of low voltage? No customer calls for low voltage were received. -What is the definition of a meter event for low voltage (duration, magnitude etc.) in silver springs? what is the definition of a meter event for low voltage? a. For the I210+c meters (NEW METERS ARE PROGRAMMED) i. SAG = 8% voltage less than the nominal voltage for a minimum of 1 second – No AMM Alarm – PQ read only ii. SWELL = 6% voltage greater than nominal voltage for a minimum of 1 second– No AMM Alarm – PQ read only iii. Under Voltage Alert is 10% voltage less than the nominal voltage for 15 minutes or more – this is the same as a CA 000400 = Low Potential on I210+c this alert comes in from AMM iv. Over Voltage Alert is 8% voltage more than the nominal voltage for 15 minutes or more – this comes in from AMM as I210C over Voltage Diagnostic 7 Set b. For the KV2c Meters (NEW METERS ARE PROGRAMMED) i. SAG = 8% voltage less than the nominal voltage for a minimum of 4 cycles – No AMM Alarm – PQ read only ii. SWELL = 6% voltage greater than nominal voltage for a minimum of 4 cycles - No AMM Alarm – PQ read only iii. Under Voltage Alert is 10% voltage less than the nominal voltage for 15 minutes or more – this alert comes in from AMM iv. Over Voltage Alert is 8% voltage more than the nominal voltage for 15 minutes or more – this alert comes in from AMM v. c. For the I210+c meters (METERS WERE ORIGINALLY PROGRAMMED) i. SAG = 10% voltage less than the nominal voltage for a minimum of 1 second – No AMM Alarm – PQ read only ii. SWELL = 10% voltage greater than nominal voltage for a minimum of 1 second– No AMM Alarm – PQ read only iii. Under Voltage Alert is 15% voltage less than the nominal voltage for 3 seconds more – this is the same as a CA 000400 = Low Potential on I210+c this alert comes in from AMM iv. Over Voltage Alert is 10% voltage more than the nominal voltage for 3 seconds more – this comes in from AMM as I210C over Voltage Diagnostic 7 Set d. For the KV2c Meters (METERS WERE ORIGINALLY PROGRAMMED) i. SAG = 10% voltage less than the nominal voltage for a minimum of 4 cycles – No AMM Alarm – PQ read only ii. SWELL = 10% voltage greater than nominal voltage for a minimum of 4 cycles - No AMM Alarm – PQ read only iii. Under Voltage Alert is 10% voltage less than the nominal voltage for 10 seconds or more – this alert comes in from AMM iv. Over Voltage Alert is 10% voltage more than the nominal voltage for 10 seconds or more - this alert comes in from AMM NOTE: The alerts received are read with normal data reads. They do not come in near realtime. It appears that the voltages were not low enough prior to the burn down to reliably trigger meter events if they are mostly programmed at +/-10% from nominal. -Is anything done with a low voltage meter event when it is received? Not on a consistent basis in any OG&E workgroup. Occasional use for data anomalies. There are some others in the company looking at voltages from other points of view such as revenue protection. -Do we know where the alternate station power transformers are for our substations? Is this clearly noted? From SP&C: No known list that is quickly referenceable exists. What if any notes were recorded regarding the temperature at which the original switching was planned? No known notes existed. Were there warnings that the switching may not be possible in hotter temperature conditions? No warnings were noted What guidelines exist to direct operators to re-analyze switching in light of new weather conditions or date changes? All switching orders should be reanalyze before execution. NOTE: Current training and available tools to the operators limit the extent to which an operator can have the situational awareness required to annunciate the problems associated with this switching. Did we recheck any load measurements between original date and actual date of execution? NO Were the recorded loads at Green Pastures the current AD readings in the field or was that from history? Field readings Do the operators even have access to the AD reading history any longer? Yes, we view thru DAA What communication was passed between Control 1 and Control 2 verbally? It appears that Control 2 may have known that simply reclosing recloser 3198 was not going to resolve the problem/outage due to overload problems, but control 1 directed the closing of 3198, resulting in another burndown. Phone calls seem to indicate good communication between control 1 and 2 originally, but the information regarding the overload and cold pickup appears to have been lost at shift change and line crew rotation. |  |  |  | Metro Service Center | FALSE |  | FALSE | System Operations |  | Rachel Davis | Douglas Mack |  | Darrell Fuller | Please review | Darrell Fuller |  | Low |  |  |  |  | 5.03 Inadequate initial training | 6.05 Inadequate review instruction | [10 empty] | Overloaded conductor | 08. Improper Loading | 12. Equipment Failure
8971 | Metro Service Center | 2019-07-30 18:30 | (Potential conductor overload) On 7/29/19 the DCC executed an Order for switching M0888, potentially over loading conductor which may have contributed to conductor burning down on 7/30/19. This switching was requested to kill out a section of line on the Midway 29 so Transmission crews could drill a pear hole for a self-supporting transmission structure. DCC moved approximately 90amps of load from the Midway 29 to the Green Pasture 24. | Level 1 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Douglas Mack | 2019-09-16 08:34 | 2019-08-05 12:23 |  | 2019-09-13 18:33 | 2019-09-10 18:30 | 2019-08-05 11:24 | 2019-09-14 11:07 |  |  | Metro DCC |  |  | Cody Magby | very thorough investigation. cm | T&D Ops |  | Level 1 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Douglas Mack |  | Summary Potential Conductor Overload Monday, July 29, 2019 the DCC executed an order for Switching M-0888, potentially over loading conductor which may have contributed to conductor burning down Monday evening, July 29, 2019. The switching was requested to de-energize a section of line on Midway 852229 for Transmission crew to drill a pier hole for a self-supporting transmission structure. DCC moved 32.43% (approximately 90amps) of load from Midway 852229 to Green Pastures 845824. Timeline Monday, June 3, 2019 Request for Equipment 19-06-03090657 Job # 1646840 Requested by: Project Coordinator Boundaries of Line or Equipment Request: Midway 12.5kv Circuit 852229 from 600amp Switch 11622 ABC Phase to cut gaps North side of Lateral 18913 C Phase. Work to be done: De-Energize line for 10 days to drill and set self-supporting Transmission poles. DCC Operator 1, noted outage on 11 transformer stations to cut gaps North of Lateral 18913 DCC Operator 1 trended Midway 852229 circuit and highest peaks for the last month at 235Amp’s. Also, showed peaks on Green Pastures 845824 on ABC Phases dated for 6/3/2019 at 3:00pm Switching Order M-0888 signed by three DCC Operators Wednesday, July 15, 2019 at 12:33pm Line Foreman 1 advised DCC Operator 2, he drove the line out and needed to make changes to switching order he was also notified they will not perform switching until Monday, July 29, 2019 and will return switching order to normal on Thursday, August 1, 2019. DCC Operator 2 placed switching order in the Book and updated the dates for switching to be performed. Monday, July 29, 2019 at 7:49am Line Foreman 1 advised DCC Operator 3; he is ready to start Switching Order M-0888 that is scheduled. Power Quality Tech 1 will be assisting concerning the Regulators. Monday, July 29, 2019 at 7:56am Power Quality Tech 2 called into DCC requesting Switching Order M-0888 to help out Line Foreman 1 as well. Monday, July 29, 2019 at 8:58am DCC Operator 3 issued and directed switching order M-0888 to Power Quality Tech 1, Line Foreman 1 and Power Quality Tech 2 Monday, July 29, 2019 at 11:28am Switching Order M-0888 completed Monday, July 29, 2019 from 11:28a-6:32pm Per Revenue Protection Investigator, there were no low voltage events in Silver Springs prior to outage at 6:32pm on Green Pastures 5824 Monday, July 29, 2019 at 6:32pm Received outages in OMS (Outage Management System) until DCC Dispatcher 1, analyzed outage and opened Recloser 3198 located Choctaw RD & NE 75 in Arcadia on Green Pastures 845824 PD-07292019-00687 Monday, July 29, 2019 at 6:36pm DCC Dispatcher 1 dispatched Troubleshooter 1, accepted outage at 6:36pm. Monday, July 29, 2019 @ 6:39pm Customer Service sent a police/fire call (350 ticket) in Harrah, stated transformer blown, line down and grass fire. Monday, July 29, 2019 @ 7:04pm Transmission Operator 1 advised DCC Operator 2, Control Operator at Horseshoe he had an alternate station power alarm showing to be fed from Midway 2229. Transmission Operator 1 asked DCC Operator 2 if he has any problems on the feeder ? (Midway 2229) DCC Operator 2 advised he shows nothing on Midway 2229. Transmission Operator 1 does he thinks there is anything downstream that Control 1 can see. DCC Operator 2 transferred Transmission Operator 1 to Control 1. Monday, July 29, 2019 @ 7:06pm Transmission Operator 1, Senior System Operator advised he has an alarm at Horseshoe Lake Power Plant. It is loss of alternate station power. Showing alternate Station Power is fed from Midway 2229 circuit. DCC Dispatcher 1 advised he saw a ticket come in on Midway 2229 as soon as another outages came in on Green Pastures 5824 …there is a line down per police/ fire ticket that came in at 6:40pm. Transmission Operator 1, advised his alarm came in at 6:33pm. DCC Dispatcher 1, advised he had Trouble man in route and is showing178 customers offline. Transmission Operator 1 advised to have DCC contact him at 8166 when power is restored. Monday, July 29, 2019 @ 8:28pm Troubleshooter 1 advised to dispatch Linecrew will a roll of # 4 primary and some sleeves. There is broke #4 primary in 3 or 4 different spots. Not sure what caused it because there are no poles down. DCC Dispatcher 1 advised he thinks it was overloaded. Monday, July 29, 2019 @ 8:33pm Transmission Operator 1 wanted to know approximate ETR because he is still getting alarms from Horseshoe Lake Plant. DCC Operator 4, advised it may be a couple of hours. Monday, July 29, 2019 @ 8:33pm DCC Dispatcher 1 dispatched Line Foreman 2, to make repairs. Line Foreman 2 advised they will be at 24 hours at 1:00am Monday, July 29, 2019 @ 8:41pm Transmission Operator 1 conferenced call DCC Operator 4 in Control 2 and Operation Foreman at the Horseshoe Lake Plant, advised they are experiencing trouble with a feed to their deep wells that provide water to their units and also to their system lake make up and blow down. He wanted to know how long the outage will take so he can formulate a plan. Monday, July 29, 2019 @ 8:45pm DCC Dispatcher 1 called Transmission Operator 1 to advise the Troubleman found #4 primary line down and Linecrew is in route. Transmission Operator 1 asked for an ETR, DCC Dispatcher 1 gave Transmission Operator 1, Line Foreman 2’s contact information to get approximate ETR. Monday, July 29, 2019 @ 8:45pm DCC Operator 4 called Line Foreman 2 asking for an ETR. Line Foreman 2 informed him it will take an hour to get onsite and maybe approximately 2 hours to make repairs. Monday, July 29, 2019 @ 8:48pm DCC Dispatcher 1 called Troubleshooter 1 advised Control 2 is needing a switchman because the Horseshoe Lake Plant was losing their water supply. Monday, July 29, 2019 @ 8:50pm DCC Operator 4 called Troubleshooter 1 informed him that he needed a switchman to perform switching to pick up the water well for the Horseshoe Lake Plant. Monday, July 29, 2019 @ 9:30pm Troubleshooter 1 advised DCC Operator 4 he found a Switch Danger Tagged and grounded. Troubleshooter 1 advised the Danger Tagged stated do not operate. DCC Operator 4 agreed there are jumpers lifted south of the Switch and that is why the Switch is grounded and the maps had not been updated. Monday, July 29, 2019 @ 9:32pm DCC Operator 4 called Transmission Operator 1 and stated he cannot pick up the wells at Horseshoe Lake Plant. There are jumpers lifted south of the Switch and there no way to back feed because of the Highway Project. The ETR will be approximately 11:30pm Monday, July 29, 2019 @ 9:44pm Technical Support Rep., asked what the ETR was for the Harrah outage? He advised on the customer’s account is saying 9:57pm. DCC Dispatcher 1 advised OMS is showing 10:57pm and will adjust it to 11:57pm. Monday, July 29, 2019 @ 9:56pm DCC Supervisor, called in and spoke with DCC Dispatcher 1 to find out the cause of the outage on Green Pastures. DCC Dispatcher 1 advised there is #4 primary line down in three different places. DCC Supervisor asked if the wire was down due to load? It will not do any good if the linecrew makes repairs it will potentially burn down again if the Green Pastures circuit is overloaded. Also, the DCC Supervisor advised the Dispatcher to check with DCC Operator 4 to see if there are any options, he can get the load off Green Pastures. Monday, July 29, 2019 @ 10:02pm DCC Supervisor, spoke with DCC Operator 4 asking what the options are to restore Green Pastures. DCC Operator 4 advised he attempted to perform switching to get the Horseshoe Lake Plant water pumps back online because they are losing their water supply but switching was done (M-0888), jumpers lifted and grounds in place south of the Switch. Tuesday, July 30, 2019 @ 12:19am DCC Operator 4 called Line Foreman 2 asking for an ETR update Horseshoe Lake Plant is making inquiries. Line Foreman 2 advised they are pulling their first set of grounds approximate time is 30 minutes. Tuesday, July 30, 2019 @ 12:20am DCC Operator 4 advised Transmission Operator 1 the line crew are pulling their ground and ETR to should 30 minutes. Tuesday, July 30, 2019 @ 12:40am DCC Dispatcher 2, gave Line Foreman 2 permission to close Recloser 3198 Tuesday, July 30, 2019 @ 12:46am Line Foreman 2 advised A Phase did not hold and there is a fire. Line Foreman 2 added they are at 24 hours and 15 minutes and is requesting to send another Linecrew to relieve him and his crew. Tuesday, July 30, 2019 @ 12:53am DCC Dispatcher 2 dispatched Linecrew Foreman, Line Foreman 3, truck 530 to relieve Line Foreman 2 and his crew. Tuesday, July 30, 2019 @ 02:08am DCC Operator 4 advised Transmission Operator 1 that Line Foreman 2 attempted to close Recloser 3198 - it burnt down some more wire. Line Foreman 2 timed out and, Line Foreman 3 heading from Shawnee will be onsite in 20 minutes. Tuesday, July 30, 2019 @ 04:44am Transmission Operator 1 advised he will be leaving soon and to contact his relief in the TCC when circuit is restored because this is their alternate feed to Horseshoe Lake Plant. Tuesday, July 30, 2019 @ 6:50am DCC Operator 4 advised Senior System Operator, Transmission Operator 2 in Transmission Control Center (TCC) repairs made and power restored at 6:50am. Senior Operator, DCC Operator 4 wrote handwritten switching to restore outage on Recloser 3198 in Sections due to cold load pickup on Green Pastures 5824 Overall Outage: 12 hours 52 Minutes Other Relevant Information: -What voltages do meter view show on the affected area from 1130 on 7/29 to 0700 7/30? NOTE: Meter view data is populated day after and is not a tool in use by the DCC for day to day situational awareness. Charts below shows the average hourly voltage for meters and what percentage of customers are below a certain voltage value. -How much load do we think was actually on the #4 that burned down? Use TLM or escalation tools from planning. Distribution planning did a study using the switching order and locations where the line burned down: Approx. 100-120 amps per phase on the burned down conductor was shown on the study. #4 ACSR is rated for 140 amps. It is not clear how closely the model reflects real world conditions particularly when the voltages were as far from normal as indicated by meter measurements. It is possible that the line was not overloaded for its normal condition and use, but perhaps weak points existed (mechanical damage from previous fault events or improperly installed jumpers, splices etc.) that caused it to fail at an amperage that was less than expected. Regardless, the voltage data following the switching event shows that this operating condition was not desirable. DMS system shows reasonably well how much load was transferred to green pastures both in SCADA telemetry and power flow, but because Green Pastures is non-scada, we do not have a good estimate of what load was on the Green Pastures circuit during the event. Distribution planning pulled data sources together manually that we do not currently have in DMS to provide this estimate. -Did OMS receive any customer calls complaining of low voltage? No customer calls for low voltage were received. -What is the definition of a meter event for low voltage (duration, magnitude etc.) in silver springs? what is the definition of a meter event for low voltage? a. For the I210+c meters (NEW METERS ARE PROGRAMMED) i. SAG = 8% voltage less than the nominal voltage for a minimum of 1 second – No AMM Alarm – PQ read only ii. SWELL = 6% voltage greater than nominal voltage for a minimum of 1 second– No AMM Alarm – PQ read only iii. Under Voltage Alert is 10% voltage less than the nominal voltage for 15 minutes or more – this is the same as a CA 000400 = Low Potential on I210+c this alert comes in from AMM iv. Over Voltage Alert is 8% voltage more than the nominal voltage for 15 minutes or more – this comes in from AMM as I210C over Voltage Diagnostic 7 Set b. For the KV2c Meters (NEW METERS ARE PROGRAMMED) i. SAG = 8% voltage less than the nominal voltage for a minimum of 4 cycles – No AMM Alarm – PQ read only ii. SWELL = 6% voltage greater than nominal voltage for a minimum of 4 cycles - No AMM Alarm – PQ read only iii. Under Voltage Alert is 10% voltage less than the nominal voltage for 15 minutes or more – this alert comes in from AMM iv. Over Voltage Alert is 8% voltage more than the nominal voltage for 15 minutes or more – this alert comes in from AMM v. c. For the I210+c meters (METERS WERE ORIGINALLY PROGRAMMED) i. SAG = 10% voltage less than the nominal voltage for a minimum of 1 second – No AMM Alarm – PQ read only ii. SWELL = 10% voltage greater than nominal voltage for a minimum of 1 second– No AMM Alarm – PQ read only iii. Under Voltage Alert is 15% voltage less than the nominal voltage for 3 seconds more – this is the same as a CA 000400 = Low Potential on I210+c this alert comes in from AMM iv. Over Voltage Alert is 10% voltage more than the nominal voltage for 3 seconds more – this comes in from AMM as I210C over Voltage Diagnostic 7 Set d. For the KV2c Meters (METERS WERE ORIGINALLY PROGRAMMED) i. SAG = 10% voltage less than the nominal voltage for a minimum of 4 cycles – No AMM Alarm – PQ read only ii. SWELL = 10% voltage greater than nominal voltage for a minimum of 4 cycles - No AMM Alarm – PQ read only iii. Under Voltage Alert is 10% voltage less than the nominal voltage for 10 seconds or more – this alert comes in from AMM iv. Over Voltage Alert is 10% voltage more than the nominal voltage for 10 seconds or more - this alert comes in from AMM NOTE: The alerts received are read with normal data reads. They do not come in near realtime. It appears that the voltages were not low enough prior to the burn down to reliably trigger meter events if they are mostly programmed at +/-10% from nominal. -Is anything done with a low voltage meter event when it is received? Not on a consistent basis in any OG&E workgroup. Occasional use for data anomalies. There are some others in the company looking at voltages from other points of view such as revenue protection. -Do we know where the alternate station power transformers are for our substations? Is this clearly noted? From SP&C: No known list that is quickly referenceable exists. What if any notes were recorded regarding the temperature at which the original switching was planned? No known notes existed. Were there warnings that the switching may not be possible in hotter temperature conditions? No warnings were noted What guidelines exist to direct operators to re-analyze switching in light of new weather conditions or date changes? All switching orders should be reanalyze before execution. NOTE: Current training and available tools to the operators limit the extent to which an operator can have the situational awareness required to annunciate the problems associated with this switching. Did we recheck any load measurements between original date and actual date of execution? NO Were the recorded loads at Green Pastures the current AD readings in the field or was that from history? Field readings Do the operators even have access to the AD reading history any longer? Yes, we view thru DAA What communication was passed between Control 1 and Control 2 verbally? It appears that Control 2 may have known that simply reclosing recloser 3198 was not going to resolve the problem/outage due to overload problems, but control 1 directed the closing of 3198, resulting in another burndown. Phone calls seem to indicate good communication between control 1 and 2 originally, but the information regarding the overload and cold pickup appears to have been lost at shift change and line crew rotation. |  |  |  | Metro Service Center | FALSE |  | FALSE | System Operations |  | Rachel Davis | Douglas Mack |  | Darrell Fuller | Please review | Darrell Fuller |  | Low |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction | [10 empty] | Overloaded conductor | 08. Improper Loading | 12. Equipment Failure
8972 | South District Service Center | 2019-08-05 17:30 | Member was driving west bound on NW 6th, as he was crossing intersection member was struck by public vehicle. No injuries occurred. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Eric Engles | 2019-08-19 14:53 | 2019-08-06 06:53 | 2019-08-06 06:53 | 2019-08-15 09:07 | 2019-08-19 16:30 | 2019-08-06 06:46 |  |  |  | Nw 6th and N walker Ave |  |  | Luke Kennedy | Field Supervisor has obtained police report and it is available upon request. Approved 08-19-19 | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | [6 empty] | South District Service Center | FALSE |  | FALSE | PD Operations Services |  | Garrison Cole | Eric Engles |  |  |  | Steve Watkins |  | Low | [93 empty] | FALSE |  | Oklahoma City | Public Vehicle Struck OGE | Both Vehicles Moving | 2017-09-10 19:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
8973 | North Service Center | 2019-08-06 10:30 | North District line crew was lifting 3 phase pad mount transformer off of flat bed trailer. As they began to lift the transformer the winch line failed and the transformer fell approximately 6 inches. No injuries or damages occurred. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Delivery | Jeffrey Warner | 2019-08-22 13:16 | 2019-08-07 07:25 | 2019-08-07 07:25 | 2019-08-16 10:01 | 2019-08-20 09:30 | 2019-08-07 07:18 | 2019-08-22 10:54 |  | 2019-08-19 13:55 | 1332 W. Memorial Rd. OKC |  |  | Lindle Coleman | I approve the communication of winch lines being dipped at the PM's. Approved 8/22/19 by LRC | T&D Ops |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Jeffrey Warner |  | North District line crew was lifting 3 phase pad mount transformer off of flat bed trailer. As they began to lift the transformer the winch line failed and the transformer fell approximately 6 inches. No injuries or damages occurred. At this time the crew halted operations and contacted their field supervisor and fleet to replace winch line. Upon further investigation they had done a vehicle inspection during their monthly June Safety Meeting. Fleet Manager informed us that there has been a process in place for a year to dip the winch lines in order to mitigate the potential for abrasions on the winch line. |  |  |  | North Service Center | FALSE |  | TRUE | Construction Services |  | Jason Clark | Jeffrey Warner |  | Terry Garrett | I approved...TG | Terry Garrett |  | Medium | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | Failure of the winch line caused the transformer to fall approximately 6 in | 06. Using Defective Equipment | 12. Equipment Failure |  | The dipping of the winch lines to prevent damage of caused by abrasion should eliminate close calls similar to this one going forward. Approved
8974 | Seminole PP; EGX Gath/Trans | 2019-08-07 15:00 | Member was operating motor vehicle and made a sharp right turn and struck fixed object. Damage to passenger rear fender. Non injury incident. | Level 2 |  | FALSE | Vehicle |  |  |  |  | OGE Energy Corp | Joel Madden | 2019-08-28 14:17 | 2019-08-07 16:36 | 2019-08-07 16:36 | 2019-08-12 13:32 | 2019-08-21 15:00 | 2019-08-07 16:24 | 2019-08-21 12:54 |  | 2019-08-14 08:32 | Seminole PP near warehouse 2 |  |  | William Young | Reviewed and approved. WCY 8-28-19 | Enterprise Services |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Joel Madden |  | Member conducted a 360 of the vehicle surroundings and noted the fire hydrant. Member entered the work truck parked directly outside of warehouse 2 bay doors. Upon pulling forward and turning right to enter the roadway, the member turned too sharply and struck the rear fender of the truck against a fire hydrant. The fire hydrant did not have any apparent damage after the incident. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | Supply Chain |  | Berry Davis | Joel Madden |  | George Wicks | Incident recorded accurately | George Wicks |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Member did not effectively evaluate the proximity of the vehicle to the nearby fire hydrant resulting in striking of the fixed object upon operating the vehicle. | 15. Using Equipment Improperly | 1. Struck Against (Running or Bumping Into) |  | Approved, Cody Vinyard 8/14/19 Not Approved, Cody Vinyard 8/12/19 In the Detailed Description of the incident pleases answer the following questions: 1. Did the operator conduct a 360 and was the hydrant visually noted prior to entering the vehicle? 2. Was there any damage to the hydrant? Corrective Action: 1. Make the addition to the corrective action of reviewing the SSOP.604.123 General Safety Requirements section (6.4- Vehicles) to emphasize a 360 inspection prior to driving a vehicle | [72 empty] | TRUE |  | Konawa | Struck Fixed Object | Turned Into Object | 2016-07-31 19:00 |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Clear
8975 | General Service Center | 2019-08-08 08:00 | As member was throwing straps to strap down his load, another member was driving by in a pick-up. The member throwing straps could not see the pick-up because he had black tubs stacked up blocking his view. When member threw strap the strap hit the truck driving by. Both members looked over truck and could not find any damage. | Level 1 |  | TRUE | Property Damage |  |  |  |  | OGE Energy Corp | Charles Shetley | 2019-08-27 08:01 | 2019-08-08 08:55 | 2019-08-08 08:55 | 2019-08-12 12:07 | 2019-08-22 08:00 | 2019-08-08 08:42 | 2019-08-21 11:43 |  |  | GSC out in Semi loading area. |  |  | Cody Vinyard | Approve, Cody Vinyard | Enterprise Services |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Charles Shetley |  | Member was strapping down load when another member was driving by in a pickup. When member threw strap his view was obstructed by black tubs double stacked on his trailer, so he did not see the other member driving by his trailer in a pickup. As member drove by the strap hit the truck. Both members looked at truck and could not find any damage. |  |  |  | General Service Center | FALSE |  | TRUE | Supply Chain |  | Christian Britton | Charles Shetley |  | George Wicks | Incident was documented accurately | George Wicks |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | As member was throwing straps to strap down his load, another member was driving by in a pick-up. The member throwing straps could not see the pick-up because he had black tubs stacked up blocking his view. When member threw strap the strap hit the truck driving by. Both members looked over truck and could not find any damage. | 18. Failure to Check, Monitor | 2. Struck By (Hit By Moving Object)
8976 | South District Service Center | 2019-08-08 10:30 | Member scraped right rear bumper with studs of left front tire. | Level 2 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Gary Parks | 2019-09-16 08:49 | 2019-08-08 14:02 | 2019-08-08 14:01 | 2019-09-03 10:25 | 2019-08-22 10:30 | 2019-08-08 10:30 | 2019-09-16 08:29 |  | 2019-09-05 13:21 | SE 83rd and Anderson Road, OKC, Oklahoma |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Gary Parks |  | On August 8th Matt Palomares was traveling south bound on Anderson rd when a public vehicle abruptly stopped to turn in front of him. Palomares tried to avoid the vehicle however did clip the right rear side of the vehicle. Upon investigation, it was determined that the member was following too closely in order to stop in time. |  |  |  | South District Service Center | FALSE |  | FALSE | Construction Services |  | Matthew Palomares | Gary Parks |  | Terry Garrett | I approve...TG | Terry Garrett |  | Medium |  |  |  |  | 5.01 Lack of experience | [11 empty] | Member following too closely and did not have enough time to react | 04. Operating at Improper Speed | 1. Struck Against (Running or Bumping Into) |  | Due to the neglect of good defensive driving practices this incident was deemed chargeable and punitive action was taken. | [72 empty] | TRUE |  | Oklahoma City | OGE Vehicle Struck Other Vehicle | Both Vehicles Moving | 2018-05-06 19:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Cloudy
8977 | Shawnee Service Center | 2019-07-28 19:30 | Wright Tree Service Forman raised the outriggers on the bucket truck and drove the truck while the trimmer was still in the bucket. The bucket was not cradled or stowed and the boom was at a 35-40 degree angle off the back of the truck. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Christopher Martin | 2019-09-23 13:33 | 2019-08-08 14:08 | 2019-08-08 14:08 | 2019-09-05 09:31 | 2019-08-11 19:30 | 2019-08-08 14:00 | 2019-09-12 12:05 |  | 2019-09-05 09:41 | Bowlegs School- Shawnee Service Center |  |  | William Young | Reviewed meeting rosters. Approved. WCY 9-23-19 | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Christopher Martin |  | During an after hours outage call a Wright Tree Service Forman raised the outriggers on the bucket truck and moved the truck so they could reposition the bucket for work. The foreman moved the aerial man lift with the boom out of stow, unsecured and with an employee still in the bucket. |  |  |  | Shawnee Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Wesley Lanier | Christopher Martin |  | Nicole Rhodes | Reviewed. | Nicole Rhodes |  | Medium | [8 empty] | 9.06 Inadequate work planning or programming | [7 empty] | During an after hours outage call a Wright Tree Service Forman raised the outriggers on the bucket truck and moved the truck so they could reposition the bucket for work. The foreman moved the aerial man lift with the boom out of stow, unsecured and with an employee still in the bucket. | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation |  | Approved with attachment of retraining roster. J. Looney, 9/5/19 |  |  |  | Vehicle |  | Christopher Martin | [5 empty] | 9. Abnormal Operation | Wesley Lanier | Wright Tree Service | Jerry Britt |  |  |  | Christopher Martin |  |  |  |  | FALSE
8978 | Horseshoe Lake Power Plant | 2019-08-08 11:00 | Member was taking oil sample from HL9 Turbine Lube oil sample line. When opening the sample valve, trapped air in the line caused lube oil to spray out in an unexpected direction, which caused the oil to splatter off of surrounding piping - which splattered on the member's torso. Non-Injury. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Garrett Williston | 2019-09-04 07:19 | 2019-08-08 15:33 | 2019-08-08 15:33 | 2019-08-21 18:28 | 2019-08-22 11:00 | 2019-08-08 15:13 | 2019-08-26 07:35 |  |  | Horseshoe Lake Unit 9 Turbine Lube Oil Reservoir Area |  |  | Chrysty Dorsey | Reviewed | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Garrett Williston |  | -On 8/8/2019, as a part of routine job responsibilities, member was collecting oil samples from HL 9 & 10 Turbine Lube Oil System. While drawing the sample from Unit 9, upon opening the sample valve, trapped air in the sample line caused oil to spray out with enough force and in a direction that caused the member to be sprayed with oil on their torso. The valve remained open and the remainder of the air was vented without further issue which allowed for the sample to be collected. Member called to inform supervision of the issue and was sent home to change and shower. Member mentioned that this was not the first time this had happened on this specific sample location. -Upon investigation, it was determined that the member had utilized an SWP to identify hazards and walk through the scope of the task. Nitrile gloves were used while drawing off the sample. However, -The sample area was surveyed, and the following items were identified: -The location of the sample point requires the member to be in an awkward position when drawing the sample. Additional SS tubing can be used to put the sample point in a more ergonomic location. Additionally, the sample line points in the same direction as the entry path to draw the sample. -The sample valve should be a valve that is designed to throttle flow. Currently installed sample valves on both Unit 9 and 10 are ¼ turn to full open ball valves, which are not necessarily designed to throttle flow. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Power Supply Services |  | James Hillman | Garrett Williston |  | Shad Sweeney | Reviewed. | Shad Sweeney |  | Low | [9 empty] | 10.01 Inadequate assessment of loss exposures |  |  | 13.02 Inadequate human factors/ergonomics considerations |  |  |  | Restricted/congested access to sample point requires member to put self in directional path of oil sample stream. Sample valve should be a valve that can throttle flow – currently installed valve on both Unit 9 and 10 is a ¼ turn to full open ball valve, which are not designed to throttle flow. | 11. Improper Position for Task | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise)
8978 | Horseshoe Lake Power Plant | 2019-08-08 11:00 | Member was taking oil sample from HL9 Turbine Lube oil sample line. When opening the sample valve, trapped air in the line caused lube oil to spray out in an unexpected direction, which caused the oil to splatter off of surrounding piping - which splattered on the member's torso. Non-Injury. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Garrett Williston | 2019-09-04 07:19 | 2019-08-08 15:33 | 2019-08-08 15:33 | 2019-08-21 18:28 | 2019-08-22 11:00 | 2019-08-08 15:13 | 2019-08-26 07:35 |  |  | Horseshoe Lake Unit 9 Turbine Lube Oil Reservoir Area |  |  | Chrysty Dorsey | Reviewed | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Garrett Williston |  | -On 8/8/2019, as a part of routine job responsibilities, member was collecting oil samples from HL 9 & 10 Turbine Lube Oil System. While drawing the sample from Unit 9, upon opening the sample valve, trapped air in the sample line caused oil to spray out with enough force and in a direction that caused the member to be sprayed with oil on their torso. The valve remained open and the remainder of the air was vented without further issue which allowed for the sample to be collected. Member called to inform supervision of the issue and was sent home to change and shower. Member mentioned that this was not the first time this had happened on this specific sample location. -Upon investigation, it was determined that the member had utilized an SWP to identify hazards and walk through the scope of the task. Nitrile gloves were used while drawing off the sample. However, -The sample area was surveyed, and the following items were identified: -The location of the sample point requires the member to be in an awkward position when drawing the sample. Additional SS tubing can be used to put the sample point in a more ergonomic location. Additionally, the sample line points in the same direction as the entry path to draw the sample. -The sample valve should be a valve that is designed to throttle flow. Currently installed sample valves on both Unit 9 and 10 are ¼ turn to full open ball valves, which are not necessarily designed to throttle flow. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Power Supply Services |  | James Hillman | Garrett Williston |  | Shad Sweeney | Reviewed. | Shad Sweeney |  | Low | [9 empty] | 10.02 Inadequate consideration of human factors/ergonomics |  |  | 13.02 Inadequate human factors/ergonomics considerations |  |  |  | Restricted/congested access to sample point requires member to put self in directional path of oil sample stream. Sample valve should be a valve that can throttle flow – currently installed valve on both Unit 9 and 10 is a ¼ turn to full open ball valve, which are not designed to throttle flow. | 11. Improper Position for Task | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise)
8979 | Seminole PP; EGX Gath/Trans | 2019-08-08 07:00 | Operator notice a hydrogen panel alarm in control room on the DCS, contacted Shift Supervisor, Operations and Maintenance were notified of leak on generator. Unit was taken offline and purged. | Level 2 |  | FALSE | System Operational Incident |  |  |  |  | Power Supply | Terry Bunch | 2020-01-27 08:52 | 2019-08-08 15:35 |  | 2020-01-20 15:12 | 2019-09-19 07:00 | 2019-08-08 15:17 | 2020-01-20 16:10 |  | 2020-01-20 15:59 | Seminole PP Unit 2 Generator |  |  | Jesse Murray | Jesse Murray -- Approved | Power Supply |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Terry Bunch |  | Control Operator had a hydrogen panel alarm on Unit 2 generator. Contacted the Shift Supervisor. Operations and Maintenance began to look for leaks with monitors. The leak was found on the generator liquid detector drain line. The drain line had a crack in the pipe at the bottom of the welded fitting. Inadequate support system was causing fatigue in the Hydrogen lines |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | Maintenance |  | Terry Bunch | Terry Bunch |  | Paul Schoelen | Terry, I think we should change the risk ranking to C4 and L2. It doesn't change the overall ranking of the incident but I think it aligns better with the actual situation we experienced. Thanks | Paul Schoelen |  | Medium | [9 empty] | 10.03 Inadequate standards, specifications and/or design criteria |  |  |  |  | 15.03 Inadequate inspection and/or monitoring |  | Determined that bending fatigue, and vibrations on the hydrogen lines from insufficient support system. | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure |  | See workflow comment for reason being returned. Updated: reviewed. CA added based on incident call. Also supervisor added a copy of the RCA conducted.
8980 | Ardmore Service Center | 2019-08-07 07:30 | While driving Service Bucket to Safety Meeting rock struck windshield | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Terry Looney | 2019-08-19 09:39 | 2019-08-09 08:19 | 2019-08-09 08:19 | 2019-08-15 11:34 | 2019-08-21 07:30 | 2019-08-09 08:07 | 2019-08-16 07:18 |  |  | Chickasaw Turnpike between Hwy 177 & Hwy 7 |  |  | Terry Hackett | Approved. Rock flew up another vehicle, member was not at fault and did not have means to mitigate this incident | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | TRUE |  | FALSE | TRUE | Terry Looney |  | While driving Service Bucket to Safety Meeting rock struck windshield |  |  |  | Ardmore Service Center | FALSE |  | FALSE | Construction Services |  | Garrid Brown | Terry Looney |  | Kenneth McKinzie | Approved | Kenneth McKinzie |  | Low |  |  |  | 4.05 Extreme concentration/perception demands | [12 empty] | Rock hit windshield | 08. Improper Loading | 2. Struck By (Hit By Moving Object) | [68 empty] | Windshield broken do to rock hitting passenger side | 300 | Garrid Brown | Vehicle (not related to operation of vehicle) |  | F07-533 | FALSE |  | Sulphur | Other | Struck By Material/Debris | 2009-04-26 19:00 |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Clear
8980 | Ardmore Service Center | 2019-08-07 07:30 | While driving Service Bucket to Safety Meeting rock struck windshield | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Delivery | Terry Looney | 2019-08-19 09:39 | 2019-08-09 08:19 | 2019-08-09 08:19 | 2019-08-15 11:34 | 2019-08-21 07:30 | 2019-08-09 08:07 | 2019-08-16 07:18 |  |  | Chickasaw Turnpike between Hwy 177 & Hwy 7 |  |  | Terry Hackett | Approved. Rock flew up another vehicle, member was not at fault and did not have means to mitigate this incident | T&D Ops |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | TRUE | Terry Looney |  | While driving Service Bucket to Safety Meeting rock struck windshield |  |  |  | Ardmore Service Center | FALSE |  | FALSE | Construction Services |  | Garrid Brown | Terry Looney |  | Kenneth McKinzie | Approved | Kenneth McKinzie |  | Low |  |  |  | 4.05 Extreme concentration/perception demands | [12 empty] | Rock hit windshield | 08. Improper Loading | 2. Struck By (Hit By Moving Object) | [68 empty] | Windshield broken do to rock hitting passenger side | 300 | Garrid Brown | Vehicle (not related to operation of vehicle) |  | F07-533 | FALSE |  | Sulphur | Other | Struck By Material/Debris | 2009-04-26 19:00 |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Clear
8981 | Metro Service Center | 2019-08-07 10:00 | Member backed into company vehicle while it was parked in his driveway. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Transco | Paul George | 2019-08-14 08:22 | 2019-08-09 12:47 | 2019-08-09 12:47 | 2019-08-09 12:04 | 2019-08-21 10:00 | 2019-08-09 12:36 | 2019-08-13 07:31 |  |  | 512 Country Club Circle Midwest City Oklahoma 73110 |  |  | Cody Vinyard | approved, Cody Vinyard | Enterprise Services |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Paul George |  | On Wednesday, 08-07-2019, at 9:25 a.m., Larry Anderson, OGE On-Call Investigator, received a phone call from Paul George, Enterprise Security Supervisor, to report a non-injury vehicle accident involving OGE member Kenny Stephenson, Security Control Center Operator and On-Call Investigator. Anderson responded to investigate the incident occurring at Stephenson's home, 512 Country Club Circle, Midwest City, OK 73110, and arrived on-scene at 10:05 a.m. Stephenson was issued OGE pool vehicle F03-1217 for on-call investigation duties, which was parked on east side of the driveway at Stephenson's home. Stephenson's personal vehicle, a 2016 silver four-door Chevrolet Silverado pickup truck with Oklahoma tag number MWCP83, was parked adjacent to and approximately 3-feet ahead of F03-1217. Spacing between vehicles was approximately 2-feet. Stephenson stated that at approximately 9:10 a.m., he was looking out the passenger-side window of his Silverado truck while backing down the driveway and unaware of his proximity to F03-1217. The left rear corner of Stephenson's truck impacted the right side of F03-1217, damaging the cab side-post structure and side-panel of truck bed. Significant sheet metal damage to the truck bed of F03-1217 extended from top bed rail to bottom edge of side-panel, between passenger side door and right rear wheel well. Moderate sheet metal damage to Stephenson's truck was limited to area between left rear wheel well and left corner of rear bumper. Anderson took Stephenson's statement of accident details, made copies of Stephenson's Oklahoma driver license #V081917219 and verification form for Safeco Insurance Company of America policy number Y8556558 (Vehicle Identification Number 3GCPCREH0GG127006), shot digital photographs of the accident scene, and departed the location at 10:45 a.m. |  |  |  | Metro Service Center | FALSE |  | FALSE | Other |  |  | Paul George |  | James Finch | All corrective action has occurred and it's recommended this matter be closed. | James Finch |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Member failed to look left while backing his vehicle to the left, causing his personal vehicle to strike the OGE vehicle | 15. Using Equipment Improperly | 1. Struck Against (Running or Bumping Into) | [68 empty] | Damaged to right side of vehicle F03-1217 | 200 | Kenneth Stephenson | Vehicle (not related to operation of vehicle) |  | F031217
8982 | Central District Office | 2019-08-07 11:00 | While making repairs to MOS 136 breakers 113 and 183 operated. | Level 1 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Joseph Manseau | 2020-02-03 08:18 | 2019-08-12 09:41 |  | 2020-01-22 15:07 | 2019-09-18 11:00 | 2019-08-08 09:38 | 2020-01-24 10:31 |  |  | Northwest substation |  |  | Cody Magby | agree cm | T&D Ops |  | Level 1 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Jeffrey Uhls |  | Operational Incident Summary On Wednesday, August 8th at Northwest substation while making repairs to MOS 136 the 138kv breakers 183 and 113 operated and then reclosed. Prior to this incident, the TCC requested system relay investigate MOS 136 due to false SCADA indications, MOS 136 was showing to be in the open position while there was still load flow. The investigation revealed that the motor assembly was not rotating far enough to provide indication to the relay that the switch was in the closed position. It was determined at this time that switching would be necessary to make repairs to the motor assembly. |  |  |  | Central District Office | FALSE |  | FALSE | PD Operations Services |  | Adam Auten | Joseph Manseau |  | James Hutchison | I have reviewed this incident report and agree with it's findings and the corrective actions as well. | James Hutchison |  | Low
8983 | Sooner Power Plant | 2019-08-13 13:30 | While removing an old 8" service water line that is being replaced from under the concrete of the service water bay at the intake. The block and hook came into contact with an 8" line that was running overhead. This caused damage to the lagging and insulation. No members or other equipment were damaged. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Lance Lantz | 2019-09-12 07:57 | 2019-08-13 16:38 | 2019-08-13 16:38 | 2019-08-27 08:23 | 2019-08-27 13:30 | 2019-08-13 16:34 | 2019-09-04 08:19 |  |  | Sooner Power Plant Intake Structure |  |  | Brady Sowell | Approved by Brady Sowell on 9/5/2019 | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Lance Lantz |  | The Zachry base crew was assigned the task to remove and replace an 8” service water tie line in the service water bay of the intake. This required the crew to work in a confined space and the opening to get the material in and out was a 24” round manway. The crew had cut the old service water line into pieces that were approximately 5’-6’ long the previous day. The three crew members were in the process of removing the old material when the incident occurred. The crew had removed approximately 6 sections of pipe and was on the last section. The last piece was approximately 6’ long and had a 90° elbow attached to one end. The crew had one member staged in the service water bay helping guide the pipe out the 24” manway. Two members were above ground, one was operating the crane, and one was helping guide the pipe out and spotting. As the pipe was passing through the manway the crane operator was watching the member in the hole that was guiding the pipe out. The other member was assisting with guiding the pipe out. The crane block contacted the metal lagging that covers the insulation on a pipe that was located approximately 12’ directly above the manway opening. This caused damage to the metal lagging and the insulation behind it. There was no damage to the crane block and no members were injured. Upon further investigation it was found the crew had removed and replaced approximately 40’ of 10” pipe two weeks prior to this incident. The 10”pipe was cut into smaller sections due to the weight of the pipe. The same rigging was used with the 10” pipe with no issues. This last section of 8” pipe was the longest section of pipe they had removed. The three members were concerned the 90° elbow was going to hang up on the man way opening and thought they had plenty of overhead clearance. Due to the fact the pipe that was struck was located directly over the top of the manway. The crew was having to pull at slight angle to maintain clearance. Due to the 90° elbow on the end they also bumped the crane back to the west to lessen the angle at which the pulled the pipe out. This was to give a little more clearance for the elbow to pass through the manway. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Maintenance |  | Lance Lantz | Lance Lantz |  | Frank Brixey | Kris please note the recommendation from Zachry as a corrective action. Another question with that pipe being overhead would a mobile crane be a better option? Keith Brixey 8/26/2019 Approved - Keith Brixey 9/4/2019 | Frank Brixey |  | Low | [8 empty] | 9.09 Inadequate identification and evaluation of loss exposures | [7 empty] | operator and spotter were both paying attention to the load and not watching the surrounding area. | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Lance Lantz | Insulation & Lagging |  |  |  |  | 2. Struck By (Hit By Moving Object) | Lance Lantz | Zachry | Tyler Bohon |  | Fixed Equipment |  | Lance Lantz |  |  |  | Overhead Crane Appliance # 0011 | TRUE | [66 empty] | 9581422
8983 | Sooner Power Plant | 2019-08-13 13:30 | While removing an old 8" service water line that is being replaced from under the concrete of the service water bay at the intake. The block and hook came into contact with an 8" line that was running overhead. This caused damage to the lagging and insulation. No members or other equipment were damaged. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Lance Lantz | 2019-09-12 07:57 | 2019-08-13 16:38 | 2019-08-13 16:38 | 2019-08-27 08:23 | 2019-08-27 13:30 | 2019-08-13 16:34 | 2019-09-04 08:19 |  |  | Sooner Power Plant Intake Structure |  |  | Brady Sowell | Approved by Brady Sowell on 9/5/2019 | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Lance Lantz |  | The Zachry base crew was assigned the task to remove and replace an 8” service water tie line in the service water bay of the intake. This required the crew to work in a confined space and the opening to get the material in and out was a 24” round manway. The crew had cut the old service water line into pieces that were approximately 5’-6’ long the previous day. The three crew members were in the process of removing the old material when the incident occurred. The crew had removed approximately 6 sections of pipe and was on the last section. The last piece was approximately 6’ long and had a 90° elbow attached to one end. The crew had one member staged in the service water bay helping guide the pipe out the 24” manway. Two members were above ground, one was operating the crane, and one was helping guide the pipe out and spotting. As the pipe was passing through the manway the crane operator was watching the member in the hole that was guiding the pipe out. The other member was assisting with guiding the pipe out. The crane block contacted the metal lagging that covers the insulation on a pipe that was located approximately 12’ directly above the manway opening. This caused damage to the metal lagging and the insulation behind it. There was no damage to the crane block and no members were injured. Upon further investigation it was found the crew had removed and replaced approximately 40’ of 10” pipe two weeks prior to this incident. The 10”pipe was cut into smaller sections due to the weight of the pipe. The same rigging was used with the 10” pipe with no issues. This last section of 8” pipe was the longest section of pipe they had removed. The three members were concerned the 90° elbow was going to hang up on the man way opening and thought they had plenty of overhead clearance. Due to the fact the pipe that was struck was located directly over the top of the manway. The crew was having to pull at slight angle to maintain clearance. Due to the 90° elbow on the end they also bumped the crane back to the west to lessen the angle at which the pulled the pipe out. This was to give a little more clearance for the elbow to pass through the manway. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Maintenance |  | Lance Lantz | Lance Lantz |  | Frank Brixey | Kris please note the recommendation from Zachry as a corrective action. Another question with that pipe being overhead would a mobile crane be a better option? Keith Brixey 8/26/2019 Approved - Keith Brixey 9/4/2019 | Frank Brixey |  | Low | [8 empty] | 9.06 Inadequate work planning or programming | [7 empty] | operator and spotter were both paying attention to the load and not watching the surrounding area. | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Lance Lantz | Insulation & Lagging |  |  |  |  | 2. Struck By (Hit By Moving Object) | Lance Lantz | Zachry | Tyler Bohon |  | Fixed Equipment |  | Lance Lantz |  |  |  | Overhead Crane Appliance # 0011 | TRUE | [66 empty] | 9581422
8983 | Sooner Power Plant | 2019-08-13 13:30 | While removing an old 8" service water line that is being replaced from under the concrete of the service water bay at the intake. The block and hook came into contact with an 8" line that was running overhead. This caused damage to the lagging and insulation. No members or other equipment were damaged. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Lance Lantz | 2019-09-12 07:57 | 2019-08-13 16:38 | 2019-08-13 16:38 | 2019-08-27 08:23 | 2019-08-27 13:30 | 2019-08-13 16:34 | 2019-09-04 08:19 |  |  | Sooner Power Plant Intake Structure |  |  | Brady Sowell | Approved by Brady Sowell on 9/5/2019 | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Lance Lantz |  | The Zachry base crew was assigned the task to remove and replace an 8” service water tie line in the service water bay of the intake. This required the crew to work in a confined space and the opening to get the material in and out was a 24” round manway. The crew had cut the old service water line into pieces that were approximately 5’-6’ long the previous day. The three crew members were in the process of removing the old material when the incident occurred. The crew had removed approximately 6 sections of pipe and was on the last section. The last piece was approximately 6’ long and had a 90° elbow attached to one end. The crew had one member staged in the service water bay helping guide the pipe out the 24” manway. Two members were above ground, one was operating the crane, and one was helping guide the pipe out and spotting. As the pipe was passing through the manway the crane operator was watching the member in the hole that was guiding the pipe out. The other member was assisting with guiding the pipe out. The crane block contacted the metal lagging that covers the insulation on a pipe that was located approximately 12’ directly above the manway opening. This caused damage to the metal lagging and the insulation behind it. There was no damage to the crane block and no members were injured. Upon further investigation it was found the crew had removed and replaced approximately 40’ of 10” pipe two weeks prior to this incident. The 10”pipe was cut into smaller sections due to the weight of the pipe. The same rigging was used with the 10” pipe with no issues. This last section of 8” pipe was the longest section of pipe they had removed. The three members were concerned the 90° elbow was going to hang up on the man way opening and thought they had plenty of overhead clearance. Due to the fact the pipe that was struck was located directly over the top of the manway. The crew was having to pull at slight angle to maintain clearance. Due to the 90° elbow on the end they also bumped the crane back to the west to lessen the angle at which the pulled the pipe out. This was to give a little more clearance for the elbow to pass through the manway. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Maintenance |  | Lance Lantz | Lance Lantz |  | Frank Brixey | Kris please note the recommendation from Zachry as a corrective action. Another question with that pipe being overhead would a mobile crane be a better option? Keith Brixey 8/26/2019 Approved - Keith Brixey 9/4/2019 | Frank Brixey |  | Low | [8 empty] | 9.03 Improper or insufficient delegation | [7 empty] | operator and spotter were both paying attention to the load and not watching the surrounding area. | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Lance Lantz | Insulation & Lagging |  |  |  |  | 2. Struck By (Hit By Moving Object) | Lance Lantz | Zachry | Tyler Bohon |  | Fixed Equipment |  | Lance Lantz |  |  |  | Overhead Crane Appliance # 0011 | TRUE | [66 empty] | 9581422
8984 | Enid Service Center | 2019-08-13 15:00 | Wright Tree Service crew was chipping brush when they noticed their foreman was on the ground gasping for air and holding his chest. He was having blurred speech as well. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate and deterime causal factors and corrective actions. WCY 8/28/19 | 2019-08-28 13:54 | OG&E Corp Services | Christopher Martin | 2019-10-02 07:04 | 2019-08-14 16:24 | 2019-08-14 16:24 | 2019-09-06 16:34 | 2019-08-27 15:00 | 2019-08-14 16:09 | 2019-09-13 10:27 | 2019-09-25 18:22 | 2019-09-09 07:37 | 822 EAST CHEROKEE AVE, ENID, OK 73701 |  |  | Jean Leger | No additional comments. | T&D Ops |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | Incident investigation findings revealed that worker had been off four days prior to the incident and that he had not hydrated while off which was a contributing factor to this incident. | Jerrie Looney | William Young |  | Enid Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Grant Ehlen | Christopher Martin |  | Christopher Martin | Corrective actions taken and documented by vendor. No further action required. | Christopher Martin | William Young | High | 1.05 Sensitivities to sensory extremes (temp, sound, etc.) |  | 3.06 Exposure to temperature extremes | [5 empty] | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Heat Stress caused by lack of hydration days prior to the incident. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed and approved. WCY 9-25-2019 | Approved, J. Looney 9.9.19 |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Christopher Martin | [5 empty] | 11. Overstress, Overpressure, Overexertion, Ergonomic | Grant Ehlen | Wright Tree Service | Frank McMurray |  |  |  | Christopher Martin
8984 | Enid Service Center | 2019-08-13 15:00 | Wright Tree Service crew was chipping brush when they noticed their foreman was on the ground gasping for air and holding his chest. He was having blurred speech as well. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate and deterime causal factors and corrective actions. WCY 8/28/19 | 2019-08-28 13:54 | OG&E Corp Services | Christopher Martin | 2019-10-02 07:04 | 2019-08-14 16:24 | 2019-08-14 16:24 | 2019-09-06 16:34 | 2019-08-27 15:00 | 2019-08-14 16:09 | 2019-09-13 10:27 | 2019-09-25 18:22 | 2019-09-09 07:37 | 822 EAST CHEROKEE AVE, ENID, OK 73701 |  |  | Jean Leger | No additional comments. | T&D Ops |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | Incident investigation findings revealed that worker had been off four days prior to the incident and that he had not hydrated while off which was a contributing factor to this incident. | Jerrie Looney | William Young |  | Enid Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Grant Ehlen | Christopher Martin |  | Christopher Martin | Corrective actions taken and documented by vendor. No further action required. | Christopher Martin | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  | 7.06 Improper attempt to save time or effort | [8 empty] | 16.01 Inadequate horizontal communication between peers | The heat index was 99 degrees at the time of the incident. The contractor was not properly hydrated and was over exerting themselves. | 40. Weather Conditions | 11. Overstress, Overpressure, Overexertion, Ergonomic | Reviewed and approved. WCY 9-25-2019 | Approved, J. Looney 9.9.19 |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Christopher Martin | [5 empty] | 11. Overstress, Overpressure, Overexertion, Ergonomic | Grant Ehlen | Wright Tree Service | Frank McMurray |  |  |  | Christopher Martin
8984 | Enid Service Center | 2019-08-13 15:00 | Wright Tree Service crew was chipping brush when they noticed their foreman was on the ground gasping for air and holding his chest. He was having blurred speech as well. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate and deterime causal factors and corrective actions. WCY 8/28/19 | 2019-08-28 13:54 | OG&E Corp Services | Christopher Martin | 2019-10-02 07:04 | 2019-08-14 16:24 | 2019-08-14 16:24 | 2019-09-06 16:34 | 2019-08-27 15:00 | 2019-08-14 16:09 | 2019-09-13 10:27 | 2019-09-25 18:22 | 2019-09-09 07:37 | 822 EAST CHEROKEE AVE, ENID, OK 73701 |  |  | Jean Leger | No additional comments. | T&D Ops |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | Incident investigation findings revealed that worker had been off four days prior to the incident and that he had not hydrated while off which was a contributing factor to this incident. | Christopher Martin | William Young |  | Enid Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Grant Ehlen | Christopher Martin |  | Christopher Martin | Corrective actions taken and documented by vendor. No further action required. | Christopher Martin | William Young | High | 1.05 Sensitivities to sensory extremes (temp, sound, etc.) |  | 3.06 Exposure to temperature extremes | [5 empty] | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Heat Stress caused by lack of hydration days prior to the incident. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Reviewed and approved. WCY 9-25-2019 | Approved, J. Looney 9.9.19 |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Christopher Martin | [5 empty] | 11. Overstress, Overpressure, Overexertion, Ergonomic | Grant Ehlen | Wright Tree Service | Frank McMurray |  |  |  | Christopher Martin
8984 | Enid Service Center | 2019-08-13 15:00 | Wright Tree Service crew was chipping brush when they noticed their foreman was on the ground gasping for air and holding his chest. He was having blurred speech as well. | Level 3 |  | FALSE | Contractor | Jean Leger | William Young | Investigate and deterime causal factors and corrective actions. WCY 8/28/19 | 2019-08-28 13:54 | OG&E Corp Services | Christopher Martin | 2019-10-02 07:04 | 2019-08-14 16:24 | 2019-08-14 16:24 | 2019-09-06 16:34 | 2019-08-27 15:00 | 2019-08-14 16:09 | 2019-09-13 10:27 | 2019-09-25 18:22 | 2019-09-09 07:37 | 822 EAST CHEROKEE AVE, ENID, OK 73701 |  |  | Jean Leger | No additional comments. | T&D Ops |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | Incident investigation findings revealed that worker had been off four days prior to the incident and that he had not hydrated while off which was a contributing factor to this incident. | Christopher Martin | William Young |  | Enid Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Grant Ehlen | Christopher Martin |  | Christopher Martin | Corrective actions taken and documented by vendor. No further action required. | Christopher Martin | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  | 7.06 Improper attempt to save time or effort | [8 empty] | 16.01 Inadequate horizontal communication between peers | The heat index was 99 degrees at the time of the incident. The contractor was not properly hydrated and was over exerting themselves. | 40. Weather Conditions | 11. Overstress, Overpressure, Overexertion, Ergonomic | Reviewed and approved. WCY 9-25-2019 | Approved, J. Looney 9.9.19 |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Christopher Martin | [5 empty] | 11. Overstress, Overpressure, Overexertion, Ergonomic | Grant Ehlen | Wright Tree Service | Frank McMurray |  |  |  | Christopher Martin
8985 | Muskogee Power Plant | 2019-08-15 16:00 | Power Delivery energized the onsite contractor feed without plant authorization the plant contact was aware of the feed being energized but the operating authority was not aware of the feed being energized. No injuries or equipment damage | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Daniel Moffett | 2019-12-05 10:06 | 2019-08-15 16:57 | 2019-08-15 16:57 | 2019-11-07 11:34 | 2019-08-29 16:00 | 2019-08-15 16:49 | 2019-11-18 15:10 |  | 2019-11-07 12:31 | Muskogee Power Plant Contractor parking lot Electrical Feed |  |  | Jesse Murray | I am kicking this back to Investigate further. I want to see an action item that clearly defines how we handle LOTO of T&D energy sources inside our plant ground. I would like to see a Utility Solution so we handle this situation the same way every time. Jesse Murray 10/2/19 Approved. Jesse Murray 12/5/19 | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Jonathan Caudle |  | During the historic floods of May 2019, MKPP personnel were de-energizing electrical equipment in low lying areas that were going to be flooded. During this process, MKPP personnel contacted T&D to de-energize T&D fed electrical equipment that was in the flood prone areas. After the flooding, plant personnel identified equipment that had possibly sustained flood damage. MKPP then assembled a workforce and plan to replace equipment that got damaged from the flood. At the end of the recon stage of the MKPP ICS event, it was decided that restoration of the MKPP contractor parking lot would be given to Facilities to coordinate replacement with Collins Electric. A Facilities member contacted a T&D engineer to request that the T&D padmount transformer in the MKPP contractor parking lot be replaced due to possible flood damage. Facilities instructed Collins Electric to supply and replace all MKPP owned and maintained equipment that was damaged from the flood that was located in the MKPP contractor parking lot. Some of the MKPP owned and maintained equipment that needed replaced included 600V secondary conductor from T&D transformer to MKPP Contractor Parking Lot Power Pad Main Breaker, MKPP Contractor Parking Lot Power Pad Main Breaker, 480V to 120/208V dry cell transformer, 120/208V electrical distribution panel, 100A Disconnects used for connecting Contractor Office Trailers, and all associated 120/208V conductor. Collins Electric installed all above listed equipment and was ready for feed to MKPP Contractor Parking Lot Power Pad to be energized. Facilities then contacted T&D to have T&D transformer energized. After arriving at the MKPP Contractor Parking Lot, T&D visually inspected the T&D transformer that was feeding the MKPP Contractor Parking Lot Power Pad. T&D mentioned that this particular T&D transformer was visually in the best shape of all previous T&D flood related transformers that they had inspected during the May 2019 flood event. T&D then proceeded to clean the T&D transformer and then perform electrical tests to insure that the transformer was still able to perform as designed. All T&D testing of the T&D transformer passed. Prior to energizing T&D transformer, Collins Electric and a Facilities Member was asked if the new plant owned Main Breaker was ready to be energized. Collins Electric and a Facilities Member then confirmed that the Main Breaker was ready to be energized. T&D then energized the T&D transformer that then energized the MKPP 600V secondary conductor that fed up to the MKPP Contractor Parking Lot Power Pad Main Breaker. T&D work was then complete. After T&D had left the MKPP Contractor Parking Lot, Collins Electric then proceeded to check voltage at the MKPP Contractor Parking Lot Power Pad Main Breaker. Once Collins Electric verified that the voltage was good, they then closed the MKPP Contractor Parking Lot Power Pad Main Breaker energizing the 480V to 120/208V dry cell transformer. Collins Electric verified that the voltage was good on the primary and secondary sides of the dry cell transformer. Collins Electric then verified voltage was good at the 120/208V electrical distribution panel. After voltage was checked good at the 120/208V electrical distribution panel, Collins Electric proceeded to energize two branch breakers feeding new contractor trailers that was replaced as a result of the flood. The missed step in this operation was that the MKPP Operating Authority or a Member of the MKPP electrical team informed of the MKPP Contractor Parking Lot Power Pad equipment being energized. The Facilities Member acting as Collins Electrics Plant Contact was not aware of needing to inform the MKPP Operating Authority or a Member of the MKPP electrical team that the MKPP Contractor Parking Lot Power Pad equipment was being energized. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Engineering & Planning |  | Daniel Moffett | Carol Rollins |  | Carol Rollins | I changed the incident description added one sentence RW | Carol Rollins |  | Medium |  |  |  |  | 5.03 Inadequate initial training | [10 empty] | 16.03. Inadequate communication between different organizations | Equipment was energized without Operating Authority being aware. | 20. Failure to Communicate, Coordinate | 9. Abnormal Operation |  | Reviewed Bob Wright an corrective action has been added this incident has been reviewed again Bob Wright | [90 empty] | 9584481
8986 | Sooner Power Plant | 2019-08-14 10:00 | While attempting to utilize trolley on 250 foot level, a washer was witnessed falling from trolley stop. Member identified that trolley stop was missing washer and nut. | Level 4 |  | TRUE | Property Damage | Jean Leger | Jerrod Moser | BIll Young will lead. | 2019-08-19 13:56 | OG&E Corp Services | Marcus Huddleston | 2019-10-15 10:50 | 2019-08-15 17:04 | 2019-08-15 17:04 | 2019-09-10 13:46 | 2019-09-23 | 2019-08-15 16:54 | 2019-09-23 17:33 |  |  | Unit 1 stack, 250 foot level, Sooner Power Plant |  |  | Jerrod Moser | approved | UTS |  | Level 4 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Marcus Huddleston |  | While performing RATA testing at the 250' level on unit one at the Sooner Power Plant a crew member thought he saw something fall off the end of the jib rail. Upon investigation the crew found that the nut and washer was missing from the bolt that secures the rail stop to the end of the jib. The crew located the washer on the ground but did not find the nut. | Elizabeth Gough | William Young |  | Sooner Power Plant | TRUE |  | TRUE | UTS - Envir. & Process Chem |  | Ronald Madron | Marcus Huddleston |  | Jean Leger | No additional comments. |  |  | Very High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.03 Improper or insufficient delegation |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Unsecured nut and wash falling form height (250') | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level
8986 | Sooner Power Plant | 2019-08-14 10:00 | While attempting to utilize trolley on 250 foot level, a washer was witnessed falling from trolley stop. Member identified that trolley stop was missing washer and nut. | Level 4 |  | TRUE | Property Damage | Jean Leger | Jerrod Moser | BIll Young will lead. | 2019-08-19 13:56 | OG&E Corp Services | Marcus Huddleston | 2019-10-15 10:50 | 2019-08-15 17:04 | 2019-08-15 17:04 | 2019-09-10 13:46 | 2019-09-23 | 2019-08-15 16:54 | 2019-09-23 17:33 |  |  | Unit 1 stack, 250 foot level, Sooner Power Plant |  |  | Jerrod Moser | approved | UTS |  | Level 4 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Marcus Huddleston |  | While performing RATA testing at the 250' level on unit one at the Sooner Power Plant a crew member thought he saw something fall off the end of the jib rail. Upon investigation the crew found that the nut and washer was missing from the bolt that secures the rail stop to the end of the jib. The crew located the washer on the ground but did not find the nut. | Elizabeth Gough | William Young |  | Sooner Power Plant | TRUE |  | TRUE | UTS - Envir. & Process Chem |  | Ronald Madron | Marcus Huddleston |  | Jean Leger | No additional comments. |  |  | Very High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.03 Improper or insufficient delegation |  |  |  |  | 14.01.2 Inadequate development of standards: coordination with process design |  |  | Unsecured nut and wash falling form height (250') | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level
8986 | Sooner Power Plant | 2019-08-14 10:00 | While attempting to utilize trolley on 250 foot level, a washer was witnessed falling from trolley stop. Member identified that trolley stop was missing washer and nut. | Level 4 |  | TRUE | Property Damage | Jean Leger | Jerrod Moser | BIll Young will lead. | 2019-08-19 13:56 | OG&E Corp Services | Marcus Huddleston | 2019-10-15 10:50 | 2019-08-15 17:04 | 2019-08-15 17:04 | 2019-09-10 13:46 | 2019-09-23 | 2019-08-15 16:54 | 2019-09-23 17:33 |  |  | Unit 1 stack, 250 foot level, Sooner Power Plant |  |  | Jerrod Moser | approved | UTS |  | Level 4 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Marcus Huddleston |  | While performing RATA testing at the 250' level on unit one at the Sooner Power Plant a crew member thought he saw something fall off the end of the jib rail. Upon investigation the crew found that the nut and washer was missing from the bolt that secures the rail stop to the end of the jib. The crew located the washer on the ground but did not find the nut. | Elizabeth Gough | William Young |  | Sooner Power Plant | TRUE |  | TRUE | UTS - Envir. & Process Chem |  | Ronald Madron | Marcus Huddleston |  | Jean Leger | No additional comments. |  |  | Very High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.03 Improper or insufficient delegation |  |  |  |  | 14.04 Inadequate monitoring of compliance |  |  | Unsecured nut and wash falling form height (250') | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level
8986 | Sooner Power Plant | 2019-08-14 10:00 | While attempting to utilize trolley on 250 foot level, a washer was witnessed falling from trolley stop. Member identified that trolley stop was missing washer and nut. | Level 4 |  | TRUE | Property Damage | Jean Leger | Jerrod Moser | BIll Young will lead. | 2019-08-19 13:56 | OG&E Corp Services | Marcus Huddleston | 2019-10-15 10:50 | 2019-08-15 17:04 | 2019-08-15 17:04 | 2019-09-10 13:46 | 2019-09-23 | 2019-08-15 16:54 | 2019-09-23 17:33 |  |  | Unit 1 stack, 250 foot level, Sooner Power Plant |  |  | Jerrod Moser | approved | UTS |  | Level 4 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Marcus Huddleston |  | While performing RATA testing at the 250' level on unit one at the Sooner Power Plant a crew member thought he saw something fall off the end of the jib rail. Upon investigation the crew found that the nut and washer was missing from the bolt that secures the rail stop to the end of the jib. The crew located the washer on the ground but did not find the nut. | Elizabeth Gough | William Young |  | Sooner Power Plant | TRUE |  | TRUE | UTS - Envir. & Process Chem |  | Ronald Madron | Marcus Huddleston |  | Jean Leger | No additional comments. |  |  | Very High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Unsecured nut and wash falling form height (250') | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level
8986 | Sooner Power Plant | 2019-08-14 10:00 | While attempting to utilize trolley on 250 foot level, a washer was witnessed falling from trolley stop. Member identified that trolley stop was missing washer and nut. | Level 4 |  | TRUE | Property Damage | Jean Leger | Jerrod Moser | BIll Young will lead. | 2019-08-19 13:56 | OG&E Corp Services | Marcus Huddleston | 2019-10-15 10:50 | 2019-08-15 17:04 | 2019-08-15 17:04 | 2019-09-10 13:46 | 2019-09-23 | 2019-08-15 16:54 | 2019-09-23 17:33 |  |  | Unit 1 stack, 250 foot level, Sooner Power Plant |  |  | Jerrod Moser | approved | UTS |  | Level 4 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Marcus Huddleston |  | While performing RATA testing at the 250' level on unit one at the Sooner Power Plant a crew member thought he saw something fall off the end of the jib rail. Upon investigation the crew found that the nut and washer was missing from the bolt that secures the rail stop to the end of the jib. The crew located the washer on the ground but did not find the nut. | Elizabeth Gough | William Young |  | Sooner Power Plant | TRUE |  | TRUE | UTS - Envir. & Process Chem |  | Ronald Madron | Marcus Huddleston |  | Jean Leger | No additional comments. |  |  | Very High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.2 Inadequate development of standards: coordination with process design |  |  | Unsecured nut and wash falling form height (250') | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level
8986 | Sooner Power Plant | 2019-08-14 10:00 | While attempting to utilize trolley on 250 foot level, a washer was witnessed falling from trolley stop. Member identified that trolley stop was missing washer and nut. | Level 4 |  | TRUE | Property Damage | Jean Leger | Jerrod Moser | BIll Young will lead. | 2019-08-19 13:56 | OG&E Corp Services | Marcus Huddleston | 2019-10-15 10:50 | 2019-08-15 17:04 | 2019-08-15 17:04 | 2019-09-10 13:46 | 2019-09-23 | 2019-08-15 16:54 | 2019-09-23 17:33 |  |  | Unit 1 stack, 250 foot level, Sooner Power Plant |  |  | Jerrod Moser | approved | UTS |  | Level 4 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Marcus Huddleston |  | While performing RATA testing at the 250' level on unit one at the Sooner Power Plant a crew member thought he saw something fall off the end of the jib rail. Upon investigation the crew found that the nut and washer was missing from the bolt that secures the rail stop to the end of the jib. The crew located the washer on the ground but did not find the nut. | Elizabeth Gough | William Young |  | Sooner Power Plant | TRUE |  | TRUE | UTS - Envir. & Process Chem |  | Ronald Madron | Marcus Huddleston |  | Jean Leger | No additional comments. |  |  | Very High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.04 Inadequate monitoring of compliance |  |  | Unsecured nut and wash falling form height (250') | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level
8986 | Sooner Power Plant | 2019-08-14 10:00 | While attempting to utilize trolley on 250 foot level, a washer was witnessed falling from trolley stop. Member identified that trolley stop was missing washer and nut. | Level 4 |  | TRUE | Property Damage | Jean Leger | Jerrod Moser | BIll Young will lead. | 2019-08-19 13:56 | OG&E Corp Services | Marcus Huddleston | 2019-10-15 10:50 | 2019-08-15 17:04 | 2019-08-15 17:04 | 2019-09-10 13:46 | 2019-09-23 | 2019-08-15 16:54 | 2019-09-23 17:33 |  |  | Unit 1 stack, 250 foot level, Sooner Power Plant |  |  | Jerrod Moser | approved | UTS |  | Level 4 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Marcus Huddleston |  | While performing RATA testing at the 250' level on unit one at the Sooner Power Plant a crew member thought he saw something fall off the end of the jib rail. Upon investigation the crew found that the nut and washer was missing from the bolt that secures the rail stop to the end of the jib. The crew located the washer on the ground but did not find the nut. | Michael Kennedy | William Young |  | Sooner Power Plant | TRUE |  | TRUE | UTS - Envir. & Process Chem |  | Ronald Madron | Marcus Huddleston |  | Jean Leger | No additional comments. |  |  | Very High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.03 Improper or insufficient delegation |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Unsecured nut and wash falling form height (250') | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level
8986 | Sooner Power Plant | 2019-08-14 10:00 | While attempting to utilize trolley on 250 foot level, a washer was witnessed falling from trolley stop. Member identified that trolley stop was missing washer and nut. | Level 4 |  | TRUE | Property Damage | Jean Leger | Jerrod Moser | BIll Young will lead. | 2019-08-19 13:56 | OG&E Corp Services | Marcus Huddleston | 2019-10-15 10:50 | 2019-08-15 17:04 | 2019-08-15 17:04 | 2019-09-10 13:46 | 2019-09-23 | 2019-08-15 16:54 | 2019-09-23 17:33 |  |  | Unit 1 stack, 250 foot level, Sooner Power Plant |  |  | Jerrod Moser | approved | UTS |  | Level 4 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Marcus Huddleston |  | While performing RATA testing at the 250' level on unit one at the Sooner Power Plant a crew member thought he saw something fall off the end of the jib rail. Upon investigation the crew found that the nut and washer was missing from the bolt that secures the rail stop to the end of the jib. The crew located the washer on the ground but did not find the nut. | Michael Kennedy | William Young |  | Sooner Power Plant | TRUE |  | TRUE | UTS - Envir. & Process Chem |  | Ronald Madron | Marcus Huddleston |  | Jean Leger | No additional comments. |  |  | Very High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.03 Improper or insufficient delegation |  |  |  |  | 14.01.2 Inadequate development of standards: coordination with process design |  |  | Unsecured nut and wash falling form height (250') | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level
8986 | Sooner Power Plant | 2019-08-14 10:00 | While attempting to utilize trolley on 250 foot level, a washer was witnessed falling from trolley stop. Member identified that trolley stop was missing washer and nut. | Level 4 |  | TRUE | Property Damage | Jean Leger | Jerrod Moser | BIll Young will lead. | 2019-08-19 13:56 | OG&E Corp Services | Marcus Huddleston | 2019-10-15 10:50 | 2019-08-15 17:04 | 2019-08-15 17:04 | 2019-09-10 13:46 | 2019-09-23 | 2019-08-15 16:54 | 2019-09-23 17:33 |  |  | Unit 1 stack, 250 foot level, Sooner Power Plant |  |  | Jerrod Moser | approved | UTS |  | Level 4 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Marcus Huddleston |  | While performing RATA testing at the 250' level on unit one at the Sooner Power Plant a crew member thought he saw something fall off the end of the jib rail. Upon investigation the crew found that the nut and washer was missing from the bolt that secures the rail stop to the end of the jib. The crew located the washer on the ground but did not find the nut. | Michael Kennedy | William Young |  | Sooner Power Plant | TRUE |  | TRUE | UTS - Envir. & Process Chem |  | Ronald Madron | Marcus Huddleston |  | Jean Leger | No additional comments. |  |  | Very High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.03 Improper or insufficient delegation |  |  |  |  | 14.04 Inadequate monitoring of compliance |  |  | Unsecured nut and wash falling form height (250') | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level
8986 | Sooner Power Plant | 2019-08-14 10:00 | While attempting to utilize trolley on 250 foot level, a washer was witnessed falling from trolley stop. Member identified that trolley stop was missing washer and nut. | Level 4 |  | TRUE | Property Damage | Jean Leger | Jerrod Moser | BIll Young will lead. | 2019-08-19 13:56 | OG&E Corp Services | Marcus Huddleston | 2019-10-15 10:50 | 2019-08-15 17:04 | 2019-08-15 17:04 | 2019-09-10 13:46 | 2019-09-23 | 2019-08-15 16:54 | 2019-09-23 17:33 |  |  | Unit 1 stack, 250 foot level, Sooner Power Plant |  |  | Jerrod Moser | approved | UTS |  | Level 4 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Marcus Huddleston |  | While performing RATA testing at the 250' level on unit one at the Sooner Power Plant a crew member thought he saw something fall off the end of the jib rail. Upon investigation the crew found that the nut and washer was missing from the bolt that secures the rail stop to the end of the jib. The crew located the washer on the ground but did not find the nut. | Michael Kennedy | William Young |  | Sooner Power Plant | TRUE |  | TRUE | UTS - Envir. & Process Chem |  | Ronald Madron | Marcus Huddleston |  | Jean Leger | No additional comments. |  |  | Very High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Unsecured nut and wash falling form height (250') | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level
8986 | Sooner Power Plant | 2019-08-14 10:00 | While attempting to utilize trolley on 250 foot level, a washer was witnessed falling from trolley stop. Member identified that trolley stop was missing washer and nut. | Level 4 |  | TRUE | Property Damage | Jean Leger | Jerrod Moser | BIll Young will lead. | 2019-08-19 13:56 | OG&E Corp Services | Marcus Huddleston | 2019-10-15 10:50 | 2019-08-15 17:04 | 2019-08-15 17:04 | 2019-09-10 13:46 | 2019-09-23 | 2019-08-15 16:54 | 2019-09-23 17:33 |  |  | Unit 1 stack, 250 foot level, Sooner Power Plant |  |  | Jerrod Moser | approved | UTS |  | Level 4 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Marcus Huddleston |  | While performing RATA testing at the 250' level on unit one at the Sooner Power Plant a crew member thought he saw something fall off the end of the jib rail. Upon investigation the crew found that the nut and washer was missing from the bolt that secures the rail stop to the end of the jib. The crew located the washer on the ground but did not find the nut. | Michael Kennedy | William Young |  | Sooner Power Plant | TRUE |  | TRUE | UTS - Envir. & Process Chem |  | Ronald Madron | Marcus Huddleston |  | Jean Leger | No additional comments. |  |  | Very High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.2 Inadequate development of standards: coordination with process design |  |  | Unsecured nut and wash falling form height (250') | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level
8986 | Sooner Power Plant | 2019-08-14 10:00 | While attempting to utilize trolley on 250 foot level, a washer was witnessed falling from trolley stop. Member identified that trolley stop was missing washer and nut. | Level 4 |  | TRUE | Property Damage | Jean Leger | Jerrod Moser | BIll Young will lead. | 2019-08-19 13:56 | OG&E Corp Services | Marcus Huddleston | 2019-10-15 10:50 | 2019-08-15 17:04 | 2019-08-15 17:04 | 2019-09-10 13:46 | 2019-09-23 | 2019-08-15 16:54 | 2019-09-23 17:33 |  |  | Unit 1 stack, 250 foot level, Sooner Power Plant |  |  | Jerrod Moser | approved | UTS |  | Level 4 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Marcus Huddleston |  | While performing RATA testing at the 250' level on unit one at the Sooner Power Plant a crew member thought he saw something fall off the end of the jib rail. Upon investigation the crew found that the nut and washer was missing from the bolt that secures the rail stop to the end of the jib. The crew located the washer on the ground but did not find the nut. | Michael Kennedy | William Young |  | Sooner Power Plant | TRUE |  | TRUE | UTS - Envir. & Process Chem |  | Ronald Madron | Marcus Huddleston |  | Jean Leger | No additional comments. |  |  | Very High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.04 Inadequate monitoring of compliance |  |  | Unsecured nut and wash falling form height (250') | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level
8986 | Sooner Power Plant | 2019-08-14 10:00 | While attempting to utilize trolley on 250 foot level, a washer was witnessed falling from trolley stop. Member identified that trolley stop was missing washer and nut. | Level 4 |  | TRUE | Property Damage | Jean Leger | Jerrod Moser | BIll Young will lead. | 2019-08-19 13:56 | OG&E Corp Services | Marcus Huddleston | 2019-10-15 10:50 | 2019-08-15 17:04 | 2019-08-15 17:04 | 2019-09-10 13:46 | 2019-09-23 | 2019-08-15 16:54 | 2019-09-23 17:33 |  |  | Unit 1 stack, 250 foot level, Sooner Power Plant |  |  | Jerrod Moser | approved | UTS |  | Level 4 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Marcus Huddleston |  | While performing RATA testing at the 250' level on unit one at the Sooner Power Plant a crew member thought he saw something fall off the end of the jib rail. Upon investigation the crew found that the nut and washer was missing from the bolt that secures the rail stop to the end of the jib. The crew located the washer on the ground but did not find the nut. | Chad Inman | William Young |  | Sooner Power Plant | TRUE |  | TRUE | UTS - Envir. & Process Chem |  | Ronald Madron | Marcus Huddleston |  | Jean Leger | No additional comments. |  |  | Very High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.03 Improper or insufficient delegation |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Unsecured nut and wash falling form height (250') | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level
8986 | Sooner Power Plant | 2019-08-14 10:00 | While attempting to utilize trolley on 250 foot level, a washer was witnessed falling from trolley stop. Member identified that trolley stop was missing washer and nut. | Level 4 |  | TRUE | Property Damage | Jean Leger | Jerrod Moser | BIll Young will lead. | 2019-08-19 13:56 | OG&E Corp Services | Marcus Huddleston | 2019-10-15 10:50 | 2019-08-15 17:04 | 2019-08-15 17:04 | 2019-09-10 13:46 | 2019-09-23 | 2019-08-15 16:54 | 2019-09-23 17:33 |  |  | Unit 1 stack, 250 foot level, Sooner Power Plant |  |  | Jerrod Moser | approved | UTS |  | Level 4 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Marcus Huddleston |  | While performing RATA testing at the 250' level on unit one at the Sooner Power Plant a crew member thought he saw something fall off the end of the jib rail. Upon investigation the crew found that the nut and washer was missing from the bolt that secures the rail stop to the end of the jib. The crew located the washer on the ground but did not find the nut. | Chad Inman | William Young |  | Sooner Power Plant | TRUE |  | TRUE | UTS - Envir. & Process Chem |  | Ronald Madron | Marcus Huddleston |  | Jean Leger | No additional comments. |  |  | Very High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.03 Improper or insufficient delegation |  |  |  |  | 14.01.2 Inadequate development of standards: coordination with process design |  |  | Unsecured nut and wash falling form height (250') | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level
8986 | Sooner Power Plant | 2019-08-14 10:00 | While attempting to utilize trolley on 250 foot level, a washer was witnessed falling from trolley stop. Member identified that trolley stop was missing washer and nut. | Level 4 |  | TRUE | Property Damage | Jean Leger | Jerrod Moser | BIll Young will lead. | 2019-08-19 13:56 | OG&E Corp Services | Marcus Huddleston | 2019-10-15 10:50 | 2019-08-15 17:04 | 2019-08-15 17:04 | 2019-09-10 13:46 | 2019-09-23 | 2019-08-15 16:54 | 2019-09-23 17:33 |  |  | Unit 1 stack, 250 foot level, Sooner Power Plant |  |  | Jerrod Moser | approved | UTS |  | Level 4 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Marcus Huddleston |  | While performing RATA testing at the 250' level on unit one at the Sooner Power Plant a crew member thought he saw something fall off the end of the jib rail. Upon investigation the crew found that the nut and washer was missing from the bolt that secures the rail stop to the end of the jib. The crew located the washer on the ground but did not find the nut. | Chad Inman | William Young |  | Sooner Power Plant | TRUE |  | TRUE | UTS - Envir. & Process Chem |  | Ronald Madron | Marcus Huddleston |  | Jean Leger | No additional comments. |  |  | Very High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.03 Improper or insufficient delegation |  |  |  |  | 14.04 Inadequate monitoring of compliance |  |  | Unsecured nut and wash falling form height (250') | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level
8986 | Sooner Power Plant | 2019-08-14 10:00 | While attempting to utilize trolley on 250 foot level, a washer was witnessed falling from trolley stop. Member identified that trolley stop was missing washer and nut. | Level 4 |  | TRUE | Property Damage | Jean Leger | Jerrod Moser | BIll Young will lead. | 2019-08-19 13:56 | OG&E Corp Services | Marcus Huddleston | 2019-10-15 10:50 | 2019-08-15 17:04 | 2019-08-15 17:04 | 2019-09-10 13:46 | 2019-09-23 | 2019-08-15 16:54 | 2019-09-23 17:33 |  |  | Unit 1 stack, 250 foot level, Sooner Power Plant |  |  | Jerrod Moser | approved | UTS |  | Level 4 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Marcus Huddleston |  | While performing RATA testing at the 250' level on unit one at the Sooner Power Plant a crew member thought he saw something fall off the end of the jib rail. Upon investigation the crew found that the nut and washer was missing from the bolt that secures the rail stop to the end of the jib. The crew located the washer on the ground but did not find the nut. | Chad Inman | William Young |  | Sooner Power Plant | TRUE |  | TRUE | UTS - Envir. & Process Chem |  | Ronald Madron | Marcus Huddleston |  | Jean Leger | No additional comments. |  |  | Very High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Unsecured nut and wash falling form height (250') | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level
8986 | Sooner Power Plant | 2019-08-14 10:00 | While attempting to utilize trolley on 250 foot level, a washer was witnessed falling from trolley stop. Member identified that trolley stop was missing washer and nut. | Level 4 |  | TRUE | Property Damage | Jean Leger | Jerrod Moser | BIll Young will lead. | 2019-08-19 13:56 | OG&E Corp Services | Marcus Huddleston | 2019-10-15 10:50 | 2019-08-15 17:04 | 2019-08-15 17:04 | 2019-09-10 13:46 | 2019-09-23 | 2019-08-15 16:54 | 2019-09-23 17:33 |  |  | Unit 1 stack, 250 foot level, Sooner Power Plant |  |  | Jerrod Moser | approved | UTS |  | Level 4 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Marcus Huddleston |  | While performing RATA testing at the 250' level on unit one at the Sooner Power Plant a crew member thought he saw something fall off the end of the jib rail. Upon investigation the crew found that the nut and washer was missing from the bolt that secures the rail stop to the end of the jib. The crew located the washer on the ground but did not find the nut. | Chad Inman | William Young |  | Sooner Power Plant | TRUE |  | TRUE | UTS - Envir. & Process Chem |  | Ronald Madron | Marcus Huddleston |  | Jean Leger | No additional comments. |  |  | Very High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.2 Inadequate development of standards: coordination with process design |  |  | Unsecured nut and wash falling form height (250') | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level
8986 | Sooner Power Plant | 2019-08-14 10:00 | While attempting to utilize trolley on 250 foot level, a washer was witnessed falling from trolley stop. Member identified that trolley stop was missing washer and nut. | Level 4 |  | TRUE | Property Damage | Jean Leger | Jerrod Moser | BIll Young will lead. | 2019-08-19 13:56 | OG&E Corp Services | Marcus Huddleston | 2019-10-15 10:50 | 2019-08-15 17:04 | 2019-08-15 17:04 | 2019-09-10 13:46 | 2019-09-23 | 2019-08-15 16:54 | 2019-09-23 17:33 |  |  | Unit 1 stack, 250 foot level, Sooner Power Plant |  |  | Jerrod Moser | approved | UTS |  | Level 4 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Marcus Huddleston |  | While performing RATA testing at the 250' level on unit one at the Sooner Power Plant a crew member thought he saw something fall off the end of the jib rail. Upon investigation the crew found that the nut and washer was missing from the bolt that secures the rail stop to the end of the jib. The crew located the washer on the ground but did not find the nut. | Chad Inman | William Young |  | Sooner Power Plant | TRUE |  | TRUE | UTS - Envir. & Process Chem |  | Ronald Madron | Marcus Huddleston |  | Jean Leger | No additional comments. |  |  | Very High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.04 Inadequate monitoring of compliance |  |  | Unsecured nut and wash falling form height (250') | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level
8986 | Sooner Power Plant | 2019-08-14 10:00 | While attempting to utilize trolley on 250 foot level, a washer was witnessed falling from trolley stop. Member identified that trolley stop was missing washer and nut. | Level 4 |  | TRUE | Property Damage | Jean Leger | Jerrod Moser | BIll Young will lead. | 2019-08-19 13:56 | OG&E Corp Services | Marcus Huddleston | 2019-10-15 10:50 | 2019-08-15 17:04 | 2019-08-15 17:04 | 2019-09-10 13:46 | 2019-09-23 | 2019-08-15 16:54 | 2019-09-23 17:33 |  |  | Unit 1 stack, 250 foot level, Sooner Power Plant |  |  | Jerrod Moser | approved | UTS |  | Level 4 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Marcus Huddleston |  | While performing RATA testing at the 250' level on unit one at the Sooner Power Plant a crew member thought he saw something fall off the end of the jib rail. Upon investigation the crew found that the nut and washer was missing from the bolt that secures the rail stop to the end of the jib. The crew located the washer on the ground but did not find the nut. | Marcus Huddleston | William Young |  | Sooner Power Plant | TRUE |  | TRUE | UTS - Envir. & Process Chem |  | Ronald Madron | Marcus Huddleston |  | Jean Leger | No additional comments. |  |  | Very High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.03 Improper or insufficient delegation |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Unsecured nut and wash falling form height (250') | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level
8986 | Sooner Power Plant | 2019-08-14 10:00 | While attempting to utilize trolley on 250 foot level, a washer was witnessed falling from trolley stop. Member identified that trolley stop was missing washer and nut. | Level 4 |  | TRUE | Property Damage | Jean Leger | Jerrod Moser | BIll Young will lead. | 2019-08-19 13:56 | OG&E Corp Services | Marcus Huddleston | 2019-10-15 10:50 | 2019-08-15 17:04 | 2019-08-15 17:04 | 2019-09-10 13:46 | 2019-09-23 | 2019-08-15 16:54 | 2019-09-23 17:33 |  |  | Unit 1 stack, 250 foot level, Sooner Power Plant |  |  | Jerrod Moser | approved | UTS |  | Level 4 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Marcus Huddleston |  | While performing RATA testing at the 250' level on unit one at the Sooner Power Plant a crew member thought he saw something fall off the end of the jib rail. Upon investigation the crew found that the nut and washer was missing from the bolt that secures the rail stop to the end of the jib. The crew located the washer on the ground but did not find the nut. | Marcus Huddleston | William Young |  | Sooner Power Plant | TRUE |  | TRUE | UTS - Envir. & Process Chem |  | Ronald Madron | Marcus Huddleston |  | Jean Leger | No additional comments. |  |  | Very High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.03 Improper or insufficient delegation |  |  |  |  | 14.01.2 Inadequate development of standards: coordination with process design |  |  | Unsecured nut and wash falling form height (250') | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level
8986 | Sooner Power Plant | 2019-08-14 10:00 | While attempting to utilize trolley on 250 foot level, a washer was witnessed falling from trolley stop. Member identified that trolley stop was missing washer and nut. | Level 4 |  | TRUE | Property Damage | Jean Leger | Jerrod Moser | BIll Young will lead. | 2019-08-19 13:56 | OG&E Corp Services | Marcus Huddleston | 2019-10-15 10:50 | 2019-08-15 17:04 | 2019-08-15 17:04 | 2019-09-10 13:46 | 2019-09-23 | 2019-08-15 16:54 | 2019-09-23 17:33 |  |  | Unit 1 stack, 250 foot level, Sooner Power Plant |  |  | Jerrod Moser | approved | UTS |  | Level 4 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Marcus Huddleston |  | While performing RATA testing at the 250' level on unit one at the Sooner Power Plant a crew member thought he saw something fall off the end of the jib rail. Upon investigation the crew found that the nut and washer was missing from the bolt that secures the rail stop to the end of the jib. The crew located the washer on the ground but did not find the nut. | Marcus Huddleston | William Young |  | Sooner Power Plant | TRUE |  | TRUE | UTS - Envir. & Process Chem |  | Ronald Madron | Marcus Huddleston |  | Jean Leger | No additional comments. |  |  | Very High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.03 Improper or insufficient delegation |  |  |  |  | 14.04 Inadequate monitoring of compliance |  |  | Unsecured nut and wash falling form height (250') | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level
8986 | Sooner Power Plant | 2019-08-14 10:00 | While attempting to utilize trolley on 250 foot level, a washer was witnessed falling from trolley stop. Member identified that trolley stop was missing washer and nut. | Level 4 |  | TRUE | Property Damage | Jean Leger | Jerrod Moser | BIll Young will lead. | 2019-08-19 13:56 | OG&E Corp Services | Marcus Huddleston | 2019-10-15 10:50 | 2019-08-15 17:04 | 2019-08-15 17:04 | 2019-09-10 13:46 | 2019-09-23 | 2019-08-15 16:54 | 2019-09-23 17:33 |  |  | Unit 1 stack, 250 foot level, Sooner Power Plant |  |  | Jerrod Moser | approved | UTS |  | Level 4 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Marcus Huddleston |  | While performing RATA testing at the 250' level on unit one at the Sooner Power Plant a crew member thought he saw something fall off the end of the jib rail. Upon investigation the crew found that the nut and washer was missing from the bolt that secures the rail stop to the end of the jib. The crew located the washer on the ground but did not find the nut. | Marcus Huddleston | William Young |  | Sooner Power Plant | TRUE |  | TRUE | UTS - Envir. & Process Chem |  | Ronald Madron | Marcus Huddleston |  | Jean Leger | No additional comments. |  |  | Very High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Unsecured nut and wash falling form height (250') | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level
8986 | Sooner Power Plant | 2019-08-14 10:00 | While attempting to utilize trolley on 250 foot level, a washer was witnessed falling from trolley stop. Member identified that trolley stop was missing washer and nut. | Level 4 |  | TRUE | Property Damage | Jean Leger | Jerrod Moser | BIll Young will lead. | 2019-08-19 13:56 | OG&E Corp Services | Marcus Huddleston | 2019-10-15 10:50 | 2019-08-15 17:04 | 2019-08-15 17:04 | 2019-09-10 13:46 | 2019-09-23 | 2019-08-15 16:54 | 2019-09-23 17:33 |  |  | Unit 1 stack, 250 foot level, Sooner Power Plant |  |  | Jerrod Moser | approved | UTS |  | Level 4 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Marcus Huddleston |  | While performing RATA testing at the 250' level on unit one at the Sooner Power Plant a crew member thought he saw something fall off the end of the jib rail. Upon investigation the crew found that the nut and washer was missing from the bolt that secures the rail stop to the end of the jib. The crew located the washer on the ground but did not find the nut. | Marcus Huddleston | William Young |  | Sooner Power Plant | TRUE |  | TRUE | UTS - Envir. & Process Chem |  | Ronald Madron | Marcus Huddleston |  | Jean Leger | No additional comments. |  |  | Very High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.01.2 Inadequate development of standards: coordination with process design |  |  | Unsecured nut and wash falling form height (250') | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level
8986 | Sooner Power Plant | 2019-08-14 10:00 | While attempting to utilize trolley on 250 foot level, a washer was witnessed falling from trolley stop. Member identified that trolley stop was missing washer and nut. | Level 4 |  | TRUE | Property Damage | Jean Leger | Jerrod Moser | BIll Young will lead. | 2019-08-19 13:56 | OG&E Corp Services | Marcus Huddleston | 2019-10-15 10:50 | 2019-08-15 17:04 | 2019-08-15 17:04 | 2019-09-10 13:46 | 2019-09-23 | 2019-08-15 16:54 | 2019-09-23 17:33 |  |  | Unit 1 stack, 250 foot level, Sooner Power Plant |  |  | Jerrod Moser | approved | UTS |  | Level 4 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Marcus Huddleston |  | While performing RATA testing at the 250' level on unit one at the Sooner Power Plant a crew member thought he saw something fall off the end of the jib rail. Upon investigation the crew found that the nut and washer was missing from the bolt that secures the rail stop to the end of the jib. The crew located the washer on the ground but did not find the nut. | Marcus Huddleston | William Young |  | Sooner Power Plant | TRUE |  | TRUE | UTS - Envir. & Process Chem |  | Ronald Madron | Marcus Huddleston |  | Jean Leger | No additional comments. |  |  | Very High |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.04 Giving inadequate policy, procedure, practices or guidelines |  |  |  |  | 14.04 Inadequate monitoring of compliance |  |  | Unsecured nut and wash falling form height (250') | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level
8987 | Metro Service Center | 2019-08-15 10:00 | Public vehicle drifted into right hand lane and made incidental contact with drivers side mirror on company vehicle. No damage | Level 1 |  | TRUE | Vehicle |  |  |  |  | OG&E Corp Services | Lindle Coleman | 2019-09-05 09:16 | 2019-08-16 09:07 | 2019-08-16 09:07 | 2019-08-16 09:25 | 2019-08-29 10:00 | 2019-08-15 10:00 | 2019-09-03 13:23 |  |  | I-40 east bound, in the right hand lane, 2 miles west of Choctaw exit. |  |  | Cody Vinyard | Approved, Cody Vinyard | Enterprise Services |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Lindle Coleman |  | OGE Member was in a company vehicle, medium size pickup, and was traveling, east on I-40, in the right hand lane at posted speed limit of 70mph. a mid-size Nissan SUV was traveling the same direction, east on I-40 in the left hand lane and a higher rate of speed and as they passed the company members vehicle they drifted over and clipped mirrors. Publics passenger mirror clipped companies drivers side mirror. No damage occurred. |  |  |  | Metro Service Center | FALSE |  | TRUE | Other |  | Brent Perdue | Lindle Coleman |  | Jerrod Moser | Make sure we discuss defensive driving with the member. Attention to surroundings. | Jerrod Moser |  | Low |  | 2.07 Slow reaction time | [14 empty] | Public distracted driving. | 19. Failure to React, Correct | 2. Struck By (Hit By Moving Object)
8987 | Metro Service Center | 2019-08-15 10:00 | Public vehicle drifted into right hand lane and made incidental contact with drivers side mirror on company vehicle. No damage | Level 1 |  | TRUE | Vehicle |  |  |  |  | OG&E Corp Services | Lindle Coleman | 2019-09-05 09:16 | 2019-08-16 09:07 | 2019-08-16 09:07 | 2019-08-16 09:25 | 2019-08-29 10:00 | 2019-08-15 10:00 | 2019-09-03 13:23 |  |  | I-40 east bound, in the right hand lane, 2 miles west of Choctaw exit. |  |  | Cody Vinyard | Approved, Cody Vinyard | Enterprise Services |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Lindle Coleman |  | OGE Member was in a company vehicle, medium size pickup, and was traveling, east on I-40, in the right hand lane at posted speed limit of 70mph. a mid-size Nissan SUV was traveling the same direction, east on I-40 in the left hand lane and a higher rate of speed and as they passed the company members vehicle they drifted over and clipped mirrors. Publics passenger mirror clipped companies drivers side mirror. No damage occurred. |  |  |  | Metro Service Center | FALSE |  | TRUE | Other |  | Brent Perdue | Lindle Coleman |  | Jerrod Moser | Make sure we discuss defensive driving with the member. Attention to surroundings. | Jerrod Moser |  | Low |  | 2.07 Slow reaction time | [14 empty] | Public Driver distracted. | 19. Failure to React, Correct | 2. Struck By (Hit By Moving Object)
8988 | River Valley | 2019-08-17 11:00 | Contract employee was tightening a bolt with an impact gun. The bolt was holding a 3 inch by 3 inch piece of angle iron. The bolt broke and the angle iron fell to the ground. The area was barricaded off with read tape and danger tags. The angle iron fell within the barricaded area. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Michael Smith | 2019-10-10 15:45 | 2019-08-17 12:37 | 2019-08-17 12:37 | 2019-09-27 14:09 | 2019-08-31 11:00 | 2019-08-17 11:46 | 2019-10-03 15:42 |  |  | River Valley PP Unit 2B floor 4.5 |  |  | Anthony Gillespie | Inspection of securing devices will help reduce the likelihood of a similar failure and the use of barrier devices such as netting should eliminate the potential for a similar accident to occur. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Michael Smith |  | Contract employee was tightening a bolt with an impact gun. The bolt was holding a 3 inch by 3 inch piece of angle iron. The bolt broke and the angle iron fell to the ground. The area was barricaded off with red tape and danger tags. The angle iron fell within the barricaded area. After inspection of the bolt it appeared to be rusty and possibly fatigued possibly causing the failure. |  |  |  | River Valley | FALSE |  | TRUE | Maintenance |  | Bradlee Pogue | Michael Smith |  | Timothy Chancellor | Approved. | Timothy Chancellor |  | Low | [14 empty] | 15.04 Improper loading or rate of use |  | The bolt was reused and after investigation appeared to be fatigued. | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure | [5 empty] | Property Damage |  | Michael Smith | [5 empty] | 2. Struck By (Hit By Moving Object) | Bradlee Pogue | Zachry | Ronald Alexander |  |  |  | Michael Smith
8988 | River Valley | 2019-08-17 11:00 | Contract employee was tightening a bolt with an impact gun. The bolt was holding a 3 inch by 3 inch piece of angle iron. The bolt broke and the angle iron fell to the ground. The area was barricaded off with read tape and danger tags. The angle iron fell within the barricaded area. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Michael Smith | 2019-10-10 15:45 | 2019-08-17 12:37 | 2019-08-17 12:37 | 2019-09-27 14:09 | 2019-08-31 11:00 | 2019-08-17 11:46 | 2019-10-03 15:42 |  |  | River Valley PP Unit 2B floor 4.5 |  |  | Anthony Gillespie | Inspection of securing devices will help reduce the likelihood of a similar failure and the use of barrier devices such as netting should eliminate the potential for a similar accident to occur. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Michael Smith |  | Contract employee was tightening a bolt with an impact gun. The bolt was holding a 3 inch by 3 inch piece of angle iron. The bolt broke and the angle iron fell to the ground. The area was barricaded off with red tape and danger tags. The angle iron fell within the barricaded area. After inspection of the bolt it appeared to be rusty and possibly fatigued possibly causing the failure. |  |  |  | River Valley | FALSE |  | TRUE | Maintenance |  | Bradlee Pogue | Michael Smith |  | Timothy Chancellor | Approved. | Timothy Chancellor |  | Low | [14 empty] | 15.04 Improper loading or rate of use |  | The bolt was reused and after investigation appeared to be fatigued. | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure | [5 empty] | Injury / Illness |  | Michael Smith | [5 empty] | 2. Struck By (Hit By Moving Object) | Bradlee Pogue | Zachry | Ronald Alexander |  |  |  | Michael Smith
8989 | North Service Center | 2019-08-18 13:00 | General Forman, Forman and two crew people were in the backyard on storm related outage trimming trees. The property owner was on-site. All the personnel completed the work and exited the yard, for some reason the Forman returned to the backyard and the dog attached him. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Brian Hall | 2019-10-09 14:46 | 2019-08-19 16:36 | 2019-08-19 16:36 | 2019-09-19 16:41 | 2019-09-01 13:00 | 2019-08-19 16:15 | 2019-09-30 15:53 |  | 2019-09-24 12:31 | 4401 South Western Oklahoma, OK 73109 |  |  | William Young | Chris and Jerrie: The incident report under cause description indicates that the dog bite was unpredictable. Based on the description, I disagree with that assessment given the fact that the dog was unsecured in the back yard but in the presence of the owner. Do we know if the owner had went back in the house leaving the dog unsecured in the yard? The dog without the owner changes the dynamic. Before entering the gate did the foreman check to see if the owner was still present? It appear not since the description below does not indicate owner present. Entering that back yard through the gate without the owner present and the dog biting is very predictable. The preventable action would have been for the foreman to go to the front door and asked for the dog to be secured. I have approved the report, but we need to be a little more probative and challenging with incidents like this. WCY 10-9-19 | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Brian Hall |  | Asplundh Tree Experts were called to a tree outage job on Sunday August 18th at 1:00 p.m. The homeowner and a rental tenant were on the property as the work was being done. The rental tenant had an unrestrained mixed bread dog on the premises when the trim work was being done. After completing the outage work, all Asplundh employees exited the job site. The Foreman had to reenter the job site through the gate to look for missing equipment. This when the dog attacked him biting him on the upper thigh. The Forman did receive medical attention from nearest medical facility. The dog was put into quarantine by Oklahoma City Animal Control, due to no vaccinations within the last five years. The Forman has not required further medical attention or missed any work hours at the time of this report. |  |  |  | North Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Brian Hall | Christopher Martin |  | Nicole Rhodes | Reviewed after additions made. No comments. | Nicole Rhodes |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Dog was unpredictable with owners presence on job site. | 03. Failure to Secure | 13. Environmental Release |  | Returned for review, J. Looney, 9/18/19 Returned for edit, J. Looney, 9/20/19 - see workflow notes |  |  |  | Injury / Illness |  | Brian Hall |  | Dog Bite | FALSE |  |  | 9. Abnormal Operation | Brian Hall | Asplundh Tree Experts | Brad Masters | Insect/Animal Bite |  | Leg | Brian Hall | Right | TRUE | Company Vehicle | [68 empty] | 8859682
8990 | Metro Service Center | 2019-08-18 18:00 | Member required medical attention after experiencing fatigue and feeling disoriented. | Level 3 |  | FALSE | Member Injury |  | Lindle Coleman | reviewed with ops leaders | 2019-08-26 09:35 | Power Delivery | Phillip Hayes | 2019-09-03 14:18 | 2019-08-20 07:50 | 2019-08-20 07:50 | 2019-08-29 06:55 | 2019-09-01 18:00 | 2019-08-20 07:33 | 2019-08-29 10:39 | 2019-08-29 10:45 | 2019-08-29 06:57 | Behind business at Robinson and Porter Street in Norman, OK |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Brent Perdue |  | The member received the initial call around 10:00 to meet the line crew at the Norman Service Center around 11:00 where they went over a tailboard explaining the job scope, obtained a service bucket, and loaded material for a CT meter loop that was damaged during a storm. After arriving at the job site the line crew and member held a documented tailboard and started work about 11:30. It was determined that the wrong CT’s were loaded after assessing the damaged CT meter loop. Around 12:00 the member had to go back to Norman Service Center to pick up and assemble the correct CT’s on the dock. He returned to the job site at approximately 13:15, and for the following 2 hours started taking down the damaged CT equipment, and installing new CT equipment. Around 15:00 the member called his supervisor to get approval for another meter tech assist him in the completion of the meter loop. The additional meter tech was needed due to the fact that he did not have his normal work truck that contained the required material to complete the job. After receiving permission from his supervisor (around 15:15-15:30) the additional meter tech was contacted and requested to come assist in the restoration. They agreed to meet at the Braums restaurant in the adjacent parking lot. (This is where the member was taking a lunch break) Before going for his lunch break, the member stopped by the line crew’s work site to see if they were planning to stop for lunch as well. The line crew said they were not stopping for lunch. At approximately 16:00 the additional meter tech arrived at Braums were he allowed the member to finish his lunch and they discussed the job scope. After talking about the job scope the additional meter tech purchased ice for his ice chest and they proceeded to the job site around 17:00. When at the job site they completed a documented tailboard and agreed that the member would perform bucket work and the additional meter tech would perform the ground duties. In about 30 minutes after starting the job, the member called down from the bucket and asked the additional meter tech to give him a Gatorade. The member complained that his hands and arms were beginning to cramp, and the additional meter tech asked if he could give the member a break. The member refused, insisting that he could finish the job. In a short time after this the member had to stop and ask for another Gatorade because the cramping was still persisting. The additional meter tech told the member to come down at this time and let him finish the job, and the member agreed. The member exited the bucket on his own power and sat on the steps of the bucket truck. The member requested that the additional meter tech get the crew foreman and inform him that he wasn’t feeling well. After the additional meter tech tried to reach out to the foreman, the member asked him to call 911. While 911 was being called the crew came over and assisted the member by giving him a wet rag and placed him in a truck with the air conditioner running until emergency services could arrive. Summary: According to the Medical Services Consultant, a licensed healthcare provider (Doctor of Osteopathic Medicine (D.O.)), the primary cause of the member’s condition was not heat related. Cause of the Event: According the Medical Services Consultant, a licensed healthcare provider (Doctor of Osteopathic Medicine (D.O.)), the member reportedly had another underlying medical condition that would have been the major cause of his illness. Timeline: • 10:00 to 11:30- Loading materials. (warehouse environment, indoor, shaded) • 11:30 to 12:00- Assessing damage. (outdoor at jobsite) • 12:00 to 13:15- Gathering and assembling materials, driving to and from the job site (approximately 15-20 minutes one way). (air conditioned vehicle, indoor and shaded warehouse environment) • 13:15 to 15:00- Rebuilding damaged meter loop. (outdoors at jobsite) • 15:00 to 15:45- Making phone calls and communicating with line crew (air conditioned vehicle, outdoor at jobsite) • 15:45 to 17:00- Walked to lunch, ate lunch, discussed job scope. (air conditioned environment) • 17:00 to 18:00- Working on meter loop. Came down and ambulance called during this time. (outdoor at jobsite). Other Facts Gathered: • The event occurred while working unplanned work/work hours due to storm. (Call out) • Member did not have his normal work truck. • Member did take some water breaks. (3-4 bottles of water, 2 bottle of Gatorade) • Witnesses mentioned that the member complained of dizziness due to hunger before taking lunch break. • Member signed on to line crew’s tailboard, but kept the CT work completely separate from the line crew work. o Sole task was to work on CT meter loop o The member also held a separate tailboard when the additional meter tech arrived at the work area. • Member had access to water from the line crew.] | Brent Perdue | Lewis Wilson | FALSE | Metro Service Center | TRUE |  | FALSE | PD Operations Services |  |  | Phillip Hayes |  | Steve Watkins | I approve. SW | Steve Watkins | Lindle Coleman | High |  |  | 3.01 Injury or illness | [13 empty] | stop work when warning signs are present | 18. Failure to Check, Monitor | 11. Overstress, Overpressure, Overexertion, Ergonomic | approved | This incident has been reviewed and the results of the investigation are all listed in the report | [24 empty] | FALSE | [5 empty] | 2019-08-18 10:00 | 0 | 0 | wet rag, placed in air conditioned truck and given fluids (water, Gatorade) | FALSE |  | According to the OG&E Medical Services Consultant the member reportedly has another under lying medical condition that would have been the major cause of this incident. |  | TRUE | Billy Atchley |  | Non-Recordable | Billy Atchley | TRUE |  | Norman Regional and Oklahoma Heart Hospital-North |  | Heart Attack |  | FALSE |  | Meter Tech | Heart |  |  | FALSE | Phillip Hayes | FALSE | 2019 | 8/18/2019 10:00:00 AM | 10 | TRUE | TRUE | TRUE | unknown | Rebuilding a CT meter loop that was damaged in a storm. | [24 empty] | 8589529
8990 | Metro Service Center | 2019-08-18 18:00 | Member required medical attention after experiencing fatigue and feeling disoriented. | Level 3 |  | FALSE | Member Injury |  | Lindle Coleman | reviewed with ops leaders | 2019-08-26 09:35 | Power Delivery | Phillip Hayes | 2019-09-03 14:18 | 2019-08-20 07:50 | 2019-08-20 07:50 | 2019-08-29 06:55 | 2019-09-01 18:00 | 2019-08-20 07:33 | 2019-08-29 10:39 | 2019-08-29 10:45 | 2019-08-29 06:57 | Behind business at Robinson and Porter Street in Norman, OK |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Brent Perdue |  | The member received the initial call around 10:00 to meet the line crew at the Norman Service Center around 11:00 where they went over a tailboard explaining the job scope, obtained a service bucket, and loaded material for a CT meter loop that was damaged during a storm. After arriving at the job site the line crew and member held a documented tailboard and started work about 11:30. It was determined that the wrong CT’s were loaded after assessing the damaged CT meter loop. Around 12:00 the member had to go back to Norman Service Center to pick up and assemble the correct CT’s on the dock. He returned to the job site at approximately 13:15, and for the following 2 hours started taking down the damaged CT equipment, and installing new CT equipment. Around 15:00 the member called his supervisor to get approval for another meter tech assist him in the completion of the meter loop. The additional meter tech was needed due to the fact that he did not have his normal work truck that contained the required material to complete the job. After receiving permission from his supervisor (around 15:15-15:30) the additional meter tech was contacted and requested to come assist in the restoration. They agreed to meet at the Braums restaurant in the adjacent parking lot. (This is where the member was taking a lunch break) Before going for his lunch break, the member stopped by the line crew’s work site to see if they were planning to stop for lunch as well. The line crew said they were not stopping for lunch. At approximately 16:00 the additional meter tech arrived at Braums were he allowed the member to finish his lunch and they discussed the job scope. After talking about the job scope the additional meter tech purchased ice for his ice chest and they proceeded to the job site around 17:00. When at the job site they completed a documented tailboard and agreed that the member would perform bucket work and the additional meter tech would perform the ground duties. In about 30 minutes after starting the job, the member called down from the bucket and asked the additional meter tech to give him a Gatorade. The member complained that his hands and arms were beginning to cramp, and the additional meter tech asked if he could give the member a break. The member refused, insisting that he could finish the job. In a short time after this the member had to stop and ask for another Gatorade because the cramping was still persisting. The additional meter tech told the member to come down at this time and let him finish the job, and the member agreed. The member exited the bucket on his own power and sat on the steps of the bucket truck. The member requested that the additional meter tech get the crew foreman and inform him that he wasn’t feeling well. After the additional meter tech tried to reach out to the foreman, the member asked him to call 911. While 911 was being called the crew came over and assisted the member by giving him a wet rag and placed him in a truck with the air conditioner running until emergency services could arrive. Summary: According to the Medical Services Consultant, a licensed healthcare provider (Doctor of Osteopathic Medicine (D.O.)), the primary cause of the member’s condition was not heat related. Cause of the Event: According the Medical Services Consultant, a licensed healthcare provider (Doctor of Osteopathic Medicine (D.O.)), the member reportedly had another underlying medical condition that would have been the major cause of his illness. Timeline: • 10:00 to 11:30- Loading materials. (warehouse environment, indoor, shaded) • 11:30 to 12:00- Assessing damage. (outdoor at jobsite) • 12:00 to 13:15- Gathering and assembling materials, driving to and from the job site (approximately 15-20 minutes one way). (air conditioned vehicle, indoor and shaded warehouse environment) • 13:15 to 15:00- Rebuilding damaged meter loop. (outdoors at jobsite) • 15:00 to 15:45- Making phone calls and communicating with line crew (air conditioned vehicle, outdoor at jobsite) • 15:45 to 17:00- Walked to lunch, ate lunch, discussed job scope. (air conditioned environment) • 17:00 to 18:00- Working on meter loop. Came down and ambulance called during this time. (outdoor at jobsite). Other Facts Gathered: • The event occurred while working unplanned work/work hours due to storm. (Call out) • Member did not have his normal work truck. • Member did take some water breaks. (3-4 bottles of water, 2 bottle of Gatorade) • Witnesses mentioned that the member complained of dizziness due to hunger before taking lunch break. • Member signed on to line crew’s tailboard, but kept the CT work completely separate from the line crew work. o Sole task was to work on CT meter loop o The member also held a separate tailboard when the additional meter tech arrived at the work area. • Member had access to water from the line crew.] | Lindle Coleman | Lewis Wilson | FALSE | Metro Service Center | TRUE |  | FALSE | PD Operations Services |  |  | Phillip Hayes |  | Steve Watkins | I approve. SW | Steve Watkins | Lindle Coleman | High |  |  | 3.01 Injury or illness | [13 empty] | stop work when warning signs are present | 18. Failure to Check, Monitor | 11. Overstress, Overpressure, Overexertion, Ergonomic | approved | This incident has been reviewed and the results of the investigation are all listed in the report | [24 empty] | FALSE | [5 empty] | 2019-08-18 10:00 | 0 | 0 | wet rag, placed in air conditioned truck and given fluids (water, Gatorade) | FALSE |  | According to the OG&E Medical Services Consultant the member reportedly has another under lying medical condition that would have been the major cause of this incident. |  | TRUE | Billy Atchley |  | Non-Recordable | Billy Atchley | TRUE |  | Norman Regional and Oklahoma Heart Hospital-North |  | Heart Attack |  | FALSE |  | Meter Tech | Heart |  |  | FALSE | Phillip Hayes | FALSE | 2019 | 8/18/2019 10:00:00 AM | 10 | TRUE | TRUE | TRUE | unknown | Rebuilding a CT meter loop that was damaged in a storm. | [24 empty] | 8589529
8990 | Metro Service Center | 2019-08-18 18:00 | Member required medical attention after experiencing fatigue and feeling disoriented. | Level 3 |  | FALSE | Member Injury |  | Lindle Coleman | reviewed with ops leaders | 2019-08-26 09:35 | Power Delivery | Phillip Hayes | 2019-09-03 14:18 | 2019-08-20 07:50 | 2019-08-20 07:50 | 2019-08-29 06:55 | 2019-09-01 18:00 | 2019-08-20 07:33 | 2019-08-29 10:39 | 2019-08-29 10:45 | 2019-08-29 06:57 | Behind business at Robinson and Porter Street in Norman, OK |  |  |  | Approve | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Brent Perdue |  | The member received the initial call around 10:00 to meet the line crew at the Norman Service Center around 11:00 where they went over a tailboard explaining the job scope, obtained a service bucket, and loaded material for a CT meter loop that was damaged during a storm. After arriving at the job site the line crew and member held a documented tailboard and started work about 11:30. It was determined that the wrong CT’s were loaded after assessing the damaged CT meter loop. Around 12:00 the member had to go back to Norman Service Center to pick up and assemble the correct CT’s on the dock. He returned to the job site at approximately 13:15, and for the following 2 hours started taking down the damaged CT equipment, and installing new CT equipment. Around 15:00 the member called his supervisor to get approval for another meter tech assist him in the completion of the meter loop. The additional meter tech was needed due to the fact that he did not have his normal work truck that contained the required material to complete the job. After receiving permission from his supervisor (around 15:15-15:30) the additional meter tech was contacted and requested to come assist in the restoration. They agreed to meet at the Braums restaurant in the adjacent parking lot. (This is where the member was taking a lunch break) Before going for his lunch break, the member stopped by the line crew’s work site to see if they were planning to stop for lunch as well. The line crew said they were not stopping for lunch. At approximately 16:00 the additional meter tech arrived at Braums were he allowed the member to finish his lunch and they discussed the job scope. After talking about the job scope the additional meter tech purchased ice for his ice chest and they proceeded to the job site around 17:00. When at the job site they completed a documented tailboard and agreed that the member would perform bucket work and the additional meter tech would perform the ground duties. In about 30 minutes after starting the job, the member called down from the bucket and asked the additional meter tech to give him a Gatorade. The member complained that his hands and arms were beginning to cramp, and the additional meter tech asked if he could give the member a break. The member refused, insisting that he could finish the job. In a short time after this the member had to stop and ask for another Gatorade because the cramping was still persisting. The additional meter tech told the member to come down at this time and let him finish the job, and the member agreed. The member exited the bucket on his own power and sat on the steps of the bucket truck. The member requested that the additional meter tech get the crew foreman and inform him that he wasn’t feeling well. After the additional meter tech tried to reach out to the foreman, the member asked him to call 911. While 911 was being called the crew came over and assisted the member by giving him a wet rag and placed him in a truck with the air conditioner running until emergency services could arrive. Summary: According to the Medical Services Consultant, a licensed healthcare provider (Doctor of Osteopathic Medicine (D.O.)), the primary cause of the member’s condition was not heat related. Cause of the Event: According the Medical Services Consultant, a licensed healthcare provider (Doctor of Osteopathic Medicine (D.O.)), the member reportedly had another underlying medical condition that would have been the major cause of his illness. Timeline: • 10:00 to 11:30- Loading materials. (warehouse environment, indoor, shaded) • 11:30 to 12:00- Assessing damage. (outdoor at jobsite) • 12:00 to 13:15- Gathering and assembling materials, driving to and from the job site (approximately 15-20 minutes one way). (air conditioned vehicle, indoor and shaded warehouse environment) • 13:15 to 15:00- Rebuilding damaged meter loop. (outdoors at jobsite) • 15:00 to 15:45- Making phone calls and communicating with line crew (air conditioned vehicle, outdoor at jobsite) • 15:45 to 17:00- Walked to lunch, ate lunch, discussed job scope. (air conditioned environment) • 17:00 to 18:00- Working on meter loop. Came down and ambulance called during this time. (outdoor at jobsite). Other Facts Gathered: • The event occurred while working unplanned work/work hours due to storm. (Call out) • Member did not have his normal work truck. • Member did take some water breaks. (3-4 bottles of water, 2 bottle of Gatorade) • Witnesses mentioned that the member complained of dizziness due to hunger before taking lunch break. • Member signed on to line crew’s tailboard, but kept the CT work completely separate from the line crew work. o Sole task was to work on CT meter loop o The member also held a separate tailboard when the additional meter tech arrived at the work area. • Member had access to water from the line crew.] | Phillip Hayes | Lewis Wilson | FALSE | Metro Service Center | TRUE |  | FALSE | PD Operations Services |  |  | Phillip Hayes |  | Steve Watkins | I approve. SW | Steve Watkins | Lindle Coleman | High |  |  | 3.01 Injury or illness | [13 empty] | stop work when warning signs are present | 18. Failure to Check, Monitor | 11. Overstress, Overpressure, Overexertion, Ergonomic | approved | This incident has been reviewed and the results of the investigation are all listed in the report | [24 empty] | FALSE | [5 empty] | 2019-08-18 10:00 | 0 | 0 | wet rag, placed in air conditioned truck and given fluids (water, Gatorade) | FALSE |  | According to the OG&E Medical Services Consultant the member reportedly has another under lying medical condition that would have been the major cause of this incident. |  | TRUE | Billy Atchley |  | Non-Recordable | Billy Atchley | TRUE |  | Norman Regional and Oklahoma Heart Hospital-North |  | Heart Attack |  | FALSE |  | Meter Tech | Heart |  |  | FALSE | Phillip Hayes | FALSE | 2019 | 8/18/2019 10:00:00 AM | 10 | TRUE | TRUE | TRUE | unknown | Rebuilding a CT meter loop that was damaged in a storm. | [24 empty] | 8589529
8991 | Metro Service Center | 2019-08-20 08:30 | This is a First Aid. Member smashed finger while putting bar into cable trailer. | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Brent Boles | 2019-08-26 10:55 | 2019-08-20 14:24 | 2019-08-20 14:24 | 2019-08-20 14:38 | 2019-09-03 08:30 | 2019-08-20 14:14 |  |  |  | Metro Service Center |  |  | Terry Hackett | Reviewed and approved. A JHA will be conducted to identify similar risks and controls for this piece of equipment. | T&D Ops |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE |  |  | While placing securement rod into the slot on the cable trailer the rod was met with resistance. The member pressed harder on the rod with his left hand, the rod began to insert quickly, and smashed his right index finger. Facts Ascertained: This is the manufactured rod that is provided with the equipment The securement rod has been known to "get in a bind" Member placed hand in the line of fire |  |  | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Taylor Barnett | Brent Boles |  |  |  | Quay Prough |  | Low | [45 empty] | FALSE |  |  | 2018-03-12 | 1995-08-03 |  | 2019-08-20 07:00 | 0 | 0 | Iced finger 15 minutes on and 15 minutes off and over the counter ibuprofen | FALSE |  | While securing reel on cable trailer, the L shaped rod that holds the reel on had resistance so member pushed harder. When bar finally dropped it twisted a bit and bar smashed the index finger on members right hand. |  | TRUE | Taylor Barnett |  | First Aid | Taylor Barnett |  |  |  |  | Crush/Smash |  | FALSE |  | Cable Splicer Appr | Finger |  | Right | FALSE | Brent Boles | FALSE |  | 8/20/2019 7:00:00 AM | 1 year 5 months | FALSE |  |  | L shaped rod on cable trailer
8992 | Muskogee Power Plant | 2019-08-20 11:00 | Onsite Reliable Services driver backed up and hit Collins Electric van | Level 2 |  | FALSE | Contractor | Stephen Merrill |  |  |  | Power Supply | Scott Stidham | 2019-11-16 11:22 | 2019-08-21 11:48 | 2019-08-21 11:48 | 2019-10-16 08:54 | 2019-09-03 11:00 | 2019-08-21 11:43 | 2019-11-11 11:02 |  | 2019-10-17 07:02 | Muskogee contractor entrance |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Phillip Messer |  | Backing incident at Muskogee Power Plant which occurred at the entrance of the plant near the guard shack. Reliable Onsite Services finished servicing equipment and returned to vehicle, then proceeded unknowingly to backup into a van. Basic Report Intake was given to local police. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | Other |  | Jerry Herriman | Scott Stidham |  | Alinor Wint | James Morris has completed action items related to this incident. |  |  | Medium | [5 empty] | 6.02 Inadequate practice | [10 empty] | awareness of surroundings | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) |  | Please add a corrective action. Corrective action added Reviewed Bob Wright |  |  |  | Vehicle |  | Robert Wright | [5 empty] | 2. Struck By (Hit By Moving Object) | Jerry Herriman | Onsite Reliable Services | Earl Martin |  |  |  | Robert Wright |  |  |  |  | FALSE
8993 | North Service Center | 2019-06-24 10:00 | Member was operating an extend stick and felt discomfort In his left leg. Member reported incident and returned back to work. | Level 2 |  | FALSE | Member Injury | Andrea Dennis |  |  |  | Power Delivery | Eric Engles | 2019-09-13 10:41 | 2019-08-22 10:24 | 2019-08-22 10:24 | 2019-09-03 09:28 | 2019-07-08 10:00 | 2019-08-22 10:19 | 2019-09-13 10:35 |  | 2019-09-05 12:46 | Guthrie High School |  |  | Lindle Coleman | reviewed | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Eric Engles |  | On June 24, 2019 Member received trouble ticket to replace a fuse in a cut out. When the member arrived he placed the fuse on the end of the extendo stick that was fully extended. He then anchored the stick on the inside of his left leg to lift it to the cutout. As he raised the fuse he felt a discomfort in his left leg/groin. The member did state that the windy conditions could have added to the strain placed on him by the extendo stick. At this time he stopped work and contacted his supervisor to fill out a first aid. However, he did not feel like any additional medical attention was necessary. Follow up with the member indicated that the member was improving. However on August 12, 2019, the member alerted his supervisor that there was still discomfort in the previously affected groin. At this point he went to the clinic who pointed him to a specialist. The specialist decided that there was further medical attention needed. |  |  | TRUE | North Service Center | FALSE |  | FALSE | Construction Services | 8919 | Kelley Watson | Eric Engles |  | Chad Self | Approved | Chad Self |  | Medium | [6 empty] | 7.06 Improper attempt to save time or effort | [5 empty] | 13.02 Inadequate human factors/ergonomics considerations |  |  |  | the strain placed on the extendo stick by the weather conditions caused the strain on the member | 40. Weather Conditions | 11. Overstress, Overpressure, Overexertion, Ergonomic |  | Approved. | [24 empty] | FALSE |  | Days away from Work (H) | 2007-05-29 | 1970-10-18 |  | 2019-06-24 07:00 | 15 | 43 |  | FALSE |  | Member was operating an extendo stick. |  |  | Kelley Watson |  | Recordable | Kelley Watson |  |  |  |  | Hernia |  | TRUE |  | Area Service Technician | Groin | Injury | Left | TRUE | Eric Engles | TRUE | 2019 | 6/24/2019 7:00:00 AM |  | FALSE |  |  | Force of lifting extendo stick
8994 | Northeast District Service Cen | 2019-08-20 08:30 | West tree crew hit gas meter leaving job site. meter had been previously identified, but ground man removed cones marking meter in preparation of leaving location, and did not remind or spot for the Forman driving the truck. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Wesley Lanier | 2019-10-02 12:53 | 2019-08-22 16:37 | 2019-08-22 16:37 | 2019-09-30 11:04 | 2019-09-03 08:30 | 2019-08-20 09:00 | 2019-09-30 15:50 |  | 2019-09-30 15:36 | Alley behind 1001 5th St., Beggs, OK |  |  | William Young | Returned for additional work on Corrective Actions. Documented safety talk around incident to be conducted for all West crews assigned to OGE work. Rosters with attendee names and signatures to be uploaded to incident record. 9-23-2019 | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Wesley Lanier |  | On Tuesday August 20th, 2019, foreman Jimmy Estes and groundsman Josh Harkey were trimming lines down an easement off of 1001 5th Street in Beggs, OK. The crew immediately identified a gas meter located on the corner of the property, at the entrance of the easement. Estes noted on his JSA the presence of the meter and Harkey marked the meter with cones prior to crew backing the truck down the easement. Harkey served as the spotter to direct the truck as it was backed in to location for trimming. The crew then completed a walk-through of the jobsite and discussed job briefing. Once the crew finished trimming and cleaned up the jobsite, Harkey picked up all the cones, including the ones around the gas meter and loaded them onto the truck. After doing so, Harkey failed to remind Estes about the gas meter and did not spot him as he pulled the truck forward out of the easement. Estes took the turn too sharp and clipped the top of the gas meter with the truck step on the passenger side. When the truck step clipped the meter it busted the top, causing a gas leak. The crew notified their General Foreman, who then contacted Oklahoma Natural Gas and West Tree Safety. Oklahoma Natural Gas arrived on the scene and began making repairs. |  |  |  | Northeast District Service Cen | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Wesley Lanier | Wesley Lanier |  | Nicole Rhodes | Reviewed. 09/12/19 | Nicole Rhodes |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction | 7.06 Improper attempt to save time or effort | 8.2.2 Improper conduct that is not condoned: Unintentional | 9.03 Improper or insufficient delegation | [7 empty] | not fully staying on task | 02. Failure to Warn | 1. Struck Against (Running or Bumping Into) |  | Please add corrective actions to OGE report, J. Looney 8/23/19 Please amend corrective action per phone msg, J. Looney, 9/26/19 Approved! J. Looney, 9/30/19 |  |  |  | Vehicle |  | Wesley Lanier | Hit gas meter |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Wesley Lanier | West Tree | Jimmy Estes |  | Fixed Equipment |  | Wesley Lanier |  |  |  |  | FALSE
8994 | Northeast District Service Cen | 2019-08-20 08:30 | West tree crew hit gas meter leaving job site. meter had been previously identified, but ground man removed cones marking meter in preparation of leaving location, and did not remind or spot for the Forman driving the truck. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Wesley Lanier | 2019-10-02 12:53 | 2019-08-22 16:37 | 2019-08-22 16:37 | 2019-09-30 11:04 | 2019-09-03 08:30 | 2019-08-20 09:00 | 2019-09-30 15:50 |  | 2019-09-30 15:36 | Alley behind 1001 5th St., Beggs, OK |  |  | William Young | Returned for additional work on Corrective Actions. Documented safety talk around incident to be conducted for all West crews assigned to OGE work. Rosters with attendee names and signatures to be uploaded to incident record. 9-23-2019 | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Wesley Lanier |  | On Tuesday August 20th, 2019, foreman Jimmy Estes and groundsman Josh Harkey were trimming lines down an easement off of 1001 5th Street in Beggs, OK. The crew immediately identified a gas meter located on the corner of the property, at the entrance of the easement. Estes noted on his JSA the presence of the meter and Harkey marked the meter with cones prior to crew backing the truck down the easement. Harkey served as the spotter to direct the truck as it was backed in to location for trimming. The crew then completed a walk-through of the jobsite and discussed job briefing. Once the crew finished trimming and cleaned up the jobsite, Harkey picked up all the cones, including the ones around the gas meter and loaded them onto the truck. After doing so, Harkey failed to remind Estes about the gas meter and did not spot him as he pulled the truck forward out of the easement. Estes took the turn too sharp and clipped the top of the gas meter with the truck step on the passenger side. When the truck step clipped the meter it busted the top, causing a gas leak. The crew notified their General Foreman, who then contacted Oklahoma Natural Gas and West Tree Safety. Oklahoma Natural Gas arrived on the scene and began making repairs. |  |  |  | Northeast District Service Cen | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Wesley Lanier | Wesley Lanier |  | Nicole Rhodes | Reviewed. 09/12/19 | Nicole Rhodes |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction | 7.06 Improper attempt to save time or effort | 8.2.2 Improper conduct that is not condoned: Unintentional | 9.03 Improper or insufficient delegation | [7 empty] | not fully staying on task | 02. Failure to Warn | 1. Struck Against (Running or Bumping Into) |  | Please add corrective actions to OGE report, J. Looney 8/23/19 Please amend corrective action per phone msg, J. Looney, 9/26/19 Approved! J. Looney, 9/30/19 |  |  |  | Property Damage |  | Wesley Lanier | Hit gas meter |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Wesley Lanier | West Tree | Jimmy Estes |  | Fixed Equipment |  | Wesley Lanier |  |  |  |  | FALSE
8995 | Sooner Power Plant | 2019-08-21 14:00 | 2C BWCP was leaking out of the motor cavity thermocouple on startup. Upon inspection there was no thermowell installed on the motor cavity. Motor cavity pressure can run 2900 psi. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | William Cash | 2019-10-08 13:24 | 2019-08-23 12:20 | 2019-08-23 12:20 | 2019-09-08 19:15 | 2019-09-04 14:00 | 2019-08-23 11:38 | 2019-09-09 11:15 |  | 2019-09-09 07:25 | Sooner Unit 2 3rd level of boiler. |  |  | Jesse Murray | Approved. Jesse Murray 10/8/19 | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | William Cash |  | While firing the unit during startup on 8/20/19 a leak was found on 2C BWCP motor cavity thermocouple. It was decided to prewarm the turbine as long as we could then remove the fire from the boiler and allow it to cool and then drain to be able to repair the thermocouple on the morning of 8/21/19. Once the Thermocouple was removed it was determined there was not a thermowell installed. A 1”x ¼” hex bushing had been installed on the pump. This bushing is rated for 3000psi. We do no know who installed the bushing or when it was installed in the motor cavity. The bushing had been painted so the pump had been rebuilt and returned with the bushing installed. Sun star was contacted and they stated they did not install the bushing and recommended a thermowell be installed. This bushing is an exact match for the one we carry in stock. Sun Star verified the pump that had been removed and shipped to them for repair had a thermowell in the motor cavity. A new thermowell and thermocouple were installed in the pump motor cavity. This pump was installed on 8/5/19 while the unit was offline for boiler feed pump repairs. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | William Cash | William Cash |  | Frank Brixey | approved Brixey - 9/9/2019 | Frank Brixey |  | Medium |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | Failure to recognize the need for a Thermowell to be installed in motor cavity. | 15. Using Equipment Improperly | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Bill, I am returning Incident 8995. The investigation is good and it is very easy to understand what happened. What I think is missing is the “why” behind what happened. You put “Failure to recognize the need for a Thermowell to be installed in motor cavity.” as the cause description and marked “Lack of experience” as a root cause. I don’t see anything in the Detailed Description of Incident field that explains why those are your root causes. I would recommend talking with the member and discussing why they made the decision to put in the bushing instead of the thermowell. Add there reasoning to the detailed description and I think this incident will be good to go. I would also recommend adding the current task list for this job to the document attachments. Brady Sowell OGE Health and Safety Sooner Power Plant 405-206-9672 See 2nd workflow comment for approving comments. Approved by Sowell on 9/9 | [90 empty] | 9588915
8996 | Muskogee Power Plant | 2019-08-23 09:00 | Member was bolting Inlet water line back up to lube oil cooler. He dropped a 3/4" nut on the platform he was standing on. The nut bounced up and off of platform, falling to the grating on the Mezzanine below (approximately 10-12'). | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Samuel Spencer | 2019-12-05 09:56 | 2019-08-23 14:11 | 2019-08-23 14:11 | 2019-10-15 14:38 | 2019-09-06 09:00 | 2019-08-23 21:30 | 2019-11-11 14:27 |  | 2019-10-17 06:55 | Unit 6 Main Turbine Lube Oil Coolers |  |  | Jesse Murray | Approved. Jesse Murray 12/5/19 | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Samuel Spencer |  | While bolting up the circulating water inlet flange on unit 6's Main Turbine Lube Oil Cooler. Member dropped a 3/4" nut. It hit the grating on the platform he was standing on and bounced over the toe board and fell 10'6" to the Mezzanine below. Member had been working with another member when the job was first started. They originally had it barricaded off on the Mezzanine level and the basement below. They had removed the barricade on the Mezzanine level to get out of the way for the Oil Flush to take place. When member returned to the job the other member had went to a different job, so he proceeded with the task. He didn't replace the barricade on the Mezzanine level, the barricade was still in place on the basement level which is ~30' bellow the Mezzanine level. Member also failed to place any drop prevention mat on the platform he was standing on. Also noted, member should have had some of the orange retaining fence that we use on our handrails up |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Maintenance |  | Charles Harris | Samuel Spencer |  | Andy Hedge | Reviewed and approve. Andy Hedge - 11/11/19 | Andy Hedge |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Member dropped 3/4" nut | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) |  | The second entry of the cause analysis was updated to include : Was the correct policy, procedure or practice being followed? No Comment 13 SSOP.604.202 on barricades wasn't fallowed. Were the appropriate hazards/risks identified? No Comment 14 Member didn't identify that barricade wasn't put back up Reviewed by Bob Wright
8997 | General Service Center | 2019-08-22 15:00 | Carrier was attempting to leave in the incorrect direction. In doing so he contacted one of the bollards protecting a fire hydrant and damaged the fender to his truck. | Level 2 |  | TRUE | Contractor |  |  |  |  | OGE Energy Corp | Jeffery Richardson | 2019-09-25 18:24 | 2019-08-23 15:59 | 2019-08-23 15:59 | 2019-09-05 09:26 | 2019-09-05 15:00 | 2019-08-23 15:43 | 2019-09-16 12:55 |  | 2019-09-12 13:37 | General Service Center Building B |  |  | William Young | Reviewed and approved. WCY 9-25-19 | Enterprise Services |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Jeffery Richardson |  | A truck arrived to pick up empty steel reels. As the Anixter employee who would load the truck was being notified the truck was observed trying to turn the corner in a forklift only area. The driver was trying to turn left by the Southwest corner of Building B. The two Anixter employees went out to stop him. The driver was told: “this is not the way the trucks are supposed to be going and who told you to go this way?” He replied “ no one. The driver was told that he would have to back up but he would be guided out of his current location. He started backing up and when he got enough room in front of him to turn the wheels of the truck to go forward, a spotter went to stand by the fire hydrant directly in front of him. He started pulling forward and the spotter threw her hands in the air to tell him to stop. He didn’t stop and hit the yellow poles protecting the fire hydrant. He did not do any damage to the pole just the bumper on the front of his truck. He backed up and pulled around the hydrant. After getting him to a safe place he stated: “he didn’t know the hydrant or poles were there.” |  |  |  | General Service Center | FALSE |  | TRUE | Supply Chain |  | Jeffery Richardson | Jeffery Richardson |  | David Essary | I review and concur. | David Essary |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | This is a contractor only incident. Truck driver failed to familiarize himself with surrounding area and as a result went the wrong way & when leaving the area contacted a bollard. | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) |  | approved, Cody Vinyard |  |  |  | Vehicle |  | Jeffery Richardson | [5 empty] | 1. Struck Against (Running or Bumping Into) | Jeffery Richardson | Anixter | Dawn Smith |  |  |  | Jeffery Richardson
8998 | Metro Service Center | 2019-08-21 12:00 | While digging in new service employee snagged a secondary that was 6ft off locate | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Delivery | Garrett Bernethy | 2019-09-16 08:35 | 2019-08-26 09:09 | 2019-08-26 09:09 | 2019-08-26 09:48 | 2019-09-04 12:00 | 2019-08-26 08:56 | 2019-09-12 14:25 |  |  | Glennpool |  |  | Marcus Huddleston | No additional comments. MLH 9/16/19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Garrett Bernethy |  | While digging in new service employee snagged a secondary that was 6ft off locate |  |  |  | Metro Service Center | FALSE |  | FALSE | Resource Planning & Coord |  | Garrett Bernethy | Garrett Bernethy |  | John Legg | ` | John Legg |  | Low | [7 empty] | 8.2.2 Improper conduct that is not condoned: Unintentional | 9.09 Inadequate identification and evaluation of loss exposures | [7 empty] | The employees were following the proper procedure, Elliot's rule states that we're not to use equipment within 3ft of locates, the locates were 6ft off. | 25. Inadequate Warning System | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Garrett Bernethy | Cut UG Electrical Service |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Garrett Bernethy | Elliot | Jacob Phillips |  | Utility Strike |  | Garrett Bernethy |  |  |  |  | FALSE | [66 empty] | 7281696
8999 | Metro Service Center | 2019-08-23 12:40 | Bucket truck was parked in a lane that was closed by Action Safety. Crew was working on building a 3ph riser. Truck was clipped by a box truck on the knuckle of the boom. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Delivery | Garrett Bernethy | 2019-09-16 08:38 | 2019-08-26 10:32 | 2019-08-26 10:32 | 2019-08-26 12:16 | 2019-09-06 12:40 | 2019-08-26 09:49 | 2019-09-12 14:28 |  |  | 712 SW 104th |  |  | Marcus Huddleston | No additional comments. MLH 9/16/19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Garrett Bernethy |  | Bucket truck was parked in a lane that was closed by Action Safety. Crew was working on building a 3ph riser. Truck was clipped by a box truck on the knuckle of the boom. No injuries to parties involved. Truck has been removed from service to be tested and inspected before further use. |  |  |  | Metro Service Center | FALSE |  | FALSE | Resource Planning & Coord |  | Garrett Bernethy | John Legg |  | John Legg | Contractor has had the equipment inspected and repaired. Contractor will close lane as opposed to shifting lanes in the future. | John Legg |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Bucket truck was parked in a lane that was closed by Action Safety. Crew was working on building a 3ph riser. Truck was clipped by a box truck on the knuckle of the boom. | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) | [5 empty] | Vehicle |  | Garrett Bernethy | [5 empty] | 2. Struck By (Hit By Moving Object) | Garrett Bernethy | Drillworx | Chad White |  |  |  | Garrett Bernethy |  |  |  |  | FALSE | [66 empty] | 8859747
9000 | Metro Service Center | 2019-08-22 14:59 | Hit gas service at 720 flaming Oaks dr. no visible yellow paint on the ground it was going to a stub out that was not hooked up. Ong come out and caped off and took out stub out. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Delivery | Garrett Bernethy | 2019-09-16 08:39 | 2019-08-26 12:29 | 2019-08-26 12:29 | 2019-08-26 13:21 | 2019-09-05 14:59 | 2019-08-26 12:17 | 2019-09-12 14:30 |  |  | 720 Flaming Oaks dr. Norman, Ok |  |  | Marcus Huddleston | No additional comments. MLH 9/16/19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Garrett Bernethy |  | Hit gas service at 720 flaming Oaks dr no visible yellow paint on the ground it was going to a stub out that was not hooked up. Ong come out and caped off and took out stub out |  |  |  | Metro Service Center | FALSE |  | FALSE | Resource Planning & Coord |  | Garrett Bernethy | John Legg |  | John Legg | gas line was not located as required by state law | John Legg |  | Low | [7 empty] | 8.2.2 Improper conduct that is not condoned: Unintentional |  |  | 11.10 Inadequate identification of hazardous materials | [5 empty] | Hit gas service at 720 flaming Oaks dr no visible yellow paint on the ground it was going to a stub out that was not hooked up. Ong come out and caped off and took out stub out | 02. Failure to Warn | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Garrett Bernethy | Struck ONG service line (line not in use) |  |  |  |  | 2. Struck By (Hit By Moving Object) | Garrett Bernethy | Pathfinder | Derrick Hernandez |  | Utility Strike |  | Garrett Bernethy |  |  |  |  | FALSE | [66 empty] | 8960586
9001 | Metro Service Center | 2019-08-21 10:00 | Woodward District 138/69kV Bank 2 & 69kV capacitor tripped offline. System Operator checked SCADA one-line and saw a voltage reading of 60.3kV next to the 69kV bus but it was still energized. Operator attempted to close the 69kV capacitor C71 but got a control failed alarm. Because of other work going on in the area off OGE system and the perceived low voltage, he opened the two remaining 69kV breakers and shed 29MW's of firm load. | Level 2 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Darrell Fuller | 2019-10-07 09:19 | 2019-08-26 13:29 |  | 2019-10-02 08:37 | 2019-10-02 10:00 | 2019-08-26 13:07 | 2019-10-06 20:34 |  | 2019-10-02 14:13 | Woodward District Substation |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Darrell Fuller |  | At 1004 on 8/20/2019 Woodward District Bank 2 and 69kV Cap C71 tripped and locked out. The 69kV bus voltage on SCADA showed 60kV. System Operator attempted to close Woodward C71 but C71 failed to close. The System Operator than opened by SCADA Woodward PCB's 84 and 83. This dropped approximately 29 mw of load. At the same time PCB 83 was opened, communications were lost to Woodward, Woodward EHV, Badger and Beaver subs. SCADA was notified along with SPP and DCC. System Operator called Sub Ops Area Supervisor and had him send someone to Woodward District sub. System Operator then contacted WFEC, they said they were performing maintenance at their Woodward Sub on their 69kV PCB 354. WFEC stated "that they also had a line operate and that they were hot to our open breakers at Woodward." The OGE System Operator knew/remembered the previous day WFEC was working on their Woodward PCB 254 which looks at our Woodward sub. This was somewhat confusing to the System Operator at this time. SCADA called and notified System Operator that communications were down because of the 69kV outage. About 30 minutes later Sub Maint Tech showed up to Woodward Sub and confirmed breaker statuses (still no SCADA visibility at this point). At 1038 System Operator had Sub Tech manually close PCB 83 (Cedar Ave T26 had auto-opened), System Operator then called WFEC and kept them on the line to monitor voltage while Sub Tech manually closed PCB 84 (closed at 1041). Cedar Ave T26 closed back automatically and voltage was acceptable. Still unsure of what happened, System Operator instructed another System Operator to clear Woodward District 138/69kV bank 2. Communications returned shortly after the 69kV loop was restored. Sometime later, DCC called to report a downed transmission line 3 mi N of Taloga W of HWY 183. System Operator used the GIS program to ascertain that it was a WFEC line (Taloga/WFEC Woodward 69kV Line); System Operator then called and gave WFEC this info. The timestamp for WFEC outage coincided with the lock out of our bank. System Operator informed Protection Coordination Engineer. PC Engineer informed the System Operator the bank tripped on over-current, not differential and he believed that it may have been due to a slow breaker at WFEC Woodward Sub. He indicated that he felt the bank could be placed back in service. I conveyed this info to the Area Supv Sub Ops; he stated he would like to perform some testing on the bank before it is placed back in service. SPP called a little later and said they were showing 110% post-contingent loading on the Woodward/Windfarm SS 138kV line. This was not showing up on OGE RTCA but was displaying on the RTCA B/U tool. SCADA EMS Engineering was call and a message was left. SPP created FG 435 Woodward/WFSS 138kV ftlo Woodward EHV/Iodine (Dewey) 138kV. Woodward District bank was checked, no issues found. Transformer was placed back in service. |  |  |  | Metro Service Center | FALSE |  | FALSE | System Operations |  | Ricardo Gutierrez | Darrell Fuller |  | Dallas Rowley | I approve of the incident investigation as well as the associated corrective action. D. Rowley | Dallas Rowley |  | Medium | [15 empty] | 16.06 Inadequate communication methods | Transformer Bank voltage reading was in the wrong location on the SCADA one-line and inaccurate voltage reading due to equipment limitations. | 35. Inadequate Information, Data | 9. Abnormal Operation |  | approve cm
9002 | Sooner Power Plant | 2019-08-27 14:30 | OG&E Member observed contractor using a forklift as a hydraulic vehicle lift to work on Kawasaki MULE F31-902. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | James Morbley | 2019-10-22 14:35 | 2019-08-27 17:15 | 2019-08-27 17:15 | 2019-09-12 10:15 | 2019-09-10 14:30 | 2019-08-27 16:40 | 2019-10-21 07:36 |  | 2019-09-12 13:26 | Sooner Power Plant |  |  | William Young | Reviewed and approved. WCY 10-22-19 | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | James Morbley |  | OGE members discovered an unattended, unsecured POLARIS UTV suspended by a forklift. OGE Fleet Manager and Safety Professional meet with vendor to review incident. Contractor improperly used forklift to expedite repair of UTV. Fleet Manager explain that proper lifting equipment is to be used and explained, if proper lifting equipment is not available at repair location, equipment needing repair is to be relocated to a shop where proper lifting equipment is available. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | UTS - Fleet Services |  | Justin Nealis | Brady Sowell |  | Paul Jefferson | We had a Safety stand down with Hugg & Hall on 8-28-2019. We reviewed the contractor reference guide and discussed vehicle and equipment lifting in detail. The contractor mechanic agreed he made a bad choice in using the fork lift with c clamps. Fleet reviews the contractor reference guide with all its contractors on an annual basis. | Paul Jefferson |  | Medium | [6 empty] | 7.06 Improper attempt to save time or effort | [5 empty] | 13.04 Inadequate availability |  |  |  | Poor choice made in an attempt to expedite equipment repair and mitigate equipment down time. | 15. Using Equipment Improperly | 9. Abnormal Operation |  | Approved, Cody Vinyard |  |  |  | Injury / Illness |  | James Morbley |  | N/A | FALSE |  |  | 5. Caught In (Pinch and Nip Points) | Justin Nealis | Hugg & Hall | Unknown | Crush/Smash |  | Unknown | James Morbley |  | FALSE
9003 | West Service Center | 2019-08-27 12:30 | A contractor (Wright Tree Service) Foreman was stung by wasp. Used his epi pen but reaction was too severe so an ambulance took him to hospital. | Level 1 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Christopher Martin | 2019-09-04 14:21 | 2019-08-27 17:39 | 2019-08-27 17:39 | 2019-09-03 14:44 | 2019-09-10 12:30 | 2019-08-27 17:20 | 2019-09-04 11:34 |  |  | West Metro Storm Event |  |  | Jerrie Looney | J. Looney, 9/4/19 Chris Martin will begin to attach rosters as evidence the contractors are actually doing the corrective action. | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Christopher Martin |  | Wright Foreman (Frank McMurry) leaned against the customer's fence near a decorative sun attached to the fence. He started to set his climbing line into the tree and was stung on the left shoulder blade by a wasp. Frank asked a coworker to get his epi pen out of the truck as he is allergic to bee stings. He laid down and then administered his epi pen once his coworker brought it to him. Frank asked his GF to take him to the hospital. As they started to leave Frank asked that an ambulance be called as he didn't feel like the epi pen was working. The ambulance gave frank Benadryl and took him to the hospital because of high blood pressure. The hospital gave frank more Benadryl and a steroid through an IV. He was released to full duty a couple hours later and given a 5 day steroid prescription. No follow up is needed. |  |  |  | West Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Grant Ehlen | Christopher Martin |  | Nicole Rhodes | Reviewed. | Nicole Rhodes |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | wasp sting to the left shoulder blade of Frank McMurry | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Injury / Illness |  | Christopher Martin |  | Wasp sting | FALSE | 43711.5208 | 43711.5208 | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Grant Ehlen | Wright Tree Service | Frank McMurry | Allergic Reaction |  | Shoulder Blades | Christopher Martin | Left | TRUE | Ambulance
9004 | General Service Center | 2019-08-27 18:00 | Contractor was leaving Koppers yard and was approaching train tracks on SW corner of yard. Driver was going slowly over the crossing when he looked to the east and saw train approaching. Driver then accelerated to attempt to get off tracks before train got to crossing. The train contacted the rear of the trailer and rolled the truck and trailer over on its side. There was limited visibility to the East at the crossing. Driver was not injured in the incident. | Level 4 |  | FALSE | Contractor | Stephen Merrill | Jerrod Moser | Please get investigation completed by Sept. 30th | 2019-09-09 06:58 | OGE Energy Corp | Charles Shetley | 2019-10-15 10:53 | 2019-08-27 19:15 | 2019-08-27 19:15 | 2019-10-10 14:15 | 2019-09-30 | 2019-08-27 18:53 | 2019-10-14 07:55 |  |  | Leaving Koppers yard located at 1109 East Reno. |  |  | Jerrod Moser | Approve | Enterprise Services |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | Heavy Haul Contractor C-Line was leaving Koppers yard and was approaching train tracks on SW corner of yard. Driver was going slowly over the crossing when he looked to the east and saw train approaching. Driver then accelerated to attempt to get off tracks before train got to crossing. The train contacted the rear of the trailer and rolled the truck and trailer over on its side. There was limited visibility to the East at the crossing. Driver was not injured in the incident. There was no railroad crossing arms or lights. The rail spur is on private property of Koppers. The distance from the railroad crossing to the first opportunity to see the train is a relativity short. | Cody Vinyard | William Young |  | General Service Center | TRUE |  | FALSE | Supply Chain |  | Charles Shetley | Charles Shetley |  | Stephen Merrill | I agree with the handling and the corrective actions. |  |  | Very High | [9 empty] | 10.06 Inadequate or improper controls | [6 empty] | Contractor was unable to see train until it was too late to prevent contact. | 25. Inadequate Warning System | 2. Struck By (Hit By Moving Object) | [5 empty] | Vehicle |  | Charles Shetley | [5 empty] | 2. Struck By (Hit By Moving Object) | Charles Shetley | C-Line | Scott Smith |  |  |  | Charles Shetley |  |  |  |  | FALSE
9004 | General Service Center | 2019-08-27 18:00 | Contractor was leaving Koppers yard and was approaching train tracks on SW corner of yard. Driver was going slowly over the crossing when he looked to the east and saw train approaching. Driver then accelerated to attempt to get off tracks before train got to crossing. The train contacted the rear of the trailer and rolled the truck and trailer over on its side. There was limited visibility to the East at the crossing. Driver was not injured in the incident. | Level 4 |  | FALSE | Contractor | Stephen Merrill | Jerrod Moser | Please get investigation completed by Sept. 30th | 2019-09-09 06:58 | OGE Energy Corp | Charles Shetley | 2019-10-15 10:53 | 2019-08-27 19:15 | 2019-08-27 19:15 | 2019-10-10 14:15 | 2019-09-30 | 2019-08-27 18:53 | 2019-10-14 07:55 |  |  | Leaving Koppers yard located at 1109 East Reno. |  |  | Jerrod Moser | Approve | Enterprise Services |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | Heavy Haul Contractor C-Line was leaving Koppers yard and was approaching train tracks on SW corner of yard. Driver was going slowly over the crossing when he looked to the east and saw train approaching. Driver then accelerated to attempt to get off tracks before train got to crossing. The train contacted the rear of the trailer and rolled the truck and trailer over on its side. There was limited visibility to the East at the crossing. Driver was not injured in the incident. There was no railroad crossing arms or lights. The rail spur is on private property of Koppers. The distance from the railroad crossing to the first opportunity to see the train is a relativity short. | Terry Brown | William Young |  | General Service Center | TRUE |  | FALSE | Supply Chain |  | Charles Shetley | Charles Shetley |  | Stephen Merrill | I agree with the handling and the corrective actions. |  |  | Very High | [9 empty] | 10.06 Inadequate or improper controls | [6 empty] | Contractor was unable to see train until it was too late to prevent contact. | 25. Inadequate Warning System | 2. Struck By (Hit By Moving Object) | [5 empty] | Vehicle |  | Charles Shetley | [5 empty] | 2. Struck By (Hit By Moving Object) | Charles Shetley | C-Line | Scott Smith |  |  |  | Charles Shetley |  |  |  |  | FALSE
9004 | General Service Center | 2019-08-27 18:00 | Contractor was leaving Koppers yard and was approaching train tracks on SW corner of yard. Driver was going slowly over the crossing when he looked to the east and saw train approaching. Driver then accelerated to attempt to get off tracks before train got to crossing. The train contacted the rear of the trailer and rolled the truck and trailer over on its side. There was limited visibility to the East at the crossing. Driver was not injured in the incident. | Level 4 |  | FALSE | Contractor | Stephen Merrill | Jerrod Moser | Please get investigation completed by Sept. 30th | 2019-09-09 06:58 | OGE Energy Corp | Charles Shetley | 2019-10-15 10:53 | 2019-08-27 19:15 | 2019-08-27 19:15 | 2019-10-10 14:15 | 2019-09-30 | 2019-08-27 18:53 | 2019-10-14 07:55 |  |  | Leaving Koppers yard located at 1109 East Reno. |  |  | Jerrod Moser | Approve | Enterprise Services |  | Level 4 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | Heavy Haul Contractor C-Line was leaving Koppers yard and was approaching train tracks on SW corner of yard. Driver was going slowly over the crossing when he looked to the east and saw train approaching. Driver then accelerated to attempt to get off tracks before train got to crossing. The train contacted the rear of the trailer and rolled the truck and trailer over on its side. There was limited visibility to the East at the crossing. Driver was not injured in the incident. There was no railroad crossing arms or lights. The rail spur is on private property of Koppers. The distance from the railroad crossing to the first opportunity to see the train is a relativity short. | Charles Shetley | William Young |  | General Service Center | TRUE |  | FALSE | Supply Chain |  | Charles Shetley | Charles Shetley |  | Stephen Merrill | I agree with the handling and the corrective actions. |  |  | Very High | [9 empty] | 10.06 Inadequate or improper controls | [6 empty] | Contractor was unable to see train until it was too late to prevent contact. | 25. Inadequate Warning System | 2. Struck By (Hit By Moving Object) | [5 empty] | Vehicle |  | Charles Shetley | [5 empty] | 2. Struck By (Hit By Moving Object) | Charles Shetley | C-Line | Scott Smith |  |  |  | Charles Shetley |  |  |  |  | FALSE
9005 | Metro Service Center | 2019-08-27 11:00 | Jaraffe (Tree Sidetrimmer) cut 7.2 kv coop distribution line with blade while exiting property from the transmission line ROW. | Level 3 |  | FALSE | Property Damage | Andrea Dennis | William Young | Team will be assigned for investigation incident by Bill Young. 8/28/19: Investigate incident determine causal factors and corrective actions. WCY | 2019-08-28 14:04 | OG&E Corp Services |  | 2019-10-25 08:37 | 2019-08-28 07:40 | 2019-08-28 07:40 | 2019-09-27 15:44 | 2019-09-10 11:00 | 2019-08-27 17:00 | 2019-09-30 15:56 | 2019-10-11 08:38 | 2019-09-27 16:07 | 10634 N. Triple X Road, Jones, OK |  |  | Andrea Dennis | I approve. | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | William Young |  | While moving a Jarraff from a job site to another the operator struck a single phase primary owned by a coop. The operator did not stow the boom fully and did not secure the blade. The boom was out of the cradle approximately 3ft. The operator is known to be a "quick" operator who "gets work done". It was revealed that the third person on the crew was not there that day. The job briefing did not identify the single phase line as a hazard. The operator stated he knew the line was there as he has driven under it on the previous day heading the opposite direction. There was no flagging near the line indicating that no one had identified the line as a hazard either day the crew was at the site. | Jerrie Looney | William Young |  | Metro Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  |  |  |  | Nicole Rhodes | Reviewed. Satisfied with actions taken after additional information added to investigation. | Nicole Rhodes | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  | 7.13 Inadequate reinforcement of proper behavior |  | 9.13 Inadequate or incorrect performance feedback | [6 empty] | 16.01 Inadequate horizontal communication between peers | 1. Failure to secure boom 2. Using equipment improperly but moving without stowing boom 3. Failure to follow company and mfr work standards 4. Failure to identify hazard 5. Inadequate Barriers 6. Inadequate preparation and planning | 02. Failure to Warn | 1. Struck Against (Running or Bumping Into) | Reviewed and approved. WCY | Returning to Shawn for edit J. Looney 9.26.19 Approved - J. Looney, 9/27/19 | [66 empty] | Cut Coop 7.2 kv line with equipment | 1000 | Steve Harris | Utility Strike |  | 749-7622
9005 | Metro Service Center | 2019-08-27 11:00 | Jaraffe (Tree Sidetrimmer) cut 7.2 kv coop distribution line with blade while exiting property from the transmission line ROW. | Level 3 |  | FALSE | Property Damage | Andrea Dennis | William Young | Team will be assigned for investigation incident by Bill Young. 8/28/19: Investigate incident determine causal factors and corrective actions. WCY | 2019-08-28 14:04 | OG&E Corp Services |  | 2019-10-25 08:37 | 2019-08-28 07:40 | 2019-08-28 07:40 | 2019-09-27 15:44 | 2019-09-10 11:00 | 2019-08-27 17:00 | 2019-09-30 15:56 | 2019-10-11 08:38 | 2019-09-27 16:07 | 10634 N. Triple X Road, Jones, OK |  |  | Andrea Dennis | I approve. | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | William Young |  | While moving a Jarraff from a job site to another the operator struck a single phase primary owned by a coop. The operator did not stow the boom fully and did not secure the blade. The boom was out of the cradle approximately 3ft. The operator is known to be a "quick" operator who "gets work done". It was revealed that the third person on the crew was not there that day. The job briefing did not identify the single phase line as a hazard. The operator stated he knew the line was there as he has driven under it on the previous day heading the opposite direction. There was no flagging near the line indicating that no one had identified the line as a hazard either day the crew was at the site. | Jerrie Looney | William Young |  | Metro Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  |  |  |  | Nicole Rhodes | Reviewed. Satisfied with actions taken after additional information added to investigation. | Nicole Rhodes | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  | 7.06 Improper attempt to save time or effort |  | 9.13 Inadequate or incorrect performance feedback | [6 empty] | 16.01 Inadequate horizontal communication between peers | 1. Failure to secure boom 2. Using equipment improperly but moving without stowing boom 3. Failure to follow company and mfr work standards 4. Failure to identify hazard 5. Inadequate Barriers 6. Inadequate preparation and planning | 02. Failure to Warn | 1. Struck Against (Running or Bumping Into) | Reviewed and approved. WCY | Returning to Shawn for edit J. Looney 9.26.19 Approved - J. Looney, 9/27/19 | [66 empty] | Cut Coop 7.2 kv line with equipment | 1000 | Steve Harris | Utility Strike |  | 749-7622
9005 | Metro Service Center | 2019-08-27 11:00 | Jaraffe (Tree Sidetrimmer) cut 7.2 kv coop distribution line with blade while exiting property from the transmission line ROW. | Level 3 |  | FALSE | Property Damage | Andrea Dennis | William Young | Team will be assigned for investigation incident by Bill Young. 8/28/19: Investigate incident determine causal factors and corrective actions. WCY | 2019-08-28 14:04 | OG&E Corp Services |  | 2019-10-25 08:37 | 2019-08-28 07:40 | 2019-08-28 07:40 | 2019-09-27 15:44 | 2019-09-10 11:00 | 2019-08-27 17:00 | 2019-09-30 15:56 | 2019-10-11 08:38 | 2019-09-27 16:07 | 10634 N. Triple X Road, Jones, OK |  |  | Andrea Dennis | I approve. | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | William Young |  | While moving a Jarraff from a job site to another the operator struck a single phase primary owned by a coop. The operator did not stow the boom fully and did not secure the blade. The boom was out of the cradle approximately 3ft. The operator is known to be a "quick" operator who "gets work done". It was revealed that the third person on the crew was not there that day. The job briefing did not identify the single phase line as a hazard. The operator stated he knew the line was there as he has driven under it on the previous day heading the opposite direction. There was no flagging near the line indicating that no one had identified the line as a hazard either day the crew was at the site. | Shawn Huff | William Young |  | Metro Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  |  |  |  | Nicole Rhodes | Reviewed. Satisfied with actions taken after additional information added to investigation. | Nicole Rhodes | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  | 7.13 Inadequate reinforcement of proper behavior |  | 9.13 Inadequate or incorrect performance feedback | [6 empty] | 16.01 Inadequate horizontal communication between peers | 1. Failure to secure boom 2. Using equipment improperly but moving without stowing boom 3. Failure to follow company and mfr work standards 4. Failure to identify hazard 5. Inadequate Barriers 6. Inadequate preparation and planning | 02. Failure to Warn | 1. Struck Against (Running or Bumping Into) | Reviewed and approved. WCY | Returning to Shawn for edit J. Looney 9.26.19 Approved - J. Looney, 9/27/19 | [66 empty] | Cut Coop 7.2 kv line with equipment | 1000 | Steve Harris | Utility Strike |  | 749-7622
9005 | Metro Service Center | 2019-08-27 11:00 | Jaraffe (Tree Sidetrimmer) cut 7.2 kv coop distribution line with blade while exiting property from the transmission line ROW. | Level 3 |  | FALSE | Property Damage | Andrea Dennis | William Young | Team will be assigned for investigation incident by Bill Young. 8/28/19: Investigate incident determine causal factors and corrective actions. WCY | 2019-08-28 14:04 | OG&E Corp Services |  | 2019-10-25 08:37 | 2019-08-28 07:40 | 2019-08-28 07:40 | 2019-09-27 15:44 | 2019-09-10 11:00 | 2019-08-27 17:00 | 2019-09-30 15:56 | 2019-10-11 08:38 | 2019-09-27 16:07 | 10634 N. Triple X Road, Jones, OK |  |  | Andrea Dennis | I approve. | T&D Ops |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | William Young |  | While moving a Jarraff from a job site to another the operator struck a single phase primary owned by a coop. The operator did not stow the boom fully and did not secure the blade. The boom was out of the cradle approximately 3ft. The operator is known to be a "quick" operator who "gets work done". It was revealed that the third person on the crew was not there that day. The job briefing did not identify the single phase line as a hazard. The operator stated he knew the line was there as he has driven under it on the previous day heading the opposite direction. There was no flagging near the line indicating that no one had identified the line as a hazard either day the crew was at the site. | Shawn Huff | William Young |  | Metro Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  |  |  |  | Nicole Rhodes | Reviewed. Satisfied with actions taken after additional information added to investigation. | Nicole Rhodes | William Young | High |  |  |  |  | 5.06 Lack of situational awareness |  | 7.06 Improper attempt to save time or effort |  | 9.13 Inadequate or incorrect performance feedback | [6 empty] | 16.01 Inadequate horizontal communication between peers | 1. Failure to secure boom 2. Using equipment improperly but moving without stowing boom 3. Failure to follow company and mfr work standards 4. Failure to identify hazard 5. Inadequate Barriers 6. Inadequate preparation and planning | 02. Failure to Warn | 1. Struck Against (Running or Bumping Into) | Reviewed and approved. WCY | Returning to Shawn for edit J. Looney 9.26.19 Approved - J. Looney, 9/27/19 | [66 empty] | Cut Coop 7.2 kv line with equipment | 1000 | Steve Harris | Utility Strike |  | 749-7622
9006 | Metro Service Center | 2019-08-27 20:00 | Finger smashed and the bone was chipped (broken bone) when contractors finger was caught between the sling and the pole as the pole was being lifted. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Delivery | Brent Perdue | 2019-09-13 10:48 | 2019-08-28 09:47 | 2019-08-28 09:47 | 2019-09-11 13:26 | 2019-09-10 20:00 | 2019-08-28 09:29 | 2019-09-13 10:41 |  | 2019-09-11 13:27 | Ranchwood Blvd. Yukon, OK |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Brent Perdue |  | See attached report |  |  |  | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Brent Perdue | Brent Perdue |  | Michael Douglas | Reviewed the incident with the contractor safety leader. Ensured that they followed through with the list of corrective actions for the member and the crew. | Michael Douglas |  | Medium |  |  |  | 4.04 Routine, monotony, demand for uneventful vigilance | [12 empty] | finger in pinch point | 11. Improper Position for Task | 7. Caught Between or Under (Crushed or Amputated) |  | the contractor has provided a report that meets our standards |  |  |  | Injury / Illness |  | Brent Perdue |  | smashed finger with chipped bone | FALSE |  |  | 5. Caught In (Pinch and Nip Points) | Brent Perdue | IUS | thomas guinn | Fracture |  | Finger | Brent Perdue |  | TRUE | Personal Vehicle
9007 | Seminole PP; EGX Gath/Trans | 2019-08-28 11:30 | Member was driving on northbound I-35 through Norman. Around 11:20 A.M. while going under an overpass, a small object struck the passenger side windshield leaving a small nick. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Justin Stahl | 2019-09-30 08:18 | 2019-08-29 08:43 | 2019-08-29 08:43 | 2019-08-30 09:15 | 2019-09-11 11:30 | 2019-08-29 08:37 | 2019-09-11 10:09 |  | 2019-09-04 07:20 | Norman, I-35 |  |  | Jesse Murray | I Approve Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Justin Stahl |  | Member was on his way to Engineering Committee Lunch at Charleston's off I-40 on 8/28. He was driving North on I-35 passing through Norman. Around 11:20 A.M., he drove under an overpass and a small object struck the passenger side windshield. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | TRUE | Other |  | Marshall Hartley | Justin Stahl |  | Scott Lee | I approve this investigation. | Scott Lee |  | Medium | [11 empty] | 12.01.4 Inadequate preventative cleaning or resurfacing |  |  |  |  | Member was on his way to Engineering Committee Lunch at Charleston's off I-40 on 8/28. He was driving North on I-35 passing through Norman. Around 11:20 A.M., he drove under an overpass and a small object struck the passenger side windshield. | 39. Road Conditions | 2. Struck By (Hit By Moving Object) |  | Reviewed
9008 | Sooner Power Plant | 2019-08-28 10:30 | Contractor was washing down reclaim area without a personal monitor for Carbon Monoxide. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Glen Hughes | 2019-09-18 13:25 | 2019-08-29 09:25 | 2019-08-29 09:25 | 2019-09-11 08:55 | 2019-09-11 10:30 | 2019-08-29 09:03 | 2019-09-11 10:17 |  |  | SoonerPP Coal Yard Reclaim Area |  |  | Brady Sowell | approved and waiting or call | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Glen Hughes |  | On Aug. 28, 2019 an OGE member notice his CO monitor reading high levels while in the coal yard reclaim area. Member noticed that there was an Evergreen contractor washing down the area while CO readings were high. Member approached the contractor and observed the contractor was not wearing a personal CO monitor. Member stopped the work being performed by the contractor and instructed him to leave the area. Member did have a conversation with the contractor to determine why he was working in the area without a personal monitor. The contractor replied he forgot to get it that morning. Member then explained the high level of CO he was working in and this is why he should always wear the monitor while in the area. Member then notified Fuel Supply Manager. Fuel Supply manager then got with the contracting group and had a safety stand down with all contractor members. Evergreen Manager was notified of the incident and he investigated and turned in a report to their safety organization for review and corrective action to take to prevent reoccurrence. Report was then delivered to the Fuel Supply Manager to attach to this incident. See attachment CCF09102019_0004 |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Fuel Supply |  | Glen Hughes | Glen Hughes |  | Kent Wilson | Approved. | Kent Wilson |  | Low | [8 empty] | 9.06 Inadequate work planning or programming | [7 empty] | Forgot to get personal monitor for area needing to be washed down | 18. Failure to Check, Monitor | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Glen Hughes | [5 empty] | 9. Abnormal Operation | Glen Hughes | Evergreen | Mark Pratt |  |  |  | Glen Hughes
9009 | Metro Service Center | 2019-08-28 20:00 | This is a first aid and system operational. While pulling cap off of 12.5kv bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Brent Boles | 2019-09-19 13:13 | 2019-08-29 10:09 | 2019-08-29 10:09 | 2019-09-11 07:38 | 2019-09-11 20:00 | 2019-08-29 09:56 | 2019-09-18 15:07 |  | 2019-09-16 07:38 | 11516 Chisholm Trail, OKC Transformer # 69084 |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | TRUE | FALSE | Brent Boles |  | This is a first aid and system operational. While pulling cap off of 7200 VAC bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. After evaluation electrical engineer, believes lightning from the storm the night before caused a pinhole in the bushing where the cap was covering. When the bushing cap was moved approximately 1" the flash occurred. Facts ascertained: Members were wearing all appropriate PPE (FR, Clear Safety Glasses, Hard Hat, and Safety Toed Boots) Switch person's shirt was tucked in It was dark when the incident occurred Quick Trip was in place Switch person was approximately 5' from the point of the flash using a shot gun and class 2 rubber gloves All other crew members were over 10' away from the point of the flash All members made a complete recovery within 24 hours |  |  | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Brent Boles | Quay Prough |  | Gary Lassley | Investigate to see if there are better safety glasses available that would have prevented a flash burn to the eyes. Also discuss if we really needed all five members observing the switching procedure. | Gary Lassley |  | Medium | [9 empty] | 10.05 Inadequate assessment of operational readiness |  |  |  |  | 15.03 Inadequate inspection and/or monitoring |  | Arc flash occurred on 7200 VAC Bushing | 12. Servicing Equipment in Operation | 9. Abnormal Operation |  | Reviewed/approved. All controls were implemented and kept the risk level of this incident at a low. | [24 empty] | FALSE |  |  | 2018-11-05 | 1996-07-16 |  | 2019-08-28 20:00 | 0 | 0 | Artificial Tears | FALSE |  | Arc Flash occurred while pulling cap off of 12.5kv bushing |  | TRUE | Colton Collins |  | First Aid | Colton Collins |  |  |  |  | Burn: Electrical |  | FALSE |  | Cable Splicer Appr | Eye |  |  |  | Quay Prough |  |  | 8/28/2019 8:00:00 PM |  | FALSE |  |  | Arc Flash | Observing Switching
9009 | Metro Service Center | 2019-08-28 20:00 | This is a first aid and system operational. While pulling cap off of 12.5kv bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Brent Boles | 2019-09-19 13:13 | 2019-08-29 10:09 | 2019-08-29 10:09 | 2019-09-11 07:38 | 2019-09-11 20:00 | 2019-08-29 09:56 | 2019-09-18 15:07 |  | 2019-09-16 07:38 | 11516 Chisholm Trail, OKC Transformer # 69084 |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | TRUE | FALSE | Brent Boles |  | This is a first aid and system operational. While pulling cap off of 7200 VAC bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. After evaluation electrical engineer, believes lightning from the storm the night before caused a pinhole in the bushing where the cap was covering. When the bushing cap was moved approximately 1" the flash occurred. Facts ascertained: Members were wearing all appropriate PPE (FR, Clear Safety Glasses, Hard Hat, and Safety Toed Boots) Switch person's shirt was tucked in It was dark when the incident occurred Quick Trip was in place Switch person was approximately 5' from the point of the flash using a shot gun and class 2 rubber gloves All other crew members were over 10' away from the point of the flash All members made a complete recovery within 24 hours |  |  | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Brent Boles | Quay Prough |  | Gary Lassley | Investigate to see if there are better safety glasses available that would have prevented a flash burn to the eyes. Also discuss if we really needed all five members observing the switching procedure. | Gary Lassley |  | Medium | [9 empty] | 10.05 Inadequate assessment of operational readiness |  |  |  |  | 15.03 Inadequate inspection and/or monitoring |  | Arc flash occurred on 7200 VAC Bushing | 12. Servicing Equipment in Operation | 9. Abnormal Operation |  | Reviewed/approved. All controls were implemented and kept the risk level of this incident at a low. | [24 empty] | FALSE |  |  | 2002-08-12 | 1969-08-12 |  | 2019-08-28 07:00 | 0 | 0 |  | FALSE |  | Arc occurred while pulling cap off of 12.5 kv bushing. |  | FALSE | Brent Boles |  | First Aid | Brent Boles |  |  |  |  | Burn: Electrical |  | FALSE |  | Foreman Underground Network | Eye |  |  | FALSE | Quay Prough | FALSE |  | 8/28/2019 7:00:00 AM |  | FALSE |  |  | Arc Flash | Observing Switching
9009 | Metro Service Center | 2019-08-28 20:00 | This is a first aid and system operational. While pulling cap off of 12.5kv bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Brent Boles | 2019-09-19 13:13 | 2019-08-29 10:09 | 2019-08-29 10:09 | 2019-09-11 07:38 | 2019-09-11 20:00 | 2019-08-29 09:56 | 2019-09-18 15:07 |  | 2019-09-16 07:38 | 11516 Chisholm Trail, OKC Transformer # 69084 |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | TRUE | FALSE | Brent Boles |  | This is a first aid and system operational. While pulling cap off of 7200 VAC bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. After evaluation electrical engineer, believes lightning from the storm the night before caused a pinhole in the bushing where the cap was covering. When the bushing cap was moved approximately 1" the flash occurred. Facts ascertained: Members were wearing all appropriate PPE (FR, Clear Safety Glasses, Hard Hat, and Safety Toed Boots) Switch person's shirt was tucked in It was dark when the incident occurred Quick Trip was in place Switch person was approximately 5' from the point of the flash using a shot gun and class 2 rubber gloves All other crew members were over 10' away from the point of the flash All members made a complete recovery within 24 hours |  |  | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Brent Boles | Quay Prough |  | Gary Lassley | Investigate to see if there are better safety glasses available that would have prevented a flash burn to the eyes. Also discuss if we really needed all five members observing the switching procedure. | Gary Lassley |  | Medium | [9 empty] | 10.05 Inadequate assessment of operational readiness |  |  |  |  | 15.03 Inadequate inspection and/or monitoring |  | Arc flash occurred on 7200 VAC Bushing | 12. Servicing Equipment in Operation | 9. Abnormal Operation |  | Reviewed/approved. All controls were implemented and kept the risk level of this incident at a low. | [24 empty] | FALSE |  |  | 1992-06-08 | 1965-11-10 |  | 2019-08-28 07:00 | 0 | 0 |  | FALSE |  | Arc flash occurred while pulling cap off of 12.5 kv bushing |  | FALSE | Adam Carey |  | First Aid | Adam Carey |  |  |  |  | Burn: Electrical |  | FALSE |  | Cable Splicer Appr | Eye |  | Left | FALSE | Brent Boles | FALSE |  | 8/28/2019 7:00:00 AM |  | FALSE |  |  | Arc Flash | Switching
9009 | Metro Service Center | 2019-08-28 20:00 | This is a first aid and system operational. While pulling cap off of 12.5kv bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Brent Boles | 2019-09-19 13:13 | 2019-08-29 10:09 | 2019-08-29 10:09 | 2019-09-11 07:38 | 2019-09-11 20:00 | 2019-08-29 09:56 | 2019-09-18 15:07 |  | 2019-09-16 07:38 | 11516 Chisholm Trail, OKC Transformer # 69084 |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | TRUE | FALSE | Brent Boles |  | This is a first aid and system operational. While pulling cap off of 7200 VAC bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. After evaluation electrical engineer, believes lightning from the storm the night before caused a pinhole in the bushing where the cap was covering. When the bushing cap was moved approximately 1" the flash occurred. Facts ascertained: Members were wearing all appropriate PPE (FR, Clear Safety Glasses, Hard Hat, and Safety Toed Boots) Switch person's shirt was tucked in It was dark when the incident occurred Quick Trip was in place Switch person was approximately 5' from the point of the flash using a shot gun and class 2 rubber gloves All other crew members were over 10' away from the point of the flash All members made a complete recovery within 24 hours |  |  | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Brent Boles | Quay Prough |  | Gary Lassley | Investigate to see if there are better safety glasses available that would have prevented a flash burn to the eyes. Also discuss if we really needed all five members observing the switching procedure. | Gary Lassley |  | Medium | [9 empty] | 10.05 Inadequate assessment of operational readiness |  |  |  |  | 15.03 Inadequate inspection and/or monitoring |  | Arc flash occurred on 7200 VAC Bushing | 12. Servicing Equipment in Operation | 9. Abnormal Operation |  | Reviewed/approved. All controls were implemented and kept the risk level of this incident at a low. | [24 empty] | FALSE |  |  | 2018-03-12 | 1995-08-03 |  | 2019-08-28 07:00 | 0 | 0 | Artificial Tears | FALSE |  | Arc flash occurred while pulling 12.5kv bushing cap |  | TRUE | Taylor Barnett |  | First Aid | Taylor Barnett |  |  |  |  | Burn: Electrical |  | FALSE |  | Cable Splicer Appr | Eye |  |  | FALSE | Brent Boles | FALSE |  | 8/28/2019 7:00:00 AM |  | FALSE |  |  | Arc flash | Observing switching
9009 | Metro Service Center | 2019-08-28 20:00 | This is a first aid and system operational. While pulling cap off of 12.5kv bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Brent Boles | 2019-09-19 13:13 | 2019-08-29 10:09 | 2019-08-29 10:09 | 2019-09-11 07:38 | 2019-09-11 20:00 | 2019-08-29 09:56 | 2019-09-18 15:07 |  | 2019-09-16 07:38 | 11516 Chisholm Trail, OKC Transformer # 69084 |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | TRUE | FALSE | Brent Boles |  | This is a first aid and system operational. While pulling cap off of 7200 VAC bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. After evaluation electrical engineer, believes lightning from the storm the night before caused a pinhole in the bushing where the cap was covering. When the bushing cap was moved approximately 1" the flash occurred. Facts ascertained: Members were wearing all appropriate PPE (FR, Clear Safety Glasses, Hard Hat, and Safety Toed Boots) Switch person's shirt was tucked in It was dark when the incident occurred Quick Trip was in place Switch person was approximately 5' from the point of the flash using a shot gun and class 2 rubber gloves All other crew members were over 10' away from the point of the flash All members made a complete recovery within 24 hours |  |  | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Brent Boles | Quay Prough |  | Gary Lassley | Investigate to see if there are better safety glasses available that would have prevented a flash burn to the eyes. Also discuss if we really needed all five members observing the switching procedure. | Gary Lassley |  | Medium | [9 empty] | 10.05 Inadequate assessment of operational readiness |  |  |  |  | 15.03 Inadequate inspection and/or monitoring |  | Arc flash occurred on 7200 VAC Bushing | 12. Servicing Equipment in Operation | 9. Abnormal Operation |  | Reviewed/approved. All controls were implemented and kept the risk level of this incident at a low. | [24 empty] | FALSE |  |  | 2019-01-14 | 1986-01-07 |  | 2019-08-28 07:00 | 0 | 0 | Artificial tears administered. | FALSE |  | Arc occurred while pulling bushing cap from 12.5kv elbow in a padmount transformer |  | TRUE | Steven Countryman |  | First Aid | Steven Countryman |  |  |  |  | Burn: Electrical |  | FALSE |  | Cable Splicer Appr | Eye |  |  | FALSE | Frank Alsip | FALSE |  | 8/28/2019 7:00:00 AM |  | FALSE |  |  | Arc Flash | Observing switching
9009 | Metro Service Center | 2019-08-28 20:00 | This is a first aid and system operational. While pulling cap off of 12.5kv bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Brent Boles | 2019-09-19 13:13 | 2019-08-29 10:09 | 2019-08-29 10:09 | 2019-09-11 07:38 | 2019-09-11 20:00 | 2019-08-29 09:56 | 2019-09-18 15:07 |  | 2019-09-16 07:38 | 11516 Chisholm Trail, OKC Transformer # 69084 |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | TRUE | FALSE | Brent Boles |  | This is a first aid and system operational. While pulling cap off of 7200 VAC bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. After evaluation electrical engineer, believes lightning from the storm the night before caused a pinhole in the bushing where the cap was covering. When the bushing cap was moved approximately 1" the flash occurred. Facts ascertained: Members were wearing all appropriate PPE (FR, Clear Safety Glasses, Hard Hat, and Safety Toed Boots) Switch person's shirt was tucked in It was dark when the incident occurred Quick Trip was in place Switch person was approximately 5' from the point of the flash using a shot gun and class 2 rubber gloves All other crew members were over 10' away from the point of the flash All members made a complete recovery within 24 hours |  |  | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Brent Boles | Quay Prough |  | Gary Lassley | Investigate to see if there are better safety glasses available that would have prevented a flash burn to the eyes. Also discuss if we really needed all five members observing the switching procedure. | Gary Lassley |  | Medium | [9 empty] | 10.06 Inadequate or improper controls | [6 empty] | NA Reference associated System operational incident | 12. Servicing Equipment in Operation | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Reviewed/approved. All controls were implemented and kept the risk level of this incident at a low. | [24 empty] | FALSE |  |  | 2018-11-05 | 1996-07-16 |  | 2019-08-28 20:00 | 0 | 0 | Artificial Tears | FALSE |  | Arc Flash occurred while pulling cap off of 12.5kv bushing |  | TRUE | Colton Collins |  | First Aid | Colton Collins |  |  |  |  | Burn: Electrical |  | FALSE |  | Cable Splicer Appr | Eye |  |  |  | Quay Prough |  |  | 8/28/2019 8:00:00 PM |  | FALSE |  |  | Arc Flash | Observing Switching
9009 | Metro Service Center | 2019-08-28 20:00 | This is a first aid and system operational. While pulling cap off of 12.5kv bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Brent Boles | 2019-09-19 13:13 | 2019-08-29 10:09 | 2019-08-29 10:09 | 2019-09-11 07:38 | 2019-09-11 20:00 | 2019-08-29 09:56 | 2019-09-18 15:07 |  | 2019-09-16 07:38 | 11516 Chisholm Trail, OKC Transformer # 69084 |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | TRUE | FALSE | Brent Boles |  | This is a first aid and system operational. While pulling cap off of 7200 VAC bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. After evaluation electrical engineer, believes lightning from the storm the night before caused a pinhole in the bushing where the cap was covering. When the bushing cap was moved approximately 1" the flash occurred. Facts ascertained: Members were wearing all appropriate PPE (FR, Clear Safety Glasses, Hard Hat, and Safety Toed Boots) Switch person's shirt was tucked in It was dark when the incident occurred Quick Trip was in place Switch person was approximately 5' from the point of the flash using a shot gun and class 2 rubber gloves All other crew members were over 10' away from the point of the flash All members made a complete recovery within 24 hours |  |  | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Brent Boles | Quay Prough |  | Gary Lassley | Investigate to see if there are better safety glasses available that would have prevented a flash burn to the eyes. Also discuss if we really needed all five members observing the switching procedure. | Gary Lassley |  | Medium | [9 empty] | 10.06 Inadequate or improper controls | [6 empty] | NA Reference associated System operational incident | 12. Servicing Equipment in Operation | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Reviewed/approved. All controls were implemented and kept the risk level of this incident at a low. | [24 empty] | FALSE |  |  | 2002-08-12 | 1969-08-12 |  | 2019-08-28 07:00 | 0 | 0 |  | FALSE |  | Arc occurred while pulling cap off of 12.5 kv bushing. |  | FALSE | Brent Boles |  | First Aid | Brent Boles |  |  |  |  | Burn: Electrical |  | FALSE |  | Foreman Underground Network | Eye |  |  | FALSE | Quay Prough | FALSE |  | 8/28/2019 7:00:00 AM |  | FALSE |  |  | Arc Flash | Observing Switching
9009 | Metro Service Center | 2019-08-28 20:00 | This is a first aid and system operational. While pulling cap off of 12.5kv bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Brent Boles | 2019-09-19 13:13 | 2019-08-29 10:09 | 2019-08-29 10:09 | 2019-09-11 07:38 | 2019-09-11 20:00 | 2019-08-29 09:56 | 2019-09-18 15:07 |  | 2019-09-16 07:38 | 11516 Chisholm Trail, OKC Transformer # 69084 |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | TRUE | FALSE | Brent Boles |  | This is a first aid and system operational. While pulling cap off of 7200 VAC bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. After evaluation electrical engineer, believes lightning from the storm the night before caused a pinhole in the bushing where the cap was covering. When the bushing cap was moved approximately 1" the flash occurred. Facts ascertained: Members were wearing all appropriate PPE (FR, Clear Safety Glasses, Hard Hat, and Safety Toed Boots) Switch person's shirt was tucked in It was dark when the incident occurred Quick Trip was in place Switch person was approximately 5' from the point of the flash using a shot gun and class 2 rubber gloves All other crew members were over 10' away from the point of the flash All members made a complete recovery within 24 hours |  |  | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Brent Boles | Quay Prough |  | Gary Lassley | Investigate to see if there are better safety glasses available that would have prevented a flash burn to the eyes. Also discuss if we really needed all five members observing the switching procedure. | Gary Lassley |  | Medium | [9 empty] | 10.06 Inadequate or improper controls | [6 empty] | NA Reference associated System operational incident | 12. Servicing Equipment in Operation | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Reviewed/approved. All controls were implemented and kept the risk level of this incident at a low. | [24 empty] | FALSE |  |  | 1992-06-08 | 1965-11-10 |  | 2019-08-28 07:00 | 0 | 0 |  | FALSE |  | Arc flash occurred while pulling cap off of 12.5 kv bushing |  | FALSE | Adam Carey |  | First Aid | Adam Carey |  |  |  |  | Burn: Electrical |  | FALSE |  | Cable Splicer Appr | Eye |  | Left | FALSE | Brent Boles | FALSE |  | 8/28/2019 7:00:00 AM |  | FALSE |  |  | Arc Flash | Switching
9009 | Metro Service Center | 2019-08-28 20:00 | This is a first aid and system operational. While pulling cap off of 12.5kv bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Brent Boles | 2019-09-19 13:13 | 2019-08-29 10:09 | 2019-08-29 10:09 | 2019-09-11 07:38 | 2019-09-11 20:00 | 2019-08-29 09:56 | 2019-09-18 15:07 |  | 2019-09-16 07:38 | 11516 Chisholm Trail, OKC Transformer # 69084 |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | TRUE | FALSE | Brent Boles |  | This is a first aid and system operational. While pulling cap off of 7200 VAC bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. After evaluation electrical engineer, believes lightning from the storm the night before caused a pinhole in the bushing where the cap was covering. When the bushing cap was moved approximately 1" the flash occurred. Facts ascertained: Members were wearing all appropriate PPE (FR, Clear Safety Glasses, Hard Hat, and Safety Toed Boots) Switch person's shirt was tucked in It was dark when the incident occurred Quick Trip was in place Switch person was approximately 5' from the point of the flash using a shot gun and class 2 rubber gloves All other crew members were over 10' away from the point of the flash All members made a complete recovery within 24 hours |  |  | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Brent Boles | Quay Prough |  | Gary Lassley | Investigate to see if there are better safety glasses available that would have prevented a flash burn to the eyes. Also discuss if we really needed all five members observing the switching procedure. | Gary Lassley |  | Medium | [9 empty] | 10.06 Inadequate or improper controls | [6 empty] | NA Reference associated System operational incident | 12. Servicing Equipment in Operation | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Reviewed/approved. All controls were implemented and kept the risk level of this incident at a low. | [24 empty] | FALSE |  |  | 2018-03-12 | 1995-08-03 |  | 2019-08-28 07:00 | 0 | 0 | Artificial Tears | FALSE |  | Arc flash occurred while pulling 12.5kv bushing cap |  | TRUE | Taylor Barnett |  | First Aid | Taylor Barnett |  |  |  |  | Burn: Electrical |  | FALSE |  | Cable Splicer Appr | Eye |  |  | FALSE | Brent Boles | FALSE |  | 8/28/2019 7:00:00 AM |  | FALSE |  |  | Arc flash | Observing switching
9009 | Metro Service Center | 2019-08-28 20:00 | This is a first aid and system operational. While pulling cap off of 12.5kv bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Brent Boles | 2019-09-19 13:13 | 2019-08-29 10:09 | 2019-08-29 10:09 | 2019-09-11 07:38 | 2019-09-11 20:00 | 2019-08-29 09:56 | 2019-09-18 15:07 |  | 2019-09-16 07:38 | 11516 Chisholm Trail, OKC Transformer # 69084 |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | TRUE | FALSE | Brent Boles |  | This is a first aid and system operational. While pulling cap off of 7200 VAC bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. After evaluation electrical engineer, believes lightning from the storm the night before caused a pinhole in the bushing where the cap was covering. When the bushing cap was moved approximately 1" the flash occurred. Facts ascertained: Members were wearing all appropriate PPE (FR, Clear Safety Glasses, Hard Hat, and Safety Toed Boots) Switch person's shirt was tucked in It was dark when the incident occurred Quick Trip was in place Switch person was approximately 5' from the point of the flash using a shot gun and class 2 rubber gloves All other crew members were over 10' away from the point of the flash All members made a complete recovery within 24 hours |  |  | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Brent Boles | Quay Prough |  | Gary Lassley | Investigate to see if there are better safety glasses available that would have prevented a flash burn to the eyes. Also discuss if we really needed all five members observing the switching procedure. | Gary Lassley |  | Medium | [9 empty] | 10.06 Inadequate or improper controls | [6 empty] | NA Reference associated System operational incident | 12. Servicing Equipment in Operation | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Reviewed/approved. All controls were implemented and kept the risk level of this incident at a low. | [24 empty] | FALSE |  |  | 2019-01-14 | 1986-01-07 |  | 2019-08-28 07:00 | 0 | 0 | Artificial tears administered. | FALSE |  | Arc occurred while pulling bushing cap from 12.5kv elbow in a padmount transformer |  | TRUE | Steven Countryman |  | First Aid | Steven Countryman |  |  |  |  | Burn: Electrical |  | FALSE |  | Cable Splicer Appr | Eye |  |  | FALSE | Frank Alsip | FALSE |  | 8/28/2019 7:00:00 AM |  | FALSE |  |  | Arc Flash | Observing switching
9009 | Metro Service Center | 2019-08-28 20:00 | This is a first aid and system operational. While pulling cap off of 12.5kv bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. | Level 2 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Brent Boles | 2019-09-19 13:13 | 2019-08-29 10:09 | 2019-08-29 10:09 | 2019-09-11 07:38 | 2019-09-11 20:00 | 2019-08-29 09:56 | 2019-09-18 15:07 |  | 2019-09-16 07:38 | 11516 Chisholm Trail, OKC Transformer # 69084 |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | System Operational Incident |  | FALSE | TRUE | FALSE |  | TRUE | FALSE | Brent Boles |  | This is a first aid and system operational. While pulling cap off of 7200 VAC bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. After evaluation electrical engineer, believes lightning from the storm the night before caused a pinhole in the bushing where the cap was covering. When the bushing cap was moved approximately 1" the flash occurred. Facts ascertained: Members were wearing all appropriate PPE (FR, Clear Safety Glasses, Hard Hat, and Safety Toed Boots) Switch person's shirt was tucked in It was dark when the incident occurred Quick Trip was in place Switch person was approximately 5' from the point of the flash using a shot gun and class 2 rubber gloves All other crew members were over 10' away from the point of the flash All members made a complete recovery within 24 hours |  |  | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Brent Boles | Quay Prough |  | Gary Lassley | Investigate to see if there are better safety glasses available that would have prevented a flash burn to the eyes. Also discuss if we really needed all five members observing the switching procedure. | Gary Lassley |  | Medium | [9 empty] | 10.05 Inadequate assessment of operational readiness |  |  |  |  | 15.03 Inadequate inspection and/or monitoring |  | Arc flash occurred on 7200 VAC Bushing | 12. Servicing Equipment in Operation | 9. Abnormal Operation |  | Reviewed/approved. All controls were implemented and kept the risk level of this incident at a low. | [24 empty] | FALSE |  |  | 2018-11-05 | 1996-07-16 |  | 2019-08-28 20:00 | 0 | 0 | Artificial Tears | FALSE |  | Arc Flash occurred while pulling cap off of 12.5kv bushing |  | TRUE | Colton Collins |  | First Aid | Colton Collins |  |  |  |  | Burn: Electrical |  | FALSE |  | Cable Splicer Appr | Eye |  |  |  | Quay Prough |  |  | 8/28/2019 8:00:00 PM |  | FALSE |  |  | Arc Flash | Observing Switching
9009 | Metro Service Center | 2019-08-28 20:00 | This is a first aid and system operational. While pulling cap off of 12.5kv bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. | Level 2 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Brent Boles | 2019-09-19 13:13 | 2019-08-29 10:09 | 2019-08-29 10:09 | 2019-09-11 07:38 | 2019-09-11 20:00 | 2019-08-29 09:56 | 2019-09-18 15:07 |  | 2019-09-16 07:38 | 11516 Chisholm Trail, OKC Transformer # 69084 |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | System Operational Incident |  | FALSE | TRUE | FALSE |  | TRUE | FALSE | Brent Boles |  | This is a first aid and system operational. While pulling cap off of 7200 VAC bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. After evaluation electrical engineer, believes lightning from the storm the night before caused a pinhole in the bushing where the cap was covering. When the bushing cap was moved approximately 1" the flash occurred. Facts ascertained: Members were wearing all appropriate PPE (FR, Clear Safety Glasses, Hard Hat, and Safety Toed Boots) Switch person's shirt was tucked in It was dark when the incident occurred Quick Trip was in place Switch person was approximately 5' from the point of the flash using a shot gun and class 2 rubber gloves All other crew members were over 10' away from the point of the flash All members made a complete recovery within 24 hours |  |  | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Brent Boles | Quay Prough |  | Gary Lassley | Investigate to see if there are better safety glasses available that would have prevented a flash burn to the eyes. Also discuss if we really needed all five members observing the switching procedure. | Gary Lassley |  | Medium | [9 empty] | 10.05 Inadequate assessment of operational readiness |  |  |  |  | 15.03 Inadequate inspection and/or monitoring |  | Arc flash occurred on 7200 VAC Bushing | 12. Servicing Equipment in Operation | 9. Abnormal Operation |  | Reviewed/approved. All controls were implemented and kept the risk level of this incident at a low. | [24 empty] | FALSE |  |  | 2002-08-12 | 1969-08-12 |  | 2019-08-28 07:00 | 0 | 0 |  | FALSE |  | Arc occurred while pulling cap off of 12.5 kv bushing. |  | FALSE | Brent Boles |  | First Aid | Brent Boles |  |  |  |  | Burn: Electrical |  | FALSE |  | Foreman Underground Network | Eye |  |  | FALSE | Quay Prough | FALSE |  | 8/28/2019 7:00:00 AM |  | FALSE |  |  | Arc Flash | Observing Switching
9009 | Metro Service Center | 2019-08-28 20:00 | This is a first aid and system operational. While pulling cap off of 12.5kv bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. | Level 2 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Brent Boles | 2019-09-19 13:13 | 2019-08-29 10:09 | 2019-08-29 10:09 | 2019-09-11 07:38 | 2019-09-11 20:00 | 2019-08-29 09:56 | 2019-09-18 15:07 |  | 2019-09-16 07:38 | 11516 Chisholm Trail, OKC Transformer # 69084 |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | System Operational Incident |  | FALSE | TRUE | FALSE |  | TRUE | FALSE | Brent Boles |  | This is a first aid and system operational. While pulling cap off of 7200 VAC bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. After evaluation electrical engineer, believes lightning from the storm the night before caused a pinhole in the bushing where the cap was covering. When the bushing cap was moved approximately 1" the flash occurred. Facts ascertained: Members were wearing all appropriate PPE (FR, Clear Safety Glasses, Hard Hat, and Safety Toed Boots) Switch person's shirt was tucked in It was dark when the incident occurred Quick Trip was in place Switch person was approximately 5' from the point of the flash using a shot gun and class 2 rubber gloves All other crew members were over 10' away from the point of the flash All members made a complete recovery within 24 hours |  |  | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Brent Boles | Quay Prough |  | Gary Lassley | Investigate to see if there are better safety glasses available that would have prevented a flash burn to the eyes. Also discuss if we really needed all five members observing the switching procedure. | Gary Lassley |  | Medium | [9 empty] | 10.05 Inadequate assessment of operational readiness |  |  |  |  | 15.03 Inadequate inspection and/or monitoring |  | Arc flash occurred on 7200 VAC Bushing | 12. Servicing Equipment in Operation | 9. Abnormal Operation |  | Reviewed/approved. All controls were implemented and kept the risk level of this incident at a low. | [24 empty] | FALSE |  |  | 1992-06-08 | 1965-11-10 |  | 2019-08-28 07:00 | 0 | 0 |  | FALSE |  | Arc flash occurred while pulling cap off of 12.5 kv bushing |  | FALSE | Adam Carey |  | First Aid | Adam Carey |  |  |  |  | Burn: Electrical |  | FALSE |  | Cable Splicer Appr | Eye |  | Left | FALSE | Brent Boles | FALSE |  | 8/28/2019 7:00:00 AM |  | FALSE |  |  | Arc Flash | Switching
9009 | Metro Service Center | 2019-08-28 20:00 | This is a first aid and system operational. While pulling cap off of 12.5kv bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. | Level 2 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Brent Boles | 2019-09-19 13:13 | 2019-08-29 10:09 | 2019-08-29 10:09 | 2019-09-11 07:38 | 2019-09-11 20:00 | 2019-08-29 09:56 | 2019-09-18 15:07 |  | 2019-09-16 07:38 | 11516 Chisholm Trail, OKC Transformer # 69084 |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | System Operational Incident |  | FALSE | TRUE | FALSE |  | TRUE | FALSE | Brent Boles |  | This is a first aid and system operational. While pulling cap off of 7200 VAC bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. After evaluation electrical engineer, believes lightning from the storm the night before caused a pinhole in the bushing where the cap was covering. When the bushing cap was moved approximately 1" the flash occurred. Facts ascertained: Members were wearing all appropriate PPE (FR, Clear Safety Glasses, Hard Hat, and Safety Toed Boots) Switch person's shirt was tucked in It was dark when the incident occurred Quick Trip was in place Switch person was approximately 5' from the point of the flash using a shot gun and class 2 rubber gloves All other crew members were over 10' away from the point of the flash All members made a complete recovery within 24 hours |  |  | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Brent Boles | Quay Prough |  | Gary Lassley | Investigate to see if there are better safety glasses available that would have prevented a flash burn to the eyes. Also discuss if we really needed all five members observing the switching procedure. | Gary Lassley |  | Medium | [9 empty] | 10.05 Inadequate assessment of operational readiness |  |  |  |  | 15.03 Inadequate inspection and/or monitoring |  | Arc flash occurred on 7200 VAC Bushing | 12. Servicing Equipment in Operation | 9. Abnormal Operation |  | Reviewed/approved. All controls were implemented and kept the risk level of this incident at a low. | [24 empty] | FALSE |  |  | 2018-03-12 | 1995-08-03 |  | 2019-08-28 07:00 | 0 | 0 | Artificial Tears | FALSE |  | Arc flash occurred while pulling 12.5kv bushing cap |  | TRUE | Taylor Barnett |  | First Aid | Taylor Barnett |  |  |  |  | Burn: Electrical |  | FALSE |  | Cable Splicer Appr | Eye |  |  | FALSE | Brent Boles | FALSE |  | 8/28/2019 7:00:00 AM |  | FALSE |  |  | Arc flash | Observing switching
9009 | Metro Service Center | 2019-08-28 20:00 | This is a first aid and system operational. While pulling cap off of 12.5kv bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. | Level 2 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Brent Boles | 2019-09-19 13:13 | 2019-08-29 10:09 | 2019-08-29 10:09 | 2019-09-11 07:38 | 2019-09-11 20:00 | 2019-08-29 09:56 | 2019-09-18 15:07 |  | 2019-09-16 07:38 | 11516 Chisholm Trail, OKC Transformer # 69084 |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | System Operational Incident |  | FALSE | TRUE | FALSE |  | TRUE | FALSE | Brent Boles |  | This is a first aid and system operational. While pulling cap off of 7200 VAC bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. After evaluation electrical engineer, believes lightning from the storm the night before caused a pinhole in the bushing where the cap was covering. When the bushing cap was moved approximately 1" the flash occurred. Facts ascertained: Members were wearing all appropriate PPE (FR, Clear Safety Glasses, Hard Hat, and Safety Toed Boots) Switch person's shirt was tucked in It was dark when the incident occurred Quick Trip was in place Switch person was approximately 5' from the point of the flash using a shot gun and class 2 rubber gloves All other crew members were over 10' away from the point of the flash All members made a complete recovery within 24 hours |  |  | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Brent Boles | Quay Prough |  | Gary Lassley | Investigate to see if there are better safety glasses available that would have prevented a flash burn to the eyes. Also discuss if we really needed all five members observing the switching procedure. | Gary Lassley |  | Medium | [9 empty] | 10.05 Inadequate assessment of operational readiness |  |  |  |  | 15.03 Inadequate inspection and/or monitoring |  | Arc flash occurred on 7200 VAC Bushing | 12. Servicing Equipment in Operation | 9. Abnormal Operation |  | Reviewed/approved. All controls were implemented and kept the risk level of this incident at a low. | [24 empty] | FALSE |  |  | 2019-01-14 | 1986-01-07 |  | 2019-08-28 07:00 | 0 | 0 | Artificial tears administered. | FALSE |  | Arc occurred while pulling bushing cap from 12.5kv elbow in a padmount transformer |  | TRUE | Steven Countryman |  | First Aid | Steven Countryman |  |  |  |  | Burn: Electrical |  | FALSE |  | Cable Splicer Appr | Eye |  |  | FALSE | Frank Alsip | FALSE |  | 8/28/2019 7:00:00 AM |  | FALSE |  |  | Arc Flash | Observing switching
9009 | Metro Service Center | 2019-08-28 20:00 | This is a first aid and system operational. While pulling cap off of 12.5kv bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. | Level 2 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Brent Boles | 2019-09-19 13:13 | 2019-08-29 10:09 | 2019-08-29 10:09 | 2019-09-11 07:38 | 2019-09-11 20:00 | 2019-08-29 09:56 | 2019-09-18 15:07 |  | 2019-09-16 07:38 | 11516 Chisholm Trail, OKC Transformer # 69084 |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | System Operational Incident |  | FALSE | TRUE | FALSE |  | TRUE | FALSE | Brent Boles |  | This is a first aid and system operational. While pulling cap off of 7200 VAC bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. After evaluation electrical engineer, believes lightning from the storm the night before caused a pinhole in the bushing where the cap was covering. When the bushing cap was moved approximately 1" the flash occurred. Facts ascertained: Members were wearing all appropriate PPE (FR, Clear Safety Glasses, Hard Hat, and Safety Toed Boots) Switch person's shirt was tucked in It was dark when the incident occurred Quick Trip was in place Switch person was approximately 5' from the point of the flash using a shot gun and class 2 rubber gloves All other crew members were over 10' away from the point of the flash All members made a complete recovery within 24 hours |  |  | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Brent Boles | Quay Prough |  | Gary Lassley | Investigate to see if there are better safety glasses available that would have prevented a flash burn to the eyes. Also discuss if we really needed all five members observing the switching procedure. | Gary Lassley |  | Medium | [9 empty] | 10.06 Inadequate or improper controls | [6 empty] | NA Reference associated System operational incident | 12. Servicing Equipment in Operation | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Reviewed/approved. All controls were implemented and kept the risk level of this incident at a low. | [24 empty] | FALSE |  |  | 2018-11-05 | 1996-07-16 |  | 2019-08-28 20:00 | 0 | 0 | Artificial Tears | FALSE |  | Arc Flash occurred while pulling cap off of 12.5kv bushing |  | TRUE | Colton Collins |  | First Aid | Colton Collins |  |  |  |  | Burn: Electrical |  | FALSE |  | Cable Splicer Appr | Eye |  |  |  | Quay Prough |  |  | 8/28/2019 8:00:00 PM |  | FALSE |  |  | Arc Flash | Observing Switching
9009 | Metro Service Center | 2019-08-28 20:00 | This is a first aid and system operational. While pulling cap off of 12.5kv bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. | Level 2 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Brent Boles | 2019-09-19 13:13 | 2019-08-29 10:09 | 2019-08-29 10:09 | 2019-09-11 07:38 | 2019-09-11 20:00 | 2019-08-29 09:56 | 2019-09-18 15:07 |  | 2019-09-16 07:38 | 11516 Chisholm Trail, OKC Transformer # 69084 |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | System Operational Incident |  | FALSE | TRUE | FALSE |  | TRUE | FALSE | Brent Boles |  | This is a first aid and system operational. While pulling cap off of 7200 VAC bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. After evaluation electrical engineer, believes lightning from the storm the night before caused a pinhole in the bushing where the cap was covering. When the bushing cap was moved approximately 1" the flash occurred. Facts ascertained: Members were wearing all appropriate PPE (FR, Clear Safety Glasses, Hard Hat, and Safety Toed Boots) Switch person's shirt was tucked in It was dark when the incident occurred Quick Trip was in place Switch person was approximately 5' from the point of the flash using a shot gun and class 2 rubber gloves All other crew members were over 10' away from the point of the flash All members made a complete recovery within 24 hours |  |  | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Brent Boles | Quay Prough |  | Gary Lassley | Investigate to see if there are better safety glasses available that would have prevented a flash burn to the eyes. Also discuss if we really needed all five members observing the switching procedure. | Gary Lassley |  | Medium | [9 empty] | 10.06 Inadequate or improper controls | [6 empty] | NA Reference associated System operational incident | 12. Servicing Equipment in Operation | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Reviewed/approved. All controls were implemented and kept the risk level of this incident at a low. | [24 empty] | FALSE |  |  | 2002-08-12 | 1969-08-12 |  | 2019-08-28 07:00 | 0 | 0 |  | FALSE |  | Arc occurred while pulling cap off of 12.5 kv bushing. |  | FALSE | Brent Boles |  | First Aid | Brent Boles |  |  |  |  | Burn: Electrical |  | FALSE |  | Foreman Underground Network | Eye |  |  | FALSE | Quay Prough | FALSE |  | 8/28/2019 7:00:00 AM |  | FALSE |  |  | Arc Flash | Observing Switching
9009 | Metro Service Center | 2019-08-28 20:00 | This is a first aid and system operational. While pulling cap off of 12.5kv bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. | Level 2 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Brent Boles | 2019-09-19 13:13 | 2019-08-29 10:09 | 2019-08-29 10:09 | 2019-09-11 07:38 | 2019-09-11 20:00 | 2019-08-29 09:56 | 2019-09-18 15:07 |  | 2019-09-16 07:38 | 11516 Chisholm Trail, OKC Transformer # 69084 |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | System Operational Incident |  | FALSE | TRUE | FALSE |  | TRUE | FALSE | Brent Boles |  | This is a first aid and system operational. While pulling cap off of 7200 VAC bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. After evaluation electrical engineer, believes lightning from the storm the night before caused a pinhole in the bushing where the cap was covering. When the bushing cap was moved approximately 1" the flash occurred. Facts ascertained: Members were wearing all appropriate PPE (FR, Clear Safety Glasses, Hard Hat, and Safety Toed Boots) Switch person's shirt was tucked in It was dark when the incident occurred Quick Trip was in place Switch person was approximately 5' from the point of the flash using a shot gun and class 2 rubber gloves All other crew members were over 10' away from the point of the flash All members made a complete recovery within 24 hours |  |  | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Brent Boles | Quay Prough |  | Gary Lassley | Investigate to see if there are better safety glasses available that would have prevented a flash burn to the eyes. Also discuss if we really needed all five members observing the switching procedure. | Gary Lassley |  | Medium | [9 empty] | 10.06 Inadequate or improper controls | [6 empty] | NA Reference associated System operational incident | 12. Servicing Equipment in Operation | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Reviewed/approved. All controls were implemented and kept the risk level of this incident at a low. | [24 empty] | FALSE |  |  | 1992-06-08 | 1965-11-10 |  | 2019-08-28 07:00 | 0 | 0 |  | FALSE |  | Arc flash occurred while pulling cap off of 12.5 kv bushing |  | FALSE | Adam Carey |  | First Aid | Adam Carey |  |  |  |  | Burn: Electrical |  | FALSE |  | Cable Splicer Appr | Eye |  | Left | FALSE | Brent Boles | FALSE |  | 8/28/2019 7:00:00 AM |  | FALSE |  |  | Arc Flash | Switching
9009 | Metro Service Center | 2019-08-28 20:00 | This is a first aid and system operational. While pulling cap off of 12.5kv bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. | Level 2 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Brent Boles | 2019-09-19 13:13 | 2019-08-29 10:09 | 2019-08-29 10:09 | 2019-09-11 07:38 | 2019-09-11 20:00 | 2019-08-29 09:56 | 2019-09-18 15:07 |  | 2019-09-16 07:38 | 11516 Chisholm Trail, OKC Transformer # 69084 |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | System Operational Incident |  | FALSE | TRUE | FALSE |  | TRUE | FALSE | Brent Boles |  | This is a first aid and system operational. While pulling cap off of 7200 VAC bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. After evaluation electrical engineer, believes lightning from the storm the night before caused a pinhole in the bushing where the cap was covering. When the bushing cap was moved approximately 1" the flash occurred. Facts ascertained: Members were wearing all appropriate PPE (FR, Clear Safety Glasses, Hard Hat, and Safety Toed Boots) Switch person's shirt was tucked in It was dark when the incident occurred Quick Trip was in place Switch person was approximately 5' from the point of the flash using a shot gun and class 2 rubber gloves All other crew members were over 10' away from the point of the flash All members made a complete recovery within 24 hours |  |  | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Brent Boles | Quay Prough |  | Gary Lassley | Investigate to see if there are better safety glasses available that would have prevented a flash burn to the eyes. Also discuss if we really needed all five members observing the switching procedure. | Gary Lassley |  | Medium | [9 empty] | 10.06 Inadequate or improper controls | [6 empty] | NA Reference associated System operational incident | 12. Servicing Equipment in Operation | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Reviewed/approved. All controls were implemented and kept the risk level of this incident at a low. | [24 empty] | FALSE |  |  | 2018-03-12 | 1995-08-03 |  | 2019-08-28 07:00 | 0 | 0 | Artificial Tears | FALSE |  | Arc flash occurred while pulling 12.5kv bushing cap |  | TRUE | Taylor Barnett |  | First Aid | Taylor Barnett |  |  |  |  | Burn: Electrical |  | FALSE |  | Cable Splicer Appr | Eye |  |  | FALSE | Brent Boles | FALSE |  | 8/28/2019 7:00:00 AM |  | FALSE |  |  | Arc flash | Observing switching
9009 | Metro Service Center | 2019-08-28 20:00 | This is a first aid and system operational. While pulling cap off of 12.5kv bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. | Level 2 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Brent Boles | 2019-09-19 13:13 | 2019-08-29 10:09 | 2019-08-29 10:09 | 2019-09-11 07:38 | 2019-09-11 20:00 | 2019-08-29 09:56 | 2019-09-18 15:07 |  | 2019-09-16 07:38 | 11516 Chisholm Trail, OKC Transformer # 69084 |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | System Operational Incident |  | FALSE | TRUE | FALSE |  | TRUE | FALSE | Brent Boles |  | This is a first aid and system operational. While pulling cap off of 7200 VAC bushing an arc occurred. Member experienced minor discomfort to eye. No other injuries. After evaluation electrical engineer, believes lightning from the storm the night before caused a pinhole in the bushing where the cap was covering. When the bushing cap was moved approximately 1" the flash occurred. Facts ascertained: Members were wearing all appropriate PPE (FR, Clear Safety Glasses, Hard Hat, and Safety Toed Boots) Switch person's shirt was tucked in It was dark when the incident occurred Quick Trip was in place Switch person was approximately 5' from the point of the flash using a shot gun and class 2 rubber gloves All other crew members were over 10' away from the point of the flash All members made a complete recovery within 24 hours |  |  | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Brent Boles | Quay Prough |  | Gary Lassley | Investigate to see if there are better safety glasses available that would have prevented a flash burn to the eyes. Also discuss if we really needed all five members observing the switching procedure. | Gary Lassley |  | Medium | [9 empty] | 10.06 Inadequate or improper controls | [6 empty] | NA Reference associated System operational incident | 12. Servicing Equipment in Operation | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Reviewed/approved. All controls were implemented and kept the risk level of this incident at a low. | [24 empty] | FALSE |  |  | 2019-01-14 | 1986-01-07 |  | 2019-08-28 07:00 | 0 | 0 | Artificial tears administered. | FALSE |  | Arc occurred while pulling bushing cap from 12.5kv elbow in a padmount transformer |  | TRUE | Steven Countryman |  | First Aid | Steven Countryman |  |  |  |  | Burn: Electrical |  | FALSE |  | Cable Splicer Appr | Eye |  |  | FALSE | Frank Alsip | FALSE |  | 8/28/2019 7:00:00 AM |  | FALSE |  |  | Arc Flash | Observing switching
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.05 Misunderstood directions |  | 7.06 Improper attempt to save time or effort |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Members did not wait on truck with speed stripper or 4 way to return in an attempt save time. Proper tools were not placed on the maintenance crew's truck 5.05: In years past it was acceptable to use the cable knife for this task 7.06 Waiting on the truck would have added time to the job 9: We do not thoroughly identify tasks that the use of a knife is permissible nor do we train on technique | 20. Failure to Communicate, Coordinate | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.05 Misunderstood directions |  | 7.06 Improper attempt to save time or effort |  | 9.09 Inadequate identification and evaluation of loss exposures | [7 empty] | Members did not wait on truck with speed stripper or 4 way to return in an attempt save time. Proper tools were not placed on the maintenance crew's truck 5.05: In years past it was acceptable to use the cable knife for this task 7.06 Waiting on the truck would have added time to the job 9: We do not thoroughly identify tasks that the use of a knife is permissible nor do we train on technique | 20. Failure to Communicate, Coordinate | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High | [6 empty] | 7.01 Improper performance is rewarded (tolerated) | 8.1.2 Improper conduct that is condoned: Unintentional | [5 empty] | 14.01.3 Inadequate development of standards: employee involvement |  |  | Knife was used instead of 4 way or speed stripper 7.01: Use of cable knife for this task has been tolerated 8.01.2: The wording tool of last resort is very generic and up for interpretation 14.01.3 We currently do not have a defined list of when the use of a knife is permissible | 16. Failure to Follow Procedure, Policy, Practice | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.05 Inadequate review instruction |  |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | Was not in proper cutting position allowing knife to cut his wrists when it slipped. 5&6: Member had limited experience performing the task and no training on doing the task with a knife | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.03 Infrequent performance |  |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | Was not in proper cutting position allowing knife to cut his wrists when it slipped. 5&6: Member had limited experience performing the task and no training on doing the task with a knife | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.01 Inadequate initial instruction |  |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | Was not in proper cutting position allowing knife to cut his wrists when it slipped. 5&6: Member had limited experience performing the task and no training on doing the task with a knife | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching |  |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | Was not in proper cutting position allowing knife to cut his wrists when it slipped. 5&6: Member had limited experience performing the task and no training on doing the task with a knife | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.02 Inadequate practice |  |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | Was not in proper cutting position allowing knife to cut his wrists when it slipped. 5&6: Member had limited experience performing the task and no training on doing the task with a knife | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.03 Inadequate initial training | 6.05 Inadequate review instruction |  |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | Was not in proper cutting position allowing knife to cut his wrists when it slipped. 5&6: Member had limited experience performing the task and no training on doing the task with a knife | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.03 Inadequate initial training | 6.03 Infrequent performance |  |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | Was not in proper cutting position allowing knife to cut his wrists when it slipped. 5&6: Member had limited experience performing the task and no training on doing the task with a knife | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.03 Inadequate initial training | 6.01 Inadequate initial instruction |  |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | Was not in proper cutting position allowing knife to cut his wrists when it slipped. 5&6: Member had limited experience performing the task and no training on doing the task with a knife | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.03 Inadequate initial training | 6.04 Lack of coaching |  |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | Was not in proper cutting position allowing knife to cut his wrists when it slipped. 5&6: Member had limited experience performing the task and no training on doing the task with a knife | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.03 Inadequate initial training | 6.02 Inadequate practice |  |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | Was not in proper cutting position allowing knife to cut his wrists when it slipped. 5&6: Member had limited experience performing the task and no training on doing the task with a knife | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.05 Misunderstood directions | 6.05 Inadequate review instruction |  |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | Was not in proper cutting position allowing knife to cut his wrists when it slipped. 5&6: Member had limited experience performing the task and no training on doing the task with a knife | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.05 Misunderstood directions | 6.03 Infrequent performance |  |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | Was not in proper cutting position allowing knife to cut his wrists when it slipped. 5&6: Member had limited experience performing the task and no training on doing the task with a knife | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.05 Misunderstood directions | 6.01 Inadequate initial instruction |  |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | Was not in proper cutting position allowing knife to cut his wrists when it slipped. 5&6: Member had limited experience performing the task and no training on doing the task with a knife | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.05 Misunderstood directions | 6.04 Lack of coaching |  |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | Was not in proper cutting position allowing knife to cut his wrists when it slipped. 5&6: Member had limited experience performing the task and no training on doing the task with a knife | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.05 Misunderstood directions | 6.02 Inadequate practice |  |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | Was not in proper cutting position allowing knife to cut his wrists when it slipped. 5&6: Member had limited experience performing the task and no training on doing the task with a knife | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.05 Inadequate review instruction |  |  | 9.09 Inadequate identification and evaluation of loss exposures | [7 empty] | Member had very little experience using cable knife to strip secondary wire. 5: Member used 4 way to strip secondary wire at his current employer 6: We do not train members on what tasks a knife is approved for or on how to properly use one | 15. Using Equipment Improperly | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.05 Inadequate review instruction |  |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Member had very little experience using cable knife to strip secondary wire. 5: Member used 4 way to strip secondary wire at his current employer 6: We do not train members on what tasks a knife is approved for or on how to properly use one | 15. Using Equipment Improperly | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.03 Infrequent performance |  |  | 9.09 Inadequate identification and evaluation of loss exposures | [7 empty] | Member had very little experience using cable knife to strip secondary wire. 5: Member used 4 way to strip secondary wire at his current employer 6: We do not train members on what tasks a knife is approved for or on how to properly use one | 15. Using Equipment Improperly | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.03 Infrequent performance |  |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Member had very little experience using cable knife to strip secondary wire. 5: Member used 4 way to strip secondary wire at his current employer 6: We do not train members on what tasks a knife is approved for or on how to properly use one | 15. Using Equipment Improperly | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.01 Inadequate initial instruction |  |  | 9.09 Inadequate identification and evaluation of loss exposures | [7 empty] | Member had very little experience using cable knife to strip secondary wire. 5: Member used 4 way to strip secondary wire at his current employer 6: We do not train members on what tasks a knife is approved for or on how to properly use one | 15. Using Equipment Improperly | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.01 Inadequate initial instruction |  |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Member had very little experience using cable knife to strip secondary wire. 5: Member used 4 way to strip secondary wire at his current employer 6: We do not train members on what tasks a knife is approved for or on how to properly use one | 15. Using Equipment Improperly | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching |  |  | 9.09 Inadequate identification and evaluation of loss exposures | [7 empty] | Member had very little experience using cable knife to strip secondary wire. 5: Member used 4 way to strip secondary wire at his current employer 6: We do not train members on what tasks a knife is approved for or on how to properly use one | 15. Using Equipment Improperly | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching |  |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Member had very little experience using cable knife to strip secondary wire. 5: Member used 4 way to strip secondary wire at his current employer 6: We do not train members on what tasks a knife is approved for or on how to properly use one | 15. Using Equipment Improperly | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.02 Inadequate practice |  |  | 9.09 Inadequate identification and evaluation of loss exposures | [7 empty] | Member had very little experience using cable knife to strip secondary wire. 5: Member used 4 way to strip secondary wire at his current employer 6: We do not train members on what tasks a knife is approved for or on how to properly use one | 15. Using Equipment Improperly | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.02 Inadequate practice |  |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Member had very little experience using cable knife to strip secondary wire. 5: Member used 4 way to strip secondary wire at his current employer 6: We do not train members on what tasks a knife is approved for or on how to properly use one | 15. Using Equipment Improperly | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High | [6 empty] | 7.13 Inadequate reinforcement of proper behavior |  | 9.09 Inadequate identification and evaluation of loss exposures |  |  |  |  | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  |  | No formal training on the use of knifes. There is also no formal training on stripping secondary wires or OH services. | 19. Failure to React, Correct | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High | [6 empty] | 7.13 Inadequate reinforcement of proper behavior |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  |  | No formal training on the use of knifes. There is also no formal training on stripping secondary wires or OH services. | 19. Failure to React, Correct | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High | [6 empty] | 7.01 Improper performance is rewarded (tolerated) | [9 empty] | A pushing action was used by the member with the intent of mitigating the potential of cutting his core. A pulling action directed away from all body parts is the best practice. 7.01: The use of cable knife was tolerated for this task 5: Member had only performed this task a handful of times | 37. Inadequate Support, Assistance | 9. Abnormal Operation | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.05 Inadequate review instruction | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.08 Incorrect instructions | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.05 Inadequate review instruction | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.09 Inadequate communication due to job turnover | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.03 Infrequent performance | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.08 Incorrect instructions | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.03 Infrequent performance | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.09 Inadequate communication due to job turnover | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.01 Inadequate initial instruction | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.08 Incorrect instructions | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.01 Inadequate initial instruction | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.09 Inadequate communication due to job turnover | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.08 Incorrect instructions | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.09 Inadequate communication due to job turnover | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.02 Inadequate practice | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.08 Incorrect instructions | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.02 Inadequate practice | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.09 Inadequate communication due to job turnover | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.08 Incorrect instructions | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.09 Inadequate communication due to job turnover | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.08 Incorrect instructions | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.09 Inadequate communication due to job turnover | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.01 Inadequate initial instruction | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.08 Incorrect instructions | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.01 Inadequate initial instruction | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.09 Inadequate communication due to job turnover | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.08 Incorrect instructions | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.09 Inadequate communication due to job turnover | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.02 Inadequate practice | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.08 Incorrect instructions | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.02 Inadequate practice | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.09 Inadequate communication due to job turnover | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.04 Inadequate update training | 6.05 Inadequate review instruction | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.08 Incorrect instructions | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.04 Inadequate update training | 6.05 Inadequate review instruction | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.09 Inadequate communication due to job turnover | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.04 Inadequate update training | 6.03 Infrequent performance | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.08 Incorrect instructions | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.04 Inadequate update training | 6.03 Infrequent performance | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.09 Inadequate communication due to job turnover | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.04 Inadequate update training | 6.01 Inadequate initial instruction | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.08 Incorrect instructions | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.04 Inadequate update training | 6.01 Inadequate initial instruction | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.09 Inadequate communication due to job turnover | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.04 Inadequate update training | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.08 Incorrect instructions | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.04 Inadequate update training | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.09 Inadequate communication due to job turnover | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.04 Inadequate update training | 6.02 Inadequate practice | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.08 Incorrect instructions | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Casey Lee | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.04 Inadequate update training | 6.02 Inadequate practice | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.09 Inadequate communication due to job turnover | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.05 Misunderstood directions |  | 7.06 Improper attempt to save time or effort |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Members did not wait on truck with speed stripper or 4 way to return in an attempt save time. Proper tools were not placed on the maintenance crew's truck 5.05: In years past it was acceptable to use the cable knife for this task 7.06 Waiting on the truck would have added time to the job 9: We do not thoroughly identify tasks that the use of a knife is permissible nor do we train on technique | 20. Failure to Communicate, Coordinate | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.05 Misunderstood directions |  | 7.06 Improper attempt to save time or effort |  | 9.09 Inadequate identification and evaluation of loss exposures | [7 empty] | Members did not wait on truck with speed stripper or 4 way to return in an attempt save time. Proper tools were not placed on the maintenance crew's truck 5.05: In years past it was acceptable to use the cable knife for this task 7.06 Waiting on the truck would have added time to the job 9: We do not thoroughly identify tasks that the use of a knife is permissible nor do we train on technique | 20. Failure to Communicate, Coordinate | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High | [6 empty] | 7.01 Improper performance is rewarded (tolerated) | 8.1.2 Improper conduct that is condoned: Unintentional | [5 empty] | 14.01.3 Inadequate development of standards: employee involvement |  |  | Knife was used instead of 4 way or speed stripper 7.01: Use of cable knife for this task has been tolerated 8.01.2: The wording tool of last resort is very generic and up for interpretation 14.01.3 We currently do not have a defined list of when the use of a knife is permissible | 16. Failure to Follow Procedure, Policy, Practice | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.05 Inadequate review instruction |  |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | Was not in proper cutting position allowing knife to cut his wrists when it slipped. 5&6: Member had limited experience performing the task and no training on doing the task with a knife | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.03 Infrequent performance |  |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | Was not in proper cutting position allowing knife to cut his wrists when it slipped. 5&6: Member had limited experience performing the task and no training on doing the task with a knife | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.01 Inadequate initial instruction |  |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | Was not in proper cutting position allowing knife to cut his wrists when it slipped. 5&6: Member had limited experience performing the task and no training on doing the task with a knife | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching |  |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | Was not in proper cutting position allowing knife to cut his wrists when it slipped. 5&6: Member had limited experience performing the task and no training on doing the task with a knife | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.02 Inadequate practice |  |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | Was not in proper cutting position allowing knife to cut his wrists when it slipped. 5&6: Member had limited experience performing the task and no training on doing the task with a knife | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.03 Inadequate initial training | 6.05 Inadequate review instruction |  |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | Was not in proper cutting position allowing knife to cut his wrists when it slipped. 5&6: Member had limited experience performing the task and no training on doing the task with a knife | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.03 Inadequate initial training | 6.03 Infrequent performance |  |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | Was not in proper cutting position allowing knife to cut his wrists when it slipped. 5&6: Member had limited experience performing the task and no training on doing the task with a knife | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.03 Inadequate initial training | 6.01 Inadequate initial instruction |  |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | Was not in proper cutting position allowing knife to cut his wrists when it slipped. 5&6: Member had limited experience performing the task and no training on doing the task with a knife | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.03 Inadequate initial training | 6.04 Lack of coaching |  |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | Was not in proper cutting position allowing knife to cut his wrists when it slipped. 5&6: Member had limited experience performing the task and no training on doing the task with a knife | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.03 Inadequate initial training | 6.02 Inadequate practice |  |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | Was not in proper cutting position allowing knife to cut his wrists when it slipped. 5&6: Member had limited experience performing the task and no training on doing the task with a knife | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.05 Misunderstood directions | 6.05 Inadequate review instruction |  |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | Was not in proper cutting position allowing knife to cut his wrists when it slipped. 5&6: Member had limited experience performing the task and no training on doing the task with a knife | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.05 Misunderstood directions | 6.03 Infrequent performance |  |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | Was not in proper cutting position allowing knife to cut his wrists when it slipped. 5&6: Member had limited experience performing the task and no training on doing the task with a knife | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.05 Misunderstood directions | 6.01 Inadequate initial instruction |  |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | Was not in proper cutting position allowing knife to cut his wrists when it slipped. 5&6: Member had limited experience performing the task and no training on doing the task with a knife | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.05 Misunderstood directions | 6.04 Lack of coaching |  |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | Was not in proper cutting position allowing knife to cut his wrists when it slipped. 5&6: Member had limited experience performing the task and no training on doing the task with a knife | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.05 Misunderstood directions | 6.02 Inadequate practice |  |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | Was not in proper cutting position allowing knife to cut his wrists when it slipped. 5&6: Member had limited experience performing the task and no training on doing the task with a knife | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.05 Inadequate review instruction |  |  | 9.09 Inadequate identification and evaluation of loss exposures | [7 empty] | Member had very little experience using cable knife to strip secondary wire. 5: Member used 4 way to strip secondary wire at his current employer 6: We do not train members on what tasks a knife is approved for or on how to properly use one | 15. Using Equipment Improperly | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.05 Inadequate review instruction |  |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Member had very little experience using cable knife to strip secondary wire. 5: Member used 4 way to strip secondary wire at his current employer 6: We do not train members on what tasks a knife is approved for or on how to properly use one | 15. Using Equipment Improperly | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.03 Infrequent performance |  |  | 9.09 Inadequate identification and evaluation of loss exposures | [7 empty] | Member had very little experience using cable knife to strip secondary wire. 5: Member used 4 way to strip secondary wire at his current employer 6: We do not train members on what tasks a knife is approved for or on how to properly use one | 15. Using Equipment Improperly | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.03 Infrequent performance |  |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Member had very little experience using cable knife to strip secondary wire. 5: Member used 4 way to strip secondary wire at his current employer 6: We do not train members on what tasks a knife is approved for or on how to properly use one | 15. Using Equipment Improperly | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.01 Inadequate initial instruction |  |  | 9.09 Inadequate identification and evaluation of loss exposures | [7 empty] | Member had very little experience using cable knife to strip secondary wire. 5: Member used 4 way to strip secondary wire at his current employer 6: We do not train members on what tasks a knife is approved for or on how to properly use one | 15. Using Equipment Improperly | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.01 Inadequate initial instruction |  |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Member had very little experience using cable knife to strip secondary wire. 5: Member used 4 way to strip secondary wire at his current employer 6: We do not train members on what tasks a knife is approved for or on how to properly use one | 15. Using Equipment Improperly | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching |  |  | 9.09 Inadequate identification and evaluation of loss exposures | [7 empty] | Member had very little experience using cable knife to strip secondary wire. 5: Member used 4 way to strip secondary wire at his current employer 6: We do not train members on what tasks a knife is approved for or on how to properly use one | 15. Using Equipment Improperly | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching |  |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Member had very little experience using cable knife to strip secondary wire. 5: Member used 4 way to strip secondary wire at his current employer 6: We do not train members on what tasks a knife is approved for or on how to properly use one | 15. Using Equipment Improperly | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.02 Inadequate practice |  |  | 9.09 Inadequate identification and evaluation of loss exposures | [7 empty] | Member had very little experience using cable knife to strip secondary wire. 5: Member used 4 way to strip secondary wire at his current employer 6: We do not train members on what tasks a knife is approved for or on how to properly use one | 15. Using Equipment Improperly | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.02 Inadequate practice |  |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Member had very little experience using cable knife to strip secondary wire. 5: Member used 4 way to strip secondary wire at his current employer 6: We do not train members on what tasks a knife is approved for or on how to properly use one | 15. Using Equipment Improperly | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High | [6 empty] | 7.13 Inadequate reinforcement of proper behavior |  | 9.09 Inadequate identification and evaluation of loss exposures |  |  |  |  | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  |  | No formal training on the use of knifes. There is also no formal training on stripping secondary wires or OH services. | 19. Failure to React, Correct | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High | [6 empty] | 7.13 Inadequate reinforcement of proper behavior |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.03.3 Inadequate maintenance of standards: monitoring use of procedures/practices/rules |  |  | No formal training on the use of knifes. There is also no formal training on stripping secondary wires or OH services. | 19. Failure to React, Correct | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High | [6 empty] | 7.01 Improper performance is rewarded (tolerated) | [9 empty] | A pushing action was used by the member with the intent of mitigating the potential of cutting his core. A pulling action directed away from all body parts is the best practice. 7.01: The use of cable knife was tolerated for this task 5: Member had only performed this task a handful of times | 37. Inadequate Support, Assistance | 9. Abnormal Operation | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.05 Inadequate review instruction | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.08 Incorrect instructions | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.05 Inadequate review instruction | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.09 Inadequate communication due to job turnover | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.03 Infrequent performance | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.08 Incorrect instructions | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.03 Infrequent performance | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.09 Inadequate communication due to job turnover | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.01 Inadequate initial instruction | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.08 Incorrect instructions | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.01 Inadequate initial instruction | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.09 Inadequate communication due to job turnover | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.08 Incorrect instructions | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.09 Inadequate communication due to job turnover | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.02 Inadequate practice | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.08 Incorrect instructions | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.01 Lack of experience | 6.02 Inadequate practice | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.09 Inadequate communication due to job turnover | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.08 Incorrect instructions | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.09 Inadequate communication due to job turnover | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.08 Incorrect instructions | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.09 Inadequate communication due to job turnover | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.01 Inadequate initial instruction | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.08 Incorrect instructions | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.01 Inadequate initial instruction | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.09 Inadequate communication due to job turnover | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.08 Incorrect instructions | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.09 Inadequate communication due to job turnover | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.02 Inadequate practice | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.08 Incorrect instructions | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.02 Inadequate practice | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.09 Inadequate communication due to job turnover | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.04 Inadequate update training | 6.05 Inadequate review instruction | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.08 Incorrect instructions | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.04 Inadequate update training | 6.05 Inadequate review instruction | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.09 Inadequate communication due to job turnover | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.04 Inadequate update training | 6.03 Infrequent performance | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.08 Incorrect instructions | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.04 Inadequate update training | 6.03 Infrequent performance | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.09 Inadequate communication due to job turnover | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.04 Inadequate update training | 6.01 Inadequate initial instruction | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.08 Incorrect instructions | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.04 Inadequate update training | 6.01 Inadequate initial instruction | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.09 Inadequate communication due to job turnover | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.04 Inadequate update training | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.08 Incorrect instructions | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.04 Inadequate update training | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.09 Inadequate communication due to job turnover | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.04 Inadequate update training | 6.02 Inadequate practice | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.08 Incorrect instructions | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9013 | Metro Service Center | 2019-08-28 16:30 | While stripping secondary wire, member cut his left forearm right above his wrist. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:22 | Power Delivery | Quay Prough | 2019-09-22 12:47 | 2019-08-29 11:49 | 2019-08-29 11:49 | 2019-09-13 08:07 | 2019-09-11 16:30 | 2019-08-29 11:30 | 2019-09-18 15:01 | 2019-09-19 13:17 | 2019-09-16 13:20 | NW 150th OKC |  |  | Andrea Dennis | I agree with the action items and with Robert's comments. As the team works through how to identify when a knife can be used, please also identify any tasks where a knife should not be used. As the team works to clarify "tool of last resort", it seems like we should consider an additional tailboard conversation to talk through how the knife will be used, the risks, and the hazards. One final question, did the foreman and member feel like they could stop and wait for the tool? | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Chad Inman |  | Crews were performing storm work. Replacing a single phase transformer with a power dolly. After new transformer was put into place it was discovered that the 350 secondary wires were not long enough to lug up. So the decision was made to splice the secondary wires to give them enough length to lug up. Foreman and affected member used cable splicing knife to strip the secondary wires. While stripping the wire member made round cut, then decided to push the knife down while making his center cut. The knife slipped and cut him on his left wrist. resulting in 7 stictches. Facts Ascertained: 3 crews were involved in the job (2 foremen) 1 foremen and 4 apprentices were not on site when the incident occurred (broke for lunch and fuel) 1 foreman and 3 apprentices were on site when the incident occurred Affected member is not currently assigned a foreman (floating) Affected member asked foreman if there was a 4 way on the truck. Foreman informed him there was not and that they would use their cable knives 4 way and speed stripper was not provided on the truck, because this crew's scope of work is maintenance (i.e. sweeping, cleaning, pumping, and inspecting) There was a 4 way and speed stripper on the other crew truck that was not on the job site Affected member and foreman used cable splicing knife instead of 4 way Foreman and affected member were the only two in the backyard at the padmount Foreman was performing the same task with the same tool approximately 24" apart from each other. Affected member performed a circle cut around the wire, then moved his left hand approximately 12" down the wire an pushed the knife (toward his hand/arm) to make the center cut. Affected member stated he had only used a knife to strip secondary wires a hand full of times and only on copper There is no formal training for the use of knifes Supervisor had performed 2 documented field observations on the crew the affected member was on (1 in June and 1 in July) with no corrective actions needed Supervisor had performed 4 documented field observations on the foreman who was on site (2 in May and 1 in June) with no corrective actions needed No work observations provided for the foreman who was not on site. | Terry Hackett | Chad Inman | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Sean Canright | Quay Prough |  | Gary Lassley | Implement a team to create training that covers and identifies proper cutting/stripping techniques. This training needs to be incorporated into the onboarding process of all new members before they ever go out into the field. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.04 Inadequate update training | 6.02 Inadequate practice | 7.11 Improper supervisory example |  | 9.07 Inadequate instructions, orientation and/or training | [6 empty] | 16.09 Inadequate communication due to job turnover | Member's were working in close proximity to each other. 5 & 6: Affected member had limited experience performing this task with a knife 7.11: Foreman directed member to use cable knife for the task and was performing the task the same way right next to him | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) | approved | Reviewed/Approved | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2019-03-25 | 1995-04-03 |  | 2019-08-28 07:00 | 0 | 0 | bandage applied to stop bleeding | FALSE |  | Knife made contact with left forearm (above the wrist) |  | TRUE | Bryan Hudson |  | Recordable | Bryan Hudson | TRUE |  | Mercy Hospital |  | Laceration |  | TRUE |  | Cable Splicer Appr | Forearm | Injury | Left | TRUE | Quay Prough | TRUE | 2019 | 8/28/2019 7:00:00 AM |  | TRUE | FALSE | TRUE | cable splicing knife | stripping secondary wire with cable splicing knife
9014 | South District Service Center | 2019-08-28 | An Asplundh tree foreman was working in a tree where a line was on the ground. Higher Ground line crew did not inspect the line and reenergized the line while the tree foreman was still in the tree. | Level 3 |  | TRUE | Contractor | Jean Leger | Lindle Coleman | `Based on discussion with ops management. | 2019-09-04 15:24 | OG&E Corp Services | Christopher Martin | 2019-10-02 06:59 | 2019-08-29 14:48 | 2019-08-29 14:48 | 2019-09-10 12:40 | 2019-09-11 | 2019-08-29 14:26 | 2019-09-12 12:04 | 2019-09-12 13:31 | 2019-09-10 11:52 | 4309 Sunnylane circle, Del City. south district service center |  |  | Jean Leger | Please ensure this contractor is disallowed for any future OGE engagement, including Mutual Assistance, unless approved by OG&E company officer. | T&D Ops |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Michael Fox |  | During a recent ICS event in the South Metro a Vegetation Foreman was working in a tree to clear tree limbs from an open wire secondary that was down in the rear of 4309 Sunnylane Circle. Contract crew from Higher Power was assigned to make repairs to the downed secondary. When crew arrived the Vegetation Foreman was 60ft away from the transformer working in a tree. Higher Power Line crew went to remove the barrel from the transformer cutout. In doing so the transformer and the downed secondary laying in the tree with the Vegetation Foreman became energized which frightened the Vegetation Foreman but didn't shock him. The Higher Power crew failed to report the incident to anyone. The Vegetation Foreman called his Supervisor to report the incident. | Luke Kennedy | Michael Fox |  | South District Service Center | FALSE |  | TRUE | PD - Resource Planning & Coord |  | Christopher Martin | Christopher Martin |  | Nicole Rhodes | The tree foreman had line of sight to the downed line and fuse which is the OSHA policy since the line was not tagged. The appropriate and timely actions were definitely taken in this incident and it was a great example of quick collaboration and resolution and I think it is an example on how we should respond to incidents to understand root cause and ensure this didn't happen again. | Nicole Rhodes | Lindle Coleman | High |  |  | 3.03 Fatigue due to lack of rest |  | 5.06 Lack of situational awareness |  |  | 8.2.1 Improper conduct that is not condoned: Intentional | [8 empty] | Higher Power energizing the line that the contract crew was still working on is what caused the close call. | 02. Failure to Warn | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | approved | The corrective actions taken against higher power aligned with their complete disregard for the safety expectations we have for our contractors. Approved 9/10/19 |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Christopher Martin | [5 empty] | 9. Abnormal Operation | Christopher Martin | Asplundh | Aaron Atkinson |  |  |  | Christopher Martin
9014 | South District Service Center | 2019-08-28 | An Asplundh tree foreman was working in a tree where a line was on the ground. Higher Ground line crew did not inspect the line and reenergized the line while the tree foreman was still in the tree. | Level 3 |  | TRUE | Contractor | Jean Leger | Lindle Coleman | `Based on discussion with ops management. | 2019-09-04 15:24 | OG&E Corp Services | Christopher Martin | 2019-10-02 06:59 | 2019-08-29 14:48 | 2019-08-29 14:48 | 2019-09-10 12:40 | 2019-09-11 | 2019-08-29 14:26 | 2019-09-12 12:04 | 2019-09-12 13:31 | 2019-09-10 11:52 | 4309 Sunnylane circle, Del City. south district service center |  |  | Jean Leger | Please ensure this contractor is disallowed for any future OGE engagement, including Mutual Assistance, unless approved by OG&E company officer. | T&D Ops |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Michael Fox |  | During a recent ICS event in the South Metro a Vegetation Foreman was working in a tree to clear tree limbs from an open wire secondary that was down in the rear of 4309 Sunnylane Circle. Contract crew from Higher Power was assigned to make repairs to the downed secondary. When crew arrived the Vegetation Foreman was 60ft away from the transformer working in a tree. Higher Power Line crew went to remove the barrel from the transformer cutout. In doing so the transformer and the downed secondary laying in the tree with the Vegetation Foreman became energized which frightened the Vegetation Foreman but didn't shock him. The Higher Power crew failed to report the incident to anyone. The Vegetation Foreman called his Supervisor to report the incident. | Christopher Martin | Michael Fox |  | South District Service Center | FALSE |  | TRUE | PD - Resource Planning & Coord |  | Christopher Martin | Christopher Martin |  | Nicole Rhodes | The tree foreman had line of sight to the downed line and fuse which is the OSHA policy since the line was not tagged. The appropriate and timely actions were definitely taken in this incident and it was a great example of quick collaboration and resolution and I think it is an example on how we should respond to incidents to understand root cause and ensure this didn't happen again. | Nicole Rhodes | Lindle Coleman | High |  |  | 3.03 Fatigue due to lack of rest |  | 5.06 Lack of situational awareness |  |  | 8.2.1 Improper conduct that is not condoned: Intentional | [8 empty] | Higher Power energizing the line that the contract crew was still working on is what caused the close call. | 02. Failure to Warn | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | approved | The corrective actions taken against higher power aligned with their complete disregard for the safety expectations we have for our contractors. Approved 9/10/19 |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Christopher Martin | [5 empty] | 9. Abnormal Operation | Christopher Martin | Asplundh | Aaron Atkinson |  |  |  | Christopher Martin
9015 | Sooner Power Plant | 2019-08-29 10:00 | After drawing review and locating preformed @ SN Aux. Eng. Generator Bldg. S-East inside corner of concrete floor, a sawed section (approx. 34''x 34" x 8") was removed. Found that receptacle conduit just below floor concrete slab depth was cut also. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Tead Haga | 2019-10-03 09:50 | 2019-08-29 18:02 | 2019-08-29 18:02 | 2019-09-13 15:54 | 2019-09-12 10:00 | 2019-08-29 16:57 | 2019-09-23 08:03 |  | 2019-09-16 07:55 | Sooner Auxiliary Engine Generator Bldg. |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Tead Haga |  | Description: On 8-27-19 @ Sooner Power Plant, Champion Concrete preformed interior saw cutting. Activity consisted of floor concrete sawing an area approximately (34" x 34" x 8") inside SN Aux. Gen. Bldg. at very S-E corner. The area had been located previously by OGE and a drawing review had been conducted by Duncan & Sons with OGE for all utilities below grade. Upon removal of concrete, it was found below grade concrete electrical to east side ext. light and receptacles had been cut @ most outer corner. Conduit was just below concrete with small percentage in concrete bottom it self. Findings: Electrical was not placed per drawings. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Engineering & Planning |  | Tead Haga | Donald Wyckoff |  | Donald Wyckoff | I have reviewed the incident investigation performed by contractor. I made some adjustments for immediate and Basic Cause attributes. Additional conversations were needed which drove approval timeline. Donald E. Wyckoff. | Donald Wyckoff |  | Medium |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.09 Inadequate identification and evaluation of loss exposures | 10.04 Inadequate monitoring of construction | [6 empty] | Drawings reference, not correct. | 09. Improper Placement | 2. Struck By (Hit By Moving Object) |  | Approved by Brady Sowell with the addition of the corrective action. |  |  |  | Property Damage |  | Brady Sowell | Electrical below grade cut. |  |  |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Tead Haga | Duncan and Sons | Marty Rains |  | Utility Strike |  | Tead Haga |  |  |  |  | FALSE | [66 empty] | 615601
9017 | Metro Service Center | 2019-08-28 19:30 | During storm restoration the Linetec crew 748 was working from the bucket truck directly above a parked privately-owned vehicle. A socket attachment fell from the drill that the lineman was using in the bucket and hit the back windshield of the vehicle parked below. The foreman discussed moving the vehicle with the homeowner at the location. The homeowner told the foreman that he dis not have the keys and it was not running and to just work around it. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Delivery | Lewis Wilson | 2019-09-24 09:26 | 2019-08-30 12:33 | 2019-08-30 12:33 | 2019-09-17 11:24 | 2019-09-11 19:30 | 2019-08-30 12:00 | 2019-09-19 12:25 |  |  | 4913 N Linn OKC, OK |  |  | Marcus Huddleston | No additional comments. MLH 9/24/19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | TRUE |  | FALSE | FALSE | Lewis Wilson |  | The crew did not have a drop zone established around the base of the pole to protect workers, equipment or property from objects falling from work conducted aloft. |  |  |  | Metro Service Center | FALSE |  | FALSE | Resource Planning & Coord |  | Lewis Wilson | Lewis Wilson |  | John Legg | Linetec should be aware of the drop zones while working at heightsl. | John Legg |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | The crew did not have a drop zone established around the base of the pole to protect workers, equipment or property from objects falling from work conducted aloft. | 16. Failure to Follow Procedure, Policy, Practice | 3. Fall from Elevation to Lower Level | [5 empty] | Vehicle |  | Lewis Wilson | Socket hit back windshield of part car |  |  |  |  | 3. Fall from Elevation to Lower Level | Lewis Wilson | Linetec | David Parker |  | Vehicle (not related to vehicle's operation) |  | Lewis Wilson |  |  |  |  | FALSE | [42 empty] | A socket attachment fell from the drill that the lineman was using in the bucket and hit the back windshield of the vehicle parked below. | 200 | Lewis Wilson | Vehicle (not related to operation of vehicle)
9017 | Metro Service Center | 2019-08-28 19:30 | During storm restoration the Linetec crew 748 was working from the bucket truck directly above a parked privately-owned vehicle. A socket attachment fell from the drill that the lineman was using in the bucket and hit the back windshield of the vehicle parked below. The foreman discussed moving the vehicle with the homeowner at the location. The homeowner told the foreman that he dis not have the keys and it was not running and to just work around it. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Delivery | Lewis Wilson | 2019-09-24 09:26 | 2019-08-30 12:33 | 2019-08-30 12:33 | 2019-09-17 11:24 | 2019-09-11 19:30 | 2019-08-30 12:00 | 2019-09-19 12:25 |  |  | 4913 N Linn OKC, OK |  |  | Marcus Huddleston | No additional comments. MLH 9/24/19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | TRUE |  | FALSE | FALSE | Lewis Wilson |  | The crew did not have a drop zone established around the base of the pole to protect workers, equipment or property from objects falling from work conducted aloft. |  |  |  | Metro Service Center | FALSE |  | FALSE | Resource Planning & Coord |  | Lewis Wilson | Lewis Wilson |  | John Legg | Linetec should be aware of the drop zones while working at heightsl. | John Legg |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | The crew did not have a drop zone established around the base of the pole to protect workers, equipment or property from objects falling from work conducted aloft. | 16. Failure to Follow Procedure, Policy, Practice | 3. Fall from Elevation to Lower Level | [5 empty] | Property Damage |  | Lewis Wilson | Socket hit back windshield of part car |  |  |  |  | 3. Fall from Elevation to Lower Level | Lewis Wilson | Linetec | David Parker |  | Vehicle (not related to vehicle's operation) |  | Lewis Wilson |  |  |  |  | FALSE | [42 empty] | A socket attachment fell from the drill that the lineman was using in the bucket and hit the back windshield of the vehicle parked below. | 200 | Lewis Wilson | Vehicle (not related to operation of vehicle)
9017 | Metro Service Center | 2019-08-28 19:30 | During storm restoration the Linetec crew 748 was working from the bucket truck directly above a parked privately-owned vehicle. A socket attachment fell from the drill that the lineman was using in the bucket and hit the back windshield of the vehicle parked below. The foreman discussed moving the vehicle with the homeowner at the location. The homeowner told the foreman that he dis not have the keys and it was not running and to just work around it. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Delivery | Lewis Wilson | 2019-09-24 09:26 | 2019-08-30 12:33 | 2019-08-30 12:33 | 2019-09-17 11:24 | 2019-09-11 19:30 | 2019-08-30 12:00 | 2019-09-19 12:25 |  |  | 4913 N Linn OKC, OK |  |  | Marcus Huddleston | No additional comments. MLH 9/24/19 | T&D Ops |  | Level 1 | Property Damage |  | TRUE | FALSE | TRUE |  | FALSE | FALSE | Lewis Wilson |  | The crew did not have a drop zone established around the base of the pole to protect workers, equipment or property from objects falling from work conducted aloft. |  |  |  | Metro Service Center | FALSE |  | FALSE | Resource Planning & Coord |  | Lewis Wilson | Lewis Wilson |  | John Legg | Linetec should be aware of the drop zones while working at heightsl. | John Legg |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | The crew did not have a drop zone established around the base of the pole to protect workers, equipment or property from objects falling from work conducted aloft. | 16. Failure to Follow Procedure, Policy, Practice | 3. Fall from Elevation to Lower Level | [5 empty] | Vehicle |  | Lewis Wilson | Socket hit back windshield of part car |  |  |  |  | 3. Fall from Elevation to Lower Level | Lewis Wilson | Linetec | David Parker |  | Vehicle (not related to vehicle's operation) |  | Lewis Wilson |  |  |  |  | FALSE | [42 empty] | A socket attachment fell from the drill that the lineman was using in the bucket and hit the back windshield of the vehicle parked below. | 200 | Lewis Wilson | Vehicle (not related to operation of vehicle)
9017 | Metro Service Center | 2019-08-28 19:30 | During storm restoration the Linetec crew 748 was working from the bucket truck directly above a parked privately-owned vehicle. A socket attachment fell from the drill that the lineman was using in the bucket and hit the back windshield of the vehicle parked below. The foreman discussed moving the vehicle with the homeowner at the location. The homeowner told the foreman that he dis not have the keys and it was not running and to just work around it. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Delivery | Lewis Wilson | 2019-09-24 09:26 | 2019-08-30 12:33 | 2019-08-30 12:33 | 2019-09-17 11:24 | 2019-09-11 19:30 | 2019-08-30 12:00 | 2019-09-19 12:25 |  |  | 4913 N Linn OKC, OK |  |  | Marcus Huddleston | No additional comments. MLH 9/24/19 | T&D Ops |  | Level 1 | Property Damage |  | TRUE | FALSE | TRUE |  | FALSE | FALSE | Lewis Wilson |  | The crew did not have a drop zone established around the base of the pole to protect workers, equipment or property from objects falling from work conducted aloft. |  |  |  | Metro Service Center | FALSE |  | FALSE | Resource Planning & Coord |  | Lewis Wilson | Lewis Wilson |  | John Legg | Linetec should be aware of the drop zones while working at heightsl. | John Legg |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | The crew did not have a drop zone established around the base of the pole to protect workers, equipment or property from objects falling from work conducted aloft. | 16. Failure to Follow Procedure, Policy, Practice | 3. Fall from Elevation to Lower Level | [5 empty] | Property Damage |  | Lewis Wilson | Socket hit back windshield of part car |  |  |  |  | 3. Fall from Elevation to Lower Level | Lewis Wilson | Linetec | David Parker |  | Vehicle (not related to vehicle's operation) |  | Lewis Wilson |  |  |  |  | FALSE | [42 empty] | A socket attachment fell from the drill that the lineman was using in the bucket and hit the back windshield of the vehicle parked below. | 200 | Lewis Wilson | Vehicle (not related to operation of vehicle)
9018 | Metro Service Center | 2019-08-30 05:30 | personal vehicle clipped by semi trailer that departed lane during heavy rain. | Level 2 |  | FALSE | Vehicle |  |  |  |  | OG&E Corp Services | Jonathan Blazs | 2019-09-17 12:19 | 2019-08-30 13:02 | 2019-08-30 13:02 | 2019-09-16 10:57 | 2019-09-13 05:30 | 2019-08-30 12:58 | 2019-09-17 07:43 |  | 2019-09-16 21:00 | I-40 Eastbound en route to Shawnee |  |  | Lindle Coleman | reviewed | T&D Ops |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Jonathan Blazs |  | While member was driving to Shawnee service center on the morning of Friday, August 30th. A tractor trailer left their lane and hit the driver's side of the OG&E member's public vehicle. This happened in the construction zone on I-40 where lanes are narrow. |  |  |  | Metro Service Center | FALSE |  | FALSE | PD - Distrib Engineering |  | Luis Sanchez | Jonathan Blazs |  | Ronald Griffin | Please add sketch to illustrate incident. | Ronald Griffin |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Public Driver failed to react when entering the members lane when they approached the slight turn in the work zone | 19. Failure to React, Correct | 2. Struck By (Hit By Moving Object) |  | Approved 9/10/19 | [72 empty] | FALSE |  | Shawnee | Public Vehicle Struck OGE | Both Vehicles Moving | 2000-02-20 18:00 |  | FALSE |  |  | Dawn |  |  | Asphalt |  | Rain
9019 | Ardmore Service Center | 2019-08-30 12:30 | OGE truck was stopped at a red light wen a 3rd party driver rear ended them. OGE truck was setting still when car hit it. No injuries or damage to company property, damage to 3rd party vehicle. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Gregory Hunt | 2019-09-05 07:11 | 2019-08-30 14:49 | 2019-08-30 14:49 | 2019-09-04 14:16 | 2019-09-13 12:30 | 2019-08-30 14:37 |  |  |  | Red Light at the Intersection of Broadway and Commerce |  |  | Cody Magby | approve cm | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | [6 empty] | Ardmore Service Center | FALSE |  | FALSE | PD Operations Services |  | Gregory Hunt | Bradley Kosemund |  |  |  | Bradley Kosemund |  | Low | [93 empty] | FALSE |  | Ardmore | Public Vehicle Struck OGE | OGE Vehicle Stopped/Parked | 2009-02-01 18:00 |  | TRUE |  |  | Day Light | 0 | 0 | Asphalt |  | Rain | FALSE | FALSE
9020 | Northeast District Service Cen | 2019-08-30 22:30 | Company vehicle ( half ton pickup) contacted public vehicle on Turner Turnpike. | Level 2 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Michael Fox | 2019-09-17 13:12 | 2019-08-31 14:16 | 2019-08-31 14:16 | 2019-09-13 13:40 | 2019-09-13 22:30 | 2019-08-31 14:02 | 2019-09-17 12:22 |  | 2019-09-16 12:57 | East bound lane of Turner Turnpike 1-44 east bound mile marker 165 |  |  | Lindle Coleman | After investigation and review of police report member was found to be following all defensive driving rules. Telemetries was reviewed and confirmed driving info, speed, direction, route, braking | T&D Ops |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Michael Fox |  | East bound lane of Turner Turnpike 1-44 east bound mile marker 165; after working storm in Norman. At 9:30pm a public vehicle pulled out onto the highway without yielding after going off the road, causing another public vehicle (that OGE was following) to abruptly swerve to avoid collision, leaving OGE member to collided with public vehicle. OHP, fire rescue, and ambulance were on the scene. Member was transported to the ER by family member and was released the same day with no injuries. Vehicle was towed and suffered front end damage. Facts: -Member stated working storm in Norman at 0600 -Member completed Defensive driving class in November 17th 2017 and is not due until 2020 -Public person that caused the collision was charged with DUI -speed limit was 75mph -Not in a construction site |  |  |  | Northeast District Service Cen | FALSE |  | FALSE | Construction Services |  | Donald Melson | Michael Fox |  | Chad Inman | I approve of the corrective action. | Chad Inman |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Public vehicle that was driving under the influence caused another public vehicle and our company vehicle to collide. | 02. Failure to Warn | 1. Struck Against (Running or Bumping Into) | [74 empty] | FALSE |  | Chandler | OGE Vehicle Struck Other Vehicle | Public Driver Failed To Yield | 2003-03-23 18:00 |  | FALSE |  |  | Night |  |  | Asphalt |  | Clear
9021 | Metro Service Center | 2019-08-26 17:00 | Juan Olivores and his crew were installing services to the apt. complex where there were parallel runs of 350 secondary running to a gang meter base. When terminating new employee Igius Castillo paired the white cables with the electricians neutral that was marked with white tape. When the equipment was heated up 3 padmount transformers were smoking due to the hot legs being hooked up to the neutral. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Delivery | Garrett Bernethy | 2019-09-16 08:42 | 2019-09-03 08:20 | 2019-09-03 08:19 | 2019-09-03 09:13 | 2019-09-09 17:00 | 2019-08-26 17:00 | 2019-09-12 14:33 |  |  | Apartment Complex |  |  | Marcus Huddleston | No additional comments. MLH 9/16/19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Garrett Bernethy |  | Juan Olivores and his crew were installing services to the apt. complex where there were parallel runs of 350 secondary running to a gang meter base. The Forman phoned the cables out and marked, as all BGC employees do, with red, white, and blue (if necessary) tape noting A & B phase and neutral was a cable with a green stipe. When terminating new employee Igius Castillo paired the white cables with the electiricians cable that was marked with white tape. The crew terminated all secondary cable, but did not energize due to all services not being ready per the project manager Chad Lovelace. A OG&E service tech then came out and heated up transformers and when he did he found 3 transformers smoking. After investigating, a hot leg was hooked up to the electricians neutral cable. The neutral cable was marked with white tape. BGC Forman Stephen Bush went to the job site with Juan Olivares on 8/26/19 at 6:00 P.M. and telephoned all cables and terminated them correctly. |  |  |  | Metro Service Center | FALSE |  | FALSE | Resource Planning & Coord |  | Garrett Bernethy | Garrett Bernethy |  | John Legg | Contractor has discussed the importance of proper cable marking with employees | John Legg |  | Low |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Juan Olivores and his crew were installing services to the apt. complex where there were parallel runs of 350 secondary running to a gang meter base. The Forman phoned the cables out and marked, as all BGC employees do, with red, white, and blue (if necessary) tape noting A & B phase and neutral was a cable with a green stipe. When terminating new employee Igius Castillo paired the white cables with the electricians cable that was marked with white tape. The crew terminated all secondary cable, but did not energize due to all services not being ready per the project manager Chad Lovelace. A OG&E service tech then came out and heated up transformers and when he did he found 3 transformers smoking. After investigating, a hot leg was hooked up to the electricians neutral cable. The neutral cable was marked with white tape. BGC Forman Stephen Bush went to the job site with Juan Olivares on 8/26/19 at 6:00 P.M. and telephoned all cables and terminated them correctly. | 09. Improper Placement | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Property Damage |  | Garrett Bernethy | 3 padmount transformers burned up due to secondaries crossed with neutral cable |  |  |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Garrett Bernethy | Brad Garrett Construction | Igius Castillo |  | Fixed Equipment |  | Garrett Bernethy |  |  |  | Padmount transformers | TRUE | [66 empty] | 7381175
9022 | South District Service Center | 2019-08-26 15:00 | Parking stand fell out of bin door causing small scratch to hood of public vehicle. | Level 3 |  | FALSE | Vehicle |  | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:11 | Power Delivery | Joshua Fisk | 2019-09-25 11:34 | 2019-09-03 11:28 | 2019-09-03 11:28 | 2019-09-13 13:41 | 2019-09-09 15:00 | 2019-09-03 11:20 | 2019-09-16 14:33 | 2019-09-16 15:03 | 2019-09-16 13:12 | SW 29TH and I-44 |  |  |  | Approve | T&D Ops |  | Level 3 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Randy Jones |  | On August 26th, Michael Mitchell arrived at South Service Center to begin his shift. After loading up his truck with materials he preceded to the work site. As he was driving north bound at approximately SW 29th & I-44 a semi pulled up beside him and alerted him that he needed to pull over. At this time he pulled over to inspect what had happened. When he came to a stop he noticed that his bin door was open. A public driver also pulled over behind him to ask if he had lost anything out of his bin. Mike replied that he had lost a parking stand. The public person then stated that it had hit the front of their car causing a small scratch to the hood and a small dent to the fender. At this point they attempted to find the parking stand that had fallen out but were not able to locate it. When Mike was asked about the bin door falling open he did not remember if it was left open or not and had not completed a 360 prior to his trip. | Nathan Gooch | Randy Jones |  | South District Service Center | FALSE |  | FALSE | Construction Services |  | Michael Mitchell | Joshua Fisk |  | Steve Watkins | Approved. | Steve Watkins | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Member failed to identify open bin door before beginning his trip. | 16. Failure to Follow Procedure, Policy, Practice | 2. Struck By (Hit By Moving Object) | approved. | Approved 9/16/19 | [72 empty] | TRUE |  | Oklahoma City | Other | Loss of Cargo/Material | 1999-11-14 18:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
9022 | South District Service Center | 2019-08-26 15:00 | Parking stand fell out of bin door causing small scratch to hood of public vehicle. | Level 3 |  | FALSE | Vehicle |  | Lindle Coleman | Based on discussion with ops management. | 2019-09-04 15:11 | Power Delivery | Joshua Fisk | 2019-09-25 11:34 | 2019-09-03 11:28 | 2019-09-03 11:28 | 2019-09-13 13:41 | 2019-09-09 15:00 | 2019-09-03 11:20 | 2019-09-16 14:33 | 2019-09-16 15:03 | 2019-09-16 13:12 | SW 29TH and I-44 |  |  |  | Approve | T&D Ops |  | Level 3 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Randy Jones |  | On August 26th, Michael Mitchell arrived at South Service Center to begin his shift. After loading up his truck with materials he preceded to the work site. As he was driving north bound at approximately SW 29th & I-44 a semi pulled up beside him and alerted him that he needed to pull over. At this time he pulled over to inspect what had happened. When he came to a stop he noticed that his bin door was open. A public driver also pulled over behind him to ask if he had lost anything out of his bin. Mike replied that he had lost a parking stand. The public person then stated that it had hit the front of their car causing a small scratch to the hood and a small dent to the fender. At this point they attempted to find the parking stand that had fallen out but were not able to locate it. When Mike was asked about the bin door falling open he did not remember if it was left open or not and had not completed a 360 prior to his trip. | Luke Kennedy | Randy Jones |  | South District Service Center | FALSE |  | FALSE | Construction Services |  | Michael Mitchell | Joshua Fisk |  | Steve Watkins | Approved. | Steve Watkins | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Member failed to identify open bin door before beginning his trip. | 16. Failure to Follow Procedure, Policy, Practice | 2. Struck By (Hit By Moving Object) | approved. | Approved 9/16/19 | [72 empty] | TRUE |  | Oklahoma City | Other | Loss of Cargo/Material | 1999-11-14 18:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
9023 | Sooner Power Plant | 2019-09-03 14:30 | Member was driving man lift out of the gate of the coal yard. Due to oncoming traffic member swung the lift basket into the gate card reader and bent it over approximately 6". No injuries. $0 property damage | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Trent Novotny | 2019-10-03 10:00 | 2019-09-03 16:44 | 2019-09-03 16:43 | 2019-09-17 14:20 | 2019-09-17 14:30 | 2019-09-03 16:25 | 2019-09-23 11:32 |  | 2019-09-20 08:47 | Sooner Power Plant Coal Yard Entry Gate |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Michael Dowell |  | Member was driving man lift back to plant after completing job at Fuel Supply Crusher Switchgear. Member was moving man lift from right side of road to left side so that he could swipe his badge on the card reader. At this time there was a truck approaching from the other side of the gate. Member had tires on man lift angled in order to steer man lift to the side of the road. Member was trying to move the man lift as far left as possible and contacted the card reader with the basket of the man lift. The card reader moved approximately 6 inches. The man lift received no damage. The man lift was a rental unit do to the plant's man lift being out of service for repair. The man lift was inspected before use. A SWP was utilized for the job but Heavy Equipment use was not marked as a hazard to be mitigated. The member stated that next time he would just wait for the truck to card in and clear the road before proceeding to the card reader. The card reader was mounted in such a way that even the lightest of contact would cause it to move. The holes in the base of the card reader were drill slightly smaller than the nuts that held it in place. All of the anchors on the card reader base were stripped. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Maintenance |  | Michael Gibbs | Trent Novotny |  | Frank Brixey | Approved. Brixey 9/23/2019 | Frank Brixey |  | Medium | [13 empty] | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Member moved man lift to side of road in order for approaching vehicle to pass. | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) |  | Added Inspection. Approved by Brady Sowell | [66 empty] | Card reader struck by man lift basket | 0 | Michael Gibbs | Industrial/Heavy Equipment |  | Rental | [18 empty] | 9589666
9024 | Shawnee Service Center | 2019-09-03 08:30 | Shawnee Construction crew was in the process of unloading 50kva pad mount when threaded flange came loose causing transformer to fall approximately 3-4 ft. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Delivery | Mark Martin | 2019-09-23 13:19 | 2019-09-05 08:16 | 2019-09-05 08:16 | 2019-09-17 09:04 | 2019-09-17 07:30 | 2019-09-05 08:06 | 2019-09-23 07:50 |  | 2019-09-20 18:57 | 409 N Kickapoo, Shawnee OK |  |  | Lindle Coleman | approve | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Mark Martin |  | On September 3rd, at 7:30 AM, Shawnee Construction Crew received a job to replace a 25kva pad mount transformer with a 50kva. When the crew arrived on the job site they had their tailboard and covered staying out from underneath the suspended load. They used 2 5/8ths bolts on each side of the transformer as anchor points on the pad mount transformer. As they began to lift the transformer the bolt slipped out causing the transformer to fall approximately 3 to 4 feet to the ground. At this point they contacted their Field Supervisor in order to fill out a Close Call report. The foreman also stated that they didn't have the threaded flanges used to lift the transformer. |  |  |  | Shawnee Service Center | FALSE |  | TRUE | Construction Services |  |  | Mark Martin |  | Terry Garrett | I approve! We need to make sure we address all of T&D when a suitable attachment is found...TG | Terry Garrett |  | Medium | [12 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | Member used a bolt as opposed to a rigging flange designed for lifting that type of equipment | 15. Using Equipment Improperly | 3. Fall from Elevation to Lower Level |  | The corrective actions will ensure that we have and use the proper rigging methods when performing this kind of lift.
9025 | Metro Service Center | 2019-08-29 18:00 | Contractor experienced brief shock from contact with secondary voltage resulting in a minor burn to the left foot. This occurred during the ICS Storm event that began on August 27th. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Delivery | Terry Hackett | 2019-09-09 08:53 | 2019-09-05 10:52 | 2019-09-05 10:52 | 2019-09-05 10:59 | 2019-09-12 18:00 | 2019-09-05 10:33 | 2019-09-09 08:30 |  | 2019-09-05 11:00 | 26 Northwest 66th Street OKC |  |  | Lindle Coleman | agreeded | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Terry Hackett |  | See attached incident report |  |  |  | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Michael Douglas | Lindle Coleman |  | Michael Douglas | I have reviewed the attached documentation and believe that this sub-contractor should not be allowed to work on OG&E property until they can provide documentation on their lineman training process. | Michael Douglas |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Contractor made contact with secondary voltage | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Reviewed/Approved |  |  |  | Injury / Illness |  | Terry Hackett |  | Minor electrical burn to left foot | FALSE |  |  | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Michael Douglas | M&M Electrical Contractor Inc | Jacob Sligar | Burn: Electrical |  | Foot | Michael Douglas | Left | FALSE
9026 | Metro Service Center | 2019-09-04 21:00 | The lead vehicle in a convoy driving to a Mutual Assistance trip to North Carolina had to make an abrupt stop to avoid striking 3 vehicles in the road that had been involved in a wreck. When the lead vehicle made the abrupt stop, it caused a series of close calls between the first two OGE vehicles following the lead. All vehicles were able to stop and avoid making contact. | Level 3 |  | TRUE | Vehicle | Andrea Dennis | Lindle Coleman | due to focus on storm work, logistics, safety, crew assignments we have collectively decided to assign the lead to the safety professional. however all incident investigation team members will contribute to analysis | 2019-09-09 11:14 | Power Delivery | Brent Perdue | 2019-10-03 16:37 | 2019-09-07 08:05 | 2019-09-07 08:05 | 2019-09-18 17:44 | 2019-09-18 21:00 | 2019-09-07 07:35 | 2019-10-01 14:53 | 2019-10-03 15:42 | 2019-09-18 17:47 | on an interstate in Raleigh, NC. |  |  | Andrea Dennis | I approve. | T&D Ops |  | Level 3 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Brent Perdue |  | The lead vehicle in a convoy driving to a Mutual Assistance trip to North Carolina had to make an abrupt stop to avoid striking 3 vehicles in the road that had been involved in a wreck. When the lead vehicle made the abrupt stop, it caused a series of close calls between the first two OGE vehicles following the lead. All vehicles were able to stop and avoid making contact | Kenneth McKinzie | Brent Perdue |  | Metro Service Center | FALSE |  | TRUE | Construction Services |  | Jeffrey Gleim | Brent Perdue |  | Kenneth McKinzie | Approved | Kenneth McKinzie | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | 3 cars involved in a wreck were in the roadway with no warning lights. | 02. Failure to Warn | 1. Struck Against (Running or Bumping Into) | approved | This near miss showed that we are staying alert while driving on convoys. it also helps us see that there are opportunities for continuous improvement. The corrective action to discuss best practices and items for improvement shows commitment to prevent near misses like this.
9027 | Horseshoe Lake Power Plant | 2019-09-09 07:30 | OGE member and contractor were riding 6 Boiler elevator to access a bad storm drain header on the roof. Just above Turbine room level they heard a series of loud bangs and initiated the E-Stop on the elevator. The OGE member notified the Control room and proceeded to remove himself and contractor from the elevator. | Level 1 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Peter Nowakowski | 2019-10-11 07:37 | 2019-09-09 09:47 | 2019-09-09 09:47 | 2019-09-23 20:58 | 2019-09-23 06:30 | 2019-09-09 09:23 | 2019-09-24 10:43 |  |  | Horseshoe Lake PP Unit 6 Boiler Elevator |  |  | Guillermo Sarmiento | It was covered on the call. No further actions items where drafted. I approve investigation and corrective action items. | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Guillermo Sarmiento |  | On Monday, September 9th, an OGE member (Steve Smith) and United Mechanical employee were traveling in the elevator to scope out a job. The task consisted of using a ladder to access the roof area to access repairs that needed to be made. The ladder was being transported inside the elevator so that it did not have to be carried up the stairs. At about 0730 the Control Room (CR) was contacted via cell phone from Steve Smith (OGE Facilities) that he and United Mechanical employee were stuck in #6 Boiler elevator. FPO obtained key to elevator door and proceeded to the Upper Burner Row where Steve had indicated they were stuck. Upon arrival FPO found Steve and Matt had been able to get outer door open on the elevator and exit. Steve explained to the FPO while ascending to the Drum level of Unit 6 they encountered loud noise from the roof box area of the elevator car. Upon the hearing the loud noise and the elevator shuffling, Steve activated the E-Stop on the elevator and contacted the Horseshoe Lake Control Room. The elevator had stopped approximately two-feet above the Upper Burner row landing. After verifying from Steve that E-stop was still active, the FPO entered the elevator car to search for damage and possible cause of the loud noise. It was found that the extension box had come in contact with part of the elevator system and received extensive damage. The box was shortened and the side walls had been blown out causing the attachment screws to tear loose. Steve and Matt were transporting an extension ladder in the box at the time of the incident, however it was short enough not to have been impacted. After the initial investigation FPO was able to remove ladder from car, pull sidewall portions of box in, reset E-Stop, and send the elevator back to the basement for further investigation. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Other |  | Stephen Smith | Peter Nowakowski |  | Michael Kennedy | Approved | Michael Kennedy |  | Low | [9 empty] | 10.08 Inadequate evaluation of changes |  |  |  |  | 15.03 Inadequate inspection and/or monitoring |  | Unidentified elevator dog house damage prior to use. | 23. Defective Tools, Equipment or Materials | 2. Struck By (Hit By Moving Object) | [92 empty] | 2365029
9028 | Metro Service Center | 2019-09-04 13:30 | While removing the cover from an electromechanical relay a bent mechanical target reset allowed for an inadvertent trip. | Level 1 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Joseph Manseau | 2019-10-02 14:10 | 2019-09-09 10:36 |  | 2019-09-30 14:53 | 2019-10-16 13:30 | 2019-09-04 14:00 | 2019-10-01 14:13 |  |  | Draper Lake substation |  |  | Cody Magby | reviewed and approve cm | T&D Ops |  | Level 1 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Joseph Manseau |  | While performing relay test for a mis-operation member removed the cover off of an electromechanical relay. While removing he noticed the mechanical target reset rod was bent and catching on the target. Before he could correct the issue the rod pressed the target up making up the instantaneous trip contact. |  |  |  | Metro Service Center | FALSE |  | FALSE | System Operations |  | Adam Auten | Joseph Manseau |  | James Hutchison | I have reviewed this incident report and the corrective action as well and approve both. | James Hutchison |  | Low | [111 empty] | 7870672
9029 | Sooner Power Plant | 2019-09-10 11:30 | First Aid Only-Member scratched finger on right hand on roofing material covering walkway that was too close to walkway handrail. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Supply | Justin Buchanan | 2019-10-08 08:13 | 2019-09-10 13:18 | 2019-09-10 13:18 | 2019-09-12 15:12 | 2019-09-24 11:30 | 2019-09-10 12:00 | 2019-09-12 15:36 |  | 2019-09-12 15:18 | Sooner east dumper walkway. |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Justin Buchanan |  | Members had witnessed a railcar wheel locked up and dragging on the track which could cause damage to the track, wheel, and fire hazard. Members ascended the steep stairway on the east end of the dumper in order to get to the dumper control room and inform the member dumping the train. As members ascended the stairway the first member scratched their middle finger on the cut edge of the roof sheeting used to cover up the offboard hydraulic units. This sheeting was within 1.5 inches or less of the handrail and OSHA guidelines specify at least 2.25 inches for clearance. Member stated that the scratch sealed off without any first aid administered. Members continued to the control room to alert the dumper operator and then informed their supervisor of the incident and hazards present. Those hazards have been determined to be the close proximity of the sheeting to the handrail and the steepness of the stairway used to gain access to the dumper control room. |  |  | FALSE | Sooner Power Plant | FALSE |  | FALSE | Maintenance |  | Christopher Grimes | Justin Buchanan |  | Frank Brixey | Approved - Brixey 9/12/2019 | Frank Brixey |  | Medium | [9 empty] | 10.03 Inadequate standards, specifications and/or design criteria |  |  |  | 14.04 Inadequate monitoring of compliance |  |  | Metal sheeting on the roof of offboard hydraulics unit was too close to handrail. | 09. Improper Placement | 6. Caught On (Snagged, Hung) |  | Approved by Brady Sowell on 9/12/2019. | [24 empty] | FALSE |  |  | 2001-07-02 | 1974-10-01 |  | 2019-09-10 07:00 | 0 | 0 |  | FALSE |  | Member was holding onto the handrail while going up the stairway to go over the train and to the control room. Cut edge of the roofing material is closer than the required 2.25" and members hand got cut by the edge of the roof sheeting when hand was slid between the handrail and roof sheeting. Stairway has also been modified from original design and is very steep. |  | FALSE | Christopher Grimes |  | First Aid | Christopher Grimes |  |  |  |  | Laceration |  | FALSE |  | Plant Mechanic Senior | Finger |  | Right | FALSE | Justin Buchanan | FALSE |  | 9/10/2019 7:00:00 AM | 18 | FALSE |  |  | Cut edge of roof sheeting. | Going up the stairway to inform Fuel Supply members in the dumper control room of a railcar that had a wheel locked up and dragging on the track. | [24 empty] | 9590600/9590624
9029 | Sooner Power Plant | 2019-09-10 11:30 | First Aid Only-Member scratched finger on right hand on roofing material covering walkway that was too close to walkway handrail. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Supply | Justin Buchanan | 2019-10-08 08:13 | 2019-09-10 13:18 | 2019-09-10 13:18 | 2019-09-12 15:12 | 2019-09-24 11:30 | 2019-09-10 12:00 | 2019-09-12 15:36 |  | 2019-09-12 15:18 | Sooner east dumper walkway. |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Justin Buchanan |  | Members had witnessed a railcar wheel locked up and dragging on the track which could cause damage to the track, wheel, and fire hazard. Members ascended the steep stairway on the east end of the dumper in order to get to the dumper control room and inform the member dumping the train. As members ascended the stairway the first member scratched their middle finger on the cut edge of the roof sheeting used to cover up the offboard hydraulic units. This sheeting was within 1.5 inches or less of the handrail and OSHA guidelines specify at least 2.25 inches for clearance. Member stated that the scratch sealed off without any first aid administered. Members continued to the control room to alert the dumper operator and then informed their supervisor of the incident and hazards present. Those hazards have been determined to be the close proximity of the sheeting to the handrail and the steepness of the stairway used to gain access to the dumper control room. |  |  | FALSE | Sooner Power Plant | FALSE |  | FALSE | Maintenance |  | Christopher Grimes | Justin Buchanan |  | Frank Brixey | Approved - Brixey 9/12/2019 | Frank Brixey |  | Medium | [9 empty] | 10.04 Inadequate monitoring of construction |  |  |  | 14.04 Inadequate monitoring of compliance |  |  | Metal sheeting on the roof of offboard hydraulics unit was too close to handrail. | 09. Improper Placement | 6. Caught On (Snagged, Hung) |  | Approved by Brady Sowell on 9/12/2019. | [24 empty] | FALSE |  |  | 2001-07-02 | 1974-10-01 |  | 2019-09-10 07:00 | 0 | 0 |  | FALSE |  | Member was holding onto the handrail while going up the stairway to go over the train and to the control room. Cut edge of the roofing material is closer than the required 2.25" and members hand got cut by the edge of the roof sheeting when hand was slid between the handrail and roof sheeting. Stairway has also been modified from original design and is very steep. |  | FALSE | Christopher Grimes |  | First Aid | Christopher Grimes |  |  |  |  | Laceration |  | FALSE |  | Plant Mechanic Senior | Finger |  | Right | FALSE | Justin Buchanan | FALSE |  | 9/10/2019 7:00:00 AM | 18 | FALSE |  |  | Cut edge of roof sheeting. | Going up the stairway to inform Fuel Supply members in the dumper control room of a railcar that had a wheel locked up and dragging on the track. | [24 empty] | 9590600/9590624
9029 | Sooner Power Plant | 2019-09-10 11:30 | First Aid Only-Member scratched finger on right hand on roofing material covering walkway that was too close to walkway handrail. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Supply | Justin Buchanan | 2019-10-08 08:13 | 2019-09-10 13:18 | 2019-09-10 13:18 | 2019-09-12 15:12 | 2019-09-24 11:30 | 2019-09-10 12:00 | 2019-09-12 15:36 |  | 2019-09-12 15:18 | Sooner east dumper walkway. |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Justin Buchanan |  | Members had witnessed a railcar wheel locked up and dragging on the track which could cause damage to the track, wheel, and fire hazard. Members ascended the steep stairway on the east end of the dumper in order to get to the dumper control room and inform the member dumping the train. As members ascended the stairway the first member scratched their middle finger on the cut edge of the roof sheeting used to cover up the offboard hydraulic units. This sheeting was within 1.5 inches or less of the handrail and OSHA guidelines specify at least 2.25 inches for clearance. Member stated that the scratch sealed off without any first aid administered. Members continued to the control room to alert the dumper operator and then informed their supervisor of the incident and hazards present. Those hazards have been determined to be the close proximity of the sheeting to the handrail and the steepness of the stairway used to gain access to the dumper control room. |  |  | FALSE | Sooner Power Plant | FALSE |  | FALSE | Maintenance |  | Christopher Grimes | Justin Buchanan |  | Frank Brixey | Approved - Brixey 9/12/2019 | Frank Brixey |  | Medium | [9 empty] | 10.02 Inadequate consideration of human factors/ergonomics |  |  |  | 14.04 Inadequate monitoring of compliance |  |  | Metal sheeting on the roof of offboard hydraulics unit was too close to handrail. | 09. Improper Placement | 6. Caught On (Snagged, Hung) |  | Approved by Brady Sowell on 9/12/2019. | [24 empty] | FALSE |  |  | 2001-07-02 | 1974-10-01 |  | 2019-09-10 07:00 | 0 | 0 |  | FALSE |  | Member was holding onto the handrail while going up the stairway to go over the train and to the control room. Cut edge of the roofing material is closer than the required 2.25" and members hand got cut by the edge of the roof sheeting when hand was slid between the handrail and roof sheeting. Stairway has also been modified from original design and is very steep. |  | FALSE | Christopher Grimes |  | First Aid | Christopher Grimes |  |  |  |  | Laceration |  | FALSE |  | Plant Mechanic Senior | Finger |  | Right | FALSE | Justin Buchanan | FALSE |  | 9/10/2019 7:00:00 AM | 18 | FALSE |  |  | Cut edge of roof sheeting. | Going up the stairway to inform Fuel Supply members in the dumper control room of a railcar that had a wheel locked up and dragging on the track. | [24 empty] | 9590600/9590624
9030 | Seminole PP; EGX Gath/Trans | 2019-09-10 15:30 | Member was moving a trailer left by ICT that was in the way for positioning of a crane to be used to install a platform. Member was using forklift to move the trailer because of a lock in the hitch and contractor was not on location. The fork of the fork lift made contact with the trailer causing minor damage to trailer. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Matthew Cox | 2019-10-03 09:56 | 2019-09-10 18:41 | 2019-09-10 18:41 | 2019-09-24 13:27 | 2019-09-24 15:30 | 2019-09-10 17:00 | 2019-09-30 06:53 |  | 2019-09-26 10:24 | Seminole Power Plant south side of 2A FD Fan and machine shop parking lot. |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Matthew Cox |  | This incident happened while members were in the process of installing platforms to access the forced draft fans outlet damper drives. The members needed to move two conex boxes belonging to Zachry and an enclosed trailer belonging to Innovative Combustion Technologies. Neither group was on site. They needed to be moved because they were sitting in the only place the crane could be positioned to reach where the platform was going. Members went to hook up the trailer to a truck, but discovered the hitch was locked. They then decided they could use a forklift to move the trailer by wrapping the safety chains on the trailer around one fork and picking up the tongue of the trailer and pulling it. When they went to stop, the trailer came forward and the tip of the fork punctured the trailer wall. The members then called me to report the incident. While talking to the members I explained we do not rig from the forks like that and we can only use approved forklift attachments to rig from the forks. Also we talked about how they used the safety chains to lift the trailer and that we are to only use lift rated chokers, slings and chains to lift with. We then contacted ICT to inform them of what had happened and they asked us to look inside and make sure nothing was damaged inside. No damage was found inside and we then put silicon over the puncture to prevent any water from coming inside. A discussion was held that the appropriate first action would have been for the members to contact their supervisor to inform him that the trailer was located in the area where the crane needed to be placed. The supervisor would have contacted ICT to request the trailer be removed and if they were unable to have the trailer removed in a timely fashion, for us to develop a plan to move it safely, such as, cutting the lock off the trailer hitch, with ICT's knowledge and approval. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | Special Services |  | Joshua Eaves | Matthew Cox |  | Kelly Casey | Matt has completed assigned task. | Kelly Casey |  | Medium |  |  |  | 4.10 Frustration | 5.06 Lack of situational awareness |  | 7.06 Improper attempt to save time or effort | [8 empty] | 16.10 Inadequate communication of safety and health data, regulations or guidelines | A trailer was moved by rigging the trailer safety chains to a fork on a forklift. The trailer shifted during re-positioning and the fork pierced the trailer. | 15. Using Equipment Improperly | 1. Struck Against (Running or Bumping Into) |  | Reviewed. | [66 empty] | Small puncture to side of trailer. | 1000 | Joshua Eaves | 3rd Party Property/Equipment | [20 empty] | 9579258
9030 | Seminole PP; EGX Gath/Trans | 2019-09-10 15:30 | Member was moving a trailer left by ICT that was in the way for positioning of a crane to be used to install a platform. Member was using forklift to move the trailer because of a lock in the hitch and contractor was not on location. The fork of the fork lift made contact with the trailer causing minor damage to trailer. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Matthew Cox | 2019-10-03 09:56 | 2019-09-10 18:41 | 2019-09-10 18:41 | 2019-09-24 13:27 | 2019-09-24 15:30 | 2019-09-10 17:00 | 2019-09-30 06:53 |  | 2019-09-26 10:24 | Seminole Power Plant south side of 2A FD Fan and machine shop parking lot. |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Matthew Cox |  | This incident happened while members were in the process of installing platforms to access the forced draft fans outlet damper drives. The members needed to move two conex boxes belonging to Zachry and an enclosed trailer belonging to Innovative Combustion Technologies. Neither group was on site. They needed to be moved because they were sitting in the only place the crane could be positioned to reach where the platform was going. Members went to hook up the trailer to a truck, but discovered the hitch was locked. They then decided they could use a forklift to move the trailer by wrapping the safety chains on the trailer around one fork and picking up the tongue of the trailer and pulling it. When they went to stop, the trailer came forward and the tip of the fork punctured the trailer wall. The members then called me to report the incident. While talking to the members I explained we do not rig from the forks like that and we can only use approved forklift attachments to rig from the forks. Also we talked about how they used the safety chains to lift the trailer and that we are to only use lift rated chokers, slings and chains to lift with. We then contacted ICT to inform them of what had happened and they asked us to look inside and make sure nothing was damaged inside. No damage was found inside and we then put silicon over the puncture to prevent any water from coming inside. A discussion was held that the appropriate first action would have been for the members to contact their supervisor to inform him that the trailer was located in the area where the crane needed to be placed. The supervisor would have contacted ICT to request the trailer be removed and if they were unable to have the trailer removed in a timely fashion, for us to develop a plan to move it safely, such as, cutting the lock off the trailer hitch, with ICT's knowledge and approval. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | Special Services |  | Joshua Eaves | Matthew Cox |  | Kelly Casey | Matt has completed assigned task. | Kelly Casey |  | Medium |  |  |  | 4.10 Frustration | 5.04 Inadequate update training |  | 7.06 Improper attempt to save time or effort | [8 empty] | 16.10 Inadequate communication of safety and health data, regulations or guidelines | A trailer was moved by rigging the trailer safety chains to a fork on a forklift. The trailer shifted during re-positioning and the fork pierced the trailer. | 15. Using Equipment Improperly | 1. Struck Against (Running or Bumping Into) |  | Reviewed. | [66 empty] | Small puncture to side of trailer. | 1000 | Joshua Eaves | 3rd Party Property/Equipment | [20 empty] | 9579258
9031 | Central District Office | 2019-09-06 15:30 | Member was stepping off the hydra lift side step and turned wrong upon landing. The step is approximately 1.5 feet off the ground, member did not jump off, just pivoted in awkward manner. He had some minor discomfort in his right knee but did not feel a need to see doctor. This is first aid only at this time. | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | William Fisher | 2019-09-19 13:38 | 2019-09-11 07:27 | 2019-09-11 07:27 | 2019-09-17 07:28 | 2019-09-20 15:30 | 2019-09-06 16:30 |  |  |  | Tulsa substation |  |  | Cody Magby | Gerald would like to investigate further cm This is a for record only at this time. Member feels fine with no pain currently. Will continue to follow up with member to monitor if pain returns. cm | T&D Ops |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | [5 empty] | FALSE | Central District Office | FALSE |  | FALSE | PD Operations Services |  | Bartley Keeler | William Fisher |  |  |  | James Hutchison |  | Low | [45 empty] | FALSE |  |  | 2005-02-28 | 1970-10-26 |  | 2019-09-06 06:00 | 0 | 0 |  | FALSE |  | Member stepped off of the hydra lift wrong and felt some discomfort in his right knee. He worked through the remainder of the day then applied some ice when he got home. |  | FALSE | Bartley Keeler |  | First Aid | Bartley Keeler |  |  |  |  | Sprain/Strain |  | FALSE |  | Substation Maint Tech | Knee |  | Right | FALSE | William Fisher | FALSE |  | 9/6/2019 6:00:00 AM | 5 | FALSE |  |  | Rock substation site | Replacing bushing on a failed power transformer
9032 | Ft Smith Service Center | 2019-09-10 14:15 | Civilian vehicle crossed center line and struck contractor vehicle head on. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Elizabeth Mason-Reynolds | 2019-10-09 14:53 | 2019-09-11 09:57 | 2019-09-11 09:57 | 2019-09-26 16:38 | 2019-09-24 14:15 | 2019-09-11 09:48 | 2019-10-08 13:25 |  | 2019-10-07 11:54 | Alma, AR |  |  | William Young | Reviewed and approved. WCY 10-9-18 | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Elizabeth Mason-Reynolds |  | Per Arkansas MV Crash Report 170919381---Operator of vehicle V1- DRG-OGE Contractor, was driving south on US Highway 71. Operator of V2- Civilian, was driving north on US Highway 71. For an unknown reason V2 crossed the center line. V1 noticed this and attempted to get as far right to avoid the collision. V1 was able to get half of his vehicle off the roadway before he was struck head on by V2. Operator of V2 did not know what happened and was not impaired at the time of the crash. |  |  |  | Ft Smith Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Elizabeth Mason-Reynolds | Elizabeth Mason-Reynolds |  | Danny Coffey | Contractor responded in a timely manner in regards to furnishing pertinent documents associated with this incident. This incident is ready to be sent to Safety Department for Final Approval. | Danny Coffey |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Civilian vehicle crossed center line and struck contractor vehicle head on. | 19. Failure to React, Correct | 2. Struck By (Hit By Moving Object) |  | Beth - please have contractor send roster to confirm the importance of defensive driving was reviewed with crews and attach to "Document Attachments". Thank you, J. Looney, 9/26/19 |  |  |  | Vehicle |  | Elizabeth Mason-Reynolds | [5 empty] | 2. Struck By (Hit By Moving Object) | Elizabeth Mason-Reynolds | DRG | Christopher Clark |  |  |  | Elizabeth Mason-Reynolds |  |  |  |  | FALSE
9033 | North Service Center | 2019-09-10 16:00 | F07/F12-506 was red tagged by hydraulic inspector for a broken selector valve. Red out of service tag was attached to steering wheel by inspector. OGE mechanic had assessed repair needed and had parts on order. While waiting for parts , with red out of service tag attached, the operator took unit out of the yard to go to work. | Level 2 |  | TRUE | Member Injury |  |  |  |  | OG&E Corp Services | Jamie Clark | 2019-10-08 13:56 | 2019-09-11 13:29 | 2019-09-11 13:29 | 2019-09-12 16:55 | 2019-09-24 16:00 | 2019-09-11 12:58 | 2019-09-18 12:37 |  | 2019-09-16 10:57 | North service center Parked in the lot between the garage and the main building |  |  | William Young | Reviewed and approved. WCY | UTS |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Jamie Clark |  | Unit F12-506 was at north garage for the annual dielectric inspection preformed by ETI. Upon the inspection the lower controls emergency override valve was found to be busted. ETI applied a out of service tag to the steering wheel at his time( 9/4/19) . The unit was looked over by a OGE mechanic and parts were order and parked between the main building and garage awaiting parts with tag still in place. 9/9/19 Work was performed but not finished and re parked in the same spot . 9/10/19 mechanic went looking for unit and it was not there. Mechanic called adviser to make contact with costumer to have unit returned to north garage. Unit was returned later that evening. Repairs were finished on 9/11/19 and returned to service. Customer has admitted that the out of service tag was on the steering wheel when he removed unit from the north garage. |  |  |  | North Service Center | FALSE |  | TRUE | UTS - Asset & LC Mgmt |  | Jamie Clark | Jamie Clark |  | Nathan Gooch | I agree with the investigation and corrective action. | Nathan Gooch |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Member disregarded out of service tag attached to steering wheel | 01. Operating Equipment Without Authority | 9. Abnormal Operation |  | Approved, Cody Vinyard | [90 empty] | 4127608
9034 | Ada Service Center | 2019-08-30 12:30 | Member was pulling mini excavator with flat bed truck. A blow out occurred on the passenger side trailer tire. Member did not notice a blowout had occurred until a public driver flagged him down. This resulted in substantial damage to the trailer. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Delivery | Lyle Just | 2019-09-17 12:30 | 2019-09-12 11:30 | 2019-09-12 11:30 | 2019-09-12 15:17 | 2019-09-13 17:30 | 2019-09-12 11:22 | 2019-09-17 12:15 |  | 2019-09-16 13:15 | I-35 S. bound between 12th street and HWY 70 Exit Ardmore OK |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Lyle Just |  | Member was driving down I-35 south in flat bed #F09-1018 pulling a mini excavator on a trailer. A blowout occurred at some point on the passenger side tire of the trailer. Member pulled the trailer for several miles and did not become aware of the blowout until a public driver got in front of him, braked, and waved him off of the road onto the shoulder. Member got off of the road onto the shoulder and discovered what had occurred. He then called his foreman, who in turned called fleet to assist. Members set up the orange triangles to make oncoming traffic aware. When fleet arrived the Ardmore Field Supervisor for the distribution crews called the mechanic to inform the driver they needed him to go to a job in Hardin City and that someone was on their way to get him. Facts Ascertained: Truck #F09-1018 Trailer # F20-781 Heavy rain and wind at the time of the incident Foreman helped member back up to trailer Member stated he then performed a 360 and headed to Ardmore Driver did not complete a DVIR Driver did not adjust mirrors Driver stated he was focused on the road ahead and did not check on the trailer while pulling it due to the heavy rain, wind, and traffic Driver did not check road way for debris Mechanic stated they picked up debris 6 miles away from the location where the truck was stopped Driver stated his speed was between 60-65 mph |  |  |  | Ada Service Center | FALSE |  | FALSE | Construction Services |  |  | Todd Janda |  | Chad Inman | I approve of the corrective actions. | Chad Inman |  | Medium |  |  |  | 4.03 Extreme judgment/decision demands | 5.06 Lack of situational awareness |  | 7.11 Improper supervisory example | [9 empty] | Member did not complete pre trip DVIR, check/adjust mirrors, or visually check trailer while driving, incident was not reported/investigated appropriately 4.03: Heavy Rain, wind, and traffic 5.06: Member pulled trailer approximately 6 miles and had to be stopped by public driver 7.07 Heavy Rain 7.11 Incident report | 16. Failure to Follow Procedure, Policy, Practice | 2. Struck By (Hit By Moving Object) |  | Reviewed/approved any administrative action will be determined by supervision | [66 empty] | Tire and wheel was damaged beyond use or repair, light assembly fell off, fender well fell off, metal was grounded down from being pulled down the road | 5000 | Derek Epperly | Industrial/Heavy Equipment |  | F20-781
9034 | Ada Service Center | 2019-08-30 12:30 | Member was pulling mini excavator with flat bed truck. A blow out occurred on the passenger side trailer tire. Member did not notice a blowout had occurred until a public driver flagged him down. This resulted in substantial damage to the trailer. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Delivery | Lyle Just | 2019-09-17 12:30 | 2019-09-12 11:30 | 2019-09-12 11:30 | 2019-09-12 15:17 | 2019-09-13 17:30 | 2019-09-12 11:22 | 2019-09-17 12:15 |  | 2019-09-16 13:15 | I-35 S. bound between 12th street and HWY 70 Exit Ardmore OK |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Lyle Just |  | Member was driving down I-35 south in flat bed #F09-1018 pulling a mini excavator on a trailer. A blowout occurred at some point on the passenger side tire of the trailer. Member pulled the trailer for several miles and did not become aware of the blowout until a public driver got in front of him, braked, and waved him off of the road onto the shoulder. Member got off of the road onto the shoulder and discovered what had occurred. He then called his foreman, who in turned called fleet to assist. Members set up the orange triangles to make oncoming traffic aware. When fleet arrived the Ardmore Field Supervisor for the distribution crews called the mechanic to inform the driver they needed him to go to a job in Hardin City and that someone was on their way to get him. Facts Ascertained: Truck #F09-1018 Trailer # F20-781 Heavy rain and wind at the time of the incident Foreman helped member back up to trailer Member stated he then performed a 360 and headed to Ardmore Driver did not complete a DVIR Driver did not adjust mirrors Driver stated he was focused on the road ahead and did not check on the trailer while pulling it due to the heavy rain, wind, and traffic Driver did not check road way for debris Mechanic stated they picked up debris 6 miles away from the location where the truck was stopped Driver stated his speed was between 60-65 mph |  |  |  | Ada Service Center | FALSE |  | FALSE | Construction Services |  |  | Todd Janda |  | Chad Inman | I approve of the corrective actions. | Chad Inman |  | Medium |  |  |  | 4.03 Extreme judgment/decision demands | 5.06 Lack of situational awareness |  | 7.07 Improper attempt to avoid discomfort | [9 empty] | Member did not complete pre trip DVIR, check/adjust mirrors, or visually check trailer while driving, incident was not reported/investigated appropriately 4.03: Heavy Rain, wind, and traffic 5.06: Member pulled trailer approximately 6 miles and had to be stopped by public driver 7.07 Heavy Rain 7.11 Incident report | 16. Failure to Follow Procedure, Policy, Practice | 2. Struck By (Hit By Moving Object) |  | Reviewed/approved any administrative action will be determined by supervision | [66 empty] | Tire and wheel was damaged beyond use or repair, light assembly fell off, fender well fell off, metal was grounded down from being pulled down the road | 5000 | Derek Epperly | Industrial/Heavy Equipment |  | F20-781
9035 | Metro Service Center | 2019-09-11 16:00 | While stringing shield wire from new reel, the wire broke. There was a kink in the wire about halfway through the reel. This is believed to be a quality issue from the manufacturer. No injury, damage, or outage. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Delivery | Jimmy Combs | 2019-10-03 15:44 | 2019-09-12 15:29 | 2019-09-12 15:29 | 2019-10-01 06:50 | 2019-09-25 16:00 | 2019-09-12 15:24 | 2019-10-03 09:05 |  | 2019-10-01 07:06 | Corner of NE 10th and Luther (Harrah Oklahoma) |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Jimmy Combs |  | While stringing shield wire from new reel, the wire broke. There was a kink in the wire about halfway through the reel. This is believed to be a quality issue from the manufacturer. No injury, damage, or outage. Facts Ascertained: Reel was manufactured by National Strand in Houston Tx Shield wire was not reeled up evenly which caused slack in the wire and allowed it to kink Members on the trailer were standing out of the line of fire The control for the brake on the front wheel is directly in the line of fire Approximately 2000' had been spoiled off of the reel with no issues |  |  |  | Metro Service Center | FALSE |  | TRUE | Construction Services |  | Hershel Goodson | Jimmy Combs |  | Gary Lassley | Review the incident with all of the Transmission Crews. Make sure to emphasize to the reel operator the importance of observing the wire as it is being reeled off the spool.....looking for any kinks or imperfections in the wire. I would also commend the crew for making sure that they were out of the line of fire during this operation. | Gary Lassley |  | Medium | [9 empty] | 10.01 Inadequate assessment of loss exposures | [6 empty] | Brake controls for front wheel are located in the direct line of fire | 09. Improper Placement | 2. Struck By (Hit By Moving Object) |  | Reviewed/Approved. A QA CAR has been put in with the manufacture national strand.
9035 | Metro Service Center | 2019-09-11 16:00 | While stringing shield wire from new reel, the wire broke. There was a kink in the wire about halfway through the reel. This is believed to be a quality issue from the manufacturer. No injury, damage, or outage. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Delivery | Jimmy Combs | 2019-10-03 15:44 | 2019-09-12 15:29 | 2019-09-12 15:29 | 2019-10-01 06:50 | 2019-09-25 16:00 | 2019-09-12 15:24 | 2019-10-03 09:05 |  | 2019-10-01 07:06 | Corner of NE 10th and Luther (Harrah Oklahoma) |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Jimmy Combs |  | While stringing shield wire from new reel, the wire broke. There was a kink in the wire about halfway through the reel. This is believed to be a quality issue from the manufacturer. No injury, damage, or outage. Facts Ascertained: Reel was manufactured by National Strand in Houston Tx Shield wire was not reeled up evenly which caused slack in the wire and allowed it to kink Members on the trailer were standing out of the line of fire The control for the brake on the front wheel is directly in the line of fire Approximately 2000' had been spoiled off of the reel with no issues |  |  |  | Metro Service Center | FALSE |  | TRUE | Construction Services |  | Hershel Goodson | Jimmy Combs |  | Gary Lassley | Review the incident with all of the Transmission Crews. Make sure to emphasize to the reel operator the importance of observing the wire as it is being reeled off the spool.....looking for any kinks or imperfections in the wire. I would also commend the crew for making sure that they were out of the line of fire during this operation. | Gary Lassley |  | Medium | [9 empty] | 10.05 Inadequate assessment of operational readiness | [6 empty] | Wire was spoiled unevenly | 23. Defective Tools, Equipment or Materials | 2. Struck By (Hit By Moving Object) |  | Reviewed/Approved. A QA CAR has been put in with the manufacture national strand.
9036 | Shawnee Service Center | 2019-09-11 12:30 | Asplundh line clearance trimmer was performing normal cycle trimming burned down secondary. | Level 1 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Wesley Lanier | 2019-10-07 12:05 | 2019-09-12 15:42 | 2019-09-12 15:42 | 2019-09-23 17:25 | 2019-09-25 12:30 | 2019-09-11 12:30 | 2019-09-30 15:52 |  |  | Behind 819 N. Park Ave Shawnee Ok |  |  | Jerrie Looney | Per Asplundh supervisor, a stand down was held with all crews and retrained in outage protocol. Approved, J. Looney, 10/7/19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Wesley Lanier |  | Climber got pruner pole across neutral and hot leg of secondary. see attached docs for more info |  |  |  | Shawnee Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Wesley Lanier | Wesley Lanier |  | Nicole Rhodes | Reviewed. Appropriate actions taken. | Nicole Rhodes |  | Low |  |  |  |  | 5.06 Lack of situational awareness |  | 7.06 Improper attempt to save time or effort | [9 empty] | over confidence not paying enough attention | 16. Failure to Follow Procedure, Policy, Practice | 2. Struck By (Hit By Moving Object) | [5 empty] | Property Damage |  | Wesley Lanier | secondarys remainded energized after burning down and laid on communications buring up communication wires going in to houses |  |  |  |  | 2. Struck By (Hit By Moving Object) | Wesley Lanier | Asplundh Tree Expert Co. | Dalton Pierot |  | 3rd Party Property/Equipment |  | Wesley Lanier |  |  |  |  | FALSE
9036 | Shawnee Service Center | 2019-09-11 12:30 | Asplundh line clearance trimmer was performing normal cycle trimming burned down secondary. | Level 1 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Wesley Lanier | 2019-10-07 12:05 | 2019-09-12 15:42 | 2019-09-12 15:42 | 2019-09-23 17:25 | 2019-09-25 12:30 | 2019-09-11 12:30 | 2019-09-30 15:52 |  |  | Behind 819 N. Park Ave Shawnee Ok |  |  | Jerrie Looney | Per Asplundh supervisor, a stand down was held with all crews and retrained in outage protocol. Approved, J. Looney, 10/7/19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Wesley Lanier |  | Climber got pruner pole across neutral and hot leg of secondary. see attached docs for more info |  |  |  | Shawnee Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Wesley Lanier | Wesley Lanier |  | Nicole Rhodes | Reviewed. Appropriate actions taken. | Nicole Rhodes |  | Low |  |  |  |  | 5.06 Lack of situational awareness |  | 7.06 Improper attempt to save time or effort | [9 empty] | over confidence not paying enough attention | 16. Failure to Follow Procedure, Policy, Practice | 2. Struck By (Hit By Moving Object) | [5 empty] | System Outage |  | Wesley Lanier | secondarys remainded energized after burning down and laid on communications buring up communication wires going in to houses |  |  |  |  | 2. Struck By (Hit By Moving Object) | Wesley Lanier | Asplundh Tree Expert Co. | Dalton Pierot |  | 3rd Party Property/Equipment |  | Wesley Lanier |  |  |  |  | FALSE
9037 | Metro Service Center | 2019-09-13 05:00 | Member was forced into a tree limb, that was laying about 3 feet in the roadway, by an oncoming vehicle. The tree was contacted to avoid a more severe incident with a vehicle. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Jeffrey Gleim | 2019-09-13 08:39 | 2019-09-13 08:15 | 2019-09-13 08:15 | 2019-09-13 08:22 | 2019-09-27 05:00 | 2019-09-13 08:06 |  |  |  | 1/4 mile south of NE 63rd on Choctaw Rd. |  |  | Brent Perdue | According to the information provided and speaking with the supervisor and manager of the driver, I approve this report due to the "Vehicle Chargeability Guidelines" under the guideline that states: Hazardous driving conditions – All vehicle incidents where there were hazardous driving conditions and the Company member performed good defensive driving techniques in an effort to avoid/minimize the risks of these hazards shall be considered on a case-by-case basis. | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | [6 empty] | Metro Service Center | FALSE |  | FALSE | PD Operations Services |  | Sean Hunteman | Jeffrey Gleim |  |  |  | Steve Watkins |  | Low | [93 empty] | FALSE |  | Jones | Struck Fixed Object | Lost Control/Ran Off Road | 2013-06-16 19:00 |  | FALSE |  |  | Night |  |  | Asphalt |  | Rain
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  | 16.08 Incorrect instructions | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  | 16.03. Inadequate communication between different organizations | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  | 16.10 Inadequate communication of safety and health data, regulations or guidelines | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.08 Incorrect instructions | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.03. Inadequate communication between different organizations | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.10 Inadequate communication of safety and health data, regulations or guidelines | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.02.5 Inadequate communication of standards: reinforcing with signs, color codes |  | 16.08 Incorrect instructions | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.02.5 Inadequate communication of standards: reinforcing with signs, color codes |  | 16.03. Inadequate communication between different organizations | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.02.5 Inadequate communication of standards: reinforcing with signs, color codes |  | 16.10 Inadequate communication of safety and health data, regulations or guidelines | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.08 Incorrect instructions | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.03. Inadequate communication between different organizations | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.10 Inadequate communication of safety and health data, regulations or guidelines | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  | 16.08 Incorrect instructions | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  | 16.03. Inadequate communication between different organizations | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  | 16.10 Inadequate communication of safety and health data, regulations or guidelines | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.08 Incorrect instructions | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.03. Inadequate communication between different organizations | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.10 Inadequate communication of safety and health data, regulations or guidelines | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.5 Inadequate communication of standards: reinforcing with signs, color codes |  | 16.08 Incorrect instructions | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.5 Inadequate communication of standards: reinforcing with signs, color codes |  | 16.03. Inadequate communication between different organizations | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.5 Inadequate communication of standards: reinforcing with signs, color codes |  | 16.10 Inadequate communication of safety and health data, regulations or guidelines | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.08 Incorrect instructions | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.03. Inadequate communication between different organizations | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.10 Inadequate communication of safety and health data, regulations or guidelines | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  | 16.08 Incorrect instructions | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  | 16.03. Inadequate communication between different organizations | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  | 16.10 Inadequate communication of safety and health data, regulations or guidelines | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.08 Incorrect instructions | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.03. Inadequate communication between different organizations | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.10 Inadequate communication of safety and health data, regulations or guidelines | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.02.5 Inadequate communication of standards: reinforcing with signs, color codes |  | 16.08 Incorrect instructions | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.02.5 Inadequate communication of standards: reinforcing with signs, color codes |  | 16.03. Inadequate communication between different organizations | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.02.5 Inadequate communication of standards: reinforcing with signs, color codes |  | 16.10 Inadequate communication of safety and health data, regulations or guidelines | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.08 Incorrect instructions | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.03. Inadequate communication between different organizations | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.10 Inadequate communication of safety and health data, regulations or guidelines | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  | 16.08 Incorrect instructions | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  | 16.03. Inadequate communication between different organizations | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  | 16.10 Inadequate communication of safety and health data, regulations or guidelines | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.08 Incorrect instructions | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.03. Inadequate communication between different organizations | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.10 Inadequate communication of safety and health data, regulations or guidelines | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.5 Inadequate communication of standards: reinforcing with signs, color codes |  | 16.08 Incorrect instructions | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.5 Inadequate communication of standards: reinforcing with signs, color codes |  | 16.03. Inadequate communication between different organizations | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.5 Inadequate communication of standards: reinforcing with signs, color codes |  | 16.10 Inadequate communication of safety and health data, regulations or guidelines | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.08 Incorrect instructions | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.03. Inadequate communication between different organizations | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.10 Inadequate communication of safety and health data, regulations or guidelines | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.02 Inadequate orientation |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  | 16.08 Incorrect instructions | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.02 Inadequate orientation |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  | 16.03. Inadequate communication between different organizations | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.02 Inadequate orientation |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  | 16.10 Inadequate communication of safety and health data, regulations or guidelines | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.02 Inadequate orientation |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.08 Incorrect instructions | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.02 Inadequate orientation |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.03. Inadequate communication between different organizations | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.02 Inadequate orientation |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.10 Inadequate communication of safety and health data, regulations or guidelines | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.02 Inadequate orientation |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.02.5 Inadequate communication of standards: reinforcing with signs, color codes |  | 16.08 Incorrect instructions | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.02 Inadequate orientation |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.02.5 Inadequate communication of standards: reinforcing with signs, color codes |  | 16.03. Inadequate communication between different organizations | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.02 Inadequate orientation |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.02.5 Inadequate communication of standards: reinforcing with signs, color codes |  | 16.10 Inadequate communication of safety and health data, regulations or guidelines | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.02 Inadequate orientation |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.08 Incorrect instructions | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.02 Inadequate orientation |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.03. Inadequate communication between different organizations | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.02 Inadequate orientation |  |  |  | 9.08 Providing inadequate reference documents, directives and guidance publications |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.10 Inadequate communication of safety and health data, regulations or guidelines | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.02 Inadequate orientation |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  | 16.08 Incorrect instructions | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.02 Inadequate orientation |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  | 16.03. Inadequate communication between different organizations | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.02 Inadequate orientation |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  | 16.10 Inadequate communication of safety and health data, regulations or guidelines | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.02 Inadequate orientation |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.08 Incorrect instructions | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.02 Inadequate orientation |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.03. Inadequate communication between different organizations | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.02 Inadequate orientation |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.10 Inadequate communication of safety and health data, regulations or guidelines | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.02 Inadequate orientation |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.5 Inadequate communication of standards: reinforcing with signs, color codes |  | 16.08 Incorrect instructions | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.02 Inadequate orientation |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.5 Inadequate communication of standards: reinforcing with signs, color codes |  | 16.03. Inadequate communication between different organizations | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.02 Inadequate orientation |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.5 Inadequate communication of standards: reinforcing with signs, color codes |  | 16.10 Inadequate communication of safety and health data, regulations or guidelines | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.02 Inadequate orientation |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.08 Incorrect instructions | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.02 Inadequate orientation |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.03. Inadequate communication between different organizations | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9038 | Horseshoe Lake Power Plant | 2019-09-13 09:00 | Member was walking down project at Tinker and identified contractor had opened engine compartment and a ladder was inside. Control Room had not been contacted and unit could start without contractor notification. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2019-10-18 14:12 | 2019-09-13 13:15 | 2019-09-13 13:15 | 2019-09-26 16:08 | 2019-09-27 08:00 | 2019-09-13 13:09 | 2019-10-11 08:14 |  |  | Tinker AFB 5A turbine engine compartment |  |  | Chrysty Dorsey | Reviewed and approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Member identified contractor had been inside Tinker AFB engine compartment without control room approval. Member asked if they had contacted control room and contractor stated that he had called 3 times and got no answer. Member had a safety stand down with contract crew to identify gaps. This meeting showed several deficiencies. Project Manager / SSG / and Horseshoe Lake Leadership coordinated with Safety Coordinators to complete action items and take-a-ways to ensure all deliverables are identified and completed. Findings from investigation: Contractor had not been given the correct phone number for the HL control room. (Supplied by PM) Contract crew had not been through orientation video. (Video does not cover anything for Tinker AFB) Ethernet nor WiFi is available at Tinker AFB. Emergency Action Plan is undefined for Tinker AFB. ( Contact numbers, Maps, Procedures) |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Kelly Casey | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low |  |  |  |  | 5.02 Inadequate orientation |  |  |  | 9.06 Inadequate work planning or programming |  |  |  |  | 14.02.1 Inadequate communication of standards: publication |  | 16.10 Inadequate communication of safety and health data, regulations or guidelines | Inadequate training | 34. Inadequate Instructions, Procedures | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Kelly Casey | Associated Fire Protection | Michael Blaszak |  |  |  | Matthew Phillips | [71 empty] | 615610
9039 | Metro Service Center | 2019-09-11 13:00 | Asplundh employee Robert lifted a log approx. 75 lbs, felt a sharp pain in lower abdomen, then notices a bulge about the size of a golf ball that evening. | Level 1 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services |  | 2019-09-24 12:50 | 2019-09-13 18:23 | 2019-09-13 18:23 | 2019-09-20 09:35 | 2019-09-25 18:00 | 2019-09-13 18:06 | 2019-09-22 15:10 |  |  | 3801 Westminister Road, OKC, OK |  |  | Jerrie Looney | Going forward, contractor will include proof of reinstruction to include date, content and roster. In this case, reinstruction should include using team lift or reducing size of log. J. Looney, 9/24/19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | Asplundh employee Robert lifted 75 lbs log and felt a sharp pain in his abdomen. Went to the doctor the next day and medical diagnosed with double hernia, Surgery is pending. Employee has not lost work time other than doctor visit. |  |  |  | Metro Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  |  |  |  | Nicole Rhodes | Reviewed. Adequate actions taken by Asplundh. | Nicole Rhodes |  | Low | 1.03 Limited ability to sustain body positions |  | 3.01 Injury or illness | [13 empty] | Asplundh employee Robert was stacking logs. | 10. Improper Lifting | 11. Overstress, Overpressure, Overexertion, Ergonomic | [5 empty] | Injury / Illness |  |  |  | Lump in Groin area | FALSE |  |  | 11. Overstress, Overpressure, Overexertion, Ergonomic |  | Asplundh Tree Experts | Robert Adame Jr | Hernia |  | Groin |  | Front | FALSE
9040 | Sooner Power Plant | 2019-09-13 12:30 | Dump trailer unlatched from truck while attempting to dump spoils. | Level 1 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services | Richard Wood | 2019-10-07 09:25 | 2019-09-14 10:45 | 2019-09-14 10:45 | 2019-09-17 16:32 | 2019-09-27 12:30 | 2019-09-14 10:38 | 2019-09-24 10:14 |  |  | Spoils Stock Pile |  |  | Marcus Huddleston | No additional comments. MLH 10/7/19 | UTS |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Richard Wood |  | While attempting to unload dump trailer at spoil pile trailer coupler became detached from truck hitch. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | UTS - Capital Projects |  | Richard Wood | Richard Wood |  | Robert Weaver | No Comments | Robert Weaver |  | Low | [5 empty] | 6.05 Inadequate review instruction | [10 empty] | While attempting to dump spoils out of trailer at spoil pile trailer coupler detached from hitch on truck. In the process of investigating, discovered that the coupler is stamped, " 5/16" hole on side of coupler for theft deterrent. No safety pin required." However the incident report states that the pin was missing. In the process of the investigation it was also determined that the trailer coupler may not have been properly secured to the hitch so as the trailer was being dumped it became detached. | 16. Failure to Follow Procedure, Policy, Practice | 12. Equipment Failure | [5 empty] | Vehicle |  | Richard Wood | [5 empty] | 12. Equipment Failure | Richard Wood | Wolfe Point Engineering | Waymon Furlow |  |  |  | Richard Wood
9041 | Metro Service Center | 2019-09-09 04:30 | Wally and Calieb. Hit a marked AT&T Copper phone line. The Copper line was exposed, visible and potholed. They were shown the phone line. Also Edgar (Forman) had walked the shot out with them before the bore guys set up to begin shooting. The ground is hard and rocky. The bore crew said that they were trying to go underneath the line and the ground had pushed them up. The result was a line hit. The proper authorities were notified as well as OGE. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Delivery | Garrett Bernethy | 2019-09-24 09:24 | 2019-09-16 08:29 | 2019-09-16 08:29 | 2019-09-16 09:04 | 2019-09-23 04:30 | 2019-09-16 08:22 | 2019-09-19 12:05 |  |  | 35.5071255611586, -97.477826234044; 1900 Ne 36th St |  |  | Marcus Huddleston | No additional comments. MLH 9/24/19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Garrett Bernethy |  | Wally and Calieb. Hit a marked AT&T Copper phone line. The Copper line was exposed, visible and potholed. They were shown the phone line. Also the Edgar (Forman) had walked the shot out with them before the bore guys set up to begin shooting. The ground is hard and rocky. The bore crew said that they were trying to go underneath the line and the ground had pushed them up. The result was a line hit. The proper authorities were notified as well as OGE. |  |  |  | Metro Service Center | FALSE |  | FALSE | Resource Planning & Coord |  | Garrett Bernethy | Garrett Bernethy |  | John Legg | Pathfinder will meet and discuss spacing pertaining to crossing other utilities. | John Legg |  | Low | [5 empty] | 6.02 Inadequate practice |  |  | 9.06 Inadequate work planning or programming | [7 empty] | Contractor hit copper line while boring | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) | [5 empty] | Property Damage |  | Garrett Bernethy | Drilled through copper line |  |  |  |  | 2. Struck By (Hit By Moving Object) | Garrett Bernethy | Pathfinder | Wally Snider |  | Utility Strike |  | Garrett Bernethy |  |  |  |  | FALSE | [66 empty] | 8433195
9042 | General Service Center | 2019-09-16 10:30 | While lifting new breaker 303 to install three of the four lifting straps broke dropping the breaker two feet. | Level 3 |  | FALSE | Contractor | Stephen Merrill | William Young | Investigate, establish causal factors and determine corrective actions. | 2019-10-08 13:52 | OGE Energy Corp | Joseph Manseau | 2020-01-02 12:47 | 2019-09-16 16:53 | 2019-09-16 16:53 | 2019-10-18 12:11 | 2019-09-30 10:30 | 2019-09-16 16:39 | 2019-12-02 11:47 | 2019-12-17 14:59 | 2019-10-18 12:13 | Johnston County Substation |  |  | Stephen Merrill | Consider this complete and closed | Enterprise Services |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Cody Vinyard |  | Heavy Haul delivered a 345kv breaker to the Johnston County Sub 303 and a clearance was unavailable at the time of delivery and a lift was unable to be made. Heavy Haul contacted Allied Crane to make the lift and requested a 40ton crane. On 9/16/19 Allied crane arrived at Johnston County Sub with a 100 ton crane to lift the breaker into position. One crane operator arrived from Allied Crane (Jason Sherman). OGE had 3 members present to for the lift of the breaker, Brandon Schwalbach, John Bull, James Hampton. The three OGE members discussed the lift with the Allied crane operator like the location the breaker needed to be placed and the weight of the breaker being 18,200lbs which they located on the name plate from the Manufacture and they also helped attach the rigging to the breaker. Jason with Allied provided the rigging to lift the breaker, 4 - 12' , 2 inch nylon slings which would be be attached to the breaker designated lifting points by shackles (6.5 ton each). A tailboard was conducted by the OGE members present and the Allied crane operator. 1st lift. The rigging that Allied provided was attached to the breaker by the OGE members 4 - 2"x12' nylon slings with 4 - 6.5ton shackles to the designated lifting eyes for the breaker. A tag line was connected as well.1st lift was started and the breaker was to uneven to complete the lift to the breaker stand approx. 50' away, with the breaker elevated approx. 2', the OGE members removed one canvas cabinet cover and partially removed the other cabinet cover and the load was set down. 2nd Lift. The Allied operator then retrieved 2 - adjustable chain and shackle extensions. rated at 5,700# each. and attached each of them directly to the breaker and the slings to the extensions. The 2nd lift was started and stopped and lowered to the ground when the breaker was still too uneven. 3rd Lift. The chain extensions were adjusted again and the breaker was lifted and only made it up to about 2' off the ground and the 2 slings attached along the long cabinet side broke in the lower eye position, and the 3rd sling next to the end cabinet side stretched and frayed in the middle of the sling. The fourth sling had no damage. Breaker fell to the ground approx. 2', one OGE member was within arms reach of the breaker, the next OGE member was holding the tag line approx. 10'-12' away, the 3rd OGE member was further away observing the lift. No injuries occurred. Damage was sustained to the the breaker, total amount of damage to the breaker was not available at the time of incident closure. Findings: Rigging- A 4 leg sling set up has no greater capacity than a 3 leg setup unless each leg is exactly equal in length and they are equally spaced around the C. O. G. With this in mind the total capacity that was stated by the Allied crane operator was inaccurate. Allied crane operator stated that his rigging had capacity in excess of 20,000#. this is not acheviable as stated above, max capacity would have been 18,600# vertical. With the angle unknown due to the not having the exact length of the extensions, total weight reduction is speculative but would be less than 18,600#. When the extensions were added the over all capacity of the 2 slings was dropped even more due to the capacity of the extensions being 5,700#. Crane computer rated the breaker at 14,000# per the crane operator. The nameplate on the breaker states weight is 18,200#. Lifting instructions sticker on the Breaker. Rigging instructions were not followed, for instance the sticker instructs to use a 15' slings. 12' slings were used. Rigging inspections could not be verified as the crane operator stated that they were done prior to leaving OKC that day. OGE members rigging training was up to date. Tailboard was lacking in crane specific hazard identification. | Justin Thomas | Cody Vinyard |  | General Service Center | FALSE |  | FALSE | Supply Chain |  | Brandon Schwalbach | Joseph Manseau |  | George Wicks | Comprehensive review completed | George Wicks | William Young | High |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance | [6 empty] | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | While lifting new breaker 303 to install three of the four lifting straps broke dropping the breaker two feet. | 08. Improper Loading | 12. Equipment Failure | Reviewed and approved. WCY 12-17-2019 | Approved, Cody Vinyard |  |  |  | Property Damage |  | Charles Shetley | [5 empty] | 12. Equipment Failure | Brandon Schwalbach | Allied | Jason Sherman |  |  |  | Charles Shetley
9042 | General Service Center | 2019-09-16 10:30 | While lifting new breaker 303 to install three of the four lifting straps broke dropping the breaker two feet. | Level 3 |  | FALSE | Contractor | Stephen Merrill | William Young | Investigate, establish causal factors and determine corrective actions. | 2019-10-08 13:52 | OGE Energy Corp | Joseph Manseau | 2020-01-02 12:47 | 2019-09-16 16:53 | 2019-09-16 16:53 | 2019-10-18 12:11 | 2019-09-30 10:30 | 2019-09-16 16:39 | 2019-12-02 11:47 | 2019-12-17 14:59 | 2019-10-18 12:13 | Johnston County Substation |  |  | Stephen Merrill | Consider this complete and closed | Enterprise Services |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Cody Vinyard |  | Heavy Haul delivered a 345kv breaker to the Johnston County Sub 303 and a clearance was unavailable at the time of delivery and a lift was unable to be made. Heavy Haul contacted Allied Crane to make the lift and requested a 40ton crane. On 9/16/19 Allied crane arrived at Johnston County Sub with a 100 ton crane to lift the breaker into position. One crane operator arrived from Allied Crane (Jason Sherman). OGE had 3 members present to for the lift of the breaker, Brandon Schwalbach, John Bull, James Hampton. The three OGE members discussed the lift with the Allied crane operator like the location the breaker needed to be placed and the weight of the breaker being 18,200lbs which they located on the name plate from the Manufacture and they also helped attach the rigging to the breaker. Jason with Allied provided the rigging to lift the breaker, 4 - 12' , 2 inch nylon slings which would be be attached to the breaker designated lifting points by shackles (6.5 ton each). A tailboard was conducted by the OGE members present and the Allied crane operator. 1st lift. The rigging that Allied provided was attached to the breaker by the OGE members 4 - 2"x12' nylon slings with 4 - 6.5ton shackles to the designated lifting eyes for the breaker. A tag line was connected as well.1st lift was started and the breaker was to uneven to complete the lift to the breaker stand approx. 50' away, with the breaker elevated approx. 2', the OGE members removed one canvas cabinet cover and partially removed the other cabinet cover and the load was set down. 2nd Lift. The Allied operator then retrieved 2 - adjustable chain and shackle extensions. rated at 5,700# each. and attached each of them directly to the breaker and the slings to the extensions. The 2nd lift was started and stopped and lowered to the ground when the breaker was still too uneven. 3rd Lift. The chain extensions were adjusted again and the breaker was lifted and only made it up to about 2' off the ground and the 2 slings attached along the long cabinet side broke in the lower eye position, and the 3rd sling next to the end cabinet side stretched and frayed in the middle of the sling. The fourth sling had no damage. Breaker fell to the ground approx. 2', one OGE member was within arms reach of the breaker, the next OGE member was holding the tag line approx. 10'-12' away, the 3rd OGE member was further away observing the lift. No injuries occurred. Damage was sustained to the the breaker, total amount of damage to the breaker was not available at the time of incident closure. Findings: Rigging- A 4 leg sling set up has no greater capacity than a 3 leg setup unless each leg is exactly equal in length and they are equally spaced around the C. O. G. With this in mind the total capacity that was stated by the Allied crane operator was inaccurate. Allied crane operator stated that his rigging had capacity in excess of 20,000#. this is not acheviable as stated above, max capacity would have been 18,600# vertical. With the angle unknown due to the not having the exact length of the extensions, total weight reduction is speculative but would be less than 18,600#. When the extensions were added the over all capacity of the 2 slings was dropped even more due to the capacity of the extensions being 5,700#. Crane computer rated the breaker at 14,000# per the crane operator. The nameplate on the breaker states weight is 18,200#. Lifting instructions sticker on the Breaker. Rigging instructions were not followed, for instance the sticker instructs to use a 15' slings. 12' slings were used. Rigging inspections could not be verified as the crane operator stated that they were done prior to leaving OKC that day. OGE members rigging training was up to date. Tailboard was lacking in crane specific hazard identification. | Charles Shetley | Cody Vinyard |  | General Service Center | FALSE |  | FALSE | Supply Chain |  | Brandon Schwalbach | Joseph Manseau |  | George Wicks | Comprehensive review completed | George Wicks | William Young | High |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance | [6 empty] | 13.03 Inadequate standards or specifications | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | While lifting new breaker 303 to install three of the four lifting straps broke dropping the breaker two feet. | 08. Improper Loading | 12. Equipment Failure | Reviewed and approved. WCY 12-17-2019 | Approved, Cody Vinyard |  |  |  | Property Damage |  | Charles Shetley | [5 empty] | 12. Equipment Failure | Brandon Schwalbach | Allied | Jason Sherman |  |  |  | Charles Shetley
9043 | Metro Service Center | 2019-09-12 12:00 | Public vehicle entered work zone and stuck contract tree trimming truck. | Level 1 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Richard Norton | 2019-09-24 14:01 | 2019-09-17 08:30 | 2019-09-17 08:30 | 2019-09-17 08:52 | 2019-09-26 12:00 | 2019-09-17 08:12 | 2019-09-23 13:46 |  |  | N/O CR 1490 & 3575 rd. Byng,OK |  |  | Jerrie Looney | Approved, J. Looney 9.24.19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Richard Norton |  | Will & Ben was parked with the truck set up (011874) with cones around the truck, both signs up when an elderly man came by he drove through the cones on the side and grazed the side of front bumper and kept going, After further investigation Jerry and the OHP it was determined the elderly man was having some medical issues and EMS was called the trooper said we was not at fault. Jack Hill and Richard Norton was notified. Jack Hill look on the GPS and no alerts was given anywhere near this time. |  |  |  | Metro Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Richard Norton | Nicole Rhodes |  | Richard Norton | Crew had all safety protocol in place, this was a dead end country road with only two homes past their location. An incoherent man entered the work zone striking the front of the truck. man driving car was taken by EMT to Hospital. | Richard Norton |  | Low | [12 empty] | 13.02 Inadequate human factors/ergonomics considerations |  |  |  | Driver of passing vehicle was having a medical issue | 39. Road Conditions | 1. Struck Against (Running or Bumping Into) | [5 empty] | Vehicle |  | Richard Norton | [5 empty] | 1. Struck Against (Running or Bumping Into) | Richard Norton | Wright Tree | Wiam Frye |  |  |  | Richard Norton |  |  |  |  | FALSE
9044 | Central District Office | 2019-09-17 11:00 | After preforming substation inspection, member was backing out of Glendale substation when he backed into a fixed structure. The member had performed his 360 but while backing lost sight of the pole and made contact with a communication box fixed to the pole. Incident was reported immediately to supervisor. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Trenton Tipton | 2019-09-19 13:40 | 2019-09-17 15:08 | 2019-09-17 15:08 | 2019-09-19 09:26 | 2019-10-01 11:00 | 2019-09-17 14:53 | 2019-09-19 11:24 |  |  | Glendale Substation |  |  | Cody Magby | reviewed the incident with the group during safety meetings. Explained to look beyond their vehicle while doing 360, choosing the best path for driving, and the importance of keeping mind on the current task. cm | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Trenton Tipton |  | Member was attempting to back out of the substation after his inspection. Member did perform his 360 but when he got in the vehicle he filled out the substation inspection form which took 5-10 minutes, taking his mind away from driving. He had left himself a path to go forward and not backup but he chose to attempt to back out. He failed to recognize there was a box protruding from the pole approximately 16 inches and was focusing on missing the control house. Member thought he was missing the house and pole but made contact with the box. He was moving slowly and did not notice impact until the glass broke. |  |  |  | Central District Office | FALSE |  | FALSE | PD Operations Services |  | David Williams | Trenton Tipton |  | James Hutchison | I have reviewed this incident report and am satisfied with the investigation as well as the corrective actions. | James Hutchison |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Member failed to mitigate the hazards of backing in a substation. There was room to chose another path that would have prevented backing. | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) | [74 empty] | TRUE |  | Del City | Struck Fixed Object | Backing Related | 2015-04-26 19:00 |  | FALSE |  |  | Day Light |  |  | Gravel |  | Clear |  |  | 9081122
9045 | Muskogee Service Center | 2019-09-17 14:30 | Member was making right hand turn and was struck from behind by a public vehicle that failed to yield. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Audie Murphy | 2019-10-03 15:40 | 2019-09-18 08:09 | 2019-09-18 08:09 | 2019-10-01 08:05 | 2019-10-01 14:30 | 2019-09-18 08:01 | 2019-10-01 10:05 |  | 2019-10-01 08:07 | 1059 W. Poplar, Ft. Gibson, OK |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | TRUE | Audie Murphy |  | Member was working a 505 "get read" order at 1059 W. Poplar and had driven past the gate because the gates were locked. So the member went to a farm south of here to see If access could be obtained from there. Member wasn’t able to get to the meter from there, so the member was driving NE back to the entrance. While arriving at the gate the member slowed to less than 5mph to turn in at the gate. Member was struck from behind by a public vehicle while attempting to make the right hand turn. investigation findings: Member called supervisor immediately after incident. Police and EMT were called to the scene OGE member refused treatment by EMT at the scene, because at the time there was no pain experienced by the member. No citations were issued. Member experienced pain after arriving home, and went to local emergency room to be checked out. member contacted foreman before going to emergency room supervisor contacted proper oge contact, to notify of the medical attention |  |  | FALSE | Muskogee Service Center | FALSE |  | FALSE | PD Operations Services |  | Terry Aldridge | Audie Murphy |  | Randy Jones | I approve . | Randy Jones |  | Medium |  | 2.07 Slow reaction time | [14 empty] | Stuck by public vehicle while making a right hand turn | 19. Failure to React, Correct | 2. Struck By (Hit By Moving Object) |  | approve | [24 empty] | FALSE |  | Days away from Work (H) | 2013-02-18 | 1959-11-14 |  | 2019-09-17 07:00 | 104 | 0 |  | FALSE |  | member was struck from behind by a public vehicle while making a right hand turn. |  |  | Terry Aldridge |  | Days Away from Work | Terry Aldridge | FALSE |  |  |  | Inflammation |  | TRUE |  | Meter Field Representative | Back | Injury |  | TRUE | Audie Murphy | FALSE |  | 9/17/2019 7:00:00 AM | 5+ years | TRUE | FALSE | TRUE | impact from public vehicle striking his company vehicle. | preparing to exit off the road on the right hand side | [6 empty] | FALSE |  | Ft. Gibson | Public Vehicle Struck OGE | Public Driver Failed To Yield | 2013-02-17 18:00 |  | FALSE |  |  | Dusk |  |  | Asphalt |  | Clear
9045 | Muskogee Service Center | 2019-09-17 14:30 | Member was making right hand turn and was struck from behind by a public vehicle that failed to yield. | Level 2 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Audie Murphy | 2019-10-03 15:40 | 2019-09-18 08:09 | 2019-09-18 08:09 | 2019-10-01 08:05 | 2019-10-01 14:30 | 2019-09-18 08:01 | 2019-10-01 10:05 |  | 2019-10-01 08:07 | 1059 W. Poplar, Ft. Gibson, OK |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Vehicle |  | FALSE | TRUE | FALSE |  | FALSE | TRUE | Audie Murphy |  | Member was working a 505 "get read" order at 1059 W. Poplar and had driven past the gate because the gates were locked. So the member went to a farm south of here to see If access could be obtained from there. Member wasn’t able to get to the meter from there, so the member was driving NE back to the entrance. While arriving at the gate the member slowed to less than 5mph to turn in at the gate. Member was struck from behind by a public vehicle while attempting to make the right hand turn. investigation findings: Member called supervisor immediately after incident. Police and EMT were called to the scene OGE member refused treatment by EMT at the scene, because at the time there was no pain experienced by the member. No citations were issued. Member experienced pain after arriving home, and went to local emergency room to be checked out. member contacted foreman before going to emergency room supervisor contacted proper oge contact, to notify of the medical attention |  |  | FALSE | Muskogee Service Center | FALSE |  | FALSE | PD Operations Services |  | Terry Aldridge | Audie Murphy |  | Randy Jones | I approve . | Randy Jones |  | Medium |  | 2.07 Slow reaction time | [14 empty] | Stuck by public vehicle while making a right hand turn | 19. Failure to React, Correct | 2. Struck By (Hit By Moving Object) |  | approve | [24 empty] | FALSE |  | Days away from Work (H) | 2013-02-18 | 1959-11-14 |  | 2019-09-17 07:00 | 104 | 0 |  | FALSE |  | member was struck from behind by a public vehicle while making a right hand turn. |  |  | Terry Aldridge |  | Days Away from Work | Terry Aldridge | FALSE |  |  |  | Inflammation |  | TRUE |  | Meter Field Representative | Back | Injury |  | TRUE | Audie Murphy | FALSE |  | 9/17/2019 7:00:00 AM | 5+ years | TRUE | FALSE | TRUE | impact from public vehicle striking his company vehicle. | preparing to exit off the road on the right hand side | [6 empty] | FALSE |  | Ft. Gibson | Public Vehicle Struck OGE | Public Driver Failed To Yield | 2013-02-17 18:00 |  | FALSE |  |  | Dusk |  |  | Asphalt |  | Clear
9046 | River Valley | 2019-09-12 10:00 | OG&E Member was entering the plant and while checking in at the guard shack location noticed some smoke coming from the rail spur area. When investigated found that a railroad tie was smoldering. Member pulled a water hose from the guard shack to extinguish and wet down the area. Member found a railcar brake key had created the issue. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Jeremiah Perryman | 2019-10-25 11:17 | 2019-09-18 11:29 | 2019-09-18 11:29 | 2019-10-10 10:10 | 2019-09-26 10:00 | 2019-09-18 10:47 | 2019-10-21 07:04 |  |  | River Valley Rail Spur entering the plant site. |  |  | Anthony Gillespie | Good investigation and coordination with railway contacts. Ongoing inspection of brake components should help to reduce likelihood of recurrence. | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Jeremiah Perryman |  | OG&E Member was entering the plant and while checking in at the guard shack location noticed some smoke coming from the rail spur area. When investigated found that a railroad tie was smoldering. Member pulled a water hose from the guard shack to extinguish and wet down the area. Member found a railcar brake key had created the issue. Plant track were walked and we found several of the brake keys laying around on the tracks. When the train is braking coming into the facility and creates heat. When they brake keys fall out then we are introducing a heat source for fires. I reached out to Bill McNally and Will Amos to discuss with our internal car inspection/repair group. They committed to looking closer at brake key conditions. |  |  |  | River Valley | FALSE |  | FALSE | Fuel Supply |  | Jeremiah Perryman | Jeremiah Perryman |  | Timothy Chancellor | Thanks for taking the time to engage KCS on car inspections. | Timothy Chancellor |  | Low | [11 empty] | 12.01.1 Inadequate preventative assessment of needs |  |  |  |  | OG&E Member was entering the plant and while checking in at the guard shack location noticed some smoke coming from the rail spur area. When investigated found that a railroad tie was smoldering. Member pulled a water hose from the guard shack to extinguish and wet down the area. Member found a railcar brake key had created the issue. | 18. Failure to Check, Monitor | 12. Equipment Failure | [68 empty] | Rail tie damaged | 300 | Jeremiah Perryman | Structural
9047 | North Service Center | 2019-09-17 12:30 | Contractor (DRG) pulled into a gas pump that did not work. They decided to back into the pump behind them and collided with a vehicle pulling into the same pump. | Level 1 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Christopher Martin | 2019-10-07 12:10 | 2019-09-18 13:48 | 2019-09-18 13:48 | 2019-09-26 09:43 | 2019-10-01 12:30 | 2019-09-18 12:00 | 2019-09-30 15:55 |  |  | Circle K gas station on NW 63rd and Broadway Extension, North Service Center. |  |  | Jerrie Looney | Approved J. Looney 10/7/19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Christopher Martin |  | Contractor (DRG) pulled into a gas pump that did not work. They decided to back into the pump behind them and collided with a vehicle pulling into the same pump. The contractor was trying to save time by backing into the spot instead of pulling forward. |  |  |  | North Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Brian Hall | Christopher Martin |  | Nicole Rhodes | Reviewed. No additional comments. | Nicole Rhodes |  | Low |  |  |  |  | 5.06 Lack of situational awareness | 6.02 Inadequate practice | [10 empty] | Contractor (DRG) back into spot for a gas pump instead of pulling forward into the spot. | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) | [5 empty] | Vehicle |  | Christopher Martin | [5 empty] | 1. Struck Against (Running or Bumping Into) | Brian Hall | Davey resourse Group | Jonathan Maxwell |  |  |  | Christopher Martin
9048 | Sooner Power Plant | 2019-09-18 13:30 | Members were assembling new racks in the warehouse. They picked up one end of two of the legs that were assembled together about 2 feet off the ground and the legs folded onto themselves. No member injuries. Minor property damage. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Trent Novotny | 2019-10-09 09:12 | 2019-09-18 16:10 | 2019-09-18 16:10 | 2019-10-03 11:04 | 2019-10-02 13:30 | 2019-09-18 15:49 | 2019-10-04 13:24 |  |  | Sooner PP ASME Warehouse |  |  | Brady Sowell | approved by sowell on 10/7. Waiting on hotsheet or incident call to close. | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Trent Novotny |  | Members were assembling racks for the ASME warehouse. They had assembled two up rights with all the cross members bolted on. They used the forklift with a jib to pick up one end around 20" to move it into a more accessible position to stand the rack up. As they picked up the end, the rack folded over resulting in bending the cross members. No member was close to the rack at the time. Members looked for a set of assembling instructions but found only prints. The members thought this would be the most efficient way to assemble them. We had a safety stand down and talked about what we could have done different and how we were going to assemble them going forward. It was decided to stand each up-right up by itself and bolt it to the floor. We also discussed contacting the vendor of the equipment to get a good set of assembling instructions. Members had a sufficient SWP filled out for the job that covered all the hazards. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Maintenance |  | Scott Buchanan | Trent Novotny |  | Frank Brixey | Trent did anyone look for instructions or contact the supplier to locate instructions? What should they have done differently? - Keith Brixey 10/1/2019 Approve - Keith Brixey 10/4/19 | Frank Brixey |  | Low | [8 empty] | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | We received no assembly instructions with the new rack. | 35. Inadequate Information, Data | 12. Equipment Failure | [68 empty] | Bent the connecting brackets of the rack. We straightened them. | 0 | Scott Buchanan | Structural | Charles Thomas | [19 empty] | 9587477
9048 | Sooner Power Plant | 2019-09-18 13:30 | Members were assembling new racks in the warehouse. They picked up one end of two of the legs that were assembled together about 2 feet off the ground and the legs folded onto themselves. No member injuries. Minor property damage. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Trent Novotny | 2019-10-09 09:12 | 2019-09-18 16:10 | 2019-09-18 16:10 | 2019-10-03 11:04 | 2019-10-02 13:30 | 2019-09-18 15:49 | 2019-10-04 13:24 |  |  | Sooner PP ASME Warehouse |  |  | Brady Sowell | approved by sowell on 10/7. Waiting on hotsheet or incident call to close. | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Trent Novotny |  | Members were assembling racks for the ASME warehouse. They had assembled two up rights with all the cross members bolted on. They used the forklift with a jib to pick up one end around 20" to move it into a more accessible position to stand the rack up. As they picked up the end, the rack folded over resulting in bending the cross members. No member was close to the rack at the time. Members looked for a set of assembling instructions but found only prints. The members thought this would be the most efficient way to assemble them. We had a safety stand down and talked about what we could have done different and how we were going to assemble them going forward. It was decided to stand each up-right up by itself and bolt it to the floor. We also discussed contacting the vendor of the equipment to get a good set of assembling instructions. Members had a sufficient SWP filled out for the job that covered all the hazards. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Maintenance |  | Scott Buchanan | Trent Novotny |  | Frank Brixey | Trent did anyone look for instructions or contact the supplier to locate instructions? What should they have done differently? - Keith Brixey 10/1/2019 Approve - Keith Brixey 10/4/19 | Frank Brixey |  | Low | [8 empty] | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | We received no assembly instructions with the new rack. | 35. Inadequate Information, Data | 12. Equipment Failure | [68 empty] | Bent the connecting brackets of the rack. We straightened them. | 0 | Scott Buchanan | Structural | Michael Case | [19 empty] | 9587477
9048 | Sooner Power Plant | 2019-09-18 13:30 | Members were assembling new racks in the warehouse. They picked up one end of two of the legs that were assembled together about 2 feet off the ground and the legs folded onto themselves. No member injuries. Minor property damage. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Trent Novotny | 2019-10-09 09:12 | 2019-09-18 16:10 | 2019-09-18 16:10 | 2019-10-03 11:04 | 2019-10-02 13:30 | 2019-09-18 15:49 | 2019-10-04 13:24 |  |  | Sooner PP ASME Warehouse |  |  | Brady Sowell | approved by sowell on 10/7. Waiting on hotsheet or incident call to close. | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Trent Novotny |  | Members were assembling racks for the ASME warehouse. They had assembled two up rights with all the cross members bolted on. They used the forklift with a jib to pick up one end around 20" to move it into a more accessible position to stand the rack up. As they picked up the end, the rack folded over resulting in bending the cross members. No member was close to the rack at the time. Members looked for a set of assembling instructions but found only prints. The members thought this would be the most efficient way to assemble them. We had a safety stand down and talked about what we could have done different and how we were going to assemble them going forward. It was decided to stand each up-right up by itself and bolt it to the floor. We also discussed contacting the vendor of the equipment to get a good set of assembling instructions. Members had a sufficient SWP filled out for the job that covered all the hazards. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Maintenance |  | Scott Buchanan | Trent Novotny |  | Frank Brixey | Trent did anyone look for instructions or contact the supplier to locate instructions? What should they have done differently? - Keith Brixey 10/1/2019 Approve - Keith Brixey 10/4/19 | Frank Brixey |  | Low | [8 empty] | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | We received no assembly instructions with the new rack. | 35. Inadequate Information, Data | 12. Equipment Failure | [68 empty] | Bent the connecting brackets of the rack. We straightened them. | 0 | Scott Buchanan | Structural | Houston Mendenhall | [19 empty] | 9587477
9049 | Durant Service Center | 2019-09-18 09:00 | This is a first aid. While cleaning up oil dry with shovel member strained shoulder. | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Lyle Just | 2019-09-19 10:35 | 2019-09-19 07:54 | 2019-09-19 07:54 | 2019-09-19 07:58 | 2019-10-02 09:00 | 2019-09-19 07:50 |  |  |  | Durant Service Center |  |  | Terry Hackett | Member advised to take otc anti inflammatory and perform Vimocity movements for shoulder pain. | T&D Ops |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | [5 empty] | FALSE | Durant Service Center | FALSE |  | FALSE | Construction Services |  | Shad Barnett | Lyle Just |  |  |  | Kenneth McKinzie |  | Low | [45 empty] | FALSE |  |  | 2005-06-13 | 1978-08-08 |  | 2019-09-18 07:00 | 0 | 0 |  | FALSE |  | Member strained shoulder while shoveling oil dry |  | FALSE | Shad Barnett |  | First Aid | Shad Barnett |  |  |  |  | Sprain/Strain |  | FALSE |  | Lineman | Shoulder |  | Right | FALSE | Lyle Just | FALSE |  | 9/18/2019 7:00:00 AM |  | FALSE |  |  | Force from shoveling
9050 | Sooner Power Plant | 2019-09-18 14:00 | Members were blowing back transmitter sensing line when the fitting blew off. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Supply | William Cash | 2019-10-08 10:39 | 2019-09-19 11:23 | 2019-09-19 11:23 | 2019-10-04 10:38 | 2019-10-02 14:00 | 2019-09-19 10:51 | 2019-10-04 13:26 |  |  | Unit 2 Scrubber 2B CFB Inlet Transmitter Rack. |  |  | Brady Sowell | Approved by Sowell with Minor changes. See WF comments for clarification. 10/7/2019. Now waiting for call or hotsheet. | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | William Cash |  | Members were blowing back sensing lines on unit 2 CFB inlet transmitter rack when the fitting blew off. A temporary line had been connected to instrument air that was regulated to 70psi. This line doesn't see much pressure in normal operation. The ferrule had not been properly set on initial install when the scrubber was built. The members reinstalled the fitting and set the ferrule. The members also verified the other fittings on the rack were properly installed. Lack of situational awareness was selected as the root cause due to the lack of information from the original installer. It could be reasonably assumed that the original installer was not aware of the improper install. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Bradley Loney | William Cash |  | Frank Brixey | Approve - Brixey | Frank Brixey |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Contractor failed to properly set ferrule when installing fitting. | 16. Failure to Follow Procedure, Policy, Practice | 2. Struck By (Hit By Moving Object) | [92 empty] | 9590730
9051 | General Service Center | 2019-09-18 16:00 | Member was hooking sling up to dozer blade arms that were loaded on a trailer standing up. While member was hooking sling member on the ground was unchaining the arms. After the last chain was loosened the arms fell causing member on trailer to have to move quickly to avoid the arm striking him. | Level 2 |  | TRUE | Member Injury |  |  |  |  | OGE Energy Corp | Charles Shetley | 2019-10-09 14:13 | 2019-09-19 15:30 | 2019-09-19 15:30 | 2019-09-19 16:10 | 2019-10-02 16:00 | 2019-09-18 15:20 | 2019-09-24 09:55 |  | 2019-09-24 07:18 | River Valley Coal yard |  |  | William Young | Reviewed and approved. WCY 10-9-19 | Enterprise Services |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Charles Shetley |  | Member was hooking sling up to dozer blade arms that were loaded on a trailer standing up. While member was hooking sling member on the ground was unchaining the arms. After the last chain was loosened the arms fell causing member on trailer to have to move quickly to avoid the arm striking him. |  |  |  | General Service Center | FALSE |  | TRUE | Supply Chain |  | Kyle Cline | Charles Shetley |  | George Wicks | Cody and Ryan met to thoroughly review the incident and arrive at corrective actions. | George Wicks |  | Medium |  |  |  |  | 5.02 Inadequate orientation | [11 empty] | Member was hooking sling up to dozer blade arms that were loaded on a trailer standing up. While member was hooking sling member on the ground was unchaining the arms. After the last chain was loosened the arms fell causing member on trailer to have to move quickly to avoid the arm striking him. | 11. Improper Position for Task | 7. Caught Between or Under (Crushed or Amputated) |  | Approved, Cody Vinyard
9052 | Metro Service Center | 2019-09-19 17:30 | Boring under ground Boring crew hit a fire water line and ruptured the line | Level 2 |  | FALSE | Property Damage |  |  |  |  | OG&E Corp Services | Steven Blansett | 2019-10-09 14:24 | 2019-09-20 10:44 | 2019-09-20 10:44 | 2019-09-20 11:13 | 2019-10-03 17:30 | 2019-09-20 10:39 | 2019-09-26 12:34 |  | 2019-09-24 09:28 | TINKER AFB Patrol Road near Munitions building 3811 |  |  | William Young | Reviewed and approved. WCY 10-9-19 | UTS |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Blansett |  | Here are some pics of where the water line was hit one pic has BLUE paint in the grass north of the bore pit that is where they hit the water line 6’ into the bore, and other pics show where it was marked to be with the blue arrows on the asphalt it is 23’ off of where the marked it. One pic shows our pot hole trying to locate line before boring, hydro 6’ south of Alutiiq marks and 8’ down found nothing we did out part far as locating with what marks were given. Alutiiq got the water shut off around 8:30pm, line was hit around 4:30pm. Justin Allen with Alutiiq was onsite and stated it that we were not at fault do to the missed marking of the water line. They called a crew in to fix the line last night. |  |  |  | Metro Service Center | FALSE |  | FALSE | UTS - Project Mgmt |  | Steven Blansett | Steven Blansett |  | Christopher Lelak | No comments. CBL 09/26/19 | Christopher Lelak |  | Medium | [15 empty] | 16.06 Inadequate communication methods | Incorrect location of water line. Crew pot holed where water line was located and did not find it after going to approximately 8 f.t depth. Since line was at 6 ft. boring proceeded. | 02. Failure to Warn | 2. Struck By (Hit By Moving Object) |  | No additional comments. MLH 9/24/19 | [66 empty] | Fire Water line (cast iron) struck with underground boring machine. | 200 | Henry Meiwes | Industrial/Heavy Equipment | [20 empty] | 1646641
9053 | Metro Service Center | 2019-09-20 08:14 | TCC System Operator was performing switching order S1315 with field personnel on location at Tryon sub. Operator was utilizing the Tryon/Spring Valley 138kV line overview SCADA screen which displays both Tryon and Spring Valley breakers. Step 1 was to open Tryon PCB 183 by SCADA. Operator opened Spring Valley PCB 183 instead of Tryon PCB 183. | Level 2 |  | FALSE | System Operational Incident |  |  |  |  | Transco | Drew Walker | 2019-10-04 14:57 | 2019-09-20 12:30 |  | 2019-10-03 08:37 | 2019-11-01 08:14 | 2019-09-20 08:20 | 2019-10-04 14:20 |  | 2019-10-03 15:42 | TCC System Operator at North District Operating Center (TCC Backup) performing remote SCADA switching |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Drew Walker |  | TCC System Operator was performing switching order S1315 with field personnel on location at Tryon sub. Operator was utilizing the Tryon/Spring Valley 138kV line overview SCADA screen which displays both Tryon and Spring Valley breakers. Step 1 was to open Tryon PCB 183 by SCADA. Operator opened Spring Valley PCB 183 instead of Tryon PCB 183. Operator failed to select correct device on the screen, failed to read point dialog pop-up window, and failed to read final command pop-up window before sending OPEN command to PCB. |  |  |  | Metro Service Center | FALSE |  | FALSE | System Operations |  | Christopher Crawford | Drew Walker |  | Darrell Fuller | I reviewed the incident and Drew's corrective actions. I approve those actions. | Darrell Fuller |  | Medium | [5 empty] | 6.05 Inadequate review instruction | [10 empty] | Failure to select proper device on SCADA screen and verify correct device is selected. | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation |  | Changed dates for Drew in CAs. Approve of everything else cm
9054 | Sooner Power Plant | 2019-09-18 14:00 | Removing firmware chip from from a communication card and prongs on chip caused small cut on knuckle of member. First aid only | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Supply | Frank Brixey | 2019-10-03 07:24 | 2019-09-20 16:19 | 2019-09-20 16:19 | 2019-09-24 08:21 | 2019-10-02 14:00 | 2019-09-18 14:00 |  |  |  | Sooner Maintenance Shop |  |  | Brady Sowell | Approved - Brixey 9/24/2019, Also approved by brady sowell on 9/30. This incident is waiting to be placed on the call. | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE |  |  | Member brought bad card to the supervisor for help while in the maintenance shop. The supervisor looked at board and wanted to check the firmware chip. He thought about using a screwdriver, but was afraid it would damage the board. He grabbed it with his fingers and pried up. It was seated firmly and required a lot of pressure. When it finally broke loose his knuckles was scraped by one of the pins causing a very minimal amount of blood. Member did not have gloves on due to the delicate work. Member reported immediately. No treatment was given and the supervisor returned to work. |  |  | FALSE | Sooner Power Plant | FALSE |  | FALSE | Maintenance |  | Justin Nealis | Frank Brixey |  |  |  | Frank Brixey |  | Low | [45 empty] | FALSE |  |  | 2011-01-03 | 1987-07-13 |  | 2019-09-18 06:30 | 0 | 0 |  | FALSE |  | Pulling firmware chip off a precipitator communication card. The chip was firmly set and took quite a large amount of force to remove. When the chip finally pulled off the pins on the backside of the chip punctured his finger. |  |  | Justin Nealis |  | First Aid | Justin Nealis |  |  |  |  | Puncture |  | FALSE |  | Supervisor Plant Maintenance | Finger |  | Right |  | Frank Brixey |  |  | 9/18/2019 6:30:00 AM | 2 | FALSE |  |  | Pin on firmware chip | [25 empty] | 18847020
9055 | Sooner Power Plant | 2019-09-23 09:30 | While unloading truck with telehandler, rebar fell off of the truck. | Level 1 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services | Richard Wood | 2019-10-07 09:26 | 2019-09-24 07:45 | 2019-09-24 07:45 | 2019-09-24 08:38 | 2019-10-07 09:30 | 2019-09-24 07:38 | 2019-09-24 10:14 |  |  | Sooner Construction Laydown Area |  |  | Marcus Huddleston | No additional comments. MLH 10/7/19 | UTS |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Richard Wood |  | Rebar was banded together with short bars on one end causing that end to be heavier. When load was lifted off of the truck, the load became unstable and fell off of forks and landed on the ground next to the truck. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | UTS - Capital Projects |  | Richard Wood | Richard Wood |  | Robert Weaver | No comments | Robert Weaver |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Employees failed to recognize hazard | 17. Failure to Identify Hazard, Risk | 9. Abnormal Operation | [5 empty] | Vehicle |  | Richard Wood | [5 empty] | 9. Abnormal Operation | Richard Wood | Wolfe Point Engineering | Waymon Furlow |  |  |  | Richard Wood
9056 | Metro Service Center | 2019-09-19 12:40 | Hit unmarked cox cable well digging up unmarked OG&E Cale to fix it | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Delivery | Garrett Bernethy | 2019-10-08 09:04 | 2019-09-24 12:01 | 2019-09-24 12:01 | 2019-09-26 10:32 | 2019-10-03 12:40 | 2019-09-24 11:55 | 2019-10-08 08:40 |  |  | Valencia Section 11 |  |  | Marcus Huddleston | No additional comments. MLH 10/8 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Garrett Bernethy |  | Hit unmarked OG&E line well trenching to put in 2”street light pipe and cable |  |  |  | Metro Service Center | FALSE |  | FALSE | Resource Planning & Coord |  | Garrett Bernethy | Garrett Bernethy |  | John Legg | Pathfinder will Discuss in safety meeting and retrain employees on looking for possible UG hazards that may exist in the way of a trench line. Talk about the importance of identifying possible hazards that may exist UG | John Legg |  | Low | [7 empty] | 8.2.2 Improper conduct that is not condoned: Unintentional | [8 empty] | Hit unmarked OG&E line well trenching to put in 2”street light pipe and cable | 25. Inadequate Warning System | 2. Struck By (Hit By Moving Object) | [5 empty] | Property Damage |  | Garrett Bernethy | cut secondairy |  |  |  |  | 2. Struck By (Hit By Moving Object) | Garrett Bernethy | Pathfinder | Derrick Hernandez |  | Utility Strike |  | Garrett Bernethy |  |  |  |  | FALSE | [66 empty] | 7381495
9057 | Corporate Headquarters Bldg | 2019-09-24 08:00 | While walking down the stairs in the corporate parking garage, the member stumbled on a rubber expansion joint. Member was holding the handrail at the time and was able to catch themselves and avoid falling. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Donnie Jones | 2019-10-31 16:37 | 2019-09-25 08:09 | 2019-09-25 08:09 | 2019-10-08 16:15 | 2019-10-08 08:00 | 2019-09-25 07:59 | 2019-10-10 11:25 |  |  | Corporate parking garage, 2nd level. |  |  | Chrysty Dorsey | Reviewed | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Bryan Pool |  | This incident occurred on September 24th at approximately 7:20 a.m. The member arrived in the parking garage on the morning of the 27th and parked her vehicle on the 3rd level. After parking the member walked to the stairs and began walking down the stairwell towards the first level, on her way to the corporate headquarters entrance. As the member was stepping off the stairs onto the 2nd level landing, her right foot landed in a rubber expansion joint. This caused her to stumble forward and her right knee contacted the concrete. There was no injury as a result of contacting the concrete. Additional information: 1) This was the members first day parking / using the corporate parking garage. The day prior to the incident (1st day of employment) the member was shown the parking garage from the 1st level but the stairs were not used. 2) The member was holding the handrail with her right hand and felt that doing so lessened the impact of the fall. 3) There were no distractions noted that contributed to this incident. 4) The members footwear was reviewed and determined not to have contributed to this incident. Upon examination of the expansion joint, there were no defects in condition that would elevate its associated risk to a higher level. The expansion joint is made of a soft rubber material, approximately 5 inches wide, which can be depressed when placing pressure directly on it. It should be noted that the expansion joint is black in color. On both sides of the expansion joint, a three-inch black strip is painted on the concrete. This creates an approximate 11-inch black strip on each landing between the main garage landing and the stairs. When focusing directly on this area the difference in the painted concrete and the expansion joint is noticeable. However, in glancing over the area or not placing eyes directly on the area the difference in material can be overlooked. The stairwell design was reviewed and found to be compliant. An additional area to note; when descending the stairs, the center point from one step to another is 12 inches. The center point distance from the bottom stair to the center of the expansion joint is 24 inches. While this is double the distance when walking down the stairs it does not feel like an unnaturally far step. Conclusions and recommendations: 1) As mentioned, this was the members first time descending the stairs. The member is now aware of the presents of the expansion joint. 2) The topic of “eyes on path” was discussed with the member. While there were no distractions associated with this incident it was discussed that more deliberate focus on the pathway could make you aware of changes in the walking surface. 3) The black paint on both sides of the expansion joint makes the change of material less noticeable. It should be recommended to the county (owners of the garage) to consider adding a more visible indication surrounding the expansion joint, such as yellow paint. 4) In addition to item 3, it should be recommended to the county that a more permanent solution such as an engineered cover that still accommodates the needed expansion joint should be installed. |  |  |  | Corporate Headquarters Bldg | FALSE |  | TRUE | Quality Assurance |  | Nichele Lastinger | Bryan Pool |  | Donnie Jones | Please move forward with corrective actions | Donnie Jones |  | Low |  |  |  |  | 5.06 Lack of situational awareness |  |  |  |  | 10.03 Inadequate standards, specifications and/or design criteria | [6 empty] | While walking down stairs, members foot was placed on expansion joint causing her to stumble. | 09. Improper Placement | 4. Fall on Same Level (Slip and Fall, Trip Over)
9058 | Metro Service Center | 2019-09-19 12:40 | Hit unmarked cox cable well digging up unmarked OG&E Cale to fix it | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Delivery | Garrett Bernethy | 2019-10-10 13:49 | 2019-09-26 10:38 | 2019-09-26 10:38 | 2019-09-26 11:00 | 2019-10-03 12:40 | 2019-09-26 10:32 | 2019-10-08 09:25 |  |  | Valencia Section 11 |  |  | Marcus Huddleston | No additional comments. MLH 10/10/19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Garrett Bernethy |  | Pathfinder was trenching on wo # 7381495 Valencia Section 11 and has hit a electric line and a att copper line. We immediately called DCC to inform them of the situation. With in about a hour we had the power back on. Afterwards we started to dig the hit line up to repair it and hit a unmarked AT&T line. We have current up to date dig tickets for the job. The locating company had marked the job prior to us beginning any work. It seems as though they had forgotten to mark the rest of the job. The job has been filmed prior to work, as well. Once the repairs have been made to the electric line, we will switch everything back to normal. Attached are our internal incident forms for the two hits. If there are any questions please let me know. |  |  |  | Metro Service Center | FALSE |  | FALSE | Resource Planning & Coord |  | Garrett Bernethy | Garrett Bernethy |  | John Legg | Pathfinder will discuss in safety meeting and retrain employees on looking for possible UG hazards that may exist in the way of a trench line. Talk about the importance of identifying possible hazards that may exist UG | John Legg |  | Low | [7 empty] | 8.2.2 Improper conduct that is not condoned: Unintentional | [8 empty] | Hit unmarked cox cable well digging up unmarked OG&E Cale to fix it | 25. Inadequate Warning System | 2. Struck By (Hit By Moving Object) | [5 empty] | Property Damage |  | Garrett Bernethy | Cut Cox Cable |  |  |  |  | 2. Struck By (Hit By Moving Object) | Garrett Bernethy | Pathfinder | Brian Neely |  | Utility Strike |  | Garrett Bernethy | [71 empty] | 7381495
9059 | Metro Service Center | 2019-09-19 12:30 | Pulled wrong riser barrel | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Delivery | Garrett Bernethy | 2019-10-10 13:50 | 2019-09-26 11:05 | 2019-09-26 11:05 | 2019-09-26 11:27 | 2019-10-03 12:30 | 2019-09-26 11:02 | 2019-10-08 09:41 |  |  | 6030 Vixen Way |  |  | Marcus Huddleston | No additional comments. MLH 10/10/19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Garrett Bernethy |  | Pulled the wrong riser barrel open when switching |  |  |  | Metro Service Center | FALSE |  | FALSE | Resource Planning & Coord |  | Garrett Bernethy | Garrett Bernethy |  | John Legg | Drillworx will discuss double checking station numbers on equipment & have switching with what phase we are working on. also understand the three way communications when switching. | John Legg |  | Low |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming | [7 empty] | Pulled the wrong fuse barrel | 36. Inadequate Preparation, Planning | 9. Abnormal Operation | [5 empty] | Switching |  | Garrett Bernethy | [5 empty] | 9. Abnormal Operation | Garrett Bernethy | Drillworx | Derrick Winsett |  |  |  | Garrett Bernethy | [71 empty] | 7954983
9060 | Sooner Power Plant | 2019-09-30 11:30 | Contractor was lifting conveyor section when the back outriggers came off the ground causing section to come back down on the cribbing. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Ashley Harris | 2019-11-15 16:25 | 2019-09-30 12:58 | 2019-09-30 12:58 | 2019-10-25 13:24 | 2019-10-14 11:30 | 2019-09-30 12:46 | 2019-10-30 15:17 |  | 2019-10-28 13:23 | Sooner Power Plant- East of 10 and 11 conveyor. |  |  | William Young | Reviewed and approved. WCY 11-15-19 | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Ashley Harris |  | GBI set up the crane to lift a tube in place for bolting two tubes together. Everyone was in position to lift the tube section. Ted Pulis who is GBI's (Great Basin Industrial) General Foreman started signaling the crane. As the crane started coming up Wayman Furlow WPE (Wolf Point Engineers & Contractors) noticed the Northeast outrigger started bouncing. Wayman got Ted's attention and stated the outrigger was bouncing. Ted then signaled to Curtis George who was the crane operator. This is when the outrigger came off thecrane mat and the load shifted South. The South end of the tube hit the other tube damaging the grip strut and one of the tube stiffener rings was bent. Additional cribbing was put under the tube and the tube was set down. Crane operator, Curtis George said he was set up outside of his lift plan. WPE- terminated crane operator that day. Ultimate Crane Services came out and inspected the crane. It was found in good condition and passed inspection. The front left float pad was not locking and needed to be aligned when the outrigger was down. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | UTS - Capital Projects |  | Richard Wood | Ashley Harris |  | Robert Weaver | I agree with the above. | Robert Weaver |  | Medium |  |  |  |  | 5.06 Lack of situational awareness |  | 7.06 Improper attempt to save time or effort | [5 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | While trying to connect 2 sections one tube section shifted into another tube. | 11. Improper Position for Task | 7. Caught Between or Under (Crushed or Amputated) |  | No additional comments. MLH 10/28/19 |  |  |  | Property Damage |  | Ashley Harris | damage to conveyor section. |  |  |  |  | 9. Abnormal Operation | Richard Wood | Wolf Point | Curtis George |  | Utility Strike |  | Ashley Harris |  |  |  |  | FALSE | [42 empty] | Damage to grating and clips. | 4950 | Wayman Furlow | Structural
9061 | Muskogee Service Center | 2019-09-30 14:30 | Trimmer was pruning limbs from the ground. Limbs were engulfing open wire secondary. a limb aprox. 4' long was cut and fell over conductor. trimmer then tried to lift limb off conductor causing hot leg to contact the neutral and causing an outage. | Level 1 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Wesley Lanier | 2019-11-15 12:17 | 2019-09-30 17:07 | 2019-09-30 17:06 | 2019-10-29 10:23 | 2019-10-14 14:30 | 2019-09-30 17:01 | 2019-11-05 10:34 |  |  | 704 N Edmond St. Muskogee OK |  |  | Jerrie Looney | See workflow comment. J. Looney, 10.25.19 Approved, J. Looney 11.15.19 Bill - see attached "Climber Certification Test" | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Wesley Lanier |  | On Monday September 30th, 2019 at approximately 2:30pm, foreman JJ Hamilton and trimmer Ryan Green were trimming open wire secondaries in the backyard of 704 N Edmond St. in Muskogee, OK. The crew had completed a walkthrough of the jobsite prior to beginning work and properly documented on their JSA. Green was using a pruner pole from ground level to clear open wire secondaries from a crepe myrtle tree. As Green was making his final cuts, he cut a limb approximately 4ft in length. This limb got hung up on the middle secondary line, and once Green attempted to push the limb off the line it caused the middle line to contact the top secondary line. As a result of the lines contacting each other the fuse blew leading to a power outage. Hamilton immediately notified his General Foreman and OG&E customer service to report the outage. Regional Safety and Compliance Specialist Hayden Vencl was notified of the incident and upon his arrival made contact Green who in turn gave RSCS Vencl the detail of the events. |  |  |  | Muskogee Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Wesley Lanier | Wesley Lanier |  | Nicole Rhodes | Reviewed. | Nicole Rhodes |  | Low | [8 empty] | 9.06 Inadequate work planning or programming | [7 empty] | Complacency – The trimmer failed to cut the limb into smaller more manageable pieces. The trimmer also failed to consider the close proximity of the limb he intended to cut in relation to electrical conductors. | 17. Failure to Identify Hazard, Risk | 6. Caught On (Snagged, Hung) | [5 empty] | System Outage |  | Wesley Lanier | [5 empty] | 3. Fall from Elevation to Lower Level | Wesley Lanier | West Tree | JJ Hamilton |  |  |  | Wesley Lanier
9062 | Metro Service Center | 2019-09-20 15:00 | while boring @ 3pm a crude oil line was hit at 4 1/2' deep at the first 2 bars drilled | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Delivery | Garrett Bernethy | 2019-10-10 13:52 | 2019-10-01 08:52 | 2019-10-01 08:52 | 2019-10-01 09:27 | 2019-10-04 15:00 | 2019-10-01 08:44 | 2019-10-08 09:45 |  |  | 803 NE 6th St. Oklahoma City, Ok |  |  | Marcus Huddleston | Requested additional information form Legg on this incident. John told me Basin was hired to clean site. MLH 10/8/19 No additional comments. MLH 10/10/19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Garrett Bernethy |  | While MDR Group (subcontractor) was drilling to place OG&E conduit they hit the crude oil line (3"). The first attempt was too dep and they pulled rods out and started to drill again but too shallow and hit the oil line. The oil company shut the line down until 9/23/2019 for a crew to permanently repair the line. MPT crew temporarily repaired the line until 9/23/2019 |  |  |  | Metro Service Center | FALSE |  | FALSE | Resource Planning & Coord |  | Garrett Bernethy | Garrett Bernethy |  | John Legg | MPT will discuss in safety meeting boring at proper depths, and identifying hazards in the way UG while shooting bores. Identify ways to identify the depths of those hazards prior to shooting bores. | John Legg |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | while boring @ 3pm a crude oil line was hit at 4 1/2' deep at the first 2 bars drilled | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) | [5 empty] | Property Damage |  | Garrett Bernethy | Struck crude oil line |  |  |  |  | 2. Struck By (Hit By Moving Object) | Garrett Bernethy | MPT | Abel Duran Saldivar |  | Utility Strike |  | Garrett Bernethy |  |  |  |  | FALSE | [66 empty] | 19232128
9063 | Ft Smith Service Center | 2019-09-30 16:00 | Member was walking along uneven surface, lost his footing and twisted his ankle. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Terry Robbins | 2019-10-22 14:31 | 2019-10-01 09:12 | 2019-10-01 09:12 | 2019-10-15 11:12 | 2019-10-14 16:00 | 2019-09-30 09:02 | 2019-10-18 10:24 |  | 2019-10-15 11:20 | 7111 Phoenix Ave Fort Smith, AR |  |  | William Young | Reviewed and approved. WCY 10-22-19 | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Terry Robbins |  | Member was on a job site with another Project Manager and Engineering Tech assisting in assessing where an easement lay. Member was walking forward, across a new road bed, pulling a 100' tape. The Engineering Tech was walking ahead of him and the other Project Manager was standing back where they were measuring from. As member continued walking across the road bed he turned his head slightly to confirm, from the other Project Manger, where he needed to walk to, stepped off the road bed, lost his footing and twisted his ankle. Member had already been in this area three other times prior to the incident. A tailboard was performed prior to any work being done and all proper ppe was being worn, but Member stated he felt in a time crunch due to his son's baseball game that evening and was not 100% focused on his task. Site conditions were clear with dry disturbed soil and weather conditions were sunny. |  |  | FALSE | Ft Smith Service Center | FALSE |  | FALSE | Resource Planning & Coord |  | Chad Bridges | Terry Robbins |  | Michael Evans | Terry is to complete slips, trips, and falls training with his team in next 30 days. I also required all other PM supervisors to complete same training with their respective teams. We held face to face safety stand down with entire Resource Coordination Forecasting and Planning team. I believe this investigation is complete. | Michael Evans |  | Medium |  |  |  | 4.09 Preoccupation with problems | [12 empty] | Member was on a job site helping another PM and Eng Tech take measurements for an easement. Member was walking across a new dirt drive while pulling the end of a 100' tape measure. The drive had been built up to meet the existing road and when he went to step off he lost his footing and twisted his ankle. The Member had already been in this area three previous times taking measurements. | 09. Improper Placement | 4. Fall on Same Level (Slip and Fall, Trip Over) |  | Sent back to add to the corrective action, I changed the response time from low to medium. No additional comments. MLH 10/15/19 | [24 empty] | FALSE |  | Job Transfer or Restriction (I) | 2015-09-14 | 1983-02-23 |  | 2019-09-30 07:00 | 0 | 18 | Member drove him to the ER. | FALSE |  | Member lost footing, stumbled and twisted ankle. |  | TRUE | Daniel Ray |  | Recordable | Daniel Ray | TRUE |  | Mercy ER | Mercy ER | Sprain/Strain |  | TRUE |  | Project Manager T&D Ops | Ankle | Injury | Left | TRUE | Terry Robbins | TRUE | 2019 | 9/30/2019 7:00:00 AM | 2 years | TRUE | FALSE | TRUE | Uneven disturbed ground | Member was walking along uneven slope. | [24 empty] | 7385105
9064 | Sooner Power Plant | 2019-09-30 10:00 | Contractor was using a hammer on a 2X4 when the hammer flew out of his hand and went behind him about 10 feet. | Level 1 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services | Ashley Harris | 2019-10-28 13:22 | 2019-10-01 10:44 | 2019-10-01 10:44 | 2019-10-10 14:29 | 2019-10-14 10:00 | 2019-10-01 10:33 | 2019-10-21 15:28 |  |  | Rebar Laydown Area |  |  | Marcus Huddleston | No additional comments. MLH 10/28/19 | UTS |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Ashley Harris |  | Kameron Stout was using a hammer on a 2x4 at a table when the hammer flew out of his hand about 10 feet before hitting the ground. This happened in the rebar laydown area. Kameron said the hammer slipped out of his hand because he did not have a good grip. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | UTS - Capital Projects |  | Pete Hamby | Ashley Harris |  | Robert Weaver | I agree with the reported information. | Robert Weaver |  | Low |  |  | 3.02 Fatigue due to task load or duration | [13 empty] | The contractor did not have a proper grip on the hammer. This caused the hammer to fly from his hand about 10 feet behind him and hit the ground. | 15. Using Equipment Improperly | 2. Struck By (Hit By Moving Object) | [5 empty] | Injury / Illness |  | Ashley Harris | [5 empty] | 2. Struck By (Hit By Moving Object) | Pete Hamby | Wolf Point | Kameron Stout |  |  |  | Ashley Harris
9065 | Sooner Power Plant | 2019-09-30 14:00 | Contractor started excavation which was less than 4 feet deep. Contractor continued removing material from excavation. Contractor entered to measure depth of excavation and found it measured at 6 feet. | Level 1 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services | Ashley Harris | 2019-10-28 13:20 | 2019-10-01 11:12 | 2019-10-01 11:12 | 2019-10-10 14:26 | 2019-10-14 14:00 | 2019-10-01 10:52 | 2019-10-21 15:26 |  |  | Sooner Power Plant- existing modified settling basin at bent 7 |  |  | Marcus Huddleston | No additional comments. MLH 10/28/19 | UTS |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Ashley Harris |  | Foreman Curtis Wright was working on excavation. He kept excavating approximately 2 more feet. A contractor went in to check the depth and it measured at 6 feet. There needed to be a daily atmospheric test and daily inspection by a competent person before entering. The large excavation had a low incline ramp for access and egress. The sides of the excavation were properly sloped. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | UTS - Capital Projects |  | Pete Hamby | Ashley Harris |  | Robert Weaver | I agree with the reported information. | Robert Weaver |  | Low |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming | [7 empty] | The excavation had not had a daily inspection by a competent person and had atmospheric testing before entering excavation. | 18. Failure to Check, Monitor | 7. Caught Between or Under (Crushed or Amputated) | [5 empty] | Injury / Illness |  | Ashley Harris | [5 empty] | 7. Caught Between or Under (Crushed or Amputated) | Pete Hamby | Wolf Point | Curtis Wright |  |  |  | Ashley Harris
9066 | Ardmore Service Center | 2019-10-01 13:30 | Company vehicle was travelling west from a four way stop sign when north bound public vehicle failed to stop and hit company vehicle. | Level 2 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Bradley Kosemund | 2019-10-04 08:21 | 2019-10-01 14:42 | 2019-10-01 14:42 | 2019-10-02 07:03 | 2019-10-15 13:30 | 2019-10-01 14:00 | 2019-10-04 07:48 |  | 2019-10-02 14:11 | Byng Oklahoma, Old highway 99 and west Broadway |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Bradley Kosemund |  | Ardmore sub ops maintenance crew had completed the scheduled work at Byng SPA substation in Byng Oklahoma and were travelling back to Ardmore. The Byng SPA substation is o 1 block from the intersection with the 4 way stop and both sub ops personnel were very familiar with the area. The OGE driver was on Broadway headed west toward the highway and stopped at the 4 way stop. The north/south road is the old highway 99 and has a speed limit of 35. OGE driver said the public vehicle was still quite a away from the intersection when he pulled out from the stop sign. The public driver was not familiar with the area and was from Wyoming in a rental vehicle. Public driver did not slow down for the stop sign or the large 2 ton van crossing the road and hit it in the drivers side rear axle. This moved the van about 10 foot sideways. All passengers were wearing seat belts. The public vehicle had an older couple in it. The driver had no injuries but his wife was transported by ambulance due to chest pains. First responders did not believe she had serious injuries. |  |  |  | Ardmore Service Center | FALSE |  | FALSE | PD Operations Services |  | Robby Calhoun | Bradley Kosemund |  | James Hutchison | I have reviewed this incident report and approve both the report and corrective action. | James Hutchison |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Public driver failed to notice stop sign or large orange van crossing intersection | 04. Operating at Improper Speed | 2. Struck By (Hit By Moving Object) |  | reviewed and approve cm | [72 empty] | FALSE |  | Byng | Public Vehicle Struck OGE | Public Driver Failed To Yield | 2003-09-14 19:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
9067 | Ardmore Service Center | 2019-10-01 12:30 | Waiting to turn out of median public driver struck pole on back of line truck. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Terry Looney | 2019-10-08 15:08 | 2019-10-01 14:59 | 2019-10-01 14:59 | 2019-10-08 15:06 | 2019-10-15 12:30 | 2019-10-01 12:30 |  |  |  | Hwy 70 & Meridian 1/4 E Lone Grove |  |  | Terry Hackett | Need to review police report and determine if there are any causal factors the company has control over. Police report and member interviews shows no improper action taken by member. | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | [6 empty] | Ardmore Service Center | FALSE |  | FALSE | Construction Services |  | Robert Beardslee | Terry Looney |  |  |  | Chad Inman |  | Low | [93 empty] | FALSE |  | Lone Grove | Public Vehicle Struck OGE | Other | 2019-05-05 19:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
9068 | Metro Service Center | 2019-10-01 13:00 | Transmission phases that were temporary dead ended, sagged into a co-op distribution circuit allowing it to spark and start a small grass fire. Crew was removing old conductor 1 span to the west of the temporary dead end and 3 spans west of where the intermittent contact occurred. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Delivery | Jimmy Combs | 2019-11-08 18:58 | 2019-10-02 08:17 | 2019-10-02 08:17 | 2019-10-25 08:12 | 2019-10-15 13:00 | 2019-10-02 08:03 | 2019-10-28 18:25 |  |  | 990 Rd and Wagon Wheel Transmission ROW (Lincoln County) |  |  | Terry Hackett | Reviewed/Approved. Implementation of corrective actions will prevent re-occurrence. | T&D Ops |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Jimmy Combs |  | Transmission phases that were temporary dead ended, sagged into a co-op distribution circuit allowing it to spark and start a small grass fire. Crew was removing old conductor 1 span to the west of the temporary dead end and 4 spans west of where the intermittent contact occurred. Facts Ascertained: Transmission line was being removed (line has been abandoned for years) Grounds were placed at the dead end and approximately 10 spans to the east Transmission line was box grounded during the entire process Transmission circuit was approximately 2.5' above the distribution co-op Arcing marks were found on middle phase of co-op and west phase of the transmission circuit Crew observed crossing from the ground and felt there was adequate clearance Wind was gusting 10-15mph out of the south No witnesses to the actual event Approximately 550' spans |  |  |  | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Tommy Nichols | Jimmy Combs |  | Gary Lassley | Jimmy Combs to ensure that the policy to require crews to verify proper distance between crossings and within 5 structures of temporary deadends the crossings must be covered up or have a guard structure in place. Document in October monthly safety meeting. Jimmy Combs will also conduct coaching session with all Transmission Construction Members to set expectation on hazard identification and risk acceptance. | Gary Lassley |  | Low | [8 empty] | 9.09 Inadequate identification and evaluation of loss exposures |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Crew did not recognize how close the transmission circuit and distribution co-op were to each other. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [68 empty] | Small grass fire along fence row | 0 | Tommy Nichols | Fire | [20 empty] | 1646754
9068 | Metro Service Center | 2019-10-01 13:00 | Transmission phases that were temporary dead ended, sagged into a co-op distribution circuit allowing it to spark and start a small grass fire. Crew was removing old conductor 1 span to the west of the temporary dead end and 3 spans west of where the intermittent contact occurred. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Delivery | Jimmy Combs | 2019-11-08 18:58 | 2019-10-02 08:17 | 2019-10-02 08:17 | 2019-10-25 08:12 | 2019-10-15 13:00 | 2019-10-02 08:03 | 2019-10-28 18:25 |  |  | 990 Rd and Wagon Wheel Transmission ROW (Lincoln County) |  |  | Terry Hackett | Reviewed/Approved. Implementation of corrective actions will prevent re-occurrence. | T&D Ops |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Jimmy Combs |  | Transmission phases that were temporary dead ended, sagged into a co-op distribution circuit allowing it to spark and start a small grass fire. Crew was removing old conductor 1 span to the west of the temporary dead end and 4 spans west of where the intermittent contact occurred. Facts Ascertained: Transmission line was being removed (line has been abandoned for years) Grounds were placed at the dead end and approximately 10 spans to the east Transmission line was box grounded during the entire process Transmission circuit was approximately 2.5' above the distribution co-op Arcing marks were found on middle phase of co-op and west phase of the transmission circuit Crew observed crossing from the ground and felt there was adequate clearance Wind was gusting 10-15mph out of the south No witnesses to the actual event Approximately 550' spans |  |  |  | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Tommy Nichols | Jimmy Combs |  | Gary Lassley | Jimmy Combs to ensure that the policy to require crews to verify proper distance between crossings and within 5 structures of temporary deadends the crossings must be covered up or have a guard structure in place. Document in October monthly safety meeting. Jimmy Combs will also conduct coaching session with all Transmission Construction Members to set expectation on hazard identification and risk acceptance. | Gary Lassley |  | Low | [8 empty] | 9.09 Inadequate identification and evaluation of loss exposures | 10.08 Inadequate evaluation of changes | [6 empty] | Inadequate cover up and distance between circuits | 21. Inadequate Guards or Barriers | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [68 empty] | Small grass fire along fence row | 0 | Tommy Nichols | Fire | [20 empty] | 1646754
9069 | Metro Service Center | 2019-10-02 08:30 | Two man Street Lighting Bucket truck struck semi in the rear end. No injuries to either occupants. | Level 3 |  | FALSE | Contractor | Andrea Dennis | William Young | This is a contractor property damage to their own vehicle no investigation necessary | 2019-12-09 17:31 | Power Delivery | John Legg |  | 2019-10-02 09:57 | 2019-10-02 09:57 | 2020-01-19 17:46 | 2019-10-16 08:30 | 2019-10-02 09:50 | 2020-01-22 12:15 | 2020-02-25 11:01 | 2020-01-20 06:42 | I35- and SW 86 |  |  |  |  | T&D Ops |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | John Legg |  | • On the morning of 10-2-19 at 8:00 am. • Scott Spencer was following another employee to ETI in north OKC to drop off a vehicle. • After merging onto northbound I-35 at the SE 89thsteet on ramp and traveling at an accelerated speed. • Scott claims the semi-truck cut him off, immediately after merging into the second lane of traffic. • After the semi-truck “cut him off” Scott claims the semi-truck came to a complete and abrupt stop. • Scott informed the police officer that he was putting his drink down and had taken his eyes off the road. • Once his eyes returned to the road, Scott realized the semi had stopped. • He attempted an evasive maneuver to no avail. • The BHI bucket clipped the side of the semi-trailer causing damage to both vehicles. • Scott immediately contacted his supervisor Mike Lewis. • Mike Lewis, in turn, notified the safety department and his supervisor Robert Moore. • Mike Lewis was the first management on scene and started the investigation. • Weather conditions sunny and clear at the time of the accident. • Road conditions were dry. All taking place during morning rush hour in OKC. | Jerrie Looney | John Legg |  | Metro Service Center | FALSE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  | Nicole Rhodes | Reviewed...appropriate corrective actions have been taken. | Nicole Rhodes | William Young | High |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Inattentive driving | 15. Using Equipment Improperly | 1. Struck Against (Running or Bumping Into) | Investigation complete, CA's complete. WCY | No additional comments. MLH 1/20/2020 |  |  |  | Vehicle |  | John Legg | [5 empty] | 1. Struck Against (Running or Bumping Into) | John Legg | Scott Spencer | BHI |  |  |  | John Legg |  |  |  |  | FALSE
9069 | Metro Service Center | 2019-10-02 08:30 | Two man Street Lighting Bucket truck struck semi in the rear end. No injuries to either occupants. | Level 3 |  | FALSE | Contractor | Andrea Dennis | William Young | This is a contractor property damage to their own vehicle no investigation necessary | 2019-12-09 17:31 | Power Delivery | John Legg |  | 2019-10-02 09:57 | 2019-10-02 09:57 | 2020-01-19 17:46 | 2019-10-16 08:30 | 2019-10-02 09:50 | 2020-01-22 12:15 | 2020-02-25 11:01 | 2020-01-20 06:42 | I35- and SW 86 |  |  |  |  | T&D Ops |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | John Legg |  | • On the morning of 10-2-19 at 8:00 am. • Scott Spencer was following another employee to ETI in north OKC to drop off a vehicle. • After merging onto northbound I-35 at the SE 89thsteet on ramp and traveling at an accelerated speed. • Scott claims the semi-truck cut him off, immediately after merging into the second lane of traffic. • After the semi-truck “cut him off” Scott claims the semi-truck came to a complete and abrupt stop. • Scott informed the police officer that he was putting his drink down and had taken his eyes off the road. • Once his eyes returned to the road, Scott realized the semi had stopped. • He attempted an evasive maneuver to no avail. • The BHI bucket clipped the side of the semi-trailer causing damage to both vehicles. • Scott immediately contacted his supervisor Mike Lewis. • Mike Lewis, in turn, notified the safety department and his supervisor Robert Moore. • Mike Lewis was the first management on scene and started the investigation. • Weather conditions sunny and clear at the time of the accident. • Road conditions were dry. All taking place during morning rush hour in OKC. | Marcus Huddleston | John Legg |  | Metro Service Center | FALSE |  | FALSE | Resource Planning & Coord |  | John Legg | John Legg |  | Nicole Rhodes | Reviewed...appropriate corrective actions have been taken. | Nicole Rhodes | William Young | High |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Inattentive driving | 15. Using Equipment Improperly | 1. Struck Against (Running or Bumping Into) | Investigation complete, CA's complete. WCY | No additional comments. MLH 1/20/2020 |  |  |  | Vehicle |  | John Legg | [5 empty] | 1. Struck Against (Running or Bumping Into) | John Legg | Scott Spencer | BHI |  |  |  | John Legg |  |  |  |  | FALSE
9070 | Seminole PP; EGX Gath/Trans | 2019-10-01 16:00 | When leaving the plant I saw the cover of the card reader laying on the ground and the reader was inoperative. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Paul Schoelen | 2019-10-31 16:38 | 2019-10-02 11:23 | 2019-10-02 11:23 | 2019-10-15 10:11 | 2019-10-15 16:00 | 2019-10-01 16:30 | 2019-10-15 10:06 |  |  | SMPP main gate |  |  | Chrysty Dorsey | Reviewed | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Paul Schoelen |  | On my way to the parking lot after work I noticed the cover of the lower gate card reader laying on the ground. It appeared to have been struck by a vehicle. The card reader would not operate the gate. Security did not have any video of the card reader being struck. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | Operations |  | Paul Schoelen | Paul Schoelen |  | Scott Lee | I approve this Investigation. | Scott Lee |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Card reader struck by vehicle. | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) | [68 empty] | Card reader appears to have been struck and broken | 500 |  | Fixed Equipment
9071 | Frontier Power Plant | 2019-10-01 09:30 | Contractor was walked down the LOTO with a site member and initialed the tags. Contractor hung their lock but did not sign onto the LOTO. No injuries. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Supply | William Hunter | 2019-10-25 09:19 | 2019-10-02 13:13 | 2019-10-02 13:13 | 2019-10-15 08:12 | 2019-10-15 09:30 | 2019-10-02 13:00 | 2019-10-21 13:08 |  |  | RO Water system. |  |  | Tanner Brady | Reviewed with supervisor. Recommend to add to Incident Call. | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | William Hunter |  | On October 1, 2019 there was a LOTO incident at Frontier Power Plant. All boundary devices were correctly hung and identified. The incident occurred due to a lack of following the proper procedure and guidelines instructed to the contracting group (Zachary). The PAE walked him down the LOTO and the contractor initialed the tags and hung his locks on the RO water skid. Frontier is currently using the Co Gen LOTO procedure compared to the OGE LOTO procedure. The contractor was instructed to sign on to the LOTO paperwork, which is similar to the Master Sign on Sheet. He was in the control room, and failed to sign onto all paperwork (MSOS). The incident was discovered at shift changeover. The OGE Member verified the LOTO was in place still, but there was no employee signed onto the paperwork. When speaking with the contracting group he stated that he had forgotten to sign on. After reviewing all of his paperwork he was signed onto the Hot work permit and SWP. The Zachary foreman was informed and there was a safety stand down to discuss the incident and review of the policies in place. |  |  | FALSE | Frontier Power Plant | FALSE |  | TRUE | Operations |  | Gary Russell | William Hunter |  | William Hunter | Reviewed LOTO Procedure and restricted the paper work to the Authorized Authority. | William Hunter |  | Low |  |  |  |  | 5.01 Lack of experience | [8 empty] | 14.04 Inadequate monitoring of compliance |  | 16.03. Inadequate communication between different organizations | Contractor did not sign onto LOTO paperwork | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation
9071 | Frontier Power Plant | 2019-10-01 09:30 | Contractor was walked down the LOTO with a site member and initialed the tags. Contractor hung their lock but did not sign onto the LOTO. No injuries. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Supply | William Hunter | 2019-10-25 09:19 | 2019-10-02 13:13 | 2019-10-02 13:13 | 2019-10-15 08:12 | 2019-10-15 09:30 | 2019-10-02 13:00 | 2019-10-21 13:08 |  |  | RO Water system. |  |  | Tanner Brady | Reviewed with supervisor. Recommend to add to Incident Call. | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | William Hunter |  | On October 1, 2019 there was a LOTO incident at Frontier Power Plant. All boundary devices were correctly hung and identified. The incident occurred due to a lack of following the proper procedure and guidelines instructed to the contracting group (Zachary). The PAE walked him down the LOTO and the contractor initialed the tags and hung his locks on the RO water skid. Frontier is currently using the Co Gen LOTO procedure compared to the OGE LOTO procedure. The contractor was instructed to sign on to the LOTO paperwork, which is similar to the Master Sign on Sheet. He was in the control room, and failed to sign onto all paperwork (MSOS). The incident was discovered at shift changeover. The OGE Member verified the LOTO was in place still, but there was no employee signed onto the paperwork. When speaking with the contracting group he stated that he had forgotten to sign on. After reviewing all of his paperwork he was signed onto the Hot work permit and SWP. The Zachary foreman was informed and there was a safety stand down to discuss the incident and review of the policies in place. |  |  | FALSE | Frontier Power Plant | FALSE |  | TRUE | Operations |  | Gary Russell | William Hunter |  | William Hunter | Reviewed LOTO Procedure and restricted the paper work to the Authorized Authority. | William Hunter |  | Low |  |  |  |  | 5.05 Misunderstood directions | [8 empty] | 14.04 Inadequate monitoring of compliance |  | 16.03. Inadequate communication between different organizations | Contractor did not sign onto LOTO paperwork | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation
9072 | Frontier Power Plant | 2019-10-01 17:00 | Brock removed Zachery's Danger Barricade Tape and tags without permission. Brock had permission to work under the same Barricade Tape. No injuries. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | William Hunter | 2019-10-25 13:25 | 2019-10-02 13:30 | 2019-10-02 13:30 | 2019-10-15 08:11 | 2019-10-15 17:00 | 2019-10-02 13:20 | 2019-10-21 13:10 |  | 2019-10-17 15:33 | Base of HRSG. East end. |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Hunter |  | On October 1, 2019 at Frontier Power Plant a danger barricade was removed from the ground level east side of the HRSG. There were two contracting companies working under the same barricade. Brock had permission to build scaffold while Zachary was on top of the unit. There were two separate tags hung on the barricade tape, one from Brock and the other from Zachary. The brock employee was instructed to remove the tag however he removed the tag and tape from the HRSG area. An OGE member noticed that it was no longer hanging and proceeded to check the barricade log. The barricade had not been returned/released from Zachary. When speaking with both groups it was determined that Brock had removed the danger barricade after finishing up their scaffold build. There was an immediate safety stand down with both groups to discuss the proper communication between everyone on site. Other results from this incident and key learnings from the plant level are that we will no longer allow contractors to have a danger barricade up over night if it doesn't still need to be hanging. For this specific job we could have taken it down and rehung the barricade when the work resumed the next day. |  |  |  | Frontier Power Plant | FALSE |  | FALSE | Other |  | Billy Stegall | William Hunter |  | William Hunter | ~ | William Hunter |  | Medium | [8 empty] | 9.09 Inadequate identification and evaluation of loss exposures | [6 empty] | 16.04 Inadequate communication between work groups | Barricade was removed before all contracting groups had finished work. | 02. Failure to Warn | 2. Struck By (Hit By Moving Object) |  | Reviewed TB 10/17/19 |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | William Hunter | [5 empty] | 2. Struck By (Hit By Moving Object) | Billy Stegall | Brock | Victor Porter |  |  |  | Matthew Gore
9072 | Frontier Power Plant | 2019-10-01 17:00 | Brock removed Zachery's Danger Barricade Tape and tags without permission. Brock had permission to work under the same Barricade Tape. No injuries. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | William Hunter | 2019-10-25 13:25 | 2019-10-02 13:30 | 2019-10-02 13:30 | 2019-10-15 08:11 | 2019-10-15 17:00 | 2019-10-02 13:20 | 2019-10-21 13:10 |  | 2019-10-17 15:33 | Base of HRSG. East end. |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Hunter |  | On October 1, 2019 at Frontier Power Plant a danger barricade was removed from the ground level east side of the HRSG. There were two contracting companies working under the same barricade. Brock had permission to build scaffold while Zachary was on top of the unit. There were two separate tags hung on the barricade tape, one from Brock and the other from Zachary. The brock employee was instructed to remove the tag however he removed the tag and tape from the HRSG area. An OGE member noticed that it was no longer hanging and proceeded to check the barricade log. The barricade had not been returned/released from Zachary. When speaking with both groups it was determined that Brock had removed the danger barricade after finishing up their scaffold build. There was an immediate safety stand down with both groups to discuss the proper communication between everyone on site. Other results from this incident and key learnings from the plant level are that we will no longer allow contractors to have a danger barricade up over night if it doesn't still need to be hanging. For this specific job we could have taken it down and rehung the barricade when the work resumed the next day. |  |  |  | Frontier Power Plant | FALSE |  | FALSE | Other |  | Billy Stegall | William Hunter |  | William Hunter | ~ | William Hunter |  | Medium | [8 empty] | 9.09 Inadequate identification and evaluation of loss exposures | [6 empty] | 16.03. Inadequate communication between different organizations | Barricade was removed before all contracting groups had finished work. | 02. Failure to Warn | 2. Struck By (Hit By Moving Object) |  | Reviewed TB 10/17/19 |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | William Hunter | [5 empty] | 2. Struck By (Hit By Moving Object) | Billy Stegall | Brock | Victor Porter |  |  |  | Matthew Gore
9072 | Frontier Power Plant | 2019-10-01 17:00 | Brock removed Zachery's Danger Barricade Tape and tags without permission. Brock had permission to work under the same Barricade Tape. No injuries. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | William Hunter | 2019-10-25 13:25 | 2019-10-02 13:30 | 2019-10-02 13:30 | 2019-10-15 08:11 | 2019-10-15 17:00 | 2019-10-02 13:20 | 2019-10-21 13:10 |  | 2019-10-17 15:33 | Base of HRSG. East end. |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Hunter |  | On October 1, 2019 at Frontier Power Plant a danger barricade was removed from the ground level east side of the HRSG. There were two contracting companies working under the same barricade. Brock had permission to build scaffold while Zachary was on top of the unit. There were two separate tags hung on the barricade tape, one from Brock and the other from Zachary. The brock employee was instructed to remove the tag however he removed the tag and tape from the HRSG area. An OGE member noticed that it was no longer hanging and proceeded to check the barricade log. The barricade had not been returned/released from Zachary. When speaking with both groups it was determined that Brock had removed the danger barricade after finishing up their scaffold build. There was an immediate safety stand down with both groups to discuss the proper communication between everyone on site. Other results from this incident and key learnings from the plant level are that we will no longer allow contractors to have a danger barricade up over night if it doesn't still need to be hanging. For this specific job we could have taken it down and rehung the barricade when the work resumed the next day. |  |  |  | Frontier Power Plant | FALSE |  | FALSE | Other |  | Billy Stegall | William Hunter |  | William Hunter | ~ | William Hunter |  | Medium | [8 empty] | 9.09 Inadequate identification and evaluation of loss exposures | [6 empty] | 16.10 Inadequate communication of safety and health data, regulations or guidelines | Barricade was removed before all contracting groups had finished work. | 02. Failure to Warn | 2. Struck By (Hit By Moving Object) |  | Reviewed TB 10/17/19 |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | William Hunter | [5 empty] | 2. Struck By (Hit By Moving Object) | Billy Stegall | Brock | Victor Porter |  |  |  | Matthew Gore
9073 | Corporate Headquarters Bldg | 2019-10-03 | Member was regenerating the demineralizer. Member reached to open the acid valve and the piping broke. Acid contacted the members hand and elbow. Member rinsed off hand and arm in the nearby safety shower and eyewash. | Level 3 |  | FALSE | Member Injury | Jean Leger | William Young | Investigate, determine causal factors and corrective actions. WCY 10-14-2019 | 2019-10-14 13:33 | OG&E Corp Services | Les Waller |  | 2019-10-03 12:55 | 2019-10-03 12:54 |  | 2019-10-17 | 2019-10-03 12:25 |  |  | 2019-10-30 14:46 | Sooner Water Treatment building. |  |  | Jerrie Looney | Returning to Les for risk ranking edit. J. Looney, 10.7.19 | UTS |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | William Young |  | In 2015, the 1A regen line was replaced as a part of capitol order 613037. The pipe measurements appear to be approximately .5 inch to short on the new piping. This creates a large amount of pipe strain on the union of the suction check valve with the regen pump. On 8/19/2019, maintenance members received order 9688687 to fix 1A acid Regen pump that was running but not pumping. A chemist informed them that usually that issue comes from debris being stuck in one of the check valves. They removed 1A suction check valve and found debris in it and removed it. When they went to reconnect the system, there was a large amount of pipe strain on the piping. Members had to use a come-a-long to pull the check valve in line with the pump. Following the maintenance repair, one of the chemist used 1A regen pump for a demin regeneration. This regen occurred on or slightly before 9/9/2019. The Chemist said the pump ran well for about 10 minutes, then he noticed his concentrations went to zero. He went to check 1A regen pump and it appeared to be leaking from the discharge check valve, not the suction check valve. He swapped to 1B regen pump and continued the demin regeneration. The chemist wrote an order on 1A discharge check valve following the leak and informed the environmental supervisor of the slight leak. On 10/3, Sooner Environmental supervisor was performing a regen on the demineralizer. He opened the acid supply valve for A regen pump. He was sprayed when the suction side check valve failed. The acid contacted his hand and sleeve. The member immediately pulled his sleeves up and began washing his hands in the emergency shower and eyewash. He then felt a burn on his upper arm. It is believed that the acid on his sleeve burned him when he pulled his sleeve up. He then realized that his pants had been sprayed as well and were beginning to burn through. He removed his clothes and continued showering. He was able to get the spraying to stop by isolating the sulfuric acid tank outside the water treatment building. Once the acid was isolated, he was able to shut off the acid supply valve for 1A regen pump and unisolate the Acid tank. He placed a caution tag on the Acid supply valve for 1A regen pump. Further investigation revealed that one of the bolts that holds the suction check valve to the regen pump had sheered. This allowed the suction check valve and piping to shift out of alignment. This led to an uncontrolled release of acid when the acid supply valve was opened. | Jerrie Looney | William Young | FALSE | Corporate Headquarters Bldg | FALSE |  | FALSE | UTS - Envir. & Process Chem |  | Matthew Grimes | Les Waller |  | Robert Benham | Since the pipe failed due to improper maintenance, having Matt write another notification does nothing to stress the importance of proper maintenance with the individuals or maintenance group as a whole. Another Corrective Action should be added to address this incident with either the individuals who performed the repair work or the maintenance group as a whole. The person responsible to complete this action should be a safety member who would review the incident, findings and lessons learned. | Robert Benham |  | High |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Member failed to identify hazard (broken pipe) | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved. J. Looney 10.30.19 | [24 empty] | FALSE |  |  | 2006-06-19 | 1978-11-27 |  | 2019-10-03 06:30 | 0 | 0 |  | FALSE |  | Piping failed and acid contacted the members hand and elbow. |  | FALSE | Matthew Grimes |  | First Aid | Matthew Grimes |  |  |  |  | Burn: Chemical |  | FALSE |  | Supv Enviro Compliance/Operational Chem | Elbow |  | Right |  | Les Waller |  |  | 10/3/2019 6:30:00 AM | 2.5 years | FALSE |  |  | Sulfuric acid. | Opening the acid valve.
9073 | Corporate Headquarters Bldg | 2019-10-03 | Member was regenerating the demineralizer. Member reached to open the acid valve and the piping broke. Acid contacted the members hand and elbow. Member rinsed off hand and arm in the nearby safety shower and eyewash. | Level 3 |  | FALSE | Member Injury | Jean Leger | William Young | Investigate, determine causal factors and corrective actions. WCY 10-14-2019 | 2019-10-14 13:33 | OG&E Corp Services | Les Waller |  | 2019-10-03 12:55 | 2019-10-03 12:54 |  | 2019-10-17 | 2019-10-03 12:25 |  |  | 2019-10-30 14:46 | Sooner Water Treatment building. |  |  | Jerrie Looney | Returning to Les for risk ranking edit. J. Looney, 10.7.19 | UTS |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | William Young |  | In 2015, the 1A regen line was replaced as a part of capitol order 613037. The pipe measurements appear to be approximately .5 inch to short on the new piping. This creates a large amount of pipe strain on the union of the suction check valve with the regen pump. On 8/19/2019, maintenance members received order 9688687 to fix 1A acid Regen pump that was running but not pumping. A chemist informed them that usually that issue comes from debris being stuck in one of the check valves. They removed 1A suction check valve and found debris in it and removed it. When they went to reconnect the system, there was a large amount of pipe strain on the piping. Members had to use a come-a-long to pull the check valve in line with the pump. Following the maintenance repair, one of the chemist used 1A regen pump for a demin regeneration. This regen occurred on or slightly before 9/9/2019. The Chemist said the pump ran well for about 10 minutes, then he noticed his concentrations went to zero. He went to check 1A regen pump and it appeared to be leaking from the discharge check valve, not the suction check valve. He swapped to 1B regen pump and continued the demin regeneration. The chemist wrote an order on 1A discharge check valve following the leak and informed the environmental supervisor of the slight leak. On 10/3, Sooner Environmental supervisor was performing a regen on the demineralizer. He opened the acid supply valve for A regen pump. He was sprayed when the suction side check valve failed. The acid contacted his hand and sleeve. The member immediately pulled his sleeves up and began washing his hands in the emergency shower and eyewash. He then felt a burn on his upper arm. It is believed that the acid on his sleeve burned him when he pulled his sleeve up. He then realized that his pants had been sprayed as well and were beginning to burn through. He removed his clothes and continued showering. He was able to get the spraying to stop by isolating the sulfuric acid tank outside the water treatment building. Once the acid was isolated, he was able to shut off the acid supply valve for 1A regen pump and unisolate the Acid tank. He placed a caution tag on the Acid supply valve for 1A regen pump. Further investigation revealed that one of the bolts that holds the suction check valve to the regen pump had sheered. This allowed the suction check valve and piping to shift out of alignment. This led to an uncontrolled release of acid when the acid supply valve was opened. | Jerrie Looney | William Young | FALSE | Corporate Headquarters Bldg | FALSE |  | FALSE | UTS - Envir. & Process Chem |  | Matthew Grimes | Les Waller |  | Robert Benham | Since the pipe failed due to improper maintenance, having Matt write another notification does nothing to stress the importance of proper maintenance with the individuals or maintenance group as a whole. Another Corrective Action should be added to address this incident with either the individuals who performed the repair work or the maintenance group as a whole. The person responsible to complete this action should be a safety member who would review the incident, findings and lessons learned. | Robert Benham |  | High | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  | 15.04 Improper loading or rate of use |  | Bolt Sheered due to Pipe strain from improperly measured piping and over torquing | 33. Presence of Harmful Materials | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved. J. Looney 10.30.19 | [24 empty] | FALSE |  |  | 2006-06-19 | 1978-11-27 |  | 2019-10-03 06:30 | 0 | 0 |  | FALSE |  | Piping failed and acid contacted the members hand and elbow. |  | FALSE | Matthew Grimes |  | First Aid | Matthew Grimes |  |  |  |  | Burn: Chemical |  | FALSE |  | Supv Enviro Compliance/Operational Chem | Elbow |  | Right |  | Les Waller |  |  | 10/3/2019 6:30:00 AM | 2.5 years | FALSE |  |  | Sulfuric acid. | Opening the acid valve.
9073 | Corporate Headquarters Bldg | 2019-10-03 | Member was regenerating the demineralizer. Member reached to open the acid valve and the piping broke. Acid contacted the members hand and elbow. Member rinsed off hand and arm in the nearby safety shower and eyewash. | Level 3 |  | FALSE | Member Injury | Jean Leger | William Young | Investigate, determine causal factors and corrective actions. WCY 10-14-2019 | 2019-10-14 13:33 | OG&E Corp Services | Les Waller |  | 2019-10-03 12:55 | 2019-10-03 12:54 |  | 2019-10-17 | 2019-10-03 12:25 |  |  | 2019-10-30 14:46 | Sooner Water Treatment building. |  |  | Jerrie Looney | Returning to Les for risk ranking edit. J. Looney, 10.7.19 | UTS |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | William Young |  | In 2015, the 1A regen line was replaced as a part of capitol order 613037. The pipe measurements appear to be approximately .5 inch to short on the new piping. This creates a large amount of pipe strain on the union of the suction check valve with the regen pump. On 8/19/2019, maintenance members received order 9688687 to fix 1A acid Regen pump that was running but not pumping. A chemist informed them that usually that issue comes from debris being stuck in one of the check valves. They removed 1A suction check valve and found debris in it and removed it. When they went to reconnect the system, there was a large amount of pipe strain on the piping. Members had to use a come-a-long to pull the check valve in line with the pump. Following the maintenance repair, one of the chemist used 1A regen pump for a demin regeneration. This regen occurred on or slightly before 9/9/2019. The Chemist said the pump ran well for about 10 minutes, then he noticed his concentrations went to zero. He went to check 1A regen pump and it appeared to be leaking from the discharge check valve, not the suction check valve. He swapped to 1B regen pump and continued the demin regeneration. The chemist wrote an order on 1A discharge check valve following the leak and informed the environmental supervisor of the slight leak. On 10/3, Sooner Environmental supervisor was performing a regen on the demineralizer. He opened the acid supply valve for A regen pump. He was sprayed when the suction side check valve failed. The acid contacted his hand and sleeve. The member immediately pulled his sleeves up and began washing his hands in the emergency shower and eyewash. He then felt a burn on his upper arm. It is believed that the acid on his sleeve burned him when he pulled his sleeve up. He then realized that his pants had been sprayed as well and were beginning to burn through. He removed his clothes and continued showering. He was able to get the spraying to stop by isolating the sulfuric acid tank outside the water treatment building. Once the acid was isolated, he was able to shut off the acid supply valve for 1A regen pump and unisolate the Acid tank. He placed a caution tag on the Acid supply valve for 1A regen pump. Further investigation revealed that one of the bolts that holds the suction check valve to the regen pump had sheered. This allowed the suction check valve and piping to shift out of alignment. This led to an uncontrolled release of acid when the acid supply valve was opened. | Jerrie Looney | William Young | FALSE | Corporate Headquarters Bldg | FALSE |  | FALSE | UTS - Envir. & Process Chem |  | Matthew Grimes | Les Waller |  | Robert Benham | Since the pipe failed due to improper maintenance, having Matt write another notification does nothing to stress the importance of proper maintenance with the individuals or maintenance group as a whole. Another Corrective Action should be added to address this incident with either the individuals who performed the repair work or the maintenance group as a whole. The person responsible to complete this action should be a safety member who would review the incident, findings and lessons learned. | Robert Benham |  | High | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  | 15.05 Inadequate maintenance |  | Bolt Sheered due to Pipe strain from improperly measured piping and over torquing | 33. Presence of Harmful Materials | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved. J. Looney 10.30.19 | [24 empty] | FALSE |  |  | 2006-06-19 | 1978-11-27 |  | 2019-10-03 06:30 | 0 | 0 |  | FALSE |  | Piping failed and acid contacted the members hand and elbow. |  | FALSE | Matthew Grimes |  | First Aid | Matthew Grimes |  |  |  |  | Burn: Chemical |  | FALSE |  | Supv Enviro Compliance/Operational Chem | Elbow |  | Right |  | Les Waller |  |  | 10/3/2019 6:30:00 AM | 2.5 years | FALSE |  |  | Sulfuric acid. | Opening the acid valve.
9073 | Corporate Headquarters Bldg | 2019-10-03 | Member was regenerating the demineralizer. Member reached to open the acid valve and the piping broke. Acid contacted the members hand and elbow. Member rinsed off hand and arm in the nearby safety shower and eyewash. | Level 3 |  | FALSE | Member Injury | Jean Leger | William Young | Investigate, determine causal factors and corrective actions. WCY 10-14-2019 | 2019-10-14 13:33 | OG&E Corp Services | Les Waller |  | 2019-10-03 12:55 | 2019-10-03 12:54 |  | 2019-10-17 | 2019-10-03 12:25 |  |  | 2019-10-30 14:46 | Sooner Water Treatment building. |  |  | Jerrie Looney | Returning to Les for risk ranking edit. J. Looney, 10.7.19 | UTS |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | William Young |  | In 2015, the 1A regen line was replaced as a part of capitol order 613037. The pipe measurements appear to be approximately .5 inch to short on the new piping. This creates a large amount of pipe strain on the union of the suction check valve with the regen pump. On 8/19/2019, maintenance members received order 9688687 to fix 1A acid Regen pump that was running but not pumping. A chemist informed them that usually that issue comes from debris being stuck in one of the check valves. They removed 1A suction check valve and found debris in it and removed it. When they went to reconnect the system, there was a large amount of pipe strain on the piping. Members had to use a come-a-long to pull the check valve in line with the pump. Following the maintenance repair, one of the chemist used 1A regen pump for a demin regeneration. This regen occurred on or slightly before 9/9/2019. The Chemist said the pump ran well for about 10 minutes, then he noticed his concentrations went to zero. He went to check 1A regen pump and it appeared to be leaking from the discharge check valve, not the suction check valve. He swapped to 1B regen pump and continued the demin regeneration. The chemist wrote an order on 1A discharge check valve following the leak and informed the environmental supervisor of the slight leak. On 10/3, Sooner Environmental supervisor was performing a regen on the demineralizer. He opened the acid supply valve for A regen pump. He was sprayed when the suction side check valve failed. The acid contacted his hand and sleeve. The member immediately pulled his sleeves up and began washing his hands in the emergency shower and eyewash. He then felt a burn on his upper arm. It is believed that the acid on his sleeve burned him when he pulled his sleeve up. He then realized that his pants had been sprayed as well and were beginning to burn through. He removed his clothes and continued showering. He was able to get the spraying to stop by isolating the sulfuric acid tank outside the water treatment building. Once the acid was isolated, he was able to shut off the acid supply valve for 1A regen pump and unisolate the Acid tank. He placed a caution tag on the Acid supply valve for 1A regen pump. Further investigation revealed that one of the bolts that holds the suction check valve to the regen pump had sheered. This allowed the suction check valve and piping to shift out of alignment. This led to an uncontrolled release of acid when the acid supply valve was opened. | Jerrie Looney | William Young | FALSE | Corporate Headquarters Bldg | FALSE |  | FALSE | UTS - Envir. & Process Chem |  | Matthew Grimes | Les Waller |  | Robert Benham | Since the pipe failed due to improper maintenance, having Matt write another notification does nothing to stress the importance of proper maintenance with the individuals or maintenance group as a whole. Another Corrective Action should be added to address this incident with either the individuals who performed the repair work or the maintenance group as a whole. The person responsible to complete this action should be a safety member who would review the incident, findings and lessons learned. | Robert Benham |  | High | [12 empty] | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.04 Improper loading or rate of use |  | Bolt Sheered due to Pipe strain from improperly measured piping and over torquing | 33. Presence of Harmful Materials | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved. J. Looney 10.30.19 | [24 empty] | FALSE |  |  | 2006-06-19 | 1978-11-27 |  | 2019-10-03 06:30 | 0 | 0 |  | FALSE |  | Piping failed and acid contacted the members hand and elbow. |  | FALSE | Matthew Grimes |  | First Aid | Matthew Grimes |  |  |  |  | Burn: Chemical |  | FALSE |  | Supv Enviro Compliance/Operational Chem | Elbow |  | Right |  | Les Waller |  |  | 10/3/2019 6:30:00 AM | 2.5 years | FALSE |  |  | Sulfuric acid. | Opening the acid valve.
9073 | Corporate Headquarters Bldg | 2019-10-03 | Member was regenerating the demineralizer. Member reached to open the acid valve and the piping broke. Acid contacted the members hand and elbow. Member rinsed off hand and arm in the nearby safety shower and eyewash. | Level 3 |  | FALSE | Member Injury | Jean Leger | William Young | Investigate, determine causal factors and corrective actions. WCY 10-14-2019 | 2019-10-14 13:33 | OG&E Corp Services | Les Waller |  | 2019-10-03 12:55 | 2019-10-03 12:54 |  | 2019-10-17 | 2019-10-03 12:25 |  |  | 2019-10-30 14:46 | Sooner Water Treatment building. |  |  | Jerrie Looney | Returning to Les for risk ranking edit. J. Looney, 10.7.19 | UTS |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | William Young |  | In 2015, the 1A regen line was replaced as a part of capitol order 613037. The pipe measurements appear to be approximately .5 inch to short on the new piping. This creates a large amount of pipe strain on the union of the suction check valve with the regen pump. On 8/19/2019, maintenance members received order 9688687 to fix 1A acid Regen pump that was running but not pumping. A chemist informed them that usually that issue comes from debris being stuck in one of the check valves. They removed 1A suction check valve and found debris in it and removed it. When they went to reconnect the system, there was a large amount of pipe strain on the piping. Members had to use a come-a-long to pull the check valve in line with the pump. Following the maintenance repair, one of the chemist used 1A regen pump for a demin regeneration. This regen occurred on or slightly before 9/9/2019. The Chemist said the pump ran well for about 10 minutes, then he noticed his concentrations went to zero. He went to check 1A regen pump and it appeared to be leaking from the discharge check valve, not the suction check valve. He swapped to 1B regen pump and continued the demin regeneration. The chemist wrote an order on 1A discharge check valve following the leak and informed the environmental supervisor of the slight leak. On 10/3, Sooner Environmental supervisor was performing a regen on the demineralizer. He opened the acid supply valve for A regen pump. He was sprayed when the suction side check valve failed. The acid contacted his hand and sleeve. The member immediately pulled his sleeves up and began washing his hands in the emergency shower and eyewash. He then felt a burn on his upper arm. It is believed that the acid on his sleeve burned him when he pulled his sleeve up. He then realized that his pants had been sprayed as well and were beginning to burn through. He removed his clothes and continued showering. He was able to get the spraying to stop by isolating the sulfuric acid tank outside the water treatment building. Once the acid was isolated, he was able to shut off the acid supply valve for 1A regen pump and unisolate the Acid tank. He placed a caution tag on the Acid supply valve for 1A regen pump. Further investigation revealed that one of the bolts that holds the suction check valve to the regen pump had sheered. This allowed the suction check valve and piping to shift out of alignment. This led to an uncontrolled release of acid when the acid supply valve was opened. | Jerrie Looney | William Young | FALSE | Corporate Headquarters Bldg | FALSE |  | FALSE | UTS - Envir. & Process Chem |  | Matthew Grimes | Les Waller |  | Robert Benham | Since the pipe failed due to improper maintenance, having Matt write another notification does nothing to stress the importance of proper maintenance with the individuals or maintenance group as a whole. Another Corrective Action should be added to address this incident with either the individuals who performed the repair work or the maintenance group as a whole. The person responsible to complete this action should be a safety member who would review the incident, findings and lessons learned. | Robert Benham |  | High | [12 empty] | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance |  | Bolt Sheered due to Pipe strain from improperly measured piping and over torquing | 33. Presence of Harmful Materials | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved. J. Looney 10.30.19 | [24 empty] | FALSE |  |  | 2006-06-19 | 1978-11-27 |  | 2019-10-03 06:30 | 0 | 0 |  | FALSE |  | Piping failed and acid contacted the members hand and elbow. |  | FALSE | Matthew Grimes |  | First Aid | Matthew Grimes |  |  |  |  | Burn: Chemical |  | FALSE |  | Supv Enviro Compliance/Operational Chem | Elbow |  | Right |  | Les Waller |  |  | 10/3/2019 6:30:00 AM | 2.5 years | FALSE |  |  | Sulfuric acid. | Opening the acid valve.
9073 | Corporate Headquarters Bldg | 2019-10-03 | Member was regenerating the demineralizer. Member reached to open the acid valve and the piping broke. Acid contacted the members hand and elbow. Member rinsed off hand and arm in the nearby safety shower and eyewash. | Level 3 |  | FALSE | Member Injury | Jean Leger | William Young | Investigate, determine causal factors and corrective actions. WCY 10-14-2019 | 2019-10-14 13:33 | OG&E Corp Services | Les Waller |  | 2019-10-03 12:55 | 2019-10-03 12:54 |  | 2019-10-17 | 2019-10-03 12:25 |  |  | 2019-10-30 14:46 | Sooner Water Treatment building. |  |  | Jerrie Looney | Returning to Les for risk ranking edit. J. Looney, 10.7.19 | UTS |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | William Young |  | In 2015, the 1A regen line was replaced as a part of capitol order 613037. The pipe measurements appear to be approximately .5 inch to short on the new piping. This creates a large amount of pipe strain on the union of the suction check valve with the regen pump. On 8/19/2019, maintenance members received order 9688687 to fix 1A acid Regen pump that was running but not pumping. A chemist informed them that usually that issue comes from debris being stuck in one of the check valves. They removed 1A suction check valve and found debris in it and removed it. When they went to reconnect the system, there was a large amount of pipe strain on the piping. Members had to use a come-a-long to pull the check valve in line with the pump. Following the maintenance repair, one of the chemist used 1A regen pump for a demin regeneration. This regen occurred on or slightly before 9/9/2019. The Chemist said the pump ran well for about 10 minutes, then he noticed his concentrations went to zero. He went to check 1A regen pump and it appeared to be leaking from the discharge check valve, not the suction check valve. He swapped to 1B regen pump and continued the demin regeneration. The chemist wrote an order on 1A discharge check valve following the leak and informed the environmental supervisor of the slight leak. On 10/3, Sooner Environmental supervisor was performing a regen on the demineralizer. He opened the acid supply valve for A regen pump. He was sprayed when the suction side check valve failed. The acid contacted his hand and sleeve. The member immediately pulled his sleeves up and began washing his hands in the emergency shower and eyewash. He then felt a burn on his upper arm. It is believed that the acid on his sleeve burned him when he pulled his sleeve up. He then realized that his pants had been sprayed as well and were beginning to burn through. He removed his clothes and continued showering. He was able to get the spraying to stop by isolating the sulfuric acid tank outside the water treatment building. Once the acid was isolated, he was able to shut off the acid supply valve for 1A regen pump and unisolate the Acid tank. He placed a caution tag on the Acid supply valve for 1A regen pump. Further investigation revealed that one of the bolts that holds the suction check valve to the regen pump had sheered. This allowed the suction check valve and piping to shift out of alignment. This led to an uncontrolled release of acid when the acid supply valve was opened. | Brady Sowell | William Young | FALSE | Corporate Headquarters Bldg | FALSE |  | FALSE | UTS - Envir. & Process Chem |  | Matthew Grimes | Les Waller |  | Robert Benham | Since the pipe failed due to improper maintenance, having Matt write another notification does nothing to stress the importance of proper maintenance with the individuals or maintenance group as a whole. Another Corrective Action should be added to address this incident with either the individuals who performed the repair work or the maintenance group as a whole. The person responsible to complete this action should be a safety member who would review the incident, findings and lessons learned. | Robert Benham |  | High |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Member failed to identify hazard (broken pipe) | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved. J. Looney 10.30.19 | [24 empty] | FALSE |  |  | 2006-06-19 | 1978-11-27 |  | 2019-10-03 06:30 | 0 | 0 |  | FALSE |  | Piping failed and acid contacted the members hand and elbow. |  | FALSE | Matthew Grimes |  | First Aid | Matthew Grimes |  |  |  |  | Burn: Chemical |  | FALSE |  | Supv Enviro Compliance/Operational Chem | Elbow |  | Right |  | Les Waller |  |  | 10/3/2019 6:30:00 AM | 2.5 years | FALSE |  |  | Sulfuric acid. | Opening the acid valve.
9073 | Corporate Headquarters Bldg | 2019-10-03 | Member was regenerating the demineralizer. Member reached to open the acid valve and the piping broke. Acid contacted the members hand and elbow. Member rinsed off hand and arm in the nearby safety shower and eyewash. | Level 3 |  | FALSE | Member Injury | Jean Leger | William Young | Investigate, determine causal factors and corrective actions. WCY 10-14-2019 | 2019-10-14 13:33 | OG&E Corp Services | Les Waller |  | 2019-10-03 12:55 | 2019-10-03 12:54 |  | 2019-10-17 | 2019-10-03 12:25 |  |  | 2019-10-30 14:46 | Sooner Water Treatment building. |  |  | Jerrie Looney | Returning to Les for risk ranking edit. J. Looney, 10.7.19 | UTS |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | William Young |  | In 2015, the 1A regen line was replaced as a part of capitol order 613037. The pipe measurements appear to be approximately .5 inch to short on the new piping. This creates a large amount of pipe strain on the union of the suction check valve with the regen pump. On 8/19/2019, maintenance members received order 9688687 to fix 1A acid Regen pump that was running but not pumping. A chemist informed them that usually that issue comes from debris being stuck in one of the check valves. They removed 1A suction check valve and found debris in it and removed it. When they went to reconnect the system, there was a large amount of pipe strain on the piping. Members had to use a come-a-long to pull the check valve in line with the pump. Following the maintenance repair, one of the chemist used 1A regen pump for a demin regeneration. This regen occurred on or slightly before 9/9/2019. The Chemist said the pump ran well for about 10 minutes, then he noticed his concentrations went to zero. He went to check 1A regen pump and it appeared to be leaking from the discharge check valve, not the suction check valve. He swapped to 1B regen pump and continued the demin regeneration. The chemist wrote an order on 1A discharge check valve following the leak and informed the environmental supervisor of the slight leak. On 10/3, Sooner Environmental supervisor was performing a regen on the demineralizer. He opened the acid supply valve for A regen pump. He was sprayed when the suction side check valve failed. The acid contacted his hand and sleeve. The member immediately pulled his sleeves up and began washing his hands in the emergency shower and eyewash. He then felt a burn on his upper arm. It is believed that the acid on his sleeve burned him when he pulled his sleeve up. He then realized that his pants had been sprayed as well and were beginning to burn through. He removed his clothes and continued showering. He was able to get the spraying to stop by isolating the sulfuric acid tank outside the water treatment building. Once the acid was isolated, he was able to shut off the acid supply valve for 1A regen pump and unisolate the Acid tank. He placed a caution tag on the Acid supply valve for 1A regen pump. Further investigation revealed that one of the bolts that holds the suction check valve to the regen pump had sheered. This allowed the suction check valve and piping to shift out of alignment. This led to an uncontrolled release of acid when the acid supply valve was opened. | Brady Sowell | William Young | FALSE | Corporate Headquarters Bldg | FALSE |  | FALSE | UTS - Envir. & Process Chem |  | Matthew Grimes | Les Waller |  | Robert Benham | Since the pipe failed due to improper maintenance, having Matt write another notification does nothing to stress the importance of proper maintenance with the individuals or maintenance group as a whole. Another Corrective Action should be added to address this incident with either the individuals who performed the repair work or the maintenance group as a whole. The person responsible to complete this action should be a safety member who would review the incident, findings and lessons learned. | Robert Benham |  | High | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  | 15.04 Improper loading or rate of use |  | Bolt Sheered due to Pipe strain from improperly measured piping and over torquing | 33. Presence of Harmful Materials | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved. J. Looney 10.30.19 | [24 empty] | FALSE |  |  | 2006-06-19 | 1978-11-27 |  | 2019-10-03 06:30 | 0 | 0 |  | FALSE |  | Piping failed and acid contacted the members hand and elbow. |  | FALSE | Matthew Grimes |  | First Aid | Matthew Grimes |  |  |  |  | Burn: Chemical |  | FALSE |  | Supv Enviro Compliance/Operational Chem | Elbow |  | Right |  | Les Waller |  |  | 10/3/2019 6:30:00 AM | 2.5 years | FALSE |  |  | Sulfuric acid. | Opening the acid valve.
9073 | Corporate Headquarters Bldg | 2019-10-03 | Member was regenerating the demineralizer. Member reached to open the acid valve and the piping broke. Acid contacted the members hand and elbow. Member rinsed off hand and arm in the nearby safety shower and eyewash. | Level 3 |  | FALSE | Member Injury | Jean Leger | William Young | Investigate, determine causal factors and corrective actions. WCY 10-14-2019 | 2019-10-14 13:33 | OG&E Corp Services | Les Waller |  | 2019-10-03 12:55 | 2019-10-03 12:54 |  | 2019-10-17 | 2019-10-03 12:25 |  |  | 2019-10-30 14:46 | Sooner Water Treatment building. |  |  | Jerrie Looney | Returning to Les for risk ranking edit. J. Looney, 10.7.19 | UTS |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | William Young |  | In 2015, the 1A regen line was replaced as a part of capitol order 613037. The pipe measurements appear to be approximately .5 inch to short on the new piping. This creates a large amount of pipe strain on the union of the suction check valve with the regen pump. On 8/19/2019, maintenance members received order 9688687 to fix 1A acid Regen pump that was running but not pumping. A chemist informed them that usually that issue comes from debris being stuck in one of the check valves. They removed 1A suction check valve and found debris in it and removed it. When they went to reconnect the system, there was a large amount of pipe strain on the piping. Members had to use a come-a-long to pull the check valve in line with the pump. Following the maintenance repair, one of the chemist used 1A regen pump for a demin regeneration. This regen occurred on or slightly before 9/9/2019. The Chemist said the pump ran well for about 10 minutes, then he noticed his concentrations went to zero. He went to check 1A regen pump and it appeared to be leaking from the discharge check valve, not the suction check valve. He swapped to 1B regen pump and continued the demin regeneration. The chemist wrote an order on 1A discharge check valve following the leak and informed the environmental supervisor of the slight leak. On 10/3, Sooner Environmental supervisor was performing a regen on the demineralizer. He opened the acid supply valve for A regen pump. He was sprayed when the suction side check valve failed. The acid contacted his hand and sleeve. The member immediately pulled his sleeves up and began washing his hands in the emergency shower and eyewash. He then felt a burn on his upper arm. It is believed that the acid on his sleeve burned him when he pulled his sleeve up. He then realized that his pants had been sprayed as well and were beginning to burn through. He removed his clothes and continued showering. He was able to get the spraying to stop by isolating the sulfuric acid tank outside the water treatment building. Once the acid was isolated, he was able to shut off the acid supply valve for 1A regen pump and unisolate the Acid tank. He placed a caution tag on the Acid supply valve for 1A regen pump. Further investigation revealed that one of the bolts that holds the suction check valve to the regen pump had sheered. This allowed the suction check valve and piping to shift out of alignment. This led to an uncontrolled release of acid when the acid supply valve was opened. | Brady Sowell | William Young | FALSE | Corporate Headquarters Bldg | FALSE |  | FALSE | UTS - Envir. & Process Chem |  | Matthew Grimes | Les Waller |  | Robert Benham | Since the pipe failed due to improper maintenance, having Matt write another notification does nothing to stress the importance of proper maintenance with the individuals or maintenance group as a whole. Another Corrective Action should be added to address this incident with either the individuals who performed the repair work or the maintenance group as a whole. The person responsible to complete this action should be a safety member who would review the incident, findings and lessons learned. | Robert Benham |  | High | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  | 15.05 Inadequate maintenance |  | Bolt Sheered due to Pipe strain from improperly measured piping and over torquing | 33. Presence of Harmful Materials | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved. J. Looney 10.30.19 | [24 empty] | FALSE |  |  | 2006-06-19 | 1978-11-27 |  | 2019-10-03 06:30 | 0 | 0 |  | FALSE |  | Piping failed and acid contacted the members hand and elbow. |  | FALSE | Matthew Grimes |  | First Aid | Matthew Grimes |  |  |  |  | Burn: Chemical |  | FALSE |  | Supv Enviro Compliance/Operational Chem | Elbow |  | Right |  | Les Waller |  |  | 10/3/2019 6:30:00 AM | 2.5 years | FALSE |  |  | Sulfuric acid. | Opening the acid valve.
9073 | Corporate Headquarters Bldg | 2019-10-03 | Member was regenerating the demineralizer. Member reached to open the acid valve and the piping broke. Acid contacted the members hand and elbow. Member rinsed off hand and arm in the nearby safety shower and eyewash. | Level 3 |  | FALSE | Member Injury | Jean Leger | William Young | Investigate, determine causal factors and corrective actions. WCY 10-14-2019 | 2019-10-14 13:33 | OG&E Corp Services | Les Waller |  | 2019-10-03 12:55 | 2019-10-03 12:54 |  | 2019-10-17 | 2019-10-03 12:25 |  |  | 2019-10-30 14:46 | Sooner Water Treatment building. |  |  | Jerrie Looney | Returning to Les for risk ranking edit. J. Looney, 10.7.19 | UTS |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | William Young |  | In 2015, the 1A regen line was replaced as a part of capitol order 613037. The pipe measurements appear to be approximately .5 inch to short on the new piping. This creates a large amount of pipe strain on the union of the suction check valve with the regen pump. On 8/19/2019, maintenance members received order 9688687 to fix 1A acid Regen pump that was running but not pumping. A chemist informed them that usually that issue comes from debris being stuck in one of the check valves. They removed 1A suction check valve and found debris in it and removed it. When they went to reconnect the system, there was a large amount of pipe strain on the piping. Members had to use a come-a-long to pull the check valve in line with the pump. Following the maintenance repair, one of the chemist used 1A regen pump for a demin regeneration. This regen occurred on or slightly before 9/9/2019. The Chemist said the pump ran well for about 10 minutes, then he noticed his concentrations went to zero. He went to check 1A regen pump and it appeared to be leaking from the discharge check valve, not the suction check valve. He swapped to 1B regen pump and continued the demin regeneration. The chemist wrote an order on 1A discharge check valve following the leak and informed the environmental supervisor of the slight leak. On 10/3, Sooner Environmental supervisor was performing a regen on the demineralizer. He opened the acid supply valve for A regen pump. He was sprayed when the suction side check valve failed. The acid contacted his hand and sleeve. The member immediately pulled his sleeves up and began washing his hands in the emergency shower and eyewash. He then felt a burn on his upper arm. It is believed that the acid on his sleeve burned him when he pulled his sleeve up. He then realized that his pants had been sprayed as well and were beginning to burn through. He removed his clothes and continued showering. He was able to get the spraying to stop by isolating the sulfuric acid tank outside the water treatment building. Once the acid was isolated, he was able to shut off the acid supply valve for 1A regen pump and unisolate the Acid tank. He placed a caution tag on the Acid supply valve for 1A regen pump. Further investigation revealed that one of the bolts that holds the suction check valve to the regen pump had sheered. This allowed the suction check valve and piping to shift out of alignment. This led to an uncontrolled release of acid when the acid supply valve was opened. | Brady Sowell | William Young | FALSE | Corporate Headquarters Bldg | FALSE |  | FALSE | UTS - Envir. & Process Chem |  | Matthew Grimes | Les Waller |  | Robert Benham | Since the pipe failed due to improper maintenance, having Matt write another notification does nothing to stress the importance of proper maintenance with the individuals or maintenance group as a whole. Another Corrective Action should be added to address this incident with either the individuals who performed the repair work or the maintenance group as a whole. The person responsible to complete this action should be a safety member who would review the incident, findings and lessons learned. | Robert Benham |  | High | [12 empty] | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.04 Improper loading or rate of use |  | Bolt Sheered due to Pipe strain from improperly measured piping and over torquing | 33. Presence of Harmful Materials | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved. J. Looney 10.30.19 | [24 empty] | FALSE |  |  | 2006-06-19 | 1978-11-27 |  | 2019-10-03 06:30 | 0 | 0 |  | FALSE |  | Piping failed and acid contacted the members hand and elbow. |  | FALSE | Matthew Grimes |  | First Aid | Matthew Grimes |  |  |  |  | Burn: Chemical |  | FALSE |  | Supv Enviro Compliance/Operational Chem | Elbow |  | Right |  | Les Waller |  |  | 10/3/2019 6:30:00 AM | 2.5 years | FALSE |  |  | Sulfuric acid. | Opening the acid valve.
9073 | Corporate Headquarters Bldg | 2019-10-03 | Member was regenerating the demineralizer. Member reached to open the acid valve and the piping broke. Acid contacted the members hand and elbow. Member rinsed off hand and arm in the nearby safety shower and eyewash. | Level 3 |  | FALSE | Member Injury | Jean Leger | William Young | Investigate, determine causal factors and corrective actions. WCY 10-14-2019 | 2019-10-14 13:33 | OG&E Corp Services | Les Waller |  | 2019-10-03 12:55 | 2019-10-03 12:54 |  | 2019-10-17 | 2019-10-03 12:25 |  |  | 2019-10-30 14:46 | Sooner Water Treatment building. |  |  | Jerrie Looney | Returning to Les for risk ranking edit. J. Looney, 10.7.19 | UTS |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | William Young |  | In 2015, the 1A regen line was replaced as a part of capitol order 613037. The pipe measurements appear to be approximately .5 inch to short on the new piping. This creates a large amount of pipe strain on the union of the suction check valve with the regen pump. On 8/19/2019, maintenance members received order 9688687 to fix 1A acid Regen pump that was running but not pumping. A chemist informed them that usually that issue comes from debris being stuck in one of the check valves. They removed 1A suction check valve and found debris in it and removed it. When they went to reconnect the system, there was a large amount of pipe strain on the piping. Members had to use a come-a-long to pull the check valve in line with the pump. Following the maintenance repair, one of the chemist used 1A regen pump for a demin regeneration. This regen occurred on or slightly before 9/9/2019. The Chemist said the pump ran well for about 10 minutes, then he noticed his concentrations went to zero. He went to check 1A regen pump and it appeared to be leaking from the discharge check valve, not the suction check valve. He swapped to 1B regen pump and continued the demin regeneration. The chemist wrote an order on 1A discharge check valve following the leak and informed the environmental supervisor of the slight leak. On 10/3, Sooner Environmental supervisor was performing a regen on the demineralizer. He opened the acid supply valve for A regen pump. He was sprayed when the suction side check valve failed. The acid contacted his hand and sleeve. The member immediately pulled his sleeves up and began washing his hands in the emergency shower and eyewash. He then felt a burn on his upper arm. It is believed that the acid on his sleeve burned him when he pulled his sleeve up. He then realized that his pants had been sprayed as well and were beginning to burn through. He removed his clothes and continued showering. He was able to get the spraying to stop by isolating the sulfuric acid tank outside the water treatment building. Once the acid was isolated, he was able to shut off the acid supply valve for 1A regen pump and unisolate the Acid tank. He placed a caution tag on the Acid supply valve for 1A regen pump. Further investigation revealed that one of the bolts that holds the suction check valve to the regen pump had sheered. This allowed the suction check valve and piping to shift out of alignment. This led to an uncontrolled release of acid when the acid supply valve was opened. | Brady Sowell | William Young | FALSE | Corporate Headquarters Bldg | FALSE |  | FALSE | UTS - Envir. & Process Chem |  | Matthew Grimes | Les Waller |  | Robert Benham | Since the pipe failed due to improper maintenance, having Matt write another notification does nothing to stress the importance of proper maintenance with the individuals or maintenance group as a whole. Another Corrective Action should be added to address this incident with either the individuals who performed the repair work or the maintenance group as a whole. The person responsible to complete this action should be a safety member who would review the incident, findings and lessons learned. | Robert Benham |  | High | [12 empty] | 13.07 Inadequate removal and replacement of unsuitable items |  | 15.05 Inadequate maintenance |  | Bolt Sheered due to Pipe strain from improperly measured piping and over torquing | 33. Presence of Harmful Materials | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved. J. Looney 10.30.19 | [24 empty] | FALSE |  |  | 2006-06-19 | 1978-11-27 |  | 2019-10-03 06:30 | 0 | 0 |  | FALSE |  | Piping failed and acid contacted the members hand and elbow. |  | FALSE | Matthew Grimes |  | First Aid | Matthew Grimes |  |  |  |  | Burn: Chemical |  | FALSE |  | Supv Enviro Compliance/Operational Chem | Elbow |  | Right |  | Les Waller |  |  | 10/3/2019 6:30:00 AM | 2.5 years | FALSE |  |  | Sulfuric acid. | Opening the acid valve.
9074 | Metro Service Center | 2019-10-03 08:30 | Member was travelling north on I-35 when front right tire blew out. Before the member could stop safely the tire damaged the fiberglass fender, headlight, and running board. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Terry Collins | 2019-10-03 15:45 | 2019-10-03 14:11 | 2019-10-03 14:11 | 2019-10-03 14:23 | 2019-10-17 08:30 | 2019-10-03 09:00 |  |  |  | I 35 northbound Mile marker 155 |  |  | Cody Magby | Tried to pull the tire up to see about age but could not find it with the limited resources. Member did a 360 prior to driving but wasn't able to see any damage or deformities. cm | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | [6 empty] | Metro Service Center | FALSE |  | FALSE | PD Operations Services |  | Trey Jones | Terry Collins |  |  |  | James Hutchison |  | Low | [93 empty] | FALSE |  | Guthrie | Other | Struck By Material/Debris | 2018-03-20 19:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
9075 | River Valley | 2019-10-01 19:00 | While brush hogging the area near the perimeter fence, the mower tire rolled over a piece of concrete causing it to make contact with a fence post. Fence post was pulled out of the ground. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Timothy Chancellor | 2019-10-25 11:20 | 2019-10-03 16:00 | 2019-10-03 16:00 | 2019-10-21 07:23 | 2019-10-15 19:00 | 2019-10-03 15:43 | 2019-10-21 07:59 |  |  | River Valley PP Security perimeter fence |  |  | Anthony Gillespie | Walking down venerable structures like fences before close proximity work is performed should greatly reduce likelihood of recurrence. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Timothy Chancellor |  | While brushhogging the rail spur slopes, the brush hog got caught on the concrete surrounding the post and pulled the post out of the ground. The fence is the outer perimeter and was newly installed. Installer was sloppy when pouring concrete leaving a chunk of the concrete above the ground that was caught by the brush hog. |  |  |  | River Valley | FALSE |  | FALSE | Other |  | Timothy Chancellor | Timothy Chancellor |  | Matthew Schuermann | Approved | Matthew Schuermann |  | Low | [6 empty] | 7.06 Improper attempt to save time or effort | [9 empty] | While pouring concrete, effort to ensure material didn't extend above grade was not taken. | 27. Poor Housekeeping, Disorder | 2. Struck By (Hit By Moving Object) | [5 empty] | Property Damage |  | Timothy Chancellor | Brush Hog hit fence post. |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Timothy Chancellor | Total Turf | Craig Robinson |  | Fixed Equipment |  | Timothy Chancellor |  |  |  |  | FALSE
9076 | Metro Service Center | 2019-10-03 13:30 | Contractor was moving Mini-x and clipped fire hydrant with blade. | Level 1 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Steven Blansett | 2019-10-14 10:58 | 2019-10-04 07:45 | 2019-10-04 07:45 | 2019-10-11 10:04 | 2019-10-17 13:30 | 2019-10-04 07:36 | 2019-10-11 11:06 |  |  | Tinker AFB outside building 3811 |  |  | Marcus Huddleston | No additional comments. MLH 10/14/19 | UTS |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Steven Blansett |  | Contractor was moving mini-x to attach a different bucket. In doing so he had to cross the driveway of building 3811. There was a vehicle in the way and he decided to go between the vehicle and the gate stop. In doing so he clipped the hydrant. |  |  |  | Metro Service Center | FALSE |  | FALSE | UTS - Project Mgmt |  | Steven Blansett | Steven Blansett |  | Christopher Lelak | No comments - CBL 10/11/19 | Christopher Lelak |  | Low | [8 empty] | 9.06 Inadequate work planning or programming | [7 empty] | Struck Fire Hydrant with Mini-x blade | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Steven Blansett | FIre Hydrant broke |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Steven Blansett | OESCO | CornDog (will get real name) |  | Industrial/Heavy Equipment |  | Steven Blansett |  |  |  |  | FALSE
9077 | Muskogee Power Plant | 2019-10-03 16:00 | Labor crew was tasked with lowering hoses down into the dumper basement. During this activity the dumper basement hoist cable became tangled on the drum and will need to be replaced. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Rodney Hyslope | 2019-11-18 08:45 | 2019-10-07 15:37 | 2019-10-07 15:37 | 2019-11-11 07:20 | 2019-10-17 15:00 | 2019-10-07 15:12 | 2019-11-12 10:58 |  | 2019-11-12 10:44 | Muskogee Power Plant coal dumper basement |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE |  |  | A contract labor crew was tasked with removing debris from the dumper sump pump pit. To do this they needed to lower some 6" flex hose to the dumper basement. In the past they have used this hoist located NW of the dumper and above the pit. On this day the hoist pendant would not move the hoist left or right only vertically and it was not positioned directly above the sump pump pit. Before work began an OGE member stopped by and informed the crew the hoist was "messed up". Rather than delay the work the crew decided to utilize the hoist in the condition it was in. The load was raised from a truck bed and then positioned over the pump pit (side loading the hoist) and lowered to the basement floor. When the job was complete they reattached the hoses and equipment to the hoist and began to raise it from the basement floor. The load was raised about 30' when the cable became tangled on the spool due to the side loading. The crew stopped the work at this point but did not inform the fuel yard personnel since they had already left for the day. The following day an employee who was working on sourcing a new pendant for the hoist called the fuel yard supervisor and reported the damaged cable and tangled spool. The next work day the fuel yard supervisor inspected the hoist and reported the incident as property damage. The investigation revealed that the crew thought due to the light weight of the load they were okay to lower it with the hoist in the position it was in. The crew suggested that they felt like the job was urgent and they would either have to carry the hoses down to the basement or utilize the hoist as it was. The discussion didn't reveal any reason for the job to have seemed urgent, we were utilizing the crew to remove metal debris from the sump pump pits as we had done in several other areas. We met with the members of the entire contract crew and discussed our expectations around stopping work, side loading any lifting devices, and reporting any incident including potential property damages. Additional information: It was acknowledged that OGE members should have hung an orange tag or LOTO'd the defective hoist pendant until the appropriate parts were sourced. We had a current notification but we failed to hang the associated equipment repair tag. The member who actually ran the hoist took full responsibility for the incident but during the interview he admitted that there was discussion amongst the crew to perform the lift. This prompted a group discussion around hazard recognition and risk tolerance. MPO and Fuel Yard Supervisor met with the individual who ran the hoist and explained their expectation for work to stop when we do not have the proper tools or equipment to perform the job. MPO and Fuel yard supervisor met with the crew and held a discussion on the expectation of reporting any incident or property damage immediately. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | Fuel Supply |  | Rodney Hyslope |  |  |  | Reviewed - Crary |  |  | Medium |  |  |  |  | 5.06 Lack of situational awareness |  | 7.06 Improper attempt to save time or effort | [6 empty] | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Hoist pendant malfunctioning | 17. Failure to Identify Hazard, Risk | 6. Caught On (Snagged, Hung) |  | Edited and reviewed Bob Wright | [66 empty] | hoist cable damaged and will need to be replaced. | 9000 | Gino | Industrial/Heavy Equipment | [20 empty] | 9591323
9077 | Muskogee Power Plant | 2019-10-03 16:00 | Labor crew was tasked with lowering hoses down into the dumper basement. During this activity the dumper basement hoist cable became tangled on the drum and will need to be replaced. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Rodney Hyslope | 2019-11-18 08:45 | 2019-10-07 15:37 | 2019-10-07 15:37 | 2019-11-11 07:20 | 2019-10-17 15:00 | 2019-10-07 15:12 | 2019-11-12 10:58 |  | 2019-11-12 10:44 | Muskogee Power Plant coal dumper basement |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE |  |  | A contract labor crew was tasked with removing debris from the dumper sump pump pit. To do this they needed to lower some 6" flex hose to the dumper basement. In the past they have used this hoist located NW of the dumper and above the pit. On this day the hoist pendant would not move the hoist left or right only vertically and it was not positioned directly above the sump pump pit. Before work began an OGE member stopped by and informed the crew the hoist was "messed up". Rather than delay the work the crew decided to utilize the hoist in the condition it was in. The load was raised from a truck bed and then positioned over the pump pit (side loading the hoist) and lowered to the basement floor. When the job was complete they reattached the hoses and equipment to the hoist and began to raise it from the basement floor. The load was raised about 30' when the cable became tangled on the spool due to the side loading. The crew stopped the work at this point but did not inform the fuel yard personnel since they had already left for the day. The following day an employee who was working on sourcing a new pendant for the hoist called the fuel yard supervisor and reported the damaged cable and tangled spool. The next work day the fuel yard supervisor inspected the hoist and reported the incident as property damage. The investigation revealed that the crew thought due to the light weight of the load they were okay to lower it with the hoist in the position it was in. The crew suggested that they felt like the job was urgent and they would either have to carry the hoses down to the basement or utilize the hoist as it was. The discussion didn't reveal any reason for the job to have seemed urgent, we were utilizing the crew to remove metal debris from the sump pump pits as we had done in several other areas. We met with the members of the entire contract crew and discussed our expectations around stopping work, side loading any lifting devices, and reporting any incident including potential property damages. Additional information: It was acknowledged that OGE members should have hung an orange tag or LOTO'd the defective hoist pendant until the appropriate parts were sourced. We had a current notification but we failed to hang the associated equipment repair tag. The member who actually ran the hoist took full responsibility for the incident but during the interview he admitted that there was discussion amongst the crew to perform the lift. This prompted a group discussion around hazard recognition and risk tolerance. MPO and Fuel Yard Supervisor met with the individual who ran the hoist and explained their expectation for work to stop when we do not have the proper tools or equipment to perform the job. MPO and Fuel yard supervisor met with the crew and held a discussion on the expectation of reporting any incident or property damage immediately. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | Fuel Supply |  | Rodney Hyslope |  |  |  | Reviewed - Crary |  |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction | 7.06 Improper attempt to save time or effort | 8.2.1 Improper conduct that is not condoned: Intentional | [5 empty] | 14.02.4 Inadequate communication of standards: training |  |  | hoist side loaded to remove hoses from sump pump pit | 10. Improper Lifting | 6. Caught On (Snagged, Hung) |  | Edited and reviewed Bob Wright | [66 empty] | hoist cable damaged and will need to be replaced. | 9000 | Gino | Industrial/Heavy Equipment | [20 empty] | 9591323
9077 | Muskogee Power Plant | 2019-10-03 16:00 | Labor crew was tasked with lowering hoses down into the dumper basement. During this activity the dumper basement hoist cable became tangled on the drum and will need to be replaced. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Rodney Hyslope | 2019-11-18 08:45 | 2019-10-07 15:37 | 2019-10-07 15:37 | 2019-11-11 07:20 | 2019-10-17 15:00 | 2019-10-07 15:12 | 2019-11-12 10:58 |  | 2019-11-12 10:44 | Muskogee Power Plant coal dumper basement |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE |  |  | A contract labor crew was tasked with removing debris from the dumper sump pump pit. To do this they needed to lower some 6" flex hose to the dumper basement. In the past they have used this hoist located NW of the dumper and above the pit. On this day the hoist pendant would not move the hoist left or right only vertically and it was not positioned directly above the sump pump pit. Before work began an OGE member stopped by and informed the crew the hoist was "messed up". Rather than delay the work the crew decided to utilize the hoist in the condition it was in. The load was raised from a truck bed and then positioned over the pump pit (side loading the hoist) and lowered to the basement floor. When the job was complete they reattached the hoses and equipment to the hoist and began to raise it from the basement floor. The load was raised about 30' when the cable became tangled on the spool due to the side loading. The crew stopped the work at this point but did not inform the fuel yard personnel since they had already left for the day. The following day an employee who was working on sourcing a new pendant for the hoist called the fuel yard supervisor and reported the damaged cable and tangled spool. The next work day the fuel yard supervisor inspected the hoist and reported the incident as property damage. The investigation revealed that the crew thought due to the light weight of the load they were okay to lower it with the hoist in the position it was in. The crew suggested that they felt like the job was urgent and they would either have to carry the hoses down to the basement or utilize the hoist as it was. The discussion didn't reveal any reason for the job to have seemed urgent, we were utilizing the crew to remove metal debris from the sump pump pits as we had done in several other areas. We met with the members of the entire contract crew and discussed our expectations around stopping work, side loading any lifting devices, and reporting any incident including potential property damages. Additional information: It was acknowledged that OGE members should have hung an orange tag or LOTO'd the defective hoist pendant until the appropriate parts were sourced. We had a current notification but we failed to hang the associated equipment repair tag. The member who actually ran the hoist took full responsibility for the incident but during the interview he admitted that there was discussion amongst the crew to perform the lift. This prompted a group discussion around hazard recognition and risk tolerance. MPO and Fuel Yard Supervisor met with the individual who ran the hoist and explained their expectation for work to stop when we do not have the proper tools or equipment to perform the job. MPO and Fuel yard supervisor met with the crew and held a discussion on the expectation of reporting any incident or property damage immediately. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | Fuel Supply |  | Rodney Hyslope |  |  |  | Reviewed - Crary |  |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction | 7.06 Improper attempt to save time or effort | 8.2.1 Improper conduct that is not condoned: Intentional | [5 empty] | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | hoist side loaded to remove hoses from sump pump pit | 10. Improper Lifting | 6. Caught On (Snagged, Hung) |  | Edited and reviewed Bob Wright | [66 empty] | hoist cable damaged and will need to be replaced. | 9000 | Gino | Industrial/Heavy Equipment | [20 empty] | 9591323
9078 | Metro Service Center | 2019-10-02 12:00 | While digging in new underground service employee hit house service that was 6ft off locate. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Delivery | Garrett Bernethy | 2019-10-10 13:53 | 2019-10-08 08:33 | 2019-10-08 08:33 | 2019-10-08 09:23 | 2019-10-16 12:00 | 2019-10-08 08:23 | 2019-10-08 09:48 |  |  | 1997 Hoxbar Rd...Ardmore, Ok |  |  | Marcus Huddleston | No additional comments. MLH 10/10/19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Garrett Bernethy |  | While digging in new underground service employee hit house service that was 6ft off locate |  |  |  | Metro Service Center | FALSE |  | FALSE | Resource Planning & Coord |  | Garrett Bernethy | Garrett Bernethy |  | John Legg | Elliot will discuss in their next safety meeting the importance of identifying possible UG hazards that may not be marked | John Legg |  | Low | [5 empty] | 6.01 Inadequate initial instruction | [7 empty] | 14.02.1 Inadequate communication of standards: publication |  |  | While digging in new underground service employee hit house service that was 6ft off locate. | 02. Failure to Warn | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Garrett Bernethy | Hit and cut UG service to house |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Garrett Bernethy | Elliot | Christian Bracket |  | Utility Strike |  | Garrett Bernethy |  |  |  |  | FALSE
9079 | Metro Service Center | 2019-10-07 14:30 | Contract Boring crew struck unmarked water line. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Steven Blansett | 2019-10-22 14:37 | 2019-10-08 08:58 | 2019-10-08 08:57 | 2019-10-21 09:07 | 2019-10-21 14:30 | 2019-10-08 08:54 | 2019-10-21 14:23 |  | 2019-10-21 10:26 | SE Corner of Marauder Gate |  |  | William Young | Reviewed and approved. WCY 10-22-19 | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | TRUE |  | FALSE | FALSE | Steven Blansett |  | Water line was marked in incorrect location |  |  |  | Metro Service Center | FALSE |  | FALSE | UTS - Capital Projects |  | Steven Blansett | Steven Blansett |  | Christopher Lelak | No comments CBL 10/21/19 | Christopher Lelak |  | Medium | [8 empty] | 9.08 Providing inadequate reference documents, directives and guidance publications | [7 empty] | Struck incorrectly marked water line by boring machine | 02. Failure to Warn | 1. Struck Against (Running or Bumping Into) |  | No additional comments. MLH 10/21 |  |  |  | Property Damage |  | Steven Blansett | Struck Water Line |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Steven Blansett | M&P | MDR operator |  | Utility Strike |  | Steven Blansett |  |  |  |  | FALSE | [42 empty] | Puncture of water line with boring machine. | 250 | Steven Blansett | Utility Strike | [20 empty] | 1647576
9079 | Metro Service Center | 2019-10-07 14:30 | Contract Boring crew struck unmarked water line. | Level 2 |  | FALSE | Property Damage |  |  |  |  | OG&E Corp Services | Steven Blansett | 2019-10-22 14:37 | 2019-10-08 08:58 | 2019-10-08 08:57 | 2019-10-21 09:07 | 2019-10-21 14:30 | 2019-10-08 08:54 | 2019-10-21 14:23 |  | 2019-10-21 10:26 | SE Corner of Marauder Gate |  |  | William Young | Reviewed and approved. WCY 10-22-19 | UTS |  | Level 2 | Property Damage |  | TRUE | FALSE | TRUE |  | FALSE | FALSE | Steven Blansett |  | Water line was marked in incorrect location |  |  |  | Metro Service Center | FALSE |  | FALSE | UTS - Capital Projects |  | Steven Blansett | Steven Blansett |  | Christopher Lelak | No comments CBL 10/21/19 | Christopher Lelak |  | Medium | [8 empty] | 9.08 Providing inadequate reference documents, directives and guidance publications | [7 empty] | Struck incorrectly marked water line by boring machine | 02. Failure to Warn | 1. Struck Against (Running or Bumping Into) |  | No additional comments. MLH 10/21 |  |  |  | Property Damage |  | Steven Blansett | Struck Water Line |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Steven Blansett | M&P | MDR operator |  | Utility Strike |  | Steven Blansett |  |  |  |  | FALSE | [42 empty] | Puncture of water line with boring machine. | 250 | Steven Blansett | Utility Strike | [20 empty] | 1647576
9080 | Metro Service Center | 2019-10-08 08:30 | An OGE vehicle was traveling westbound on SE 29th when a public vehicle ran a stop sign at SE. 29 and Phillips. The OGE vehicle struck the public vehicle. No injuries were reported. Fleet was contacted and the OGE vehicle was towed. | Level 2 |  | FALSE | Vehicle |  |  |  |  | OGE Energy Corp | Jay Holbrook | 2020-01-06 16:50 | 2019-10-08 13:51 | 2019-10-08 13:51 | 2019-10-22 10:44 | 2019-10-22 08:30 | 2019-10-08 12:43 | 2019-12-06 11:23 |  | 2019-10-30 07:09 | SE 29th and Phillips |  |  | William Young | Reviewed and approved. WCY 1-6-2020 | Enterprise Services |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Jay Holbrook |  | An OGE vehicle was traveling westbound on SE 29th when a public vehicle ran a stop sign at SE. 29 and Phillips. The OGE vehicle struck the public vehicle. No injuries were reported. Fleet was contacted and the OGE vehicle was towed. OGE vehicle number F36-145. Police were contacted and an on-scene investigation was conducted by OKC police department. Collision report attached. |  |  |  | Metro Service Center | FALSE |  | FALSE | IT |  | Orrin Copeland | Jay Holbrook |  | John Grunsted | I have reviewed and discussed with Jay. Approved | John Grunsted |  | Medium | [5 empty] | 6.03 Infrequent performance | [10 empty] | The public driver failed to yield right-of-way to OGE vehicle. | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) |  | Approved, Cody Vinyard | [72 empty] | FALSE |  | Oklahoma City | OGE Vehicle Struck Other Vehicle | Public Driver Failed To Yield | 2019-07-28 19:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
9080 | Metro Service Center | 2019-10-08 08:30 | An OGE vehicle was traveling westbound on SE 29th when a public vehicle ran a stop sign at SE. 29 and Phillips. The OGE vehicle struck the public vehicle. No injuries were reported. Fleet was contacted and the OGE vehicle was towed. | Level 2 |  | FALSE | Vehicle |  |  |  |  | OGE Energy Corp | Jay Holbrook | 2020-01-06 16:50 | 2019-10-08 13:51 | 2019-10-08 13:51 | 2019-10-22 10:44 | 2019-10-22 08:30 | 2019-10-08 12:43 | 2019-12-06 11:23 |  | 2019-10-30 07:09 | SE 29th and Phillips |  |  | William Young | Reviewed and approved. WCY 1-6-2020 | Enterprise Services |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Jay Holbrook |  | An OGE vehicle was traveling westbound on SE 29th when a public vehicle ran a stop sign at SE. 29 and Phillips. The OGE vehicle struck the public vehicle. No injuries were reported. Fleet was contacted and the OGE vehicle was towed. OGE vehicle number F36-145. Police were contacted and an on-scene investigation was conducted by OKC police department. Collision report attached. |  |  |  | Metro Service Center | FALSE |  | FALSE | IT |  | Orrin Copeland | Jay Holbrook |  | John Grunsted | I have reviewed and discussed with Jay. Approved | John Grunsted |  | Medium | [5 empty] | 6.02 Inadequate practice | [10 empty] | The public driver failed to yield right-of-way to OGE vehicle. | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) |  | Approved, Cody Vinyard | [72 empty] | FALSE |  | Oklahoma City | OGE Vehicle Struck Other Vehicle | Public Driver Failed To Yield | 2019-07-28 19:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
9081 | Metro Service Center | 2019-10-08 11:00 | Chemical Weed Control mower operator making a turn cut the turn too short and caught the top of the mower deck on the bottom solar panel. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Shawn Huff | 2019-11-15 16:57 | 2019-10-08 14:32 | 2019-10-08 14:32 | 2019-10-24 09:00 | 2019-10-22 11:00 | 2019-10-08 14:23 | 2019-11-05 10:35 |  | 2019-10-30 14:44 | Covington Solar Farm |  |  | William Young | Reviewed and approved. WCY 11-15-19 | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Shawn Huff |  | Preston was maneuvering his tractor, that was pulling a brush hog mower unit behind it, around a row of solar panels. He cut the corner too sharp and this allowed the mower deck to go under the last solar panel. While doing this the gear box on top of the mower deck was not able to clear the panel and struck it. This resulted in the panel shattering and a repair order created. |  |  |  | Metro Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Shawn Huff | Michael Fox |  | Nicole Rhodes | Reviewed and appropriate actions taken. | Nicole Rhodes |  | Medium |  |  |  | 4.04 Routine, monotony, demand for uneventful vigilance | [12 empty] | Turned too sharply. | 15. Using Equipment Improperly | 1. Struck Against (Running or Bumping Into) |  | "Chemical Weed Control will provide training on the use of the tractor while pulling a brush hog mower deck. Items to focus on is deck clearance, turning radius and what is the potential for lack of focus". Shawn - we need the contractor to send the roster showing he did the training mentioned above. Thank you. J. Looney, 10.18.19 Approved. J. Looney 10.30.19 |  |  |  | Vehicle |  | Shawn Huff | Solar panel was shattered and support bent |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Shawn Huff | Chemical Weed Control | Preston Belt |  | Fixed Equipment |  | Shawn Huff |  |  |  |  | FALSE
9081 | Metro Service Center | 2019-10-08 11:00 | Chemical Weed Control mower operator making a turn cut the turn too short and caught the top of the mower deck on the bottom solar panel. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Shawn Huff | 2019-11-15 16:57 | 2019-10-08 14:32 | 2019-10-08 14:32 | 2019-10-24 09:00 | 2019-10-22 11:00 | 2019-10-08 14:23 | 2019-11-05 10:35 |  | 2019-10-30 14:44 | Covington Solar Farm |  |  | William Young | Reviewed and approved. WCY 11-15-19 | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Shawn Huff |  | Preston was maneuvering his tractor, that was pulling a brush hog mower unit behind it, around a row of solar panels. He cut the corner too sharp and this allowed the mower deck to go under the last solar panel. While doing this the gear box on top of the mower deck was not able to clear the panel and struck it. This resulted in the panel shattering and a repair order created. |  |  |  | Metro Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Shawn Huff | Michael Fox |  | Nicole Rhodes | Reviewed and appropriate actions taken. | Nicole Rhodes |  | Medium |  |  |  | 4.04 Routine, monotony, demand for uneventful vigilance | [12 empty] | Turned too sharply. | 15. Using Equipment Improperly | 1. Struck Against (Running or Bumping Into) |  | "Chemical Weed Control will provide training on the use of the tractor while pulling a brush hog mower deck. Items to focus on is deck clearance, turning radius and what is the potential for lack of focus". Shawn - we need the contractor to send the roster showing he did the training mentioned above. Thank you. J. Looney, 10.18.19 Approved. J. Looney 10.30.19 |  |  |  | Property Damage |  | Shawn Huff | Solar panel was shattered and support bent |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Shawn Huff | Chemical Weed Control | Preston Belt |  | Fixed Equipment |  | Shawn Huff |  |  |  |  | FALSE
9082 | Redbud Plant | 2019-10-08 09:00 | Contractor failed to sign in/out of Non-Permit Confined Space prior to entry and exit. No injuries. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Grant Craft | 2019-11-13 08:50 | 2019-10-08 14:36 | 2019-10-08 14:36 | 2019-10-15 12:00 | 2019-10-22 08:00 | 2019-10-08 14:05 | 2019-11-06 13:53 |  |  | Redbud Unit #1 HRSG Gas Path |  |  | Guillermo Sarmiento | Approve of the investigation, findings, and corrective actions. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Grant Craft |  | During conversation with HRST Contractor, it was discovered that he had forgotten to sign onto the Non permit confined space for #1 HRSG. The contractor knew he was supposed to sign on the permit but the area where the permit was located was congested with scaffold builders and Danger Barricaded at the time he intended to enter the space. He stated that he got distracted by the other work and forgot to sign on when he entered the space. |  |  |  | Redbud Plant | FALSE |  | TRUE | Maintenance |  | Grant Craft | Thomas Ward |  | Robert Doupe | RDD Apoproved | Robert Doupe |  | Low |  |  |  |  | 5.05 Misunderstood directions |  |  |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | The contractor knew he was supposed to sign on the permit but the area where the permit was located was congested with scaffold builders and Danger Barricaded at the time he intended to enter the space. He stated that he got distracted by the other work and forgot to sign on when he entered the space. | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Grant Craft | [5 empty] | 9. Abnormal Operation | Grant Craft | HRST | Lester Stanley |  |  |  | Shea Timothy | [71 empty] | 18829308
9083 | Metro Service Center | 2019-09-30 14:00 | First Aid Member bent down to hook chain on reel stand bar and felt pain in lower back when straightening up. | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Jimmie Walters | 2019-10-09 13:12 | 2019-10-09 12:16 | 2019-10-09 12:16 | 2019-10-09 12:20 | 2019-10-14 14:00 | 2019-10-09 12:09 |  |  |  | Calumet Oklahoma transmission right of way Maple RD. project |  |  | Terry Hackett | Member is feeling okay now. Followed up with member on industrial athlete resources, general first aid, and proper form. This is a low likelihood and low consequence first aid. | T&D Ops |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | [5 empty] | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Brad Webb | Jimmie Walters |  |  |  | Gary Lassley |  | Low | [45 empty] | FALSE |  |  | 2010-09-13 | 1970-07-09 |  | 2019-09-30 07:00 | 0 | 0 |  | FALSE |  | Bending over to hook up lifting chain |  | FALSE | Brad Webb |  | First Aid | Brad Webb |  |  |  |  | Sprain/Strain |  | FALSE |  | Transmission Lineman Apprentice | Back |  | Lower |  | Jimmie Walters |  |  | 9/30/2019 7:00:00 AM |  | FALSE |  |  | N/A
9084 | Horseshoe Lake Power Plant | 2019-10-09 14:00 | Truck driver was picking up a piece of rental equipment for a contractor. After he loaded the equipment, he drove to the corner and made a U-turn. During the turn, he damaged approx. 30ft of fence and a gate. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Timothy Fisher | 2019-11-13 08:59 | 2019-10-09 15:07 | 2019-10-09 15:07 | 2019-10-29 10:15 | 2019-10-23 13:00 | 2019-10-09 14:57 | 2019-10-29 10:57 |  |  | Horseshoe Lake Power Plant Units 9 and 10 Northeast corner |  |  | Guillermo Sarmiento | Added United rentals report to the detailed description. Have reviewed report and approve. 11/12/19 approve of the contents and corrective actions. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Timothy Fisher |  | Truck driver was picking up a piece of rental equipment for a contractor. After he loaded the equipment, he drove to the corner and made a U-turn. During the turn, he damaged approx. 30ft of fence and a gate. United rental report is as follows: The United Rentals driver struck a fence while picking up a piece of equipment from the OGE Horseshoe lake jobsite. Driver was parked on the outside section of fencing at customers yard but next to their fence while picking up a piece of United Rental equipment. After the equipment was loaded and the driver was pulling away his tail swung and hit the chain link fence. He struck a pole and caused damage to the pole and 2 sections of fence including a gate. The driver did not know he had struck the fence until one of the OGE employees flagged him down and told him he had hit the fence. The driver did call the branch to inform us he had struck the fence. He then told the branch manager he was unaware he had struck the fence with his truck tail until someone had flagged him down. He was compliant with the customer requests to stay until they had taken pictures and done a quick look at the fence and truck. Corrective Actions: The driver should have assessed the environment and obstacles to avoid hitting the fence. His turn radius was tight to avoid hitting the fence. Driver could have pulled up and backed into the open gate area leaving more room to make the turn. There were also other contractors on sight that could have been used to help spot his truck. Driver has been tasked with completing a Decision Driving class. This is entails an online class and also a driving section of the class where the employee must around with a trained instructor for several hours. This will be completed in by Nov 12. Driver has also retaken our elearning class, United for Safety. This is a class required for all United Rentals employees that governs safety awareness on jobsite and at the yard. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Maintenance |  | Timothy Fisher | Timothy Fisher |  | Daniel Perry | Added United Rentals investigation document. We need to add a corrective action to ensure United Rentals fixes the fence. We need to check with Supply Chain about filling out a SCAR. I have reviewed the updated investigation and I approve. | Daniel Perry |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Truck driver was picking up a piece of rental equipment for a contractor. After he loaded the equipment, he drove to the corner and made a U-turn. During the turn, he damaged approx. 30ft of fence and a gate. | 11. Improper Position for Task | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Timothy Fisher | Damaged Fence |  |  |  |  | 2. Struck By (Hit By Moving Object) | Timothy Fisher | Travis Simmons | United Rental |  | Fixed Equipment |  | Timothy Fisher |  |  |  |  | FALSE
9085 | Redbud Plant | 2019-10-09 19:00 | Redbud Operations night shift performed shiftly confined space atmospheric monitoring and found high CO levels in HRSG Gas Path during external plasma cutting on HRSG. Work was stopped and space was reevaluated after 45 minutes and air quality was satisfactory. No injuries occurred. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Grant Craft | 2019-11-16 11:21 | 2019-10-10 08:54 | 2019-10-10 08:54 | 2019-10-19 09:40 | 2019-10-23 18:00 | 2019-10-10 08:15 | 2019-11-06 14:01 |  | 2019-10-29 07:49 | Redbud Unit #1 HRSG Gas Path |  |  | Jesse Murray | I Approve. Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Grant Craft |  | On the night in question, the crew Shift Supervisor had asked operations member to perform the atmospheric conditions “sniffing” for the requested areas. Upon arriving at the S1 door of Unit 1 HRSG, member witnessed a Bremco employee inside the door of S2 on Unit 1 HRSG. The Bremco employee had just started grinding shortly after member arrival. There was an attendant stationed outside. The member also witnessed another employee outside door S3 of Unit 1 HRSG operating a plasma cutter. Once Operations member began atmospheric testing (sniffing) door S1 on Unit 1 HRSG, the hand held monitor immediately began to spike on Carbon Monoxide. Operations member immediately informed the Bremco employees inside the HRSG to exit the space. The Bremco foreman was close by and was informed that all inside work was halted. Verification was made that that there were no other personnel inside the HRSG. Operations member then verified all entrants had signed off of the day shift confined space entry form. Operations member then radioed the SS advising that there was an issue identified while performing the confined space testing. Upon the SS arrival, the hand held monitor had not zeroed out. The SS and Operations member retrieved an additional hand held monitor in order to ensure consistency in atmospheric testing. Both monitors showed approximately identical readings for Carbon Monoxide (CO). Levels detected were as high as 161 ppm inside the HRS testing doors S1, S2, N1, and N2. The elevated walkways just outside the HRSG were also “sniffed”. CO readings where approximately 25 ppm to 40 ppm. The ground level areas where also “sniffed” and showed CO readings from 8ppm to about 20 ppm. The Oxygen levels, however, never dropped below 20.9%. The SS then walked around Unit 1 HRSG and verified that no external engines where producing exhaust fumes i.e. welders, light plants, etc. Work was shut down for the rest of the day until verification of no atmospheric hazard was made by performing periodic air monitoring. While the space was vacated and allowed to ventilate, operations crew and safety coordinator discussed potential causes. Here are some key findings: 1. Contractors did perform a JSA and were wearing all required PPE while performing tasks inside the HRSG. 2. All applicable permits were filled out and in place. 3. Monitors were calibrated and fresh air tested and were found to be in good operation prior to testing atmosphere. 4. Interference was thought to be a possibility due to high CO and generally stable levels of Oxygen. a. It was thought that products produced by plasma cutting or gases used to plasma cutting may have contributed to the monitor readings. b. Plasma cutter was using only compressed air (plant air); no inert gas was being utilized. 5. OSHA Permissible Exposure Limit (PEL) is 50ppm TWA; IDLH is 1200ppm. Observed levels were 161ppm max. 6. Levels where at 0ppm CO and 20.9% Oxygen everytime monitoring was performed post incident. 7. Bremco employees performing hot work were not wearing personal monitors while performing hot work in the space. 8. While other work, besides hot work, was being performed in the space, it did not contribute or cause the high levels of CO. |  |  |  | Redbud Plant | FALSE |  | TRUE | Operations |  | Grant Craft | Thomas Ward |  | Robert Doupe | Approved | Robert Doupe |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [8 empty] | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Plasma cutting caused atmospheric issue in Confined Space | 17. Failure to Identify Hazard, Risk | 10. Product Contamination |  | Reviewed incident, Discussed some changes with Grant Craft. Added more corrective action Items. We agreed on all the changes made and the way report is currently. |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Grant Craft | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Grant Craft | BREMCO | Dave Hockenbury |  |  |  | Scott Carroll | [71 empty] | 9572235
9086 | Redbud Plant | 2019-10-10 11:00 | Contractor cutting with torch on exterior of HRSG caused scaffold boards to smolder. Scaffold was covered with fire blanket but slag got through and ignited the scaffold boards underneath. The wood was extinguished with a bucket of water. No injuries or property damage occurred. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Grant Craft | 2019-11-13 08:45 | 2019-10-10 11:20 | 2019-10-10 11:20 | 2019-10-16 09:19 | 2019-10-24 10:00 | 2019-10-10 10:57 | 2019-11-06 13:55 |  |  | Redbud Unit #1 HRSG Exterior South Side |  |  | Guillermo Sarmiento | Reviewed and agree with the investigation and action items. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | TRUE |  | FALSE | FALSE | Grant Craft |  | Welding contractor was cutting with a torch on the outside of the HRSG for the installation of Duct Burner view ports. They were working on a scaffold approximately 10' off the ground which was built with metal planks but had short, custom cut scaffold boards placed on top to close a gap between the scaffold planks and the HRSG to improve fall/dropped object protection. The welders had covered the boards with fire proof blanket but slag got through the blanket and appeared to ignite the boards from underneath, in between the metal planks and wood. The contractors used a short burst of a fire extinguisher and broke the scaffold boards away to separate the smoldering wood. Operations obtained a bucket of water to fully extinguish the smoldering wood. The scaffold was then modified to remove the wood covering. The Welding contractor was following all proper procedures by the following 1-They had a Hot Work Permit 2-They were properly using a fire watch |  |  |  | Redbud Plant | FALSE |  | TRUE | Maintenance |  | Grant Craft | Thomas Ward |  | Robert Doupe | RDD Approved | Robert Doupe |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Scaffold Boards ignited by performing Hot Work | 26. Fire & Explosion Hazards | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Property Damage |  | Grant Craft | [5 empty] | 12. Equipment Failure | Grant Craft | Bremco | Dave Hockenbury |  |  |  | Scott Carroll | [71 empty] | 9572235
9086 | Redbud Plant | 2019-10-10 11:00 | Contractor cutting with torch on exterior of HRSG caused scaffold boards to smolder. Scaffold was covered with fire blanket but slag got through and ignited the scaffold boards underneath. The wood was extinguished with a bucket of water. No injuries or property damage occurred. | Level 1 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Grant Craft | 2019-11-13 08:45 | 2019-10-10 11:20 | 2019-10-10 11:20 | 2019-10-16 09:19 | 2019-10-24 10:00 | 2019-10-10 10:57 | 2019-11-06 13:55 |  |  | Redbud Unit #1 HRSG Exterior South Side |  |  | Guillermo Sarmiento | Reviewed and agree with the investigation and action items. | Power Supply |  | Level 1 | Property Damage |  | TRUE | FALSE | TRUE |  | FALSE | FALSE | Grant Craft |  | Welding contractor was cutting with a torch on the outside of the HRSG for the installation of Duct Burner view ports. They were working on a scaffold approximately 10' off the ground which was built with metal planks but had short, custom cut scaffold boards placed on top to close a gap between the scaffold planks and the HRSG to improve fall/dropped object protection. The welders had covered the boards with fire proof blanket but slag got through the blanket and appeared to ignite the boards from underneath, in between the metal planks and wood. The contractors used a short burst of a fire extinguisher and broke the scaffold boards away to separate the smoldering wood. Operations obtained a bucket of water to fully extinguish the smoldering wood. The scaffold was then modified to remove the wood covering. The Welding contractor was following all proper procedures by the following 1-They had a Hot Work Permit 2-They were properly using a fire watch |  |  |  | Redbud Plant | FALSE |  | TRUE | Maintenance |  | Grant Craft | Thomas Ward |  | Robert Doupe | RDD Approved | Robert Doupe |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Scaffold Boards ignited by performing Hot Work | 26. Fire & Explosion Hazards | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Property Damage |  | Grant Craft | [5 empty] | 12. Equipment Failure | Grant Craft | Bremco | Dave Hockenbury |  |  |  | Scott Carroll | [71 empty] | 9572235
9087 | Shawnee Service Center | 2019-10-09 12:00 | Member was driving a maintenance van approximately 45 mph when he attempted to miss an unknown object in the road. He managed to avoid the object but made contact with the curb with right rear dual wheel. The impact bent the wheel and deflated the tire. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Dean Beaudoin | 2019-10-21 14:25 | 2019-10-10 14:03 | 2019-10-10 14:03 | 2019-10-10 14:08 | 2019-10-23 12:00 | 2019-10-09 13:30 |  |  |  | SE 15th and Eastern Oklahoma City, OK |  |  | Cody Magby | approved cm | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | [6 empty] | Shawnee Service Center | FALSE |  | FALSE | PD Operations Services |  | Martin Visnieski | Dean Beaudoin |  |  |  | James Hutchison |  | Low | [93 empty] | FALSE |  | Oklahoma City | Other | Unknown | 2007-03-04 18:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
9088 | Muskogee Power Plant | 2019-10-10 15:12 | 9th level east side of "B" Air PreHeater. Plastic bag with old parts fell off of grease filler pump while coiling air hose to one floor below (level 8) and was recovered. Old fill nozzle of grease system pump, a SS tube about 8 inches long with fittings on each end was in the bag but fell out and fell further. The objects fell through the gap between the grating toeboard and the transite siding to the right of the door 9th level. Member searched all levels for object which was not found. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Supply |  | 2019-11-05 16:39 | 2019-10-10 15:59 | 2019-10-10 16:06 | 2019-11-05 16:37 | 2019-10-24 15:12 | 2019-10-10 15:59 | 2019-11-05 16:38 |  |  | MK06 - Level 9 east side 6B APH walkway near door to boiler. |  |  | Chrysty Dorsey | Please see workflow comments for reason being returned. CD Update: Approved. CD | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Patrick Coleman |  | Member had placed a small plastic bag containing parts a contractor had removed and replaced with new in the new Air Pre-Heater upper guide bearing on MK06 both the A and B sides. Member was coiling an air hose the contractor had used to power the fill cart pump to fill the grease reservoirs. The plastic bag was placed on the fill cart to keep it from falling. When moving the fill cart the last few inches out of the walkway, the cart bounced on the grating slightly causing the plactic bag with the parts to slide off of the fill cart. The bag fell from the 9th level to the 8th level of the north exterior east side of unit 6 boiler structure. One of the pieces of tubing in the bag fell out of the bag and through the grating and could be heard bouncing down the structure. The area was not barricaded as there was not scheduled work to be done there with the possibility of tools or material falling. The piece of tubing that fell was approximately 9 inches long and weighted less than 10 oz. The member looked for the lost tubing without success. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Power Supply Services |  |  |  |  | Patrick Coleman | Patrick Coleman | Patrick Coleman |  | Low |  |  |  |  | 5.06 Lack of situational awareness |  | 7.06 Improper attempt to save time or effort |  | 9.06 Inadequate work planning or programming | [7 empty] | Parts bag placed on cart that was to be moved. As cart was moved, the bag of parts fell off. | 09. Improper Placement | 2. Struck By (Hit By Moving Object)
9089 | Sooner Power Plant | 2019-10-11 09:20 | Contractor (Badger) was hydro excavating to locate utilities for drilled pier at the Northeast corner of 10 &11 conveyor Tower A. The Contractor was standing near the edge of the approximately two foot wide, three foot deep excavation when the side sloughed off causing contractor to fall into excavation. Contactor landed on his feet and was uninjured. | Level 2 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services | Ashley Harris | 2019-12-16 07:17 | 2019-10-11 14:11 | 2019-10-11 14:11 | 2019-11-19 14:46 | 2019-10-25 09:20 | 2019-10-11 14:03 | 2019-11-26 09:31 |  | 2019-11-25 16:17 | Sooner Power Plant- Northeast corner of 10 & 11 conveyor Tower A |  |  | William Young | Returned to investigation stage for CA revisions. WCY 11-15-19 Reviewed workflow it appears that revisions have been made to CA to meet with Badger and require fall restraint where where similar risks exist. However, there is no way to track "when they will be back on site and ensure that we have the follow-up meeting. A meeting needs to be held with Badger to discuss and close out CA. I will review with Mark Huddleston before returning to investigation. WCY 12-9-2019. Reviewed with Mark 12-16-2019. Approved based on revised CA. WCY. | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Ashley Harris |  | Contractor (Badger) was hydro excavating to locate utilities for drilled pier at the Northeast corner of 10 &11 conveyor Tower A. The Contractor was standing near the edge of the approximately two foot wide, three foot deep excavation when the side sloughed off causing contractor to fall into excavation. Contactor landed on his feet and was uninjured. Keith Filley was excavating for pipe exposure next to previously excavated pier hole. Some of the gravel backfill flowed into the new excavation which created a void in the previous pier. Keith stepped in the middle of excavations to show where pipe was located. At this point more backfill flowed into the new excavation causing him to fall into the previous excavation. Keith landed on his feet in 3 foot excavation. I asked about fall prevention. The contractors then started using body harness and retractable lanyard because excavation would be well over 4 feet deep when finished. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | UTS - Capital Projects |  | Richard Wood | Ashley Harris |  | Robert Weaver | Agree with the above. | Robert Weaver |  | Medium | [9 empty] | 10.06 Inadequate or improper controls | [5 empty] | 16.06 Inadequate communication methods | Contractor was standing on edge showing location of pipe between two excavations when the backfill started flowing into excavation and caused him to fall and land on his feet in 3 foot excavation. | 11. Improper Position for Task | 3. Fall from Elevation to Lower Level |  | corrective action 8156 is not a CA. Please review and make necessary changes. MLH 10/28/19 No additional comments MLH 11/4 |  |  |  | Injury / Illness |  | Ashley Harris | [5 empty] | 4. Fall on Same Level (Slip and Fall, Trip Over) | Richard Wood | Wolf Point Engineers and Contractors | Keith Filley |  |  |  | Ashley Harris
9090 | Muskogee Power Plant | 2019-10-12 12:00 | The washer retainer and the stack of Belleville washers vibrated off governor valve 6 actuator falling and landing on the control wiring conduit and EH lines. A few of the washers fell on the turbine deck next to the governor valve. There is a small opening that the washers potentially could have fallen below to the mezzanine deck. There was no one in the area and this is low traffic area. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Joel Leavell | 2019-12-05 10:15 | 2019-10-12 12:59 | 2019-10-12 12:59 | 2019-11-12 01:38 | 2019-10-26 12:00 | 2019-10-12 12:31 | 2019-11-25 07:58 |  | 2019-11-15 14:34 | Muskogee PP Unit 5 Turbine deck governor valve number 6 |  |  | Jesse Murray | I Approve. Jesse Murray 12/5/19 | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Joel Leavell |  | Saturday October 12, 2019 one of the Operations interns was making rounds on the turbine deck. The Operations intern took a picture asked Shift Supervisor regarding Muskogee 5 Main Turbine governor valve #6. Operations intern asked about the missing Belleville washers. Upon investigation the Belleville washer retainer and washers appeared to vibrate off the governor valve. There are no witnesses observing the event directly. The washer retainer and the washers were all recovered in the immediate area. There was potential for the washers and or washer retainer to fall to the level below. The washer retainer was caught by the control lines for governor valves (see pictures). The fasteners were not recovered. Notification 446186 was written to re-install washers. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Damian Duran | Joel Leavell |  | Jonathan Stogsdill | Reviewed Steve Crary |  |  | Medium | [14 empty] | 15.03 Inadequate inspection and/or monitoring |  | The two fasteners that hold the washer retainer came out allowing the washer retainer and washers to slide off the mounting spot and fall. | 23. Defective Tools, Equipment or Materials | 3. Fall from Elevation to Lower Level |  | reviewed Bob Wright | [90 empty] | 9591875
9091 | Metro Service Center | 2019-10-14 12:30 | While opening gang operated switchgear, the switchgear failed and an arc occurred. No injuries | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Delivery | Kenny La Ferney | 2019-10-30 11:29 | 2019-10-15 08:36 | 2019-10-15 08:36 | 2019-10-15 09:58 | 2019-10-28 12:30 | 2019-10-15 08:26 | 2019-10-28 18:21 |  | 2019-10-23 14:58 | Tinker AFB |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Kenny La Ferney |  | Members were performing switching order m1640 to switch tinker 5 back after the tinker 5 outage over the weekend. At step 125b opening the normal open switch 249620 switch #2. Upon opening the switch a flash occurred and operated the breaker at the sub. Work was stopped and another tailboard was conducted, equipment was tested dead and grounded. Facts Ascertained: - After incident occurred system lab tested the cable (DC Thumper) and found B Phase insulator was arcing - Found porcelain insulator broke on B Phase - Members were wearing FR/Safety Glasses/Hard hats/EH Safety Toed Boot -Switchman was wearing Class 2 rubber gloves -Back up switchman had class 2 rubber gloves readily available on his hip - Shirts were tucked in - Switchman has been through distribution switching training - Door was open on the switch gear - The potential equipment failure and hazards were identified during the tailboard and implemented - 12.5KV phase to phase. - Fire extinguisher was used after the fact to extinguish remaining flame inside the switch gear - One member stated he felt heat from the arc and thought his leg may have sustained a minor burn. After evaluation it was determined no burns were present. |  |  |  | Metro Service Center | FALSE |  | TRUE | Construction Services |  | Dale Allen | Kenny La Ferney |  | Gary Lassley | Supervisor to share the incident and how the simple risk assessment, Safety procedures, tailboard, and processes protected all member from injury. Members did everything in their control to prevent an injury. | Gary Lassley |  | Medium | [14 empty] | 15.05 Inadequate maintenance |  | Equipment failed due to broke insulator on B Phase | 23. Defective Tools, Equipment or Materials | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Reviewed/Approved TMH | [90 empty] | 7965137
9092 | Sooner Power Plant | 2019-10-14 15:00 | Contract Member was observed working off of elevated incomplete scaffolding without being tied off. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Marc Trammell | 2019-12-05 10:00 | 2019-10-15 09:34 | 2019-10-15 09:34 | 2019-11-12 11:14 | 2019-10-28 15:00 | 2019-10-14 16:30 | 2019-11-12 15:55 |  | 2019-11-12 15:05 | Sooner Plant Unit #1 AQCS Building inside, near A Train Medium Pressure Fluidizing Blowers, on elevated scaffolding. |  |  | Jesse Murray | Approved. Jesse Murray 12/5/19 | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marc Trammell |  | Sooner Plant, Unit #1 AQCS Building inside, Northeast corner, A Train Medium Pressure Fluidizing Blowers, Work on elevated scaffolding for monorail/hoist installation. At approximately 2:35 PM on Monday October 14th, 2019 an OGE Team was conducting a safety audit inside Unit #1 AQCS Building. A Zachry contract member was observed from an above adjacent level working/walking and exiting via access ladder on an overhead scaffolding (approx. 20 feet high) that did not have a complete guard rail or toe board system. The Zachry member was first observed working in his tool bag on an area of the scaffolding that did have adjacent guard railing and toe board. He was then seen walking approx. 8 feet to the access ladder area of the scaffolding to lower his tool bag down to the ground via a rope. He then proceeded down the access ladder to the ground. The access ladder area did not have complete guard railing or toe boards, and the Zachry member was not tied off. A subsequent conversation on the observed incident was had with the Zachry member's supervision. Feedback from the Zachry member's internal conversation with his supervision was that he admitted that he was not tied off in the ladder access area. He said he had previously unhooked his harness while working in another area of the scaffold, and simply neglected to reattach it while traveling over to lower his tool bag to the ground and exit the scaffold. Conversation with the OGE member who observed the incident fed back that he did not see the Zachry member tied off at any time on the scaffolding. Zachry member from the incident was wearing a personnel tie off harness. Conversation with Zachry supervision fed back that their member was tied off at one point working on the scaffold, but untied to go over the ladder access area of the scaffold. Conversation with Zachry supervision fed back that they would typically use a personnel tie off beam strap ("cheater") in this situation to tie off to approved existing structure. Investigation of the scaffold showed that due to what it was built around and to access rendered it not having complete guard railing and toe board. The original scaffold tag from initial erection on October 8th, 2019 denoted guard railing and toe boards missing and 100% tie off required. Zachry member had fall protection training upon initial hire and it was renewed annually after. Corrective action driven by Zachry management decision was to terminate the member involved in the incident from employment for 30 days. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Engineering & Planning |  | Marc Trammell | Marc Trammell |  | Donald Wyckoff | I have reviewed the revised incident report provided by Zachry that followed their reporting process. I approve of action items. | Donald Wyckoff |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Contractor failed to realize he was not tied off while working on a scaffold that required it. | 16. Failure to Follow Procedure, Policy, Practice | 3. Fall from Elevation to Lower Level |  | Approved by Brady Sowell on 10/31 |  |  |  | Injury / Illness |  | Marc Trammell | [5 empty] | 3. Fall from Elevation to Lower Level | Marc Trammell | Zachry Industrial | Casey Hayden |  |  |  | Marc Trammell | [71 empty] | 615684
9093 | Metro Service Center | 2019-10-14 16:00 | Contract employee fell from approximately 25' while descending transmission tower. | Level 3 |  | FALSE | Contractor | Jerrod Moser | William Young | Investigate incident, establish causal factors and determine corrective actions. WCY 10-29-19 | 2019-10-29 13:32 | OG&E Corp Services | Stewart Smith | 2020-02-11 08:33 | 2019-10-15 16:00 | 2019-10-15 16:00 | 2020-01-30 12:43 | 2019-10-28 15:00 | 2019-10-15 15:52 | 2020-01-30 14:52 | 2020-02-05 15:23 | 2020-01-30 12:44 | Spiro, Oklahoma |  |  | Jerrod Moser | Close per J. Moser - bjt | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On the afternoon of October 14, 2019, Jody O’Neal a Tower Technician for Tower Inspection, Inc. (TII) was the last man on the tower finishing up his day’s work and descending the high voltage transmission tower near Spiro, Oklahoma. At approximately 4:10 PM, Mr. O’Neal fell from an estimated height of 25 feet while climbing down a fixed ladder where he sustained multiple injuries to his head, neck, face and left arm. Although Mr. O’Neal was fully equipped with a full body harness and safety climb sleeve, the fact that he fell indicates he was not tied off to the safety climb system at the time of the accident. No one saw Mr. O’Neal fall. Tower members in the vicinity of the fall were inspected and there was no evidence of impact by Mr. O’Neal to any members. The assumption is that all injuries were a result of impact from the ground. | Stewart Smith | William Young |  | Metro Service Center | TRUE |  | FALSE | UTS - Capital Projects |  | Stewart Smith | Stewart Smith |  | Christopher Lelak | No comments - CBL 01/30/2020 | Christopher Lelak | William Young | High |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | At approximately 4:10 PM, Mr. O’Neal fell from an estimated height of 25 feet while climbing down a fixed ladder where he sustained multiple injuries to his head, neck, face and left arm. | 03. Failure to Secure | 3. Fall from Elevation to Lower Level | Reviewed TII incident report and corrective actions. Approved, WCY 2/5/2020 | No additional comments. MLH 1/30/2020 |  |  |  | Injury / Illness |  | Stewart Smith |  | Broke arm. Damaged Neck vertebrae. | FALSE | 43753.7083 | 43753.6875 | 3. Fall from Elevation to Lower Level | Stewart Smith | Tower Inspection Inc. | Jody O'Neal | Fracture |  | Arm | Stewart Smith | Left | TRUE | Helicopter
9093 | Metro Service Center | 2019-10-14 16:00 | Contract employee fell from approximately 25' while descending transmission tower. | Level 3 |  | FALSE | Contractor | Jerrod Moser | William Young | Investigate incident, establish causal factors and determine corrective actions. WCY 10-29-19 | 2019-10-29 13:32 | OG&E Corp Services | Stewart Smith | 2020-02-11 08:33 | 2019-10-15 16:00 | 2019-10-15 16:00 | 2020-01-30 12:43 | 2019-10-28 15:00 | 2019-10-15 15:52 | 2020-01-30 14:52 | 2020-02-05 15:23 | 2020-01-30 12:44 | Spiro, Oklahoma |  |  | Jerrod Moser | Close per J. Moser - bjt | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Marcus Huddleston |  | On the afternoon of October 14, 2019, Jody O’Neal a Tower Technician for Tower Inspection, Inc. (TII) was the last man on the tower finishing up his day’s work and descending the high voltage transmission tower near Spiro, Oklahoma. At approximately 4:10 PM, Mr. O’Neal fell from an estimated height of 25 feet while climbing down a fixed ladder where he sustained multiple injuries to his head, neck, face and left arm. Although Mr. O’Neal was fully equipped with a full body harness and safety climb sleeve, the fact that he fell indicates he was not tied off to the safety climb system at the time of the accident. No one saw Mr. O’Neal fall. Tower members in the vicinity of the fall were inspected and there was no evidence of impact by Mr. O’Neal to any members. The assumption is that all injuries were a result of impact from the ground. | Marcus Huddleston | William Young |  | Metro Service Center | TRUE |  | FALSE | UTS - Capital Projects |  | Stewart Smith | Stewart Smith |  | Christopher Lelak | No comments - CBL 01/30/2020 | Christopher Lelak | William Young | High |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | At approximately 4:10 PM, Mr. O’Neal fell from an estimated height of 25 feet while climbing down a fixed ladder where he sustained multiple injuries to his head, neck, face and left arm. | 03. Failure to Secure | 3. Fall from Elevation to Lower Level | Reviewed TII incident report and corrective actions. Approved, WCY 2/5/2020 | No additional comments. MLH 1/30/2020 |  |  |  | Injury / Illness |  | Stewart Smith |  | Broke arm. Damaged Neck vertebrae. | FALSE | 43753.7083 | 43753.6875 | 3. Fall from Elevation to Lower Level | Stewart Smith | Tower Inspection Inc. | Jody O'Neal | Fracture |  | Arm | Stewart Smith | Left | TRUE | Helicopter
9094 | Northeast District Service Cen | 2019-10-12 09:00 | Service crew was trouble shooting a possible bad order 3 phase primary. The crew was performing switching to isolate cable between cubicle 24943 and transformer 42484. While opening switch in the cubicle one of the porcelain insulators broke on the load side that hold the switch gear. Switch was held up by cable no flash occurred the other crew member opened riser to de-energize the cable. | Level 3 |  | TRUE | Member Injury | Andrea Dennis | Lindle Coleman | reviewed with Luke | 2019-10-30 14:59 | Power Delivery | Donald Melson | 2019-11-07 12:42 | 2019-10-16 09:40 | 2019-10-16 09:40 | 2019-10-30 15:02 | 2019-10-26 09:00 | 2019-10-12 09:06 | 2019-10-31 13:01 | 2019-10-31 13:46 | 2019-10-30 14:07 | E. 151st St. & S Grant St. in Bixby |  |  | Andrea Dennis | I approve. | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Randell Gilbert |  | Older piece of equipment that is no longer used for new installations. Insulator broke from age of equipment. | Donald Melson | Randell Gilbert |  | Northeast District Service Cen | FALSE |  | TRUE | Construction Services |  | Joshua McKinney | Donald Melson |  | Michael Fox | We have no way really to know that this equipment style may fail more than others. I think we just need to reiterate that we use all PPE before unlocking the cabinet and remain on until job task is compete and cabinet is locked back. | Michael Fox | Lindle Coleman | High | [14 empty] | 15.02 Improper extension of service life |  | Bottom insulator broke while isolating cubicle. | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure | approved | Good communication, thanks for reporting.
9094 | Northeast District Service Cen | 2019-10-12 09:00 | Service crew was trouble shooting a possible bad order 3 phase primary. The crew was performing switching to isolate cable between cubicle 24943 and transformer 42484. While opening switch in the cubicle one of the porcelain insulators broke on the load side that hold the switch gear. Switch was held up by cable no flash occurred the other crew member opened riser to de-energize the cable. | Level 3 |  | TRUE | Member Injury | Andrea Dennis | Lindle Coleman | reviewed with Luke | 2019-10-30 14:59 | Power Delivery | Donald Melson | 2019-11-07 12:42 | 2019-10-16 09:40 | 2019-10-16 09:40 | 2019-10-30 15:02 | 2019-10-26 09:00 | 2019-10-12 09:06 | 2019-10-31 13:01 | 2019-10-31 13:46 | 2019-10-30 14:07 | E. 151st St. & S Grant St. in Bixby |  |  | Andrea Dennis | I approve. | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Randell Gilbert |  | Older piece of equipment that is no longer used for new installations. Insulator broke from age of equipment. | Hannah Everett | Randell Gilbert |  | Northeast District Service Cen | FALSE |  | TRUE | Construction Services |  | Joshua McKinney | Donald Melson |  | Michael Fox | We have no way really to know that this equipment style may fail more than others. I think we just need to reiterate that we use all PPE before unlocking the cabinet and remain on until job task is compete and cabinet is locked back. | Michael Fox | Lindle Coleman | High | [14 empty] | 15.02 Improper extension of service life |  | Bottom insulator broke while isolating cubicle. | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure | approved | Good communication, thanks for reporting.
9095 | North Service Center | 2019-10-09 09:30 | While waiting to turn left at stop light, public vehicle towing trailer turned too sharply in front of company vehicle. After verifying no one had pulled up behind company vehicle, company vehicle backed up to avoid collision. | Level 1 |  | TRUE | Vehicle |  |  |  |  | Power Delivery | Mark Loveless | 2019-10-22 07:39 | 2019-10-16 14:27 | 2019-10-16 14:27 | 2019-10-16 14:41 | 2019-10-23 09:30 | 2019-10-16 14:17 | 2019-10-17 09:45 |  |  | Intersection of Hudiburg Dr and Tinker Diagonal |  |  | Luke Kennedy | Good close call reporting | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Mark Loveless |  | While waiting to turn left at stop light, public vehicle towing trailer turned too sharply in front of company vehicle. After verifying no one had pulled up behind company vehicle, company vehicle backed up to avoid collision. |  |  |  | North Service Center | FALSE |  | TRUE | Distribution Eng & Tech Services |  | Kyler Hixson | Mark Loveless |  | Ronald Griffin | I appreciate this close call being reported. | Ronald Griffin |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Public drive inattentive to turning radius. | 19. Failure to React, Correct | 2. Struck By (Hit By Moving Object)
9096 | North Service Center | 2019-10-09 10:00 | While turning left on wet street rear wheels lost traction and vehicle spun 270 degrees without striking public vehicle facing east bound. | Level 1 |  | TRUE | Vehicle |  |  |  |  | Power Delivery | Mark Loveless | 2019-10-22 07:38 | 2019-10-16 14:58 | 2019-10-16 14:58 | 2019-10-16 15:07 | 2019-10-23 09:00 | 2019-10-16 14:51 | 2019-10-17 09:40 |  |  | North bound Industrial at SE 29th Street |  |  | Luke Kennedy | Good close call reporting | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Mark Loveless |  | 2. At approximately 10:00am on Wednesday October 9th, we were driving north on Industrial Blvd after having exited I-40. Waiting to turn left onto SE 29th ST, heading west. It had been sprinkling and the ground was wet. When the light turned green and allowed us to turn left, we proceeded into the intersection at a moderate rate. Halfway through the turn, the rear wheels of the truck lost traction, sending us into a spin. We spun 270 degrees, and stopped. We were feet away from an East bound vehicle, and also facing East. Upon returning to the office, the tires were inspected. The two rear wheels and passenger front wheel had tread measured to past the top of Lincoln’s head on a penny, but the front driver’s side tire measures nearly halfway up the penny. According to the Manufacturing date, the three worn tires were from June of 2015 and showed signs of dry rot while the front drivers side tire was from January 2015 but is in better condition. Could not determine whether the tire condition attributed to the loss of traction. |  |  |  | North Service Center | FALSE |  | TRUE | Distribution Eng & Tech Services |  | Kyler Hixson | Mark Loveless |  | Ronald Griffin | I appreciate this close call being reported. | Ronald Griffin |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Executed turn too fast for wet road conditions. | 39. Road Conditions | 1. Struck Against (Running or Bumping Into)
9097 | Horseshoe Lake Power Plant | 2019-10-16 15:30 | A worker was torqueing nuts in a sequence on the LP Cylinder #2, moving back and forth across the cylinder. When she attempted to move to the other side, she lost her footing and fell to her knee. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Daniel Perry | 2019-11-13 08:56 | 2019-10-17 16:27 | 2019-10-17 16:27 | 2019-10-23 11:32 | 2019-10-30 15:30 | 2019-10-17 16:03 | 2019-11-06 13:59 |  |  | Horseshoe Lake Unit 8 LP Cylinder #2. |  |  | Guillermo Sarmiento | Worked with Tim to complete investigation. Approve content and action items. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Daniel Perry |  | At approximately 1530 on 10/16/19, Siemens employee approached her Craft Labor Supervisor informing him that she had tangled her feet while moving across the LP Cylinder #2 to operate a hydraulic torqueing wrench. She tripped on a hydraulic hose and bumped her knee. Ice was applied to the affected area (right knee). She reported that it had swollen slightly, and declined wanting to go to the hospital. The Siemens project manager was notified and together they called Work Care. The employee spoke to a nurse and was given instructions on how to care for her knee. Following the phone call, the crew was reminded of the morning’s safety message which was changing conditions and body awareness. Findings: 1. A Take 5 was completed but the working at elevation with fall protection was not identified Fall Protection was being used). 2. Take 5 did not identify Falling object potential (nuts being installed or socket being used.) 3. Back page of Take 5 did list harness are being required as well as a face shield 4. Watch footing was identified, but the hose as being the cause was not. 5. Take 5 Debrief did identify the hose as the factor in causing the incident. 6. The incident was reported in a timely manner to OGE personnel. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Maintenance |  | Daniel Perry | Daniel Perry |  | Robert Doupe | RDD Approved | Robert Doupe |  | Low |  |  | 3.09 Constrained movement |  | 5.06 Lack of situational awareness | [11 empty] | Siemens member was working on top of the HL Unit 8 LP Cylinder #2 and fell to one knee while moving from one side of the component to the other. Members foot caught on a hydraulic hose which caused her to lose her footing and go down on one knee. | 17. Failure to Identify Hazard, Risk | 4. Fall on Same Level (Slip and Fall, Trip Over) | [5 empty] | Injury / Illness |  | Daniel Perry |  | Bumped Knee | FALSE |  |  | 4. Fall on Same Level (Slip and Fall, Trip Over) | Daniel Perry | Siemens | Lynda Hawley | Abrasion |  | Knee | Daniel Perry | Right | FALSE | [69 empty] | 9581777
9098 | Metro Service Center | 2019-10-18 08:53 | Summary: TCC System Operator initiated return switching of 345kV equipment before the contractor clearance was returned. Details: OGE switchmen arrived on location as planned, called TCC, TCC Operator gave authorization to begin return switching, OGE switchmen began switching. Field switchmen stopped and called back to ask if the clearance had been returned. At this time the System Operator realized that the clearance was still active and halted switching. No devices were switched in the field; only verifications were performed before the switchmen called in to question the clearance. | Level 3 |  | FALSE | System Operational Incident | Andrea Dennis | Lindle Coleman | per magby | 2019-10-23 13:25 | Transco | Drew Walker | 2019-11-12 12:30 | 2019-10-18 11:41 |  | 2019-11-04 11:18 | 2019-11-29 08:53 | 2019-10-18 09:04 | 2019-11-05 18:13 | 2019-11-08 12:04 | 2019-11-05 10:12 | Metro Transmission Control Center |  |  | Andrea Dennis | I approve. | T&D Ops |  | Level 3 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Jeffrey Uhls |  | Operational Incident Summary On, Friday, October 18, 2019 a TCC System Operator initiated return switching at Badger Substation on SWO S0876 to return the Badger 345Kv Beaver County Line1 and Bus 1 back in service before the contractor clearance was returned. An OGE System Maintenance Technician switchmen arrived on location at Badger Substation as planned and called the TCC. The TCC Operator gave authorization to begin return switching on SWO S0876, Steps 56 – 82 after completing three-way communication to confirm switching order number and verifying the switching steps. The System Maintenance Technician switchmen began switching and completed steps 56 and 57, verifying breakers 318 and 314 were open and on manual. The switchmen noticed that he did not have a Clearance return time and stopped, called back into the TCC to ask if the clearance had been returned. At this time the System Operator realized that the clearance was still active and halted switching. No devices were switched in the field; only verifications were performed before the switchmen called in to question the clearance. Chain of Events: • The Contractor Foreman notified TCC that he was on site at Beaver County substation awaiting the arrival of the switchmen; he informed the TCC operator that once the switchmen were on site he call back and return his clearance. • System Maintenance Technician arrived at Badger substation, called the TCC and informed him he and a System Maintenance Foreman were on site and ready to start switching. o He also informed the TCC operate that two other System Maintenance technicians were headed to Beaver County substation to perform switching at that location. • After performing three-way communication to confirm switching order number S0876 was being referenced and verifying the switching steps; the switchmen was given authorization to begin executing the return switching steps 56-82. o The System Maintenance technician executed Step 56; “Verify Open and On Manual” breaker 318, followed by Step 57 “Verify Open and On Manual” breaker 314 at Badger substation. • The System Maintenance Foreman noticed there was no time for the return of the clearance and asked the Maintenance technician if he was given a time for its return. o The System Maintenance technician called the TCC Operator to obtain the time the clearance was returned. • The TCC Operator checked the clearance report; he realized the clearance was still outstanding and had not been returned. o The TCC Operator asked if they had started executing the switching. The System Maintenance technician informed him Steps 56 and 57 were performed but these steps only had them verifying breakers 314 and 318 were open and on manual. That not devices or equipment had been operated. o The TCC Operator halted switching activities. • The TCC Operator contacted the Clearance Holder to verify he would be returning the clearance that day. The contractor informed the operator that he was awaiting the switchmen to arrive at Beaver County substation and would release it at that time. o Once the switchmen arrived at Beaver County substation the Contractor Foreman called into the TCC and released Clearance A127 on the Beaver County to Badger 345kv Line 1 and Bus 1 at 10:09. • With the clearance now returned the TCC Operator contacted the System Maintenance technician and proceed with placing the Beaver County to Badger 345kv Line 1 and Bus 1 back to normal. o Three-way communication was again utilized to confirm the switching order number and to verify the steps to be executed. o Switching Order S0876 was then completed with no further incident. Incident Facts Ascertained: • Prior to starting any switching activities, the contractor foreman called into the TCC informing them he was on site at Beaver County substation and would return his clearance once the switchman arrived. o This call was taken by one TCC Operator, but another TCC Operator directed the switching. • The TCC Operator reviewed the SWO S0876 prior to directing the switching order but did not confirm the status of the clearance during this review. Causal Factors: • Failure to follow procedures and confirm Clearance A127 had been returned prior to authorizing the start of SWO S0876 directly contributed to the cause of the incident. Opportunities for Improvement: • Incorporate a step into the switching order to verify that all clearances associated with the switching have been returned. o This additional step will guarantee the status of the clearance(s) have been confirmed prior to starting any switching activities. | Darrell Fuller | Jeffrey Uhls |  | Metro Service Center | FALSE |  | FALSE | System Operations |  | Eric Brown | Drew Walker |  | Darrell Fuller | I believe the actions taken will close the identified gap. This practice will be implemented into DCC clearance return switching as well. Great job everyone. | Darrell Fuller | Lindle Coleman | High |  | 2.10 Memory failure |  |  | 5.06 Lack of situational awareness | [11 empty] | Failure to verify all clearances returned before starting return switching to energize equipment. | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation | approved | I feel like this was a great investigation and a learning opportunity. The corrective action should prevent similar reoccurrence in the future. Great job Jeff and Drew. CM
9098 | Metro Service Center | 2019-10-18 08:53 | Summary: TCC System Operator initiated return switching of 345kV equipment before the contractor clearance was returned. Details: OGE switchmen arrived on location as planned, called TCC, TCC Operator gave authorization to begin return switching, OGE switchmen began switching. Field switchmen stopped and called back to ask if the clearance had been returned. At this time the System Operator realized that the clearance was still active and halted switching. No devices were switched in the field; only verifications were performed before the switchmen called in to question the clearance. | Level 3 |  | FALSE | System Operational Incident | Andrea Dennis | Lindle Coleman | per magby | 2019-10-23 13:25 | Transco | Drew Walker | 2019-11-12 12:30 | 2019-10-18 11:41 |  | 2019-11-04 11:18 | 2019-11-29 08:53 | 2019-10-18 09:04 | 2019-11-05 18:13 | 2019-11-08 12:04 | 2019-11-05 10:12 | Metro Transmission Control Center |  |  | Andrea Dennis | I approve. | T&D Ops |  | Level 3 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Jeffrey Uhls |  | Operational Incident Summary On, Friday, October 18, 2019 a TCC System Operator initiated return switching at Badger Substation on SWO S0876 to return the Badger 345Kv Beaver County Line1 and Bus 1 back in service before the contractor clearance was returned. An OGE System Maintenance Technician switchmen arrived on location at Badger Substation as planned and called the TCC. The TCC Operator gave authorization to begin return switching on SWO S0876, Steps 56 – 82 after completing three-way communication to confirm switching order number and verifying the switching steps. The System Maintenance Technician switchmen began switching and completed steps 56 and 57, verifying breakers 318 and 314 were open and on manual. The switchmen noticed that he did not have a Clearance return time and stopped, called back into the TCC to ask if the clearance had been returned. At this time the System Operator realized that the clearance was still active and halted switching. No devices were switched in the field; only verifications were performed before the switchmen called in to question the clearance. Chain of Events: • The Contractor Foreman notified TCC that he was on site at Beaver County substation awaiting the arrival of the switchmen; he informed the TCC operator that once the switchmen were on site he call back and return his clearance. • System Maintenance Technician arrived at Badger substation, called the TCC and informed him he and a System Maintenance Foreman were on site and ready to start switching. o He also informed the TCC operate that two other System Maintenance technicians were headed to Beaver County substation to perform switching at that location. • After performing three-way communication to confirm switching order number S0876 was being referenced and verifying the switching steps; the switchmen was given authorization to begin executing the return switching steps 56-82. o The System Maintenance technician executed Step 56; “Verify Open and On Manual” breaker 318, followed by Step 57 “Verify Open and On Manual” breaker 314 at Badger substation. • The System Maintenance Foreman noticed there was no time for the return of the clearance and asked the Maintenance technician if he was given a time for its return. o The System Maintenance technician called the TCC Operator to obtain the time the clearance was returned. • The TCC Operator checked the clearance report; he realized the clearance was still outstanding and had not been returned. o The TCC Operator asked if they had started executing the switching. The System Maintenance technician informed him Steps 56 and 57 were performed but these steps only had them verifying breakers 314 and 318 were open and on manual. That not devices or equipment had been operated. o The TCC Operator halted switching activities. • The TCC Operator contacted the Clearance Holder to verify he would be returning the clearance that day. The contractor informed the operator that he was awaiting the switchmen to arrive at Beaver County substation and would release it at that time. o Once the switchmen arrived at Beaver County substation the Contractor Foreman called into the TCC and released Clearance A127 on the Beaver County to Badger 345kv Line 1 and Bus 1 at 10:09. • With the clearance now returned the TCC Operator contacted the System Maintenance technician and proceed with placing the Beaver County to Badger 345kv Line 1 and Bus 1 back to normal. o Three-way communication was again utilized to confirm the switching order number and to verify the steps to be executed. o Switching Order S0876 was then completed with no further incident. Incident Facts Ascertained: • Prior to starting any switching activities, the contractor foreman called into the TCC informing them he was on site at Beaver County substation and would return his clearance once the switchman arrived. o This call was taken by one TCC Operator, but another TCC Operator directed the switching. • The TCC Operator reviewed the SWO S0876 prior to directing the switching order but did not confirm the status of the clearance during this review. Causal Factors: • Failure to follow procedures and confirm Clearance A127 had been returned prior to authorizing the start of SWO S0876 directly contributed to the cause of the incident. Opportunities for Improvement: • Incorporate a step into the switching order to verify that all clearances associated with the switching have been returned. o This additional step will guarantee the status of the clearance(s) have been confirmed prior to starting any switching activities. | Drew Walker | Jeffrey Uhls |  | Metro Service Center | FALSE |  | FALSE | System Operations |  | Eric Brown | Drew Walker |  | Darrell Fuller | I believe the actions taken will close the identified gap. This practice will be implemented into DCC clearance return switching as well. Great job everyone. | Darrell Fuller | Lindle Coleman | High |  | 2.10 Memory failure |  |  | 5.06 Lack of situational awareness | [11 empty] | Failure to verify all clearances returned before starting return switching to energize equipment. | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation | approved | I feel like this was a great investigation and a learning opportunity. The corrective action should prevent similar reoccurrence in the future. Great job Jeff and Drew. CM
9098 | Metro Service Center | 2019-10-18 08:53 | Summary: TCC System Operator initiated return switching of 345kV equipment before the contractor clearance was returned. Details: OGE switchmen arrived on location as planned, called TCC, TCC Operator gave authorization to begin return switching, OGE switchmen began switching. Field switchmen stopped and called back to ask if the clearance had been returned. At this time the System Operator realized that the clearance was still active and halted switching. No devices were switched in the field; only verifications were performed before the switchmen called in to question the clearance. | Level 3 |  | FALSE | System Operational Incident | Andrea Dennis | Lindle Coleman | per magby | 2019-10-23 13:25 | Transco | Drew Walker | 2019-11-12 12:30 | 2019-10-18 11:41 |  | 2019-11-04 11:18 | 2019-11-29 08:53 | 2019-10-18 09:04 | 2019-11-05 18:13 | 2019-11-08 12:04 | 2019-11-05 10:12 | Metro Transmission Control Center |  |  | Andrea Dennis | I approve. | T&D Ops |  | Level 3 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Jeffrey Uhls |  | Operational Incident Summary On, Friday, October 18, 2019 a TCC System Operator initiated return switching at Badger Substation on SWO S0876 to return the Badger 345Kv Beaver County Line1 and Bus 1 back in service before the contractor clearance was returned. An OGE System Maintenance Technician switchmen arrived on location at Badger Substation as planned and called the TCC. The TCC Operator gave authorization to begin return switching on SWO S0876, Steps 56 – 82 after completing three-way communication to confirm switching order number and verifying the switching steps. The System Maintenance Technician switchmen began switching and completed steps 56 and 57, verifying breakers 318 and 314 were open and on manual. The switchmen noticed that he did not have a Clearance return time and stopped, called back into the TCC to ask if the clearance had been returned. At this time the System Operator realized that the clearance was still active and halted switching. No devices were switched in the field; only verifications were performed before the switchmen called in to question the clearance. Chain of Events: • The Contractor Foreman notified TCC that he was on site at Beaver County substation awaiting the arrival of the switchmen; he informed the TCC operator that once the switchmen were on site he call back and return his clearance. • System Maintenance Technician arrived at Badger substation, called the TCC and informed him he and a System Maintenance Foreman were on site and ready to start switching. o He also informed the TCC operate that two other System Maintenance technicians were headed to Beaver County substation to perform switching at that location. • After performing three-way communication to confirm switching order number S0876 was being referenced and verifying the switching steps; the switchmen was given authorization to begin executing the return switching steps 56-82. o The System Maintenance technician executed Step 56; “Verify Open and On Manual” breaker 318, followed by Step 57 “Verify Open and On Manual” breaker 314 at Badger substation. • The System Maintenance Foreman noticed there was no time for the return of the clearance and asked the Maintenance technician if he was given a time for its return. o The System Maintenance technician called the TCC Operator to obtain the time the clearance was returned. • The TCC Operator checked the clearance report; he realized the clearance was still outstanding and had not been returned. o The TCC Operator asked if they had started executing the switching. The System Maintenance technician informed him Steps 56 and 57 were performed but these steps only had them verifying breakers 314 and 318 were open and on manual. That not devices or equipment had been operated. o The TCC Operator halted switching activities. • The TCC Operator contacted the Clearance Holder to verify he would be returning the clearance that day. The contractor informed the operator that he was awaiting the switchmen to arrive at Beaver County substation and would release it at that time. o Once the switchmen arrived at Beaver County substation the Contractor Foreman called into the TCC and released Clearance A127 on the Beaver County to Badger 345kv Line 1 and Bus 1 at 10:09. • With the clearance now returned the TCC Operator contacted the System Maintenance technician and proceed with placing the Beaver County to Badger 345kv Line 1 and Bus 1 back to normal. o Three-way communication was again utilized to confirm the switching order number and to verify the steps to be executed. o Switching Order S0876 was then completed with no further incident. Incident Facts Ascertained: • Prior to starting any switching activities, the contractor foreman called into the TCC informing them he was on site at Beaver County substation and would return his clearance once the switchman arrived. o This call was taken by one TCC Operator, but another TCC Operator directed the switching. • The TCC Operator reviewed the SWO S0876 prior to directing the switching order but did not confirm the status of the clearance during this review. Causal Factors: • Failure to follow procedures and confirm Clearance A127 had been returned prior to authorizing the start of SWO S0876 directly contributed to the cause of the incident. Opportunities for Improvement: • Incorporate a step into the switching order to verify that all clearances associated with the switching have been returned. o This additional step will guarantee the status of the clearance(s) have been confirmed prior to starting any switching activities. | Michael Gaunder | Jeffrey Uhls |  | Metro Service Center | FALSE |  | FALSE | System Operations |  | Eric Brown | Drew Walker |  | Darrell Fuller | I believe the actions taken will close the identified gap. This practice will be implemented into DCC clearance return switching as well. Great job everyone. | Darrell Fuller | Lindle Coleman | High |  | 2.10 Memory failure |  |  | 5.06 Lack of situational awareness | [11 empty] | Failure to verify all clearances returned before starting return switching to energize equipment. | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation | approved | I feel like this was a great investigation and a learning opportunity. The corrective action should prevent similar reoccurrence in the future. Great job Jeff and Drew. CM
9099 | South District Service Center | 2019-10-18 10:30 | Company member was travelling northbound on 36th when he was struck by a public driver who failed to yield at the intersection. | Level 3 |  | FALSE | Vehicle | Jean Leger | Lindle Coleman | per discussion with Kennedy | 2019-10-23 13:19 | Power Delivery | Joshua Fisk | 2019-11-07 10:16 | 2019-10-18 14:21 | 2019-10-18 14:21 | 2019-10-30 08:12 | 2019-11-01 10:30 | 2019-10-18 14:08 | 2019-11-01 09:20 | 2019-11-01 18:14 | 2019-10-31 12:38 | Intersection of 36th and Tecumseh |  |  | Jean Leger | No additional comments. | T&D Ops |  | Level 3 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Gary Parks |  | Company member was travelling northbound on 36th when he was struck by a public driver who failed to yield at the intersection. Public person was issued a citation for failure to yield. | Luke Kennedy | Gary Parks |  | South District Service Center | FALSE |  | FALSE | Construction Services |  | Carl Bilyeu | Joshua Fisk |  | Terry Garrett | I approve...TG | Terry Garrett | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Company member was travelling northbound on 36th when he was struck by a public driver who failed to yield at the intersection. | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) | Reviewed | Safety stand down conducted the Monday following the vehicle incidents to discuss the importance of proactive defensive driving habits. | [72 empty] | FALSE |  | Norman | Public Vehicle Struck OGE | Both Vehicles Moving | 2001-12-30 18:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
9100 | South District Service Center | 2019-10-18 19:30 | Public vehicle failed to yield while executing left turn at intersection and hit company vehicle travelling eastbound. | Level 3 |  | FALSE | Vehicle | Andrea Dennis | Lindle Coleman | per Kennedy | 2019-10-23 13:29 | Power Delivery | Gary Parks | 2019-11-07 12:40 | 2019-10-21 10:34 | 2019-10-21 10:34 | 2019-10-30 07:40 | 2019-11-01 19:30 | 2019-10-21 10:20 | 2019-11-01 09:23 | 2019-11-01 18:11 | 2019-10-31 12:34 | Intersection of Robinson & Interstate dr |  |  | Andrea Dennis | I approve. | T&D Ops |  | Level 3 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Gary Parks |  | Public vehicle failed to yield while executing left turn at intersection and hit company vehicle travelling eastbound. Public driver was issued an at fault warning from the police. | Luke Kennedy | Gary Parks |  | South District Service Center | FALSE |  | FALSE | Construction Services |  | Chad Gleave | Gary Parks |  | Terry Garrett | Approve | Terry Garrett | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Public vehicle failed to yield while executing left turn at intersection and hit company vehicle travelling eastbound. | 19. Failure to React, Correct | 2. Struck By (Hit By Moving Object) | approved | While the member had virtually no time to execute defensive driving techniques we did talk about proactively scanning intersections during the safety stand down | [72 empty] | FALSE |  | Norman | Public Vehicle Struck OGE | Both Vehicles Moving | 2019-01-06 18:00 |  | TRUE |  |  | Night | 0 | 1 | Asphalt |  | Clear | TRUE | FALSE
9101 | Muskogee Service Center | 2019-10-21 15:30 | Member was going North on Cherokee St, when public vehicle failed to yield at intersection causing member to strike public vehicle. Both vehicles were drivable. No injuries occurred. | Level 2 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Randell Gilbert | 2019-11-08 12:03 | 2019-10-22 13:24 | 2019-10-22 13:24 | 2019-11-06 08:59 | 2019-11-04 15:30 | 2019-10-21 15:30 | 2019-11-08 11:32 |  | 2019-11-06 10:16 | S. Cherokee Dr. and E Peak Blvd. |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Randell Gilbert |  | Member was going North on Cherokee St, when public vehicle failed to yield at intersection causing member to strike public vehicle. Both vehicles were drivable. No injuries occurred. No citation given. Member was traveling 5 mph below speed limit and was able to slow to 10 mph at impact, verified on telemetrics. |  |  |  | Muskogee Service Center | FALSE |  | FALSE | Construction Services |  | Reid Williams | Randell Gilbert |  | Chad Inman | I approve the corrective action listed above. Multiple intersections were identified and diversion plans were also identified. CI | Chad Inman |  | Medium |  | 2.07 Slow reaction time | [14 empty] | Public vehicle failed to yield at intersection causing member to strike public vehicle | 02. Failure to Warn | 1. Struck Against (Running or Bumping Into) |  | Reviewed | [72 empty] | FALSE |  | Muskogee | Public Vehicle Struck OGE | Public Driver Failed To Yield | 2018-02-25 18:00 |  | FALSE |  |  | Day Light | 0 | 0 | Asphalt |  | Clear | FALSE | FALSE
9102 | Redbud Plant | 2019-10-22 01:00 | Skytrak fork assembly was found damaged. no injuries | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Scott Carroll | 2019-11-19 17:54 | 2019-10-22 13:48 | 2019-10-22 13:48 | 2019-11-06 13:36 | 2019-11-05 01:00 | 2019-10-22 09:00 | 2019-11-14 07:37 |  |  | Redbud Unit 1CTG west side |  |  | Guillermo Sarmiento | have reviewed incident and agree with the findings and corrective actions. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | TRUE |  | FALSE | FALSE | Scott Carroll |  | The non-conforming condition was discovered on day shift pre-use inspection. The welded safety ring approximately 1/8” in thickness had broken from its welded position on the bar as was discovered next to the mast in the rocks. Fork mast had been removed to complete a task on the generator the previous shift. The condition would not have been seen at night, as the surface is black in color and powder coated, the missing welded ring would not have inspected with rigor, as the forklift inspection is a visual and test of functionality and the mast welds would not have been included on this type of inspection. Forklift Mast was quarantined and removed by Plant for repair, inspection, re-qualification and return to service. During the pre-work inspection of the fork trucks, it was discovered that the end of the pin that supports the forks on the Genie GTH-1256, had been sheared off. (see att.) When going over the inspection on the forklift. Employee noticed the bar that holds the forks to the mast was broken. Employee notified the supervisor, and suspend all operations and use of the lift. During the pre-work inspection of the fork trucks, it was discovered that the end of the pin that supports the forks on the Genie GTH-1256, had been sheared off. (see att.) When going over the inspection on the forklift. Employee noticed the bar that holds the forks to the mast was broken. Employee notified the supervisor, and suspend all operations and use of the lift. |  |  |  | Redbud Plant | FALSE |  | TRUE | Maintenance |  | Bruce Pruitt | Scott Carroll |  | Benjamin Dickinson | Investigation accepted. | Benjamin Dickinson |  | Low | [10 empty] | 11.07 Improper handling of materials | [5 empty] | Mast assembly was found damaged during inspection. | 08. Improper Loading | 12. Equipment Failure | [5 empty] | Property Damage |  | Scott Carroll | [5 empty] | 9. Abnormal Operation | Bruce Pruitt | GE | Field Core |  |  |  | Bruce Pruitt
9102 | Redbud Plant | 2019-10-22 01:00 | Skytrak fork assembly was found damaged. no injuries | Level 1 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Scott Carroll | 2019-11-19 17:54 | 2019-10-22 13:48 | 2019-10-22 13:48 | 2019-11-06 13:36 | 2019-11-05 01:00 | 2019-10-22 09:00 | 2019-11-14 07:37 |  |  | Redbud Unit 1CTG west side |  |  | Guillermo Sarmiento | have reviewed incident and agree with the findings and corrective actions. | Power Supply |  | Level 1 | Property Damage |  | TRUE | FALSE | TRUE |  | FALSE | FALSE | Scott Carroll |  | The non-conforming condition was discovered on day shift pre-use inspection. The welded safety ring approximately 1/8” in thickness had broken from its welded position on the bar as was discovered next to the mast in the rocks. Fork mast had been removed to complete a task on the generator the previous shift. The condition would not have been seen at night, as the surface is black in color and powder coated, the missing welded ring would not have inspected with rigor, as the forklift inspection is a visual and test of functionality and the mast welds would not have been included on this type of inspection. Forklift Mast was quarantined and removed by Plant for repair, inspection, re-qualification and return to service. During the pre-work inspection of the fork trucks, it was discovered that the end of the pin that supports the forks on the Genie GTH-1256, had been sheared off. (see att.) When going over the inspection on the forklift. Employee noticed the bar that holds the forks to the mast was broken. Employee notified the supervisor, and suspend all operations and use of the lift. During the pre-work inspection of the fork trucks, it was discovered that the end of the pin that supports the forks on the Genie GTH-1256, had been sheared off. (see att.) When going over the inspection on the forklift. Employee noticed the bar that holds the forks to the mast was broken. Employee notified the supervisor, and suspend all operations and use of the lift. |  |  |  | Redbud Plant | FALSE |  | TRUE | Maintenance |  | Bruce Pruitt | Scott Carroll |  | Benjamin Dickinson | Investigation accepted. | Benjamin Dickinson |  | Low | [10 empty] | 11.07 Improper handling of materials | [5 empty] | Mast assembly was found damaged during inspection. | 08. Improper Loading | 12. Equipment Failure | [5 empty] | Property Damage |  | Scott Carroll | [5 empty] | 9. Abnormal Operation | Bruce Pruitt | GE | Field Core |  |  |  | Bruce Pruitt
9103 | Sooner Power Plant | 2019-10-21 17:00 | While placing papers into backpack at the end of the day, member received a paper cut to their left thumb. | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Supply | Bryan Pool | 2019-10-30 10:55 | 2019-10-22 13:54 | 2019-10-22 13:54 | 2019-10-22 14:13 | 2019-11-04 17:00 | 2019-10-22 13:36 |  |  |  | Sooner Power Plant, Admin office |  |  | Brady Sowell | approved. Waiting to be on the hotsheet or call | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | [5 empty] | FALSE | Sooner Power Plant | FALSE |  | FALSE | Quality Assurance |  | Schnelle Broome | Bryan Pool |  |  |  | Donnie Jones |  | Low | [45 empty] | FALSE |  |  | 1999-06-21 | 1968-11-06 |  | 2019-10-21 07:00 | 0 | 0 |  | FALSE |  | Packing items into backpack at the end of the day, edge of paper came into contact with left thumb causing small paper cut. |  | FALSE | Schnelle Broome |  | First Aid | Schnelle Broome |  |  |  |  | Abrasion |  | FALSE |  | Quality Assurance Coord Specialist | Thumb (1) |  | Left | FALSE | Bryan Pool | FALSE |  | 10/21/2019 7:00:00 AM | 7 | FALSE |  |  | Paper
9104 | North Service Center | 2019-10-21 20:30 | Employee was performing switching in a pad mount transformer. Was pulling off a bushing cap on a feed through and when it finally released it caused employee to twist and he felt discomfort in his knee. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Jeffrey Warner | 2019-11-01 18:12 | 2019-10-22 14:46 | 2019-10-22 14:45 | 2019-10-28 12:47 | 2019-11-04 20:30 | 2019-10-22 14:25 | 2019-11-01 09:22 |  | 2019-10-31 12:29 | Working a trouble call at N.W. 140th and N. Walker Ave. |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Jeffrey Warner |  | Employee was performing switching in a pad mount transformer. Was pulling off a bushing cap on a feed through and when it finally released it caused employee to twist and he felt discomfort in his knee |  |  | FALSE | North Service Center | FALSE |  | FALSE | Construction Services |  | Tommy Robertson | Jeffrey Warner |  | Terry Garrett | Approve..TG | Terry Garrett |  | Medium | [9 empty] | 10.02 Inadequate consideration of human factors/ergonomics | [6 empty] | Twisting of the body when the cap released. | 24. Congestion or Restricted Action | 11. Overstress, Overpressure, Overexertion, Ergonomic |  | I followed up again with the member and his status has continued to improve | [24 empty] | FALSE |  |  | 1995-05-08 | 1968-09-19 |  | 2019-10-21 07:00 | 0 | 0 | When employee arrived home after the trouble call, he took ibuprofen and applied ice and elevation to the knee. | FALSE |  | Member was in the process of testing the cable in the bad transformer dead and grounding it. When pulling a cap off of the bushing on the parking stand, it was difficult to remove. When it finally released, employee twisted and felt a discomfort in his knee. |  | TRUE | Tommy Robertson |  | First Aid | Tommy Robertson |  |  |  |  | Sprain/Strain |  | FALSE |  | Foreman Construction | Knee |  | Left | FALSE | Jeffrey Warner | FALSE |  | 10/21/2019 7:00:00 AM | 24 yrs. | FALSE |  |  | The twisting motion of the employee when the cap became unstuck. | Changing out a pad mount transformer.
9105 | Metro Service Center | 2019-10-23 16:30 | Member was driving on Ottawa road going at a speed of around 15 to 30 mph. As Member approached oncoming driveway an H and H heat and air truck parked at a angle began backing, ultimately striking OGE vehicle right side, blowing out tire and damaging tool boxes. | Level 2 |  | FALSE | Vehicle |  |  |  |  | OGE Energy Corp | Phillip Messer | 2019-11-15 16:34 | 2019-10-24 09:43 | 2019-10-24 09:43 | 2019-10-30 11:58 | 2019-11-06 16:30 | 2019-10-23 17:00 | 2019-10-31 12:13 |  | 2019-10-30 16:29 | 401 Romanway East Noble Ok |  |  | William Young | Reviewed and approved. WCY 11-15-19 | Enterprise Services |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Phillip Messer |  | Private vehicle was backing out of a private drive located at 204 Roman Way East. OGE vehicle was traveling south on Roman way east. Private vehicle entered the roadway and struck OGE vehicle. AOI was approximately 229' south of the south edge of Kent drive and approximately 15' west of the east edge of Roman Way East. |  |  |  | Metro Service Center | FALSE |  | FALSE | Real Estate |  | Charles Harris | Phillip Messer |  | Vance Krebs | Approved, Vance Krebs | Vance Krebs |  | Medium |  |  |  |  | 5.06 Lack of situational awareness |  |  |  |  | 10.07 Inadequate monitoring of initial operation | [6 empty] | Private vehicle operator appropriate attention to surrounding while operating a vehicle | 39. Road Conditions | 2. Struck By (Hit By Moving Object) |  | Approved, Cody Vinyard | [72 empty] | FALSE |  | Noble | Public Vehicle Struck OGE | Both Vehicles Moving | 2017-02-12 18:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
9106 | Metro Garage | 2019-10-22 13:00 | Fleet mechanic responded to an engine will not crank on unit f05-314. When the mechanic raised the hood he found one of batteries had blown the side of the battery case apart and vented battery fluid in the engine compartment. | Level 2 |  | TRUE | Member Injury |  |  |  |  | OG&E Corp Services | Nathan Gooch | 2019-12-09 16:58 | 2019-10-24 10:18 | 2019-10-24 10:18 | 2019-10-30 09:42 | 2019-11-05 13:00 | 2019-10-23 10:03 | 2019-11-29 13:13 |  | 2019-10-30 16:21 | 401 ROMAN WAY EAST NOBLE, OK |  |  | William Young | Reviewed and approved. WCY 12-9-2019 | UTS |  | Level 2 | Member Injury |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Nathan Gooch |  | Fleet mechanic responded to an engine will not crank on unit f05-314. When the mechanic raised the hood he found one of batteries had blown the side of the battery case apart and vented battery fluid in the engine compartment. After investigating found the fleet mechanic had been called out the 10/23/19, the day before, for the same thing. At that time the mechanic just jump started the truck and did not test the batteries. The operated drove the vehicle the rest of the day with no issues. He parked the truck overnight and the truck did not start the next morning. On 10/24/19 the Fleet mechanic was called out again for the same problem, that is when he discovered the passenger side battery had ruptured. The mechanic replaced both batteries and cleaned the vented battery acid. |  |  |  | Metro Garage | FALSE |  | TRUE | UTS - Fleet Services |  | Donald Roxberry | Nathan Gooch |  | Paul Jefferson | I approve corrective actions. | Paul Jefferson |  | Medium | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | Dead battery failed after jump start. | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure |  | Approved, Cody Vinyard
9106 | Metro Garage | 2019-10-22 13:00 | Fleet mechanic responded to an engine will not crank on unit f05-314. When the mechanic raised the hood he found one of batteries had blown the side of the battery case apart and vented battery fluid in the engine compartment. | Level 2 |  | TRUE | Property Damage |  |  |  |  | OG&E Corp Services | Nathan Gooch | 2019-12-09 16:58 | 2019-10-24 10:18 | 2019-10-24 10:18 | 2019-10-30 09:42 | 2019-11-05 13:00 | 2019-10-23 10:03 | 2019-11-29 13:13 |  | 2019-10-30 16:21 | 401 ROMAN WAY EAST NOBLE, OK |  |  | William Young | Reviewed and approved. WCY 12-9-2019 | UTS |  | Level 2 | Property Damage |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Nathan Gooch |  | Fleet mechanic responded to an engine will not crank on unit f05-314. When the mechanic raised the hood he found one of batteries had blown the side of the battery case apart and vented battery fluid in the engine compartment. After investigating found the fleet mechanic had been called out the 10/23/19, the day before, for the same thing. At that time the mechanic just jump started the truck and did not test the batteries. The operated drove the vehicle the rest of the day with no issues. He parked the truck overnight and the truck did not start the next morning. On 10/24/19 the Fleet mechanic was called out again for the same problem, that is when he discovered the passenger side battery had ruptured. The mechanic replaced both batteries and cleaned the vented battery acid. |  |  |  | Metro Garage | FALSE |  | TRUE | UTS - Fleet Services |  | Donald Roxberry | Nathan Gooch |  | Paul Jefferson | I approve corrective actions. | Paul Jefferson |  | Medium | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | Dead battery failed after jump start. | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure |  | Approved, Cody Vinyard
9107 | West Service Center | 2019-10-24 11:05 | Driving in left lane passing semi truck. Driver side window exploded, glass shattered. Pulled off interstate at rest area. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Delivery | Brian Routh | 2019-10-31 13:40 | 2019-10-24 12:07 | 2019-10-25 10:52 | 2019-10-30 15:17 | 2019-11-07 11:05 | 2019-10-24 12:06 | 2019-10-30 15:27 |  |  | Northbound I-35 about mile marker 56 |  |  | Luke Kennedy | Approved 10/31/19 | T&D Ops |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Brian Routh |  | Member was returning from Dallas TX after mutual assistance storm assessment work for Oncor in company vehicle. While driving on Interstate 35 approximately 2 miles north of Hwy 7, the driver side door window shattered, apparently struck by some object. Member was driving in the left lane to pass a couple of semi trucks with no other vehicles in front of member. Member pulled off of Interstate 35 at rest area that was about 1 1/2 miles north of the incident. Member called supervisor to report and also called fleet service. |  |  |  | West Service Center | FALSE |  | FALSE | Distribution Eng & Tech Services |  | Brian Routh | Ronald Griffin |  | Ronald Griffin | Grateful this property damage didn't result in a vehicle incident. | Ronald Griffin |  | Low | [11 empty] | 12.01.4 Inadequate preventative cleaning or resurfacing |  |  |  |  | Driving in left lane passing semi truck. Driver side window exploded, glass shattered. Pulled off interstate at rest area. | 39. Road Conditions | 2. Struck By (Hit By Moving Object) | [68 empty] | Driver side door window shattered. | 180 | Brian Routh | Vehicle (not related to operation of vehicle) |  | F01-1161
9108 | Central District Office | 2019-10-23 09:00 | Member was assisting in traffic control for heavy haulers. He was walking at an accelerated pace and turned to look back at the traffic. When he did he twisted his left knee causing minor discomfort. No medical treatment needed at this time. | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Gerald Smith | 2019-11-05 10:07 | 2019-10-24 14:20 | 2019-10-24 14:20 | 2019-10-24 14:26 | 2019-11-06 09:00 | 2019-10-24 14:15 |  |  |  | Park place substation |  |  | Cody Magby | Member visited OGE doctor and was evaluated with no problems. For record only cm | T&D Ops |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | [5 empty] | FALSE | Central District Office | FALSE |  | FALSE | PD Operations Services |  | Terry Collins | Gerald Smith |  |  |  | James Hutchison |  | Low | [45 empty] | FALSE |  |  | 2005-05-23 | 1962-12-31 |  | 2019-10-23 07:00 | 0 | 0 |  | FALSE |  | while turning back to look at traffic, twisted wrong causing discomfort |  | FALSE | Terry Collins |  | First Aid | Terry Collins |  |  |  |  | Sprain/Strain |  | FALSE |  | Foreman Maintenance | Knee |  | Left | FALSE | Gerald Smith | FALSE |  | 10/23/2019 7:00:00 AM | 14 | FALSE |  |  | ground
9109 | West Service Center | 2019-10-23 13:00 | Contractor (Wright Tree Service) responded to outage call. A neighbors generator was on. When the tree climber started pruning a limb with a handsaw he felt a tingling sensation. | Level 3 |  | TRUE | Contractor | Andrea Dennis | William Young | Investigate, establish causal factors and corrective actions. WCY 10-29-19 | 2019-10-29 13:42 | OG&E Corp Services | Christopher Martin |  | 2019-10-24 16:06 | 2019-10-24 16:06 | 2019-11-15 16:55 | 2019-11-06 13:00 | 2019-10-23 13:00 | 2019-12-09 12:03 | 2020-02-14 14:37 | 2019-12-06 12:57 | NW 28th St and N Geraldine Ave |  |  |  |  | T&D Ops |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | West Crew member Juan Ramirez clearing tree limbs in primary and secondary was using hand pruner on extendo. Then climbed tree with hand saw to finish and felt tingling. Next door neighbor to the house where the crew was working had a generator running. The crew turned off the generator and they finished clearing the limbs. They indicated this took 2-3 minutes. Home owner complained about crew turning off generator. Crew indicated that they had knocked on door but no one answered.. | Jerrie Looney | William Young |  | West Service Center | FALSE |  | TRUE | PD - Resource Planning & Coord |  | Grant Ehlen | Christopher Martin |  | Michael Fox | We have shared our expectations with our GF's | Michael Fox | William Young | High |  |  |  |  | 5.03 Inadequate initial training | [11 empty] | Crew did not follow company policy when they identified home owner generator. Procedure required foreman to contact GF who in turn contacts OGE. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Contractor conducted safety meetings with their workers covering processes and procedures related to the incident (Wright AWM 7.4, Storm work, prep and generators). Meeting was held on 10-28-2019 and attendance documented (see attached documents). WCY 2-14-2020. | Approved - J. Looney 12/6/19 |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Christopher Martin | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Grant Ehlen | Wright Tree Service | Juan Ramirez |  |  |  | Christopher Martin
9109 | West Service Center | 2019-10-23 13:00 | Contractor (Wright Tree Service) responded to outage call. A neighbors generator was on. When the tree climber started pruning a limb with a handsaw he felt a tingling sensation. | Level 3 |  | TRUE | Contractor | Andrea Dennis | William Young | Investigate, establish causal factors and corrective actions. WCY 10-29-19 | 2019-10-29 13:42 | OG&E Corp Services | Christopher Martin |  | 2019-10-24 16:06 | 2019-10-24 16:06 | 2019-11-15 16:55 | 2019-11-06 13:00 | 2019-10-23 13:00 | 2019-12-09 12:03 | 2020-02-14 14:37 | 2019-12-06 12:57 | NW 28th St and N Geraldine Ave |  |  |  |  | T&D Ops |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | William Young |  | West Crew member Juan Ramirez clearing tree limbs in primary and secondary was using hand pruner on extendo. Then climbed tree with hand saw to finish and felt tingling. Next door neighbor to the house where the crew was working had a generator running. The crew turned off the generator and they finished clearing the limbs. They indicated this took 2-3 minutes. Home owner complained about crew turning off generator. Crew indicated that they had knocked on door but no one answered.. | Christopher Martin | William Young |  | West Service Center | FALSE |  | TRUE | PD - Resource Planning & Coord |  | Grant Ehlen | Christopher Martin |  | Michael Fox | We have shared our expectations with our GF's | Michael Fox | William Young | High |  |  |  |  | 5.03 Inadequate initial training | [11 empty] | Crew did not follow company policy when they identified home owner generator. Procedure required foreman to contact GF who in turn contacts OGE. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Contractor conducted safety meetings with their workers covering processes and procedures related to the incident (Wright AWM 7.4, Storm work, prep and generators). Meeting was held on 10-28-2019 and attendance documented (see attached documents). WCY 2-14-2020. | Approved - J. Looney 12/6/19 |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Christopher Martin | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Grant Ehlen | Wright Tree Service | Juan Ramirez |  |  |  | Christopher Martin
9110 | Ardmore Service Center | 2019-10-25 12:00 | Crew was leaving the substation. The first vehicle pulled through the gate and then backed up out of the drive to let the second vehicle out so the third members could close and lock the substation gate. When the first vehicle was backing out of the second vehicle's way he made contact with a pole with the right rear corner of the service body bed. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Bradley Kosemund | 2019-11-12 10:52 | 2019-10-25 14:25 | 2019-10-25 14:25 | 2019-11-04 16:02 | 2019-11-08 12:00 | 2019-10-25 14:17 | 2019-11-07 14:36 |  |  | Ardmore substation |  |  | Cody Magby | I approve of the investigation and CA CM | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Bradley Kosemund |  | First driver had pulled out of the substation and had backed down the sidewalk in front of the substation to stay out of the road and let the second driver out. The third person was closing and locking the gate. When the first driver backed down the sidewalk the pole was in the passenger side blind spot and the driver made contact. No damage to the pole and minor damage to the passenger side rear portion of the service body. |  |  |  | Ardmore Service Center | FALSE |  | FALSE | PD Operations Services |  | Chris Wilkinson | Bradley Kosemund |  | James Hutchison | I have reviewed this incident report and approve it's findings and corrective actions. | James Hutchison |  | Low | [9 empty] | 10.03 Inadequate standards, specifications and/or design criteria | [6 empty] | Member was backing off the driveway to let second vehicle out | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) | [74 empty] | TRUE |  | Ardmore | Struck Fixed Object | Backing Related | 2009-02-01 18:00 |  | FALSE |  |  | Day Light |  |  | Grass |  | Rain
9111 | River Valley | 2019-10-25 15:00 | While utilizing pliers to remove a fitting on the inside of the feeder, pliers slipped off fitting resulting in right thumb striking opening of feeder. Proper PPE was being worn at time of incident. | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Supply | Michael Smith | 2019-12-13 08:17 | 2019-10-25 15:39 | 2019-10-25 15:39 | 2019-12-05 12:33 | 2019-11-08 15:00 | 2019-10-25 15:23 | 2019-12-09 07:15 |  |  | River Valley PP Unit 1A 1AB coal feeder on west side |  |  | Anthony Gillespie | Proper communication of expectations and follow through of those expectations should reduce the likelihood of recurrence. | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Michael Smith |  | While utilizing pliers to remove a fitting on the inside of the feeder, pliers slipped off fitting resulting in right thumb striking opening of feeder. Approximate size of opening is 12" x 12". Proper PPE was being worn at time of incident. |  |  | FALSE | River Valley | FALSE |  | FALSE | Maintenance |  | James Brooks | Michael Smith |  | Timothy Chancellor | Approved | Timothy Chancellor |  | Low | [12 empty] | 13.02 Inadequate human factors/ergonomics considerations |  |  |  | Due to tight working space, slip joint pliers were not the best choice of tool for job being performed. Locking style pliers would have ensured secure grip on joint being removed. | 23. Defective Tools, Equipment or Materials | 1. Struck Against (Running or Bumping Into) | [26 empty] | FALSE |  |  | 2019-05-28 | 1956-05-02 |  | 2019-10-25 07:00 | 0 | 0 |  | FALSE |  |  |  | FALSE | James Brooks |  | Uninjured | James Brooks | [6 empty] | FALSE |  | ICE Technician Senior |  |  |  |  | Michael Smith | FALSE |  | 10/25/2019 7:00:00 AM | 20+ | FALSE
9112 | North Service Center | 2019-10-19 13:00 | Member was climbing pole, felt some discomfort in his right knee. No medical attention was needed. | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Jeffrey Warner | 2019-10-31 13:31 | 2019-10-28 12:51 | 2019-10-28 12:51 | 2019-10-28 12:54 | 2019-11-02 12:00 | 2019-10-28 12:47 |  |  |  | Kansas City International Lineman Rodeo |  |  | Luke Kennedy | approved 10/31/19 | T&D Ops |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | [5 empty] | FALSE | North Service Center | FALSE |  | FALSE | Construction Services |  | Jason Clark | Jeffrey Warner |  |  |  | Terry Garrett |  | Low | [45 empty] | FALSE |  |  | 1992-04-06 | 1971-03-17 |  | 2019-10-19 07:00 | 0 | 0 |  | FALSE |  | Climbing pole. |  | FALSE | Jason Clark |  | First Aid | Jason Clark | FALSE |  |  |  | Sprain/Strain |  | FALSE |  | Lineman | Knee |  | Right |  | Mark Calvert |  |  | 10/19/2019 7:00:00 AM |  | TRUE |  |  | Pole
9113 | Metro Service Center | 2019-10-28 10:30 | While performing live tripping on PCB 301 breaker failure at Pecan Creeks substation member reset lockout out of sequence. | Level 1 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Joseph Manseau | 2020-01-20 16:22 | 2019-10-29 07:32 |  | 2020-01-08 12:37 | 2019-12-09 10:30 | 2019-10-28 11:00 | 2020-01-20 07:13 |  |  | Pecan Creek substation |  |  | Cody Magby | agree cm | T&D Ops |  | Level 1 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Joseph Manseau |  | On Monday, !0/28/2019 while performing live tripping test at Pecan Creek substation on PCB 301 the System Relay Technician reset the Lockout Relay out of sequence. A Breaker Failure functional test was being performed on PCR 301, the resetting of the lockout relay caused the corresponding breakers to reclose after their initial trip. |  |  |  | Metro Service Center | FALSE |  | FALSE | PD Operations Services |  | Adam Auten | Joseph Manseau |  | James Hutchison | I have reviewed this incident and agree with it's findings and the corrective action. We are starting to perform more live tripping and as we do it will become even more important to review each operating scheme to have a plan and sequence in place. | James Hutchison |  | Low
9114 | Metro Service Center | 2019-10-16 15:00 | Employee grabbed edge of trackhoe bucket for support to climb out of trench. The bucket rolled and pinched both ring fingers. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Delivery | Garrett Bernethy | 2019-12-16 15:04 | 2019-10-29 07:58 | 2019-10-29 07:58 | 2019-10-29 08:36 | 2019-10-30 15:00 | 2019-10-29 07:40 | 2019-11-20 10:37 |  | 2019-11-04 13:51 | 1231 N. Dewey Ave, OKC |  |  | William Young | Reviewed and approved with comment. Some questions I have are: How deep was the trench? At 4' OSHA triggers means of ingress/egress. Less than 4' you need to risk assess and determine means and methods for ingress/egress. Did Red Dirt have a Pre-Task plan? Did it specify means of ingress/egress in this specific instance. Did the August training they mention in their Incident Report specifically address means in trench ingress/egress and prohibit the grabbing of mechanical equipment such as the "bucket". I want to have a meeting with Red Dirt to further review this incident and address the above questions. I will create a separate CA in Intelex to track this follow-up action. W.C. Young 12-16-2019. | T&D Ops |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Garrett Bernethy |  | Employee grabbed edge of trackhoe bucket for support to climb out of trench. The bucket rolled and pinched both ring fingers. |  |  |  | Metro Service Center | FALSE |  | FALSE | Resource Planning & Coord |  | Garrett Bernethy | Garrett Bernethy |  | John Legg | Contractor has Discuss the accident in safety meeting and talk about all possible hazards that need to be identified prior to the start of work and during the work. | John Legg |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [7 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | Employee grabbed edge of trackhoe bucket for support to climb out of trench. The bucket rolled and pinched both ring fingers. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) |  | No additional comments. MLH 11/4/19 |  |  |  | Injury / Illness |  | Garrett Bernethy |  | Smashed the ring fingers of both hands | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Garrett Bernethy | Red Dirt | Luis Torres Ramirez | Crush/Smash |  | Finger | Garrett Bernethy | Left | TRUE | Company Vehicle | [68 empty] | 7379706
9115 | Frontier Power Plant | 2019-10-28 10:30 | Operator was switching the Duplex Hydraulic Filters from the North Filter to the South Filter when the gasket on the South Filter blew spraying Lube Oil onto the groin area of the member. Member was wearing proper PPE; no injuries were sustained. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | William Hunter | 2020-01-22 14:11 | 2019-10-29 13:30 | 2019-10-29 13:30 | 2020-01-14 13:37 | 2019-11-11 10:30 | 2019-10-29 12:59 | 2020-01-17 13:36 |  | 2020-01-15 14:12 | GT Accessory Compartment. |  |  | Jesse Murray | Returning to investigation. Please clean up corrective actions and add facts and corrective actions talked about on 12-11-19 incident call. We need to add a corrective action to address the JHA review process. How do we ensure we review JHAs prior to starting job? Pressure gauge addition would be another good corrective action to prove 0 energy state. Possible laminate instructions at job site? Approved. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | William Hunter |  | The member had been involved once before with swapping the online filter to the offline filter and changing the filter out. This time he was working alone when he swapped the online filter to the offline filter. Not fully understanding the swapping procedure, he didn't open the equalizing valve to pressurize the off line filter and open the vent to ensure that all the air was vented off prior to swapping the filter. Had the equalizing valve been opened and air vented off, the off line filter would have been pressurized to operating pressure without being exposed to the full flow capacity of the filter. Had there been a leak the filter would not have been swapped. When he swapped the filter, the gasket blew spraying oil onto his groin area and this also tripped the Gas Turbine on low hydraulic pressure. There was no injury and the member was sent home to shower and change his clothing. |  |  |  | Frontier Power Plant | FALSE |  | TRUE | Operations |  | Louis Blake | Gary Russell |  | Justin Damron | In addition to the corrective actions, it was noted during this process that the access door covering the opening was difficult to remove and re-position due to its size and the slight vacuum on the space. As part of the mitigation process, we should find an engineering solution for this issue as well. | Justin Damron |  | Medium | [14 empty] | 15.03 Inadequate inspection and/or monitoring |  | The cover gasket on the standby filter was defective. When the standby filter was placed in service, the gasket failed allowing hydraulic oil to spray onto the groin area of the member swapping the filter. | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure |  | Updated Corrective Actions. Bill updated description.
9116 | Northeast District Service Cen | 2019-10-29 13:30 | Members were in pickup and stopped at Hwy 66 and Hwy 117 for a red light. A public vehicle rear ended company vehicle while at the light. Vehicles were drivable and there were no serious injuries. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Michael Fox | 2019-11-01 08:37 | 2019-10-29 14:24 | 2019-10-29 14:24 | 2019-10-31 13:02 | 2019-11-12 12:30 | 2019-10-29 14:16 |  |  |  | Hwy 66 and Hwy 117 signal light. |  |  | Hannah Everett | Reviewed | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE |  |  | Members were on there way to lunch when they stopped at Hwy 66 and Hwy 117 for a red light. A public vehicle rear ended company vehicle while stopped at red light. Vehicles were drivable and there were no serious injuries. Two members were involved. Not aware of any citations given. |  |  |  | Northeast District Service Cen | FALSE |  | FALSE | Construction Services |  | Donald Melson | Michael Fox |  |  |  | Chad Inman |  | Low | [93 empty] | FALSE |  | Sapulpa | Public Vehicle Struck OGE | OGE Vehicle Stopped/Parked | 2003-03-23 18:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
9117 | Central District Office | 2019-10-29 | Central Material Handler was exiting the southwest overhead door in a John Deer gator UTV. UTV strobe light assembly struck the bottom of the overhead door. Overhead door was damaged. No damaged occurred to the UTV. | Level 1 |  | FALSE | Property Damage |  |  |  |  | OGE Energy Corp | Glen McClain | 2019-10-30 16:30 | 2019-10-30 07:42 | 2019-10-30 07:42 | 2019-10-30 08:04 | 2019-11-12 | 2019-10-30 07:33 | 2019-10-30 13:55 |  |  | Central warehouse, southwest overhead door |  |  | Cody Vinyard | Approved, Cody Vinyard | Enterprise Services |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Glen McClain |  | On Oct. 29 2019, Member was preparing to make my weekly ride to Metro from Central storeroom in the gator. Member approached the overhead door and proceed to open it. Member then got in the gator and started to drive thru the door way forgetting the gator had a steal pole sticking up in the air with a light attached. The pole then caught on the door and pulled the bottom panel out from its track on one side. Member contacted facilities and reported the incident. That southwest overhead door was damaged. Door is tagged out of service, until repairs are made. |  |  |  | Central District Office | FALSE |  | FALSE | Supply Chain |  | Garrett Skaggs | Glen McClain |  | George Wicks | Member will focus on being aware of his surroundings and recognizing hazards. | George Wicks |  | Low | [6 empty] | 7.06 Improper attempt to save time or effort | [9 empty] | Member drove UTV/gator into overhead door | 11. Improper Position for Task | 1. Struck Against (Running or Bumping Into) | [68 empty] | Bottom panel of overhead door was damaged | 500 | Garrett Skaggs | Structural
9118 | River Valley | 2019-10-29 17:30 | Contractor stopped at the plant exit gate. The contractor believed the security guard waived him forward to exit the plant. The contractor did not wait for the exit gate to raise and drove into the security exit bar. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Michael Smith | 2019-12-06 08:58 | 2019-10-30 08:21 | 2019-10-31 07:15 | 2019-12-05 12:15 | 2019-11-12 17:30 | 2019-10-30 08:20 | 2019-12-05 12:17 |  |  | River Valley PP Security gate |  |  | Anthony Gillespie | Sharing the expectation for a renewed focus on situational awareness should help to reduce the likelihood to this incident reoccurring. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | TRUE |  | FALSE | TRUE | Michael Smith |  | Contractor stopped at the plant exit gate. The contractor believed the security guard waived him forward to exit the plant. The contractor did not wait for the exit gate to raise and drove into the security exit bar. Contractor stopped at the plant exit gate. The contractor believed the security guard waived him forward to exit the plant. The contractor did not wait for the exit gate to raise and drove into the security exit bar. |  |  |  | River Valley | FALSE |  | FALSE | Other |  | Larry Hammons | Michael Smith |  | Michael Smith | Corrective actions listed should be appropriate to reduce further recurrence. | Michael Smith |  | Low |  |  |  | 4.04 Routine, monotony, demand for uneventful vigilance | [12 empty] | Contractor inattention led to contact with the gate. | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) | [5 empty] | Vehicle |  | Michael Smith | Bent exit gate |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Larry Hammons | Zachary | Bill Cloyd |  | Structural |  | Michael Smith |  |  |  |  | FALSE | [42 empty] | Exit bar was bent. | 500 | Bill Cloyd | Structural |  |  | FALSE |  | Panama | Struck Fixed Object | Drove Forward Into Object |  |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Clear
9118 | River Valley | 2019-10-29 17:30 | Contractor stopped at the plant exit gate. The contractor believed the security guard waived him forward to exit the plant. The contractor did not wait for the exit gate to raise and drove into the security exit bar. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Michael Smith | 2019-12-06 08:58 | 2019-10-30 08:21 | 2019-10-31 07:15 | 2019-12-05 12:15 | 2019-11-12 17:30 | 2019-10-30 08:20 | 2019-12-05 12:17 |  |  | River Valley PP Security gate |  |  | Anthony Gillespie | Sharing the expectation for a renewed focus on situational awareness should help to reduce the likelihood to this incident reoccurring. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | TRUE |  | FALSE | TRUE | Michael Smith |  | Contractor stopped at the plant exit gate. The contractor believed the security guard waived him forward to exit the plant. The contractor did not wait for the exit gate to raise and drove into the security exit bar. Contractor stopped at the plant exit gate. The contractor believed the security guard waived him forward to exit the plant. The contractor did not wait for the exit gate to raise and drove into the security exit bar. |  |  |  | River Valley | FALSE |  | FALSE | Other |  | Larry Hammons | Michael Smith |  | Michael Smith | Corrective actions listed should be appropriate to reduce further recurrence. | Michael Smith |  | Low |  |  |  | 4.04 Routine, monotony, demand for uneventful vigilance | [12 empty] | Contractor inattention led to contact with the gate. | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Michael Smith | Bent exit gate |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Larry Hammons | Zachary | Bill Cloyd |  | Structural |  | Michael Smith |  |  |  |  | FALSE | [42 empty] | Exit bar was bent. | 500 | Bill Cloyd | Structural |  |  | FALSE |  | Panama | Struck Fixed Object | Drove Forward Into Object |  |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Clear
9118 | River Valley | 2019-10-29 17:30 | Contractor stopped at the plant exit gate. The contractor believed the security guard waived him forward to exit the plant. The contractor did not wait for the exit gate to raise and drove into the security exit bar. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Supply | Michael Smith | 2019-12-06 08:58 | 2019-10-30 08:21 | 2019-10-31 07:15 | 2019-12-05 12:15 | 2019-11-12 17:30 | 2019-10-30 08:20 | 2019-12-05 12:17 |  |  | River Valley PP Security gate |  |  | Anthony Gillespie | Sharing the expectation for a renewed focus on situational awareness should help to reduce the likelihood to this incident reoccurring. | Power Supply |  | Level 1 | Vehicle |  | TRUE | FALSE | TRUE |  | FALSE | TRUE | Michael Smith |  | Contractor stopped at the plant exit gate. The contractor believed the security guard waived him forward to exit the plant. The contractor did not wait for the exit gate to raise and drove into the security exit bar. Contractor stopped at the plant exit gate. The contractor believed the security guard waived him forward to exit the plant. The contractor did not wait for the exit gate to raise and drove into the security exit bar. |  |  |  | River Valley | FALSE |  | FALSE | Other |  | Larry Hammons | Michael Smith |  | Michael Smith | Corrective actions listed should be appropriate to reduce further recurrence. | Michael Smith |  | Low |  |  |  | 4.04 Routine, monotony, demand for uneventful vigilance | [12 empty] | Contractor inattention led to contact with the gate. | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) | [5 empty] | Vehicle |  | Michael Smith | Bent exit gate |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Larry Hammons | Zachary | Bill Cloyd |  | Structural |  | Michael Smith |  |  |  |  | FALSE | [42 empty] | Exit bar was bent. | 500 | Bill Cloyd | Structural |  |  | FALSE |  | Panama | Struck Fixed Object | Drove Forward Into Object |  |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Clear
9118 | River Valley | 2019-10-29 17:30 | Contractor stopped at the plant exit gate. The contractor believed the security guard waived him forward to exit the plant. The contractor did not wait for the exit gate to raise and drove into the security exit bar. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Supply | Michael Smith | 2019-12-06 08:58 | 2019-10-30 08:21 | 2019-10-31 07:15 | 2019-12-05 12:15 | 2019-11-12 17:30 | 2019-10-30 08:20 | 2019-12-05 12:17 |  |  | River Valley PP Security gate |  |  | Anthony Gillespie | Sharing the expectation for a renewed focus on situational awareness should help to reduce the likelihood to this incident reoccurring. | Power Supply |  | Level 1 | Vehicle |  | TRUE | FALSE | TRUE |  | FALSE | TRUE | Michael Smith |  | Contractor stopped at the plant exit gate. The contractor believed the security guard waived him forward to exit the plant. The contractor did not wait for the exit gate to raise and drove into the security exit bar. Contractor stopped at the plant exit gate. The contractor believed the security guard waived him forward to exit the plant. The contractor did not wait for the exit gate to raise and drove into the security exit bar. |  |  |  | River Valley | FALSE |  | FALSE | Other |  | Larry Hammons | Michael Smith |  | Michael Smith | Corrective actions listed should be appropriate to reduce further recurrence. | Michael Smith |  | Low |  |  |  | 4.04 Routine, monotony, demand for uneventful vigilance | [12 empty] | Contractor inattention led to contact with the gate. | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Michael Smith | Bent exit gate |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Larry Hammons | Zachary | Bill Cloyd |  | Structural |  | Michael Smith |  |  |  |  | FALSE | [42 empty] | Exit bar was bent. | 500 | Bill Cloyd | Structural |  |  | FALSE |  | Panama | Struck Fixed Object | Drove Forward Into Object |  |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Clear
9118 | River Valley | 2019-10-29 17:30 | Contractor stopped at the plant exit gate. The contractor believed the security guard waived him forward to exit the plant. The contractor did not wait for the exit gate to raise and drove into the security exit bar. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Michael Smith | 2019-12-06 08:58 | 2019-10-30 08:21 | 2019-10-31 07:15 | 2019-12-05 12:15 | 2019-11-12 17:30 | 2019-10-30 08:20 | 2019-12-05 12:17 |  |  | River Valley PP Security gate |  |  | Anthony Gillespie | Sharing the expectation for a renewed focus on situational awareness should help to reduce the likelihood to this incident reoccurring. | Power Supply |  | Level 1 | Property Damage |  | TRUE | FALSE | TRUE |  | FALSE | TRUE | Michael Smith |  | Contractor stopped at the plant exit gate. The contractor believed the security guard waived him forward to exit the plant. The contractor did not wait for the exit gate to raise and drove into the security exit bar. Contractor stopped at the plant exit gate. The contractor believed the security guard waived him forward to exit the plant. The contractor did not wait for the exit gate to raise and drove into the security exit bar. |  |  |  | River Valley | FALSE |  | FALSE | Other |  | Larry Hammons | Michael Smith |  | Michael Smith | Corrective actions listed should be appropriate to reduce further recurrence. | Michael Smith |  | Low |  |  |  | 4.04 Routine, monotony, demand for uneventful vigilance | [12 empty] | Contractor inattention led to contact with the gate. | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) | [5 empty] | Vehicle |  | Michael Smith | Bent exit gate |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Larry Hammons | Zachary | Bill Cloyd |  | Structural |  | Michael Smith |  |  |  |  | FALSE | [42 empty] | Exit bar was bent. | 500 | Bill Cloyd | Structural |  |  | FALSE |  | Panama | Struck Fixed Object | Drove Forward Into Object |  |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Clear
9118 | River Valley | 2019-10-29 17:30 | Contractor stopped at the plant exit gate. The contractor believed the security guard waived him forward to exit the plant. The contractor did not wait for the exit gate to raise and drove into the security exit bar. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Michael Smith | 2019-12-06 08:58 | 2019-10-30 08:21 | 2019-10-31 07:15 | 2019-12-05 12:15 | 2019-11-12 17:30 | 2019-10-30 08:20 | 2019-12-05 12:17 |  |  | River Valley PP Security gate |  |  | Anthony Gillespie | Sharing the expectation for a renewed focus on situational awareness should help to reduce the likelihood to this incident reoccurring. | Power Supply |  | Level 1 | Property Damage |  | TRUE | FALSE | TRUE |  | FALSE | TRUE | Michael Smith |  | Contractor stopped at the plant exit gate. The contractor believed the security guard waived him forward to exit the plant. The contractor did not wait for the exit gate to raise and drove into the security exit bar. Contractor stopped at the plant exit gate. The contractor believed the security guard waived him forward to exit the plant. The contractor did not wait for the exit gate to raise and drove into the security exit bar. |  |  |  | River Valley | FALSE |  | FALSE | Other |  | Larry Hammons | Michael Smith |  | Michael Smith | Corrective actions listed should be appropriate to reduce further recurrence. | Michael Smith |  | Low |  |  |  | 4.04 Routine, monotony, demand for uneventful vigilance | [12 empty] | Contractor inattention led to contact with the gate. | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Michael Smith | Bent exit gate |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Larry Hammons | Zachary | Bill Cloyd |  | Structural |  | Michael Smith |  |  |  |  | FALSE | [42 empty] | Exit bar was bent. | 500 | Bill Cloyd | Structural |  |  | FALSE |  | Panama | Struck Fixed Object | Drove Forward Into Object |  |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Clear
9119 | Redbud Plant | 2019-10-30 14:30 | Member was backing cart out of gravel area and while turning, cart rolled over onto driver side. No members injured. | Level 2 |  | TRUE | Vehicle |  |  |  |  | Power Supply | Robert Pennington | 2019-12-05 10:12 | 2019-10-30 14:56 | 2019-10-30 14:56 | 2019-11-15 16:23 | 2019-11-13 14:30 | 2019-10-30 14:45 | 2019-11-21 08:18 |  | 2019-11-19 17:32 | Redbud PP Unit 4, CTG Collector End, Outside Compartment |  |  | Jesse Murray | Jesse Murray 12/5/19 Approved. | Power Supply |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Robert Pennington |  | Aerotech member was working in the Unit 4 Collector Cab for Hot Gas Path Outage. Member was asked to get extra parts from warehouse. The area (west side of unit, outside of access door to Collector Cab building) cart was parked in and the travel path were free of congestion. The path of travel on the gravel was damp from drizzling rain that had occurred earlier. Member performed vehicle 360 and fastened seatbelt once in cart. Member started to drive in reverse and after traveling for approximately 40 ft., he turned to the right. He then felt front cart wheels start to slide and hit brakes. The cart turned over on the driver side. Member unbuckled his seatbelt and was able to safely get out of vehicle via passenger side door. Member received no injuries and cart took minimal damage. After surveying the area, a rock the size of a fist had scratch mark on it directly in the path of travel. It is believed that a combination of speed, direction of travel i.e. turning, braking too hard, and the rock may have caught the front wheel causing the turn over. Member had previously completed Parking and Vehicle Situational Awareness WBT. |  |  |  | Redbud Plant | FALSE |  | TRUE | Operations |  | Robert Pennington | Robert Pennington |  | Thomas Ward | Reviewed investigation and approve findings and action items. | Thomas Ward |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Driving too fast while in reverse and turning. | 15. Using Equipment Improperly | 9. Abnormal Operation |  | Have reviewed investigation and discussed action items with Rob. Agree with finding and report. | [90 empty] | 615566
9120 | Sooner Power Plant | 2019-10-31 02:30 | Member was in process of hanging LOTO on "A Clarifier Auto Back Flush Piping". Member had to enter barricaded area to get to valve to remove grating (valve is below grating). Member had called SS to ask to cross barricade. While walking inside barricaded area member stepped on grating and grating collapsed. Causing member to fall to grating. Member caught himself with hands and scraped right knee. Member did not require first aid. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Supply | Marc Hodgson | 2019-11-16 11:27 | 2019-10-31 03:25 | 2019-10-31 03:25 | 2019-11-06 12:58 | 2019-11-14 02:30 | 2019-10-31 02:40 | 2019-11-11 09:02 |  | 2019-11-07 12:54 | Sooner Plant Water Treatment Area between Water Treatment Building and Sand Filter Building. |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | On the morning of October 31, 2019 at about 0215 hours, members were instructed to hang a LOTO “A Clarifier Auto Backflush valve”. Members had a tail board with Shift Supervisor and Control Room operator prior to leaving to hang LOTO. Members took barricade tags with them as they were going to have to remove grating to close valve that was included in the LOTO. Once the members arrived at the area they seen that there was already a barricade in place for grating on the pit adjacent to the pit that had the valve in it. Members called Shift Supervisor to make aware of barricade and have permission to cross it in order to access area to remove and hang LOTO. Member then went to check “B Clarifier” to confirm that they were accessing the correct valve in “A Clarifier” pit. Once member confirmed this was the correct valve, he proceeded to cross barricade to help with the removal of toe links. He was aware of the hazards with in the barricaded area and had eyes on path to make sure that he did not step near hole that was in the grating. He was walking and had one foot (left) on the cement that is about 4 inches wide and his other foot (right) was on the grating. When member put his weight on his right foot the grating collapsed causing member to fall to his bottom catching himself with hands. His right leg went through the opening where the grating collapsed. Members then stopped work on LOTO, checked on member that had fail after initial evaluation, members brought him into dry warm area to evaluate member more thoroughly. Member did not have any major cuts or bruising, had some soreness to wrists and minor scrape on right knee cap. Member was wearing all appropriate PPE. Notification #447184 was written with a priority 2 to have grating repaired/replaced. Shift Supervisor contacted member the next day to check on him and member stated that he was feeling fine. FINDINGS • Notification was written for bad grating (see attachment), however it was not in the correct “planning center” for Sooner. It never pulled into our notification list. The “function location” was correct. • Currently, RO reject waste is being temporarily piped across grating to this ditch. This was re-routed because permanent underground line that drains to this ditch has a hole in it. • Regen waste (Acid/Caustic mix) was previously temporarily pumped across this grating to this ditch which could have led to the corrosion of the grating. Due to a failure of the neutralization tank • Barricade tag read “grating damage” with floor/deck opening marked. Members thought this was for the hole in the grating, not the eroded grating. Barricade erector knew grating was eroded but wrote "damaged grating". • Area is not very well lighted • Barricade has been in place for close to 2 years, originally the barricade was put in place not for bad grating but to eliminate exposure to the acid/caustic waste that was discharging into this ditch. As situation changed barricade boundaries stayed the same but the reasons for the barricade being in place changed. • RO reject line failed in place in December of 2017, plans were made to repair then halted due the probability that the Water House may be replaced. When decision was made to stay with the current Water House, it was asked for again to have replaced and is currently waiting on approval to be replaced. |  |  | FALSE | Sooner Power Plant | FALSE |  | FALSE | Operations |  | Marc Hodgson | Marc Hodgson |  | Alexander Taybah | The grating was replaced immediately right after the incident as an immediate corrective action. I approve. | Alexander Taybah |  | Medium |  |  |  | 4.07 Confusing directions/demands | 5.06 Lack of situational awareness | [11 empty] | Barricade tag read “grating damage” with floor/deck opening marked. Members thought this was for the hole in the grating, not the eroded grating. | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level |  | Approved by Brady Sowell on 11/7 | [24 empty] | FALSE |  |  | 2018-01-22 | 1983-08-25 |  | 2019-10-30 18:00 | 0 | 0 |  | FALSE |  | Member fell through grating. |  | FALSE | John Fortenberry |  | First Aid | John Fortenberry |  |  |  |  | Abrasion |  | FALSE |  | Plant Operator I | Knee |  | Right |  | Marc Hodgson |  |  | 10/30/2019 6:00:00 PM | 22 months | FALSE |  |  | Grating | Had a job briefing with Shift Supervisor and other members of crew that were involving in hanging LOTO.
9120 | Sooner Power Plant | 2019-10-31 02:30 | Member was in process of hanging LOTO on "A Clarifier Auto Back Flush Piping". Member had to enter barricaded area to get to valve to remove grating (valve is below grating). Member had called SS to ask to cross barricade. While walking inside barricaded area member stepped on grating and grating collapsed. Causing member to fall to grating. Member caught himself with hands and scraped right knee. Member did not require first aid. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Supply | Marc Hodgson | 2019-11-16 11:27 | 2019-10-31 03:25 | 2019-10-31 03:25 | 2019-11-06 12:58 | 2019-11-14 02:30 | 2019-10-31 02:40 | 2019-11-11 09:02 |  | 2019-11-07 12:54 | Sooner Plant Water Treatment Area between Water Treatment Building and Sand Filter Building. |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | On the morning of October 31, 2019 at about 0215 hours, members were instructed to hang a LOTO “A Clarifier Auto Backflush valve”. Members had a tail board with Shift Supervisor and Control Room operator prior to leaving to hang LOTO. Members took barricade tags with them as they were going to have to remove grating to close valve that was included in the LOTO. Once the members arrived at the area they seen that there was already a barricade in place for grating on the pit adjacent to the pit that had the valve in it. Members called Shift Supervisor to make aware of barricade and have permission to cross it in order to access area to remove and hang LOTO. Member then went to check “B Clarifier” to confirm that they were accessing the correct valve in “A Clarifier” pit. Once member confirmed this was the correct valve, he proceeded to cross barricade to help with the removal of toe links. He was aware of the hazards with in the barricaded area and had eyes on path to make sure that he did not step near hole that was in the grating. He was walking and had one foot (left) on the cement that is about 4 inches wide and his other foot (right) was on the grating. When member put his weight on his right foot the grating collapsed causing member to fall to his bottom catching himself with hands. His right leg went through the opening where the grating collapsed. Members then stopped work on LOTO, checked on member that had fail after initial evaluation, members brought him into dry warm area to evaluate member more thoroughly. Member did not have any major cuts or bruising, had some soreness to wrists and minor scrape on right knee cap. Member was wearing all appropriate PPE. Notification #447184 was written with a priority 2 to have grating repaired/replaced. Shift Supervisor contacted member the next day to check on him and member stated that he was feeling fine. FINDINGS • Notification was written for bad grating (see attachment), however it was not in the correct “planning center” for Sooner. It never pulled into our notification list. The “function location” was correct. • Currently, RO reject waste is being temporarily piped across grating to this ditch. This was re-routed because permanent underground line that drains to this ditch has a hole in it. • Regen waste (Acid/Caustic mix) was previously temporarily pumped across this grating to this ditch which could have led to the corrosion of the grating. Due to a failure of the neutralization tank • Barricade tag read “grating damage” with floor/deck opening marked. Members thought this was for the hole in the grating, not the eroded grating. Barricade erector knew grating was eroded but wrote "damaged grating". • Area is not very well lighted • Barricade has been in place for close to 2 years, originally the barricade was put in place not for bad grating but to eliminate exposure to the acid/caustic waste that was discharging into this ditch. As situation changed barricade boundaries stayed the same but the reasons for the barricade being in place changed. • RO reject line failed in place in December of 2017, plans were made to repair then halted due the probability that the Water House may be replaced. When decision was made to stay with the current Water House, it was asked for again to have replaced and is currently waiting on approval to be replaced. |  |  | FALSE | Sooner Power Plant | FALSE |  | FALSE | Operations |  | Marc Hodgson | Marc Hodgson |  | Alexander Taybah | The grating was replaced immediately right after the incident as an immediate corrective action. I approve. | Alexander Taybah |  | Medium | [11 empty] | 12.02.2 Inadequate reparative scheduling of work |  |  |  |  | • Currently, RO reject waste is being temporarily piped across grating to this ditch. This was re-routed because permanent underground line that drains to this ditch has a hole in it. • Regen waste (Acid/Caustic mix) was previously temporarily pumped across this grating to this ditch which could have led to the corrosion of the grating. Due to a failure of the neutralization tank | 33. Presence of Harmful Materials | 3. Fall from Elevation to Lower Level |  | Approved by Brady Sowell on 11/7 | [24 empty] | FALSE |  |  | 2018-01-22 | 1983-08-25 |  | 2019-10-30 18:00 | 0 | 0 |  | FALSE |  | Member fell through grating. |  | FALSE | John Fortenberry |  | First Aid | John Fortenberry |  |  |  |  | Abrasion |  | FALSE |  | Plant Operator I | Knee |  | Right |  | Marc Hodgson |  |  | 10/30/2019 6:00:00 PM | 22 months | FALSE |  |  | Grating | Had a job briefing with Shift Supervisor and other members of crew that were involving in hanging LOTO.
9120 | Sooner Power Plant | 2019-10-31 02:30 | Member was in process of hanging LOTO on "A Clarifier Auto Back Flush Piping". Member had to enter barricaded area to get to valve to remove grating (valve is below grating). Member had called SS to ask to cross barricade. While walking inside barricaded area member stepped on grating and grating collapsed. Causing member to fall to grating. Member caught himself with hands and scraped right knee. Member did not require first aid. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Supply | Marc Hodgson | 2019-11-16 11:27 | 2019-10-31 03:25 | 2019-10-31 03:25 | 2019-11-06 12:58 | 2019-11-14 02:30 | 2019-10-31 02:40 | 2019-11-11 09:02 |  | 2019-11-07 12:54 | Sooner Plant Water Treatment Area between Water Treatment Building and Sand Filter Building. |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Marc Hodgson |  | On the morning of October 31, 2019 at about 0215 hours, members were instructed to hang a LOTO “A Clarifier Auto Backflush valve”. Members had a tail board with Shift Supervisor and Control Room operator prior to leaving to hang LOTO. Members took barricade tags with them as they were going to have to remove grating to close valve that was included in the LOTO. Once the members arrived at the area they seen that there was already a barricade in place for grating on the pit adjacent to the pit that had the valve in it. Members called Shift Supervisor to make aware of barricade and have permission to cross it in order to access area to remove and hang LOTO. Member then went to check “B Clarifier” to confirm that they were accessing the correct valve in “A Clarifier” pit. Once member confirmed this was the correct valve, he proceeded to cross barricade to help with the removal of toe links. He was aware of the hazards with in the barricaded area and had eyes on path to make sure that he did not step near hole that was in the grating. He was walking and had one foot (left) on the cement that is about 4 inches wide and his other foot (right) was on the grating. When member put his weight on his right foot the grating collapsed causing member to fall to his bottom catching himself with hands. His right leg went through the opening where the grating collapsed. Members then stopped work on LOTO, checked on member that had fail after initial evaluation, members brought him into dry warm area to evaluate member more thoroughly. Member did not have any major cuts or bruising, had some soreness to wrists and minor scrape on right knee cap. Member was wearing all appropriate PPE. Notification #447184 was written with a priority 2 to have grating repaired/replaced. Shift Supervisor contacted member the next day to check on him and member stated that he was feeling fine. FINDINGS • Notification was written for bad grating (see attachment), however it was not in the correct “planning center” for Sooner. It never pulled into our notification list. The “function location” was correct. • Currently, RO reject waste is being temporarily piped across grating to this ditch. This was re-routed because permanent underground line that drains to this ditch has a hole in it. • Regen waste (Acid/Caustic mix) was previously temporarily pumped across this grating to this ditch which could have led to the corrosion of the grating. Due to a failure of the neutralization tank • Barricade tag read “grating damage” with floor/deck opening marked. Members thought this was for the hole in the grating, not the eroded grating. Barricade erector knew grating was eroded but wrote "damaged grating". • Area is not very well lighted • Barricade has been in place for close to 2 years, originally the barricade was put in place not for bad grating but to eliminate exposure to the acid/caustic waste that was discharging into this ditch. As situation changed barricade boundaries stayed the same but the reasons for the barricade being in place changed. • RO reject line failed in place in December of 2017, plans were made to repair then halted due the probability that the Water House may be replaced. When decision was made to stay with the current Water House, it was asked for again to have replaced and is currently waiting on approval to be replaced. |  |  | FALSE | Sooner Power Plant | FALSE |  | FALSE | Operations |  | Marc Hodgson | Marc Hodgson |  | Alexander Taybah | The grating was replaced immediately right after the incident as an immediate corrective action. I approve. | Alexander Taybah |  | Medium | [8 empty] | 9.06 Inadequate work planning or programming |  |  |  | 13.07 Inadequate removal and replacement of unsuitable items |  |  |  | Notification was written for bad grating, however it was not in the correct “planning center” for Sooner. It never pulled into our notification list. The “function location” was correct. | 23. Defective Tools, Equipment or Materials | 3. Fall from Elevation to Lower Level |  | Approved by Brady Sowell on 11/7 | [24 empty] | FALSE |  |  | 2018-01-22 | 1983-08-25 |  | 2019-10-30 18:00 | 0 | 0 |  | FALSE |  | Member fell through grating. |  | FALSE | John Fortenberry |  | First Aid | John Fortenberry |  |  |  |  | Abrasion |  | FALSE |  | Plant Operator I | Knee |  | Right |  | Marc Hodgson |  |  | 10/30/2019 6:00:00 PM | 22 months | FALSE |  |  | Grating | Had a job briefing with Shift Supervisor and other members of crew that were involving in hanging LOTO.
9121 | Shawnee Service Center | 2019-10-31 08:30 | Company Vehicle was travelling southbound on Milt Phillips when public driver pulled out from behind a building into the path of the company driver. Front left fender contacted the rear left quarter panel of public vehicle. No injuries occurred. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Mark Martin | 2019-11-12 09:26 | 2019-10-31 11:03 | 2019-10-31 11:03 | 2019-10-31 11:06 | 2019-11-14 07:30 | 2019-10-31 10:56 |  |  |  | Milt Phillips & Broadway Seminole, OK |  |  | Luke Kennedy | Approved | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | [6 empty] | Shawnee Service Center | FALSE |  | FALSE | Construction Services |  | Austin Berg | Mark Martin |  |  |  | Terry Garrett |  | Low | [93 empty] | FALSE |  | Seminole | Public Vehicle Struck OGE | Both Vehicles Moving | 2014-05-18 19:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
9122 | Seminole PP; EGX Gath/Trans | 2019-10-30 18:50 | While cleaning in the administrative offices, a janitorial contractor noticed a burning smell. She investigated and determined the source of the smell to be a space heater under a desk. There was no visible evidence of fire or of burning material. | Level 1 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Bryan Pool | 2019-12-19 16:13 | 2019-10-31 14:23 | 2019-10-31 14:23 | 2019-12-05 10:34 | 2019-11-13 18:50 | 2019-10-31 09:00 | 2019-12-05 14:06 |  |  | Seminole Power Plant, Administrative office |  |  | Chrysty Dorsey | Reviewed and Approved | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Bryan Pool |  | Janitorial contractors arrived at Seminole plant at approximately 6:30 on October 30th to perform nightly cleaning duties. Upon arrival they notified the control room that they were onsite. At approximately 6:50, while cleaning in one of the administrative offices, the contractor noticed the smell of something burning. The contractor surveyed the area to see if she could determine the source of the smell. She discovered an operating space heater under the office desk which she concluded to be the source of the smell. She wanted to check with someone prior to unplugging the heater so she called the OGE administrative contact. Note: the OGE contact was not at the plant. After explaining the situation to the OGE member, both concluded that the heater should be unplugged. The contractor unplugged the heater and continued with her duties. Shortly after this, the contractor found another similar heater in the women’s bathroom which she also unplugged. The next morning when the member who had the heater in her office arrived, she was informed of the events from the previous evening. She then reported the event to her supervisor as a near miss. Investigation findings: A visual inspection of the heater and surrounding areas was performed. The heater showed no signs of failure nor evidence that combustion had occurred. Likewise, the area immediately surrounding the heater was free of debris and showed no signs that combustion had occurred. Furthermore, the heater was disassembled and inspected. The internal components of the heater showed no indication that combustion had occurred. Based on the examination of the area and an internal and external inspection of the heater, it was concluded that combustion had not occurred. It was determined that the smell noticed by the janitorial contractor was most likely a normal smell of the heating coils operating OR possibly a smell associate with dust or similar airborne material settling onto the heating coils. Investigation Findings: 1) It was determined that the heater in question was an unapproved heater. OGE has two heaters approved for office environments, one radiant heat floor heater and one desktop ceramic heater. 2) Procedures and training content were both reviewed to ensure approved heater requirements were adequately communicated. The Seminole Fire Prevention Operating Instruction States: “Only OGE approved “under desk” space heaters may be utilized in office areas. These heaters must be used consistent with manufacturer design and use instructions and properly installed and maintained.” Within the office safety WBT there is an interactive office safety inspection, in which one of the examples is an unapproved heater under a desk. After the participant reviews the picture and enters comments into the inspection the following screen describes the hazard in the picture and shows pictures of both approved heaters and lists the respective material numbers. The member reviewed the Fire Prevention OI on March 16th of 2018 and completed the office safety WBT on June 5th of 2019. It was concluded, through conversations with the member, that it was known that the heater was not approved for use. The member indicated that the heater had been in the office when she began employment 13 years ago and she never removed it due to its preferred heating ability. 3) Additionally, through the investigation it was discovered that this particular heater was covered under a 2010 Consumer Product Safety Commission (CPSC) recall. The reason for the recall was reports of “fire and burn hazards”. The heaters were sold exclusively at Wal-Mart for $18. The recall covered 2.2 million units and at the time of the recall Wal-Mart had received 21 reports of incidents associated with the heaters. More details of the recall can be found on the attachment titled “CPSC Recall Sheet”. While this heater was covered under the recall, the determination still stands that there was no malfunction nor combustion. Additional findings: Approved heater availability – At the time of the investigation both approved heaters were out of stock in the general service center, with no open purchase orders. Additionally, neither of the items had a safety stock listed. Supply Chain was notified of the inventory issue and safety stock issue and is working to resolve the issue. An additional item to note is that the heaters were only extended to certain plants within Power Supply. Both items will need extended to all Power Supply locations before the heaters can be ordered at the plants. Initial report of the event – As indicated in the investigation findings, when the contractor noticed the burning smell she worked to identify the source and then notified her administrative contact who was off-site. The correct action would have been to notify the control room upon the initial indication of the burning smell. The contractor had received the plant orientation video which states “All emergency situations must be phoned into the control room at x8651 or 405-553-8651”. Through conversations with the contractor she believed that contacting her administrative contact was the correct action and it never occurred to her to contact the control room. Additionally, upon receiving the call from the contractor, the administrative contact should have directed her to notify the control room. Approved heater performance – During the investigation it was suggested that the approved heaters are lacking in their heating ability and therefore people still have unapproved heaters in service. While this does not justify use of unapproved heaters, there will be a corrective action added to investigation additional heater options. Facility Inspection – As follow-up to this near miss, an inspection was done of administrative offices at Seminole. There were 6 additional unapproved heaters found that were removed from service. It is possible that similar conditions exist at other locations. A corrective action will be created for safety task forces to perform inspections of administrative areas in search of unapproved heaters. Notification of recalled items – In discussions with Supply Chain, while we may receive notice of recalled items through manufacturers and suppliers it is not a full-proof system that guarantees we are informed of all recalled items. It is however more likely we would receive notice of a recall for an item that had an approved material number. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | TRUE | Quality Assurance |  |  | Bryan Pool |  | Donnie Jones | Very good action items created from the investigation. I concur with moving forward with implementing necessary changes. | Donnie Jones |  | Low | [6 empty] | 7.07 Improper attempt to avoid discomfort | [9 empty] | Unapproved heater in use | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise)
9123 | River Valley | 2019-10-30 13:30 | Operator was emptying ash from a rocker box hopper into a rental dump truck using a forklift. Operator didn't see the arm supporting the dump truck tarp and drove hopper into arm bending it. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | George Haney | 2019-11-25 13:39 | 2019-10-31 14:54 | 2019-10-31 14:53 | 2019-11-15 09:49 | 2019-11-13 13:30 | 2019-10-30 14:30 | 2019-11-25 09:58 |  |  | Ground floor level west of 2B boiler |  |  | Anthony Gillespie | Corrective actions appropriate to reduce likelihood of reoccurrence. | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | George Haney |  | Operator was emptying ash from a rocker box hopper into a rental dump truck using a forklift. Operator didn't see the arm supporting the dump truck tarp and drove hopper into arm bending it. Operator was emptying rocks from screens for bed ash vacuum system using a rocker box hopper dump material into a rental dump truck using a forklift. Operator didn't see the arm supporting the dump truck tarp and drove hopper into arm bending it. Reviewing the pictures took after the damage was found showed that the tarp arm was very hard to see against the cloud foggy sky. Misting rain also contributed to the visibility as the operator said it was getting on his safety glasses. |  |  |  | River Valley | FALSE |  | FALSE | Operations |  | Bernard Terbieten Jr | George Haney |  | Timothy Chancellor | Agree with need for spotter when using these hoppers. | Timothy Chancellor |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [7 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | Misting rain and fog conditions effected vision | 40. Weather Conditions | 1. Struck Against (Running or Bumping Into) | [68 empty] | bent tarp arm | 1000 | Bernard Terbieten Jr | Industrial/Heavy Equipment |  | Rental | [18 empty] | WO 9590878
9124 | Sooner Power Plant | 2019-11-02 10:00 | Member mistakenly drilled into fire water line thinking it was a floor drain line. LOTO was taken on fire water system and line was repaired. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Trent Novotny | 2019-12-04 10:50 | 2019-11-02 13:14 | 2019-11-05 15:48 | 2019-11-18 07:56 | 2019-11-16 10:00 | 2019-11-02 12:48 | 2019-11-18 08:01 |  |  | Sooner PP Unit 2 Level 5.5 on West side of boiler |  |  | Brady Sowell | Sowell approves on 11/25. This incident is now waiting to be placed on the hotsheet or call. | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Frank Brixey |  | An order was assigned to a mechanical crew and upon the supervisors review he noticed the order to be vague. The supervisor spoke to his planner about the job and he didn't have any more details. The order stated to see a certain member for more details, but that person was on vacation. The supervisor went ahead and handed the order to a mechanic, but told him that they needed to walk the job together. The job was to install a solid floor below the ignitor oil header over-pressure system with drains in this area to contain any fuel oil spills to prevent the fuel oil from dripping onto pulverizer piping below. The supervisor and member went to level 5.5 corner 2 and determined the design and location of the drip pan and looked for a where to tie into the fuel oil drain line. They spotted what they believed to be a fuel oil drain line and traced with their eyes and saw the line penetrate the diamond plate floor fuel oil catch pan on the next level. They made a quick hasty decision that this had to be the drain line and didn't go up to the next level to verify exactly what that pipe was for and planned to tie into that pipe. After getting everything prepped to install, the mechanic drilled a 1/4" hole into the line and water began to spray out. The member traced the line to the next level and realized it was a fire water line. The mechanic contacted supervisor. Supervisor went to operations and notified them of what had happened. Operations hung a LOTO and the mechanic welded over the hole. The work stopped there until additional information from engineering is provided for where to tie in. Upon investigation it was determined that the order shouldn't have been executed without more details. The order should have been a configuration control event, but due to the age of the order it had been in the backlog prior to marking orders for CC. Planner did not catch it before dispatching order. The supervisor and mechanic should have stopped the job until more information was provided. Do to the pressure of schedule success metric and a strong drive to complete work the supervisor felt they could get the work done safely with the information provided so carried on with the work. LOTO was not needed due to tying into an open drain line. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Houston Mendenhall | Trent Novotny |  | Frank Brixey | Approved - Brixey 11/18/2019 | Frank Brixey |  | Low | [6 empty] | 7.06 Improper attempt to save time or effort | [9 empty] | Failure to identify proper drain line | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [92 empty] | 5676029
9124 | Sooner Power Plant | 2019-11-02 10:00 | Member mistakenly drilled into fire water line thinking it was a floor drain line. LOTO was taken on fire water system and line was repaired. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Trent Novotny | 2019-12-04 10:50 | 2019-11-02 13:14 | 2019-11-05 15:48 | 2019-11-18 07:56 | 2019-11-16 10:00 | 2019-11-02 12:48 | 2019-11-18 08:01 |  |  | Sooner PP Unit 2 Level 5.5 on West side of boiler |  |  | Brady Sowell | Sowell approves on 11/25. This incident is now waiting to be placed on the hotsheet or call. | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Frank Brixey |  | An order was assigned to a mechanical crew and upon the supervisors review he noticed the order to be vague. The supervisor spoke to his planner about the job and he didn't have any more details. The order stated to see a certain member for more details, but that person was on vacation. The supervisor went ahead and handed the order to a mechanic, but told him that they needed to walk the job together. The job was to install a solid floor below the ignitor oil header over-pressure system with drains in this area to contain any fuel oil spills to prevent the fuel oil from dripping onto pulverizer piping below. The supervisor and member went to level 5.5 corner 2 and determined the design and location of the drip pan and looked for a where to tie into the fuel oil drain line. They spotted what they believed to be a fuel oil drain line and traced with their eyes and saw the line penetrate the diamond plate floor fuel oil catch pan on the next level. They made a quick hasty decision that this had to be the drain line and didn't go up to the next level to verify exactly what that pipe was for and planned to tie into that pipe. After getting everything prepped to install, the mechanic drilled a 1/4" hole into the line and water began to spray out. The member traced the line to the next level and realized it was a fire water line. The mechanic contacted supervisor. Supervisor went to operations and notified them of what had happened. Operations hung a LOTO and the mechanic welded over the hole. The work stopped there until additional information from engineering is provided for where to tie in. Upon investigation it was determined that the order shouldn't have been executed without more details. The order should have been a configuration control event, but due to the age of the order it had been in the backlog prior to marking orders for CC. Planner did not catch it before dispatching order. The supervisor and mechanic should have stopped the job until more information was provided. Do to the pressure of schedule success metric and a strong drive to complete work the supervisor felt they could get the work done safely with the information provided so carried on with the work. LOTO was not needed due to tying into an open drain line. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Houston Mendenhall | Trent Novotny |  | Frank Brixey | Approved - Brixey 11/18/2019 | Frank Brixey |  | Low | [8 empty] | 9.06 Inadequate work planning or programming | [7 empty] | Order was not planned properly or marked configuration control | 35. Inadequate Information, Data | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [92 empty] | 5676029
9125 | River Valley | 2019-11-02 08:25 | Zachry contractors removed the bolts form the wrong unit condensate pump. The crew was supposed to be working on unit 1 and went to unit 2 and began removing bolts on the running unit's condensate pump suction expansion joint. | Level 3 |  | TRUE | Contractor | Donnie Jones | Jesse Murray | Jesse, I would like for Lee Morris to be on this team for sure. I would like to include Travis Morgan as well (our newly named LOTO coord.). Regards, Andy | 2019-11-12 11:39 | Power Supply | Melton Morris |  | 2019-11-02 15:32 | 2019-11-02 15:32 | 2019-12-13 10:21 | 2019-11-16 08:25 | 2019-11-02 08:30 | 2020-01-14 16:28 | 2020-02-05 12:11 | 2019-12-20 11:19 | River Valley Unit 2 Condensate pump suction expansion joint. |  |  |  |  | Power Supply |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Melton Morris |  | A crew of contractors were assigned a task to remove the expansion joint on a condensate pump to inspect the strainer and the joint. The person who portrayed himself as the Zachary crew leader to OG&E contact was walked through the job. This individual then went and got the tools and the rest of his crew, but they went to the incorrect unit when they returned to go to work. The individual lead the crew back to the wrong unit, the actual crew leader stopped off to use the restroom while the crew proceeded to work.. The TSA that the Zachary supervision completed was inadequate and the crew leader did not verify the job location prior to the crew removing bolts. The OG&E contact member was waiting for the crew on the correct unit, but the crew never showed back up. The person who portrayed himself as the crew leader then falsified his statement to Zachary supervision and said "Someone in a full brim yellow hardhat told him to go to the unit they was working on". Zachary supervision dismissed his story as false and agreed that the crew walked to the incorrect unit where no tags or locks were present and they did not verify the line was drained prior to removing the bolts. | Travis Morgan | Melton Morris |  | River Valley | FALSE |  | TRUE | Operations |  | Ricky Welch | Melton Morris |  | Timothy Chancellor | Approved | Timothy Chancellor | Jesse Murray | High |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Zachary new hires had not begun Zachary accelerated orientation program. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. Jesse Murray 2/5/20 | Corrective actions listed should greatly reduce the likelihood of a similar incident reoccurring once completed. |  |  |  | Clearance / LOTO |  | Melton Morris | [5 empty] | 9. Abnormal Operation | Ricky Welch | Zachry | Aaron Hall |  |  |  | Brian Hillebrand
9125 | River Valley | 2019-11-02 08:25 | Zachry contractors removed the bolts form the wrong unit condensate pump. The crew was supposed to be working on unit 1 and went to unit 2 and began removing bolts on the running unit's condensate pump suction expansion joint. | Level 3 |  | TRUE | Contractor | Donnie Jones | Jesse Murray | Jesse, I would like for Lee Morris to be on this team for sure. I would like to include Travis Morgan as well (our newly named LOTO coord.). Regards, Andy | 2019-11-12 11:39 | Power Supply | Melton Morris |  | 2019-11-02 15:32 | 2019-11-02 15:32 | 2019-12-13 10:21 | 2019-11-16 08:25 | 2019-11-02 08:30 | 2020-01-14 16:28 | 2020-02-05 12:11 | 2019-12-20 11:19 | River Valley Unit 2 Condensate pump suction expansion joint. |  |  |  |  | Power Supply |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Melton Morris |  | A crew of contractors were assigned a task to remove the expansion joint on a condensate pump to inspect the strainer and the joint. The person who portrayed himself as the Zachary crew leader to OG&E contact was walked through the job. This individual then went and got the tools and the rest of his crew, but they went to the incorrect unit when they returned to go to work. The individual lead the crew back to the wrong unit, the actual crew leader stopped off to use the restroom while the crew proceeded to work.. The TSA that the Zachary supervision completed was inadequate and the crew leader did not verify the job location prior to the crew removing bolts. The OG&E contact member was waiting for the crew on the correct unit, but the crew never showed back up. The person who portrayed himself as the crew leader then falsified his statement to Zachary supervision and said "Someone in a full brim yellow hardhat told him to go to the unit they was working on". Zachary supervision dismissed his story as false and agreed that the crew walked to the incorrect unit where no tags or locks were present and they did not verify the line was drained prior to removing the bolts. | Travis Morgan | Melton Morris |  | River Valley | FALSE |  | TRUE | Operations |  | Ricky Welch | Melton Morris |  | Timothy Chancellor | Approved | Timothy Chancellor | Jesse Murray | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Zachary new hires had not begun Zachary accelerated orientation program. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. Jesse Murray 2/5/20 | Corrective actions listed should greatly reduce the likelihood of a similar incident reoccurring once completed. |  |  |  | Clearance / LOTO |  | Melton Morris | [5 empty] | 9. Abnormal Operation | Ricky Welch | Zachry | Aaron Hall |  |  |  | Brian Hillebrand
9125 | River Valley | 2019-11-02 08:25 | Zachry contractors removed the bolts form the wrong unit condensate pump. The crew was supposed to be working on unit 1 and went to unit 2 and began removing bolts on the running unit's condensate pump suction expansion joint. | Level 3 |  | TRUE | Contractor | Donnie Jones | Jesse Murray | Jesse, I would like for Lee Morris to be on this team for sure. I would like to include Travis Morgan as well (our newly named LOTO coord.). Regards, Andy | 2019-11-12 11:39 | Power Supply | Melton Morris |  | 2019-11-02 15:32 | 2019-11-02 15:32 | 2019-12-13 10:21 | 2019-11-16 08:25 | 2019-11-02 08:30 | 2020-01-14 16:28 | 2020-02-05 12:11 | 2019-12-20 11:19 | River Valley Unit 2 Condensate pump suction expansion joint. |  |  |  |  | Power Supply |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Melton Morris |  | A crew of contractors were assigned a task to remove the expansion joint on a condensate pump to inspect the strainer and the joint. The person who portrayed himself as the Zachary crew leader to OG&E contact was walked through the job. This individual then went and got the tools and the rest of his crew, but they went to the incorrect unit when they returned to go to work. The individual lead the crew back to the wrong unit, the actual crew leader stopped off to use the restroom while the crew proceeded to work.. The TSA that the Zachary supervision completed was inadequate and the crew leader did not verify the job location prior to the crew removing bolts. The OG&E contact member was waiting for the crew on the correct unit, but the crew never showed back up. The person who portrayed himself as the crew leader then falsified his statement to Zachary supervision and said "Someone in a full brim yellow hardhat told him to go to the unit they was working on". Zachary supervision dismissed his story as false and agreed that the crew walked to the incorrect unit where no tags or locks were present and they did not verify the line was drained prior to removing the bolts. | Travis Morgan | Melton Morris |  | River Valley | FALSE |  | TRUE | Operations |  | Ricky Welch | Melton Morris |  | Timothy Chancellor | Approved | Timothy Chancellor | Jesse Murray | High |  |  |  |  | 5.02 Inadequate orientation |  |  |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Zachary new hires had not begun Zachary accelerated orientation program. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. Jesse Murray 2/5/20 | Corrective actions listed should greatly reduce the likelihood of a similar incident reoccurring once completed. |  |  |  | Clearance / LOTO |  | Melton Morris | [5 empty] | 9. Abnormal Operation | Ricky Welch | Zachry | Aaron Hall |  |  |  | Brian Hillebrand
9125 | River Valley | 2019-11-02 08:25 | Zachry contractors removed the bolts form the wrong unit condensate pump. The crew was supposed to be working on unit 1 and went to unit 2 and began removing bolts on the running unit's condensate pump suction expansion joint. | Level 3 |  | TRUE | Contractor | Donnie Jones | Jesse Murray | Jesse, I would like for Lee Morris to be on this team for sure. I would like to include Travis Morgan as well (our newly named LOTO coord.). Regards, Andy | 2019-11-12 11:39 | Power Supply | Melton Morris |  | 2019-11-02 15:32 | 2019-11-02 15:32 | 2019-12-13 10:21 | 2019-11-16 08:25 | 2019-11-02 08:30 | 2020-01-14 16:28 | 2020-02-05 12:11 | 2019-12-20 11:19 | River Valley Unit 2 Condensate pump suction expansion joint. |  |  |  |  | Power Supply |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Melton Morris |  | A crew of contractors were assigned a task to remove the expansion joint on a condensate pump to inspect the strainer and the joint. The person who portrayed himself as the Zachary crew leader to OG&E contact was walked through the job. This individual then went and got the tools and the rest of his crew, but they went to the incorrect unit when they returned to go to work. The individual lead the crew back to the wrong unit, the actual crew leader stopped off to use the restroom while the crew proceeded to work.. The TSA that the Zachary supervision completed was inadequate and the crew leader did not verify the job location prior to the crew removing bolts. The OG&E contact member was waiting for the crew on the correct unit, but the crew never showed back up. The person who portrayed himself as the crew leader then falsified his statement to Zachary supervision and said "Someone in a full brim yellow hardhat told him to go to the unit they was working on". Zachary supervision dismissed his story as false and agreed that the crew walked to the incorrect unit where no tags or locks were present and they did not verify the line was drained prior to removing the bolts. | Travis Morgan | Melton Morris |  | River Valley | FALSE |  | TRUE | Operations |  | Ricky Welch | Melton Morris |  | Timothy Chancellor | Approved | Timothy Chancellor | Jesse Murray | High | [8 empty] | 9.09 Inadequate identification and evaluation of loss exposures | [7 empty] | Zachary TSA (Zachary Pre Job Safety Form) was not adequate in addressing the job steps and associated hazards. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. Jesse Murray 2/5/20 | Corrective actions listed should greatly reduce the likelihood of a similar incident reoccurring once completed. |  |  |  | Clearance / LOTO |  | Melton Morris | [5 empty] | 9. Abnormal Operation | Ricky Welch | Zachry | Aaron Hall |  |  |  | Brian Hillebrand
9125 | River Valley | 2019-11-02 08:25 | Zachry contractors removed the bolts form the wrong unit condensate pump. The crew was supposed to be working on unit 1 and went to unit 2 and began removing bolts on the running unit's condensate pump suction expansion joint. | Level 3 |  | TRUE | Contractor | Donnie Jones | Jesse Murray | Jesse, I would like for Lee Morris to be on this team for sure. I would like to include Travis Morgan as well (our newly named LOTO coord.). Regards, Andy | 2019-11-12 11:39 | Power Supply | Melton Morris |  | 2019-11-02 15:32 | 2019-11-02 15:32 | 2019-12-13 10:21 | 2019-11-16 08:25 | 2019-11-02 08:30 | 2020-01-14 16:28 | 2020-02-05 12:11 | 2019-12-20 11:19 | River Valley Unit 2 Condensate pump suction expansion joint. |  |  |  |  | Power Supply |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Melton Morris |  | A crew of contractors were assigned a task to remove the expansion joint on a condensate pump to inspect the strainer and the joint. The person who portrayed himself as the Zachary crew leader to OG&E contact was walked through the job. This individual then went and got the tools and the rest of his crew, but they went to the incorrect unit when they returned to go to work. The individual lead the crew back to the wrong unit, the actual crew leader stopped off to use the restroom while the crew proceeded to work.. The TSA that the Zachary supervision completed was inadequate and the crew leader did not verify the job location prior to the crew removing bolts. The OG&E contact member was waiting for the crew on the correct unit, but the crew never showed back up. The person who portrayed himself as the crew leader then falsified his statement to Zachary supervision and said "Someone in a full brim yellow hardhat told him to go to the unit they was working on". Zachary supervision dismissed his story as false and agreed that the crew walked to the incorrect unit where no tags or locks were present and they did not verify the line was drained prior to removing the bolts. | Travis Morgan | Melton Morris |  | River Valley | FALSE |  | TRUE | Operations |  | Ricky Welch | Melton Morris |  | Timothy Chancellor | Approved | Timothy Chancellor | Jesse Murray | High | [8 empty] | 9.06 Inadequate work planning or programming | [7 empty] | Zachary TSA (Zachary Pre Job Safety Form) was not adequate in addressing the job steps and associated hazards. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. Jesse Murray 2/5/20 | Corrective actions listed should greatly reduce the likelihood of a similar incident reoccurring once completed. |  |  |  | Clearance / LOTO |  | Melton Morris | [5 empty] | 9. Abnormal Operation | Ricky Welch | Zachry | Aaron Hall |  |  |  | Brian Hillebrand
9125 | River Valley | 2019-11-02 08:25 | Zachry contractors removed the bolts form the wrong unit condensate pump. The crew was supposed to be working on unit 1 and went to unit 2 and began removing bolts on the running unit's condensate pump suction expansion joint. | Level 3 |  | TRUE | Contractor | Donnie Jones | Jesse Murray | Jesse, I would like for Lee Morris to be on this team for sure. I would like to include Travis Morgan as well (our newly named LOTO coord.). Regards, Andy | 2019-11-12 11:39 | Power Supply | Melton Morris |  | 2019-11-02 15:32 | 2019-11-02 15:32 | 2019-12-13 10:21 | 2019-11-16 08:25 | 2019-11-02 08:30 | 2020-01-14 16:28 | 2020-02-05 12:11 | 2019-12-20 11:19 | River Valley Unit 2 Condensate pump suction expansion joint. |  |  |  |  | Power Supply |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Melton Morris |  | A crew of contractors were assigned a task to remove the expansion joint on a condensate pump to inspect the strainer and the joint. The person who portrayed himself as the Zachary crew leader to OG&E contact was walked through the job. This individual then went and got the tools and the rest of his crew, but they went to the incorrect unit when they returned to go to work. The individual lead the crew back to the wrong unit, the actual crew leader stopped off to use the restroom while the crew proceeded to work.. The TSA that the Zachary supervision completed was inadequate and the crew leader did not verify the job location prior to the crew removing bolts. The OG&E contact member was waiting for the crew on the correct unit, but the crew never showed back up. The person who portrayed himself as the crew leader then falsified his statement to Zachary supervision and said "Someone in a full brim yellow hardhat told him to go to the unit they was working on". Zachary supervision dismissed his story as false and agreed that the crew walked to the incorrect unit where no tags or locks were present and they did not verify the line was drained prior to removing the bolts. | Travis Morgan | Melton Morris |  | River Valley | FALSE |  | TRUE | Operations |  | Ricky Welch | Melton Morris |  | Timothy Chancellor | Approved | Timothy Chancellor | Jesse Murray | High |  |  |  |  | 5.01 Lack of experience |  | 7.08 Improper attempt to gain attention | [9 empty] | A crew of contractors were assigned a task to remove the expansion joint on a condensate pump to inspect the strainer and the joint. The person who portrayed himself as the crew leader to OG&E contact was walked through the job. This individual then went and got the tools and the rest of his crew, but they went to the incorrect unit when they returned to go to work. | 17. Failure to Identify Hazard, Risk | 9. Abnormal Operation | Approved. Jesse Murray 2/5/20 | Corrective actions listed should greatly reduce the likelihood of a similar incident reoccurring once completed. |  |  |  | Clearance / LOTO |  | Melton Morris | [5 empty] | 9. Abnormal Operation | Ricky Welch | Zachry | Aaron Hall |  |  |  | Brian Hillebrand
9125 | River Valley | 2019-11-02 08:25 | Zachry contractors removed the bolts form the wrong unit condensate pump. The crew was supposed to be working on unit 1 and went to unit 2 and began removing bolts on the running unit's condensate pump suction expansion joint. | Level 3 |  | TRUE | Contractor | Donnie Jones | Jesse Murray | Jesse, I would like for Lee Morris to be on this team for sure. I would like to include Travis Morgan as well (our newly named LOTO coord.). Regards, Andy | 2019-11-12 11:39 | Power Supply | Melton Morris |  | 2019-11-02 15:32 | 2019-11-02 15:32 | 2019-12-13 10:21 | 2019-11-16 08:25 | 2019-11-02 08:30 | 2020-01-14 16:28 | 2020-02-05 12:11 | 2019-12-20 11:19 | River Valley Unit 2 Condensate pump suction expansion joint. |  |  |  |  | Power Supply |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Melton Morris |  | A crew of contractors were assigned a task to remove the expansion joint on a condensate pump to inspect the strainer and the joint. The person who portrayed himself as the Zachary crew leader to OG&E contact was walked through the job. This individual then went and got the tools and the rest of his crew, but they went to the incorrect unit when they returned to go to work. The individual lead the crew back to the wrong unit, the actual crew leader stopped off to use the restroom while the crew proceeded to work.. The TSA that the Zachary supervision completed was inadequate and the crew leader did not verify the job location prior to the crew removing bolts. The OG&E contact member was waiting for the crew on the correct unit, but the crew never showed back up. The person who portrayed himself as the crew leader then falsified his statement to Zachary supervision and said "Someone in a full brim yellow hardhat told him to go to the unit they was working on". Zachary supervision dismissed his story as false and agreed that the crew walked to the incorrect unit where no tags or locks were present and they did not verify the line was drained prior to removing the bolts. | Travis Morgan | Melton Morris |  | River Valley | FALSE |  | TRUE | Operations |  | Ricky Welch | Melton Morris |  | Timothy Chancellor | Approved | Timothy Chancellor | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness |  | 7.08 Improper attempt to gain attention | [9 empty] | A crew of contractors were assigned a task to remove the expansion joint on a condensate pump to inspect the strainer and the joint. The person who portrayed himself as the crew leader to OG&E contact was walked through the job. This individual then went and got the tools and the rest of his crew, but they went to the incorrect unit when they returned to go to work. | 17. Failure to Identify Hazard, Risk | 9. Abnormal Operation | Approved. Jesse Murray 2/5/20 | Corrective actions listed should greatly reduce the likelihood of a similar incident reoccurring once completed. |  |  |  | Clearance / LOTO |  | Melton Morris | [5 empty] | 9. Abnormal Operation | Ricky Welch | Zachry | Aaron Hall |  |  |  | Brian Hillebrand
9125 | River Valley | 2019-11-02 08:25 | Zachry contractors removed the bolts form the wrong unit condensate pump. The crew was supposed to be working on unit 1 and went to unit 2 and began removing bolts on the running unit's condensate pump suction expansion joint. | Level 3 |  | TRUE | Contractor | Donnie Jones | Jesse Murray | Jesse, I would like for Lee Morris to be on this team for sure. I would like to include Travis Morgan as well (our newly named LOTO coord.). Regards, Andy | 2019-11-12 11:39 | Power Supply | Melton Morris |  | 2019-11-02 15:32 | 2019-11-02 15:32 | 2019-12-13 10:21 | 2019-11-16 08:25 | 2019-11-02 08:30 | 2020-01-14 16:28 | 2020-02-05 12:11 | 2019-12-20 11:19 | River Valley Unit 2 Condensate pump suction expansion joint. |  |  |  |  | Power Supply |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Melton Morris |  | A crew of contractors were assigned a task to remove the expansion joint on a condensate pump to inspect the strainer and the joint. The person who portrayed himself as the Zachary crew leader to OG&E contact was walked through the job. This individual then went and got the tools and the rest of his crew, but they went to the incorrect unit when they returned to go to work. The individual lead the crew back to the wrong unit, the actual crew leader stopped off to use the restroom while the crew proceeded to work.. The TSA that the Zachary supervision completed was inadequate and the crew leader did not verify the job location prior to the crew removing bolts. The OG&E contact member was waiting for the crew on the correct unit, but the crew never showed back up. The person who portrayed himself as the crew leader then falsified his statement to Zachary supervision and said "Someone in a full brim yellow hardhat told him to go to the unit they was working on". Zachary supervision dismissed his story as false and agreed that the crew walked to the incorrect unit where no tags or locks were present and they did not verify the line was drained prior to removing the bolts. | Travis Morgan | Melton Morris |  | River Valley | FALSE |  | TRUE | Operations |  | Ricky Welch | Melton Morris |  | Timothy Chancellor | Approved | Timothy Chancellor | Jesse Murray | High |  |  |  |  | 5.01 Lack of experience | [11 empty] | Failure to verify zero energy on running equipment. | 12. Servicing Equipment in Operation | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. Jesse Murray 2/5/20 | Corrective actions listed should greatly reduce the likelihood of a similar incident reoccurring once completed. |  |  |  | Clearance / LOTO |  | Melton Morris | [5 empty] | 9. Abnormal Operation | Ricky Welch | Zachry | Aaron Hall |  |  |  | Brian Hillebrand
9125 | River Valley | 2019-11-02 08:25 | Zachry contractors removed the bolts form the wrong unit condensate pump. The crew was supposed to be working on unit 1 and went to unit 2 and began removing bolts on the running unit's condensate pump suction expansion joint. | Level 3 |  | TRUE | Contractor | Donnie Jones | Jesse Murray | Jesse, I would like for Lee Morris to be on this team for sure. I would like to include Travis Morgan as well (our newly named LOTO coord.). Regards, Andy | 2019-11-12 11:39 | Power Supply | Melton Morris |  | 2019-11-02 15:32 | 2019-11-02 15:32 | 2019-12-13 10:21 | 2019-11-16 08:25 | 2019-11-02 08:30 | 2020-01-14 16:28 | 2020-02-05 12:11 | 2019-12-20 11:19 | River Valley Unit 2 Condensate pump suction expansion joint. |  |  |  |  | Power Supply |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Melton Morris |  | A crew of contractors were assigned a task to remove the expansion joint on a condensate pump to inspect the strainer and the joint. The person who portrayed himself as the Zachary crew leader to OG&E contact was walked through the job. This individual then went and got the tools and the rest of his crew, but they went to the incorrect unit when they returned to go to work. The individual lead the crew back to the wrong unit, the actual crew leader stopped off to use the restroom while the crew proceeded to work.. The TSA that the Zachary supervision completed was inadequate and the crew leader did not verify the job location prior to the crew removing bolts. The OG&E contact member was waiting for the crew on the correct unit, but the crew never showed back up. The person who portrayed himself as the crew leader then falsified his statement to Zachary supervision and said "Someone in a full brim yellow hardhat told him to go to the unit they was working on". Zachary supervision dismissed his story as false and agreed that the crew walked to the incorrect unit where no tags or locks were present and they did not verify the line was drained prior to removing the bolts. | Travis Morgan | Melton Morris |  | River Valley | FALSE |  | TRUE | Operations |  | Ricky Welch | Melton Morris |  | Timothy Chancellor | Approved | Timothy Chancellor | Jesse Murray | High |  |  |  |  | 5.05 Misunderstood directions | [11 empty] | Failure to verify zero energy on running equipment. | 12. Servicing Equipment in Operation | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. Jesse Murray 2/5/20 | Corrective actions listed should greatly reduce the likelihood of a similar incident reoccurring once completed. |  |  |  | Clearance / LOTO |  | Melton Morris | [5 empty] | 9. Abnormal Operation | Ricky Welch | Zachry | Aaron Hall |  |  |  | Brian Hillebrand
9125 | River Valley | 2019-11-02 08:25 | Zachry contractors removed the bolts form the wrong unit condensate pump. The crew was supposed to be working on unit 1 and went to unit 2 and began removing bolts on the running unit's condensate pump suction expansion joint. | Level 3 |  | TRUE | Contractor | Donnie Jones | Jesse Murray | Jesse, I would like for Lee Morris to be on this team for sure. I would like to include Travis Morgan as well (our newly named LOTO coord.). Regards, Andy | 2019-11-12 11:39 | Power Supply | Melton Morris |  | 2019-11-02 15:32 | 2019-11-02 15:32 | 2019-12-13 10:21 | 2019-11-16 08:25 | 2019-11-02 08:30 | 2020-01-14 16:28 | 2020-02-05 12:11 | 2019-12-20 11:19 | River Valley Unit 2 Condensate pump suction expansion joint. |  |  |  |  | Power Supply |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Melton Morris |  | A crew of contractors were assigned a task to remove the expansion joint on a condensate pump to inspect the strainer and the joint. The person who portrayed himself as the Zachary crew leader to OG&E contact was walked through the job. This individual then went and got the tools and the rest of his crew, but they went to the incorrect unit when they returned to go to work. The individual lead the crew back to the wrong unit, the actual crew leader stopped off to use the restroom while the crew proceeded to work.. The TSA that the Zachary supervision completed was inadequate and the crew leader did not verify the job location prior to the crew removing bolts. The OG&E contact member was waiting for the crew on the correct unit, but the crew never showed back up. The person who portrayed himself as the crew leader then falsified his statement to Zachary supervision and said "Someone in a full brim yellow hardhat told him to go to the unit they was working on". Zachary supervision dismissed his story as false and agreed that the crew walked to the incorrect unit where no tags or locks were present and they did not verify the line was drained prior to removing the bolts. | Travis Morgan | Melton Morris |  | River Valley | FALSE |  | TRUE | Operations |  | Ricky Welch | Melton Morris |  | Timothy Chancellor | Approved | Timothy Chancellor | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Failure to verify zero energy on running equipment. | 12. Servicing Equipment in Operation | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. Jesse Murray 2/5/20 | Corrective actions listed should greatly reduce the likelihood of a similar incident reoccurring once completed. |  |  |  | Clearance / LOTO |  | Melton Morris | [5 empty] | 9. Abnormal Operation | Ricky Welch | Zachry | Aaron Hall |  |  |  | Brian Hillebrand
9125 | River Valley | 2019-11-02 08:25 | Zachry contractors removed the bolts form the wrong unit condensate pump. The crew was supposed to be working on unit 1 and went to unit 2 and began removing bolts on the running unit's condensate pump suction expansion joint. | Level 3 |  | TRUE | Contractor | Donnie Jones | Jesse Murray | Jesse, I would like for Lee Morris to be on this team for sure. I would like to include Travis Morgan as well (our newly named LOTO coord.). Regards, Andy | 2019-11-12 11:39 | Power Supply | Melton Morris |  | 2019-11-02 15:32 | 2019-11-02 15:32 | 2019-12-13 10:21 | 2019-11-16 08:25 | 2019-11-02 08:30 | 2020-01-14 16:28 | 2020-02-05 12:11 | 2019-12-20 11:19 | River Valley Unit 2 Condensate pump suction expansion joint. |  |  |  |  | Power Supply |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Melton Morris |  | A crew of contractors were assigned a task to remove the expansion joint on a condensate pump to inspect the strainer and the joint. The person who portrayed himself as the Zachary crew leader to OG&E contact was walked through the job. This individual then went and got the tools and the rest of his crew, but they went to the incorrect unit when they returned to go to work. The individual lead the crew back to the wrong unit, the actual crew leader stopped off to use the restroom while the crew proceeded to work.. The TSA that the Zachary supervision completed was inadequate and the crew leader did not verify the job location prior to the crew removing bolts. The OG&E contact member was waiting for the crew on the correct unit, but the crew never showed back up. The person who portrayed himself as the crew leader then falsified his statement to Zachary supervision and said "Someone in a full brim yellow hardhat told him to go to the unit they was working on". Zachary supervision dismissed his story as false and agreed that the crew walked to the incorrect unit where no tags or locks were present and they did not verify the line was drained prior to removing the bolts. | Anthony Gillespie | Melton Morris |  | River Valley | FALSE |  | TRUE | Operations |  | Ricky Welch | Melton Morris |  | Timothy Chancellor | Approved | Timothy Chancellor | Jesse Murray | High |  |  |  |  | 5.01 Lack of experience |  |  |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Zachary new hires had not begun Zachary accelerated orientation program. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. Jesse Murray 2/5/20 | Corrective actions listed should greatly reduce the likelihood of a similar incident reoccurring once completed. |  |  |  | Clearance / LOTO |  | Melton Morris | [5 empty] | 9. Abnormal Operation | Ricky Welch | Zachry | Aaron Hall |  |  |  | Brian Hillebrand
9125 | River Valley | 2019-11-02 08:25 | Zachry contractors removed the bolts form the wrong unit condensate pump. The crew was supposed to be working on unit 1 and went to unit 2 and began removing bolts on the running unit's condensate pump suction expansion joint. | Level 3 |  | TRUE | Contractor | Donnie Jones | Jesse Murray | Jesse, I would like for Lee Morris to be on this team for sure. I would like to include Travis Morgan as well (our newly named LOTO coord.). Regards, Andy | 2019-11-12 11:39 | Power Supply | Melton Morris |  | 2019-11-02 15:32 | 2019-11-02 15:32 | 2019-12-13 10:21 | 2019-11-16 08:25 | 2019-11-02 08:30 | 2020-01-14 16:28 | 2020-02-05 12:11 | 2019-12-20 11:19 | River Valley Unit 2 Condensate pump suction expansion joint. |  |  |  |  | Power Supply |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Melton Morris |  | A crew of contractors were assigned a task to remove the expansion joint on a condensate pump to inspect the strainer and the joint. The person who portrayed himself as the Zachary crew leader to OG&E contact was walked through the job. This individual then went and got the tools and the rest of his crew, but they went to the incorrect unit when they returned to go to work. The individual lead the crew back to the wrong unit, the actual crew leader stopped off to use the restroom while the crew proceeded to work.. The TSA that the Zachary supervision completed was inadequate and the crew leader did not verify the job location prior to the crew removing bolts. The OG&E contact member was waiting for the crew on the correct unit, but the crew never showed back up. The person who portrayed himself as the crew leader then falsified his statement to Zachary supervision and said "Someone in a full brim yellow hardhat told him to go to the unit they was working on". Zachary supervision dismissed his story as false and agreed that the crew walked to the incorrect unit where no tags or locks were present and they did not verify the line was drained prior to removing the bolts. | Anthony Gillespie | Melton Morris |  | River Valley | FALSE |  | TRUE | Operations |  | Ricky Welch | Melton Morris |  | Timothy Chancellor | Approved | Timothy Chancellor | Jesse Murray | High |  |  |  |  | 5.03 Inadequate initial training |  |  |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Zachary new hires had not begun Zachary accelerated orientation program. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. Jesse Murray 2/5/20 | Corrective actions listed should greatly reduce the likelihood of a similar incident reoccurring once completed. |  |  |  | Clearance / LOTO |  | Melton Morris | [5 empty] | 9. Abnormal Operation | Ricky Welch | Zachry | Aaron Hall |  |  |  | Brian Hillebrand
9125 | River Valley | 2019-11-02 08:25 | Zachry contractors removed the bolts form the wrong unit condensate pump. The crew was supposed to be working on unit 1 and went to unit 2 and began removing bolts on the running unit's condensate pump suction expansion joint. | Level 3 |  | TRUE | Contractor | Donnie Jones | Jesse Murray | Jesse, I would like for Lee Morris to be on this team for sure. I would like to include Travis Morgan as well (our newly named LOTO coord.). Regards, Andy | 2019-11-12 11:39 | Power Supply | Melton Morris |  | 2019-11-02 15:32 | 2019-11-02 15:32 | 2019-12-13 10:21 | 2019-11-16 08:25 | 2019-11-02 08:30 | 2020-01-14 16:28 | 2020-02-05 12:11 | 2019-12-20 11:19 | River Valley Unit 2 Condensate pump suction expansion joint. |  |  |  |  | Power Supply |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Melton Morris |  | A crew of contractors were assigned a task to remove the expansion joint on a condensate pump to inspect the strainer and the joint. The person who portrayed himself as the Zachary crew leader to OG&E contact was walked through the job. This individual then went and got the tools and the rest of his crew, but they went to the incorrect unit when they returned to go to work. The individual lead the crew back to the wrong unit, the actual crew leader stopped off to use the restroom while the crew proceeded to work.. The TSA that the Zachary supervision completed was inadequate and the crew leader did not verify the job location prior to the crew removing bolts. The OG&E contact member was waiting for the crew on the correct unit, but the crew never showed back up. The person who portrayed himself as the crew leader then falsified his statement to Zachary supervision and said "Someone in a full brim yellow hardhat told him to go to the unit they was working on". Zachary supervision dismissed his story as false and agreed that the crew walked to the incorrect unit where no tags or locks were present and they did not verify the line was drained prior to removing the bolts. | Anthony Gillespie | Melton Morris |  | River Valley | FALSE |  | TRUE | Operations |  | Ricky Welch | Melton Morris |  | Timothy Chancellor | Approved | Timothy Chancellor | Jesse Murray | High |  |  |  |  | 5.02 Inadequate orientation |  |  |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Zachary new hires had not begun Zachary accelerated orientation program. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. Jesse Murray 2/5/20 | Corrective actions listed should greatly reduce the likelihood of a similar incident reoccurring once completed. |  |  |  | Clearance / LOTO |  | Melton Morris | [5 empty] | 9. Abnormal Operation | Ricky Welch | Zachry | Aaron Hall |  |  |  | Brian Hillebrand
9125 | River Valley | 2019-11-02 08:25 | Zachry contractors removed the bolts form the wrong unit condensate pump. The crew was supposed to be working on unit 1 and went to unit 2 and began removing bolts on the running unit's condensate pump suction expansion joint. | Level 3 |  | TRUE | Contractor | Donnie Jones | Jesse Murray | Jesse, I would like for Lee Morris to be on this team for sure. I would like to include Travis Morgan as well (our newly named LOTO coord.). Regards, Andy | 2019-11-12 11:39 | Power Supply | Melton Morris |  | 2019-11-02 15:32 | 2019-11-02 15:32 | 2019-12-13 10:21 | 2019-11-16 08:25 | 2019-11-02 08:30 | 2020-01-14 16:28 | 2020-02-05 12:11 | 2019-12-20 11:19 | River Valley Unit 2 Condensate pump suction expansion joint. |  |  |  |  | Power Supply |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Melton Morris |  | A crew of contractors were assigned a task to remove the expansion joint on a condensate pump to inspect the strainer and the joint. The person who portrayed himself as the Zachary crew leader to OG&E contact was walked through the job. This individual then went and got the tools and the rest of his crew, but they went to the incorrect unit when they returned to go to work. The individual lead the crew back to the wrong unit, the actual crew leader stopped off to use the restroom while the crew proceeded to work.. The TSA that the Zachary supervision completed was inadequate and the crew leader did not verify the job location prior to the crew removing bolts. The OG&E contact member was waiting for the crew on the correct unit, but the crew never showed back up. The person who portrayed himself as the crew leader then falsified his statement to Zachary supervision and said "Someone in a full brim yellow hardhat told him to go to the unit they was working on". Zachary supervision dismissed his story as false and agreed that the crew walked to the incorrect unit where no tags or locks were present and they did not verify the line was drained prior to removing the bolts. | Anthony Gillespie | Melton Morris |  | River Valley | FALSE |  | TRUE | Operations |  | Ricky Welch | Melton Morris |  | Timothy Chancellor | Approved | Timothy Chancellor | Jesse Murray | High | [8 empty] | 9.09 Inadequate identification and evaluation of loss exposures | [7 empty] | Zachary TSA (Zachary Pre Job Safety Form) was not adequate in addressing the job steps and associated hazards. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. Jesse Murray 2/5/20 | Corrective actions listed should greatly reduce the likelihood of a similar incident reoccurring once completed. |  |  |  | Clearance / LOTO |  | Melton Morris | [5 empty] | 9. Abnormal Operation | Ricky Welch | Zachry | Aaron Hall |  |  |  | Brian Hillebrand
9125 | River Valley | 2019-11-02 08:25 | Zachry contractors removed the bolts form the wrong unit condensate pump. The crew was supposed to be working on unit 1 and went to unit 2 and began removing bolts on the running unit's condensate pump suction expansion joint. | Level 3 |  | TRUE | Contractor | Donnie Jones | Jesse Murray | Jesse, I would like for Lee Morris to be on this team for sure. I would like to include Travis Morgan as well (our newly named LOTO coord.). Regards, Andy | 2019-11-12 11:39 | Power Supply | Melton Morris |  | 2019-11-02 15:32 | 2019-11-02 15:32 | 2019-12-13 10:21 | 2019-11-16 08:25 | 2019-11-02 08:30 | 2020-01-14 16:28 | 2020-02-05 12:11 | 2019-12-20 11:19 | River Valley Unit 2 Condensate pump suction expansion joint. |  |  |  |  | Power Supply |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Melton Morris |  | A crew of contractors were assigned a task to remove the expansion joint on a condensate pump to inspect the strainer and the joint. The person who portrayed himself as the Zachary crew leader to OG&E contact was walked through the job. This individual then went and got the tools and the rest of his crew, but they went to the incorrect unit when they returned to go to work. The individual lead the crew back to the wrong unit, the actual crew leader stopped off to use the restroom while the crew proceeded to work.. The TSA that the Zachary supervision completed was inadequate and the crew leader did not verify the job location prior to the crew removing bolts. The OG&E contact member was waiting for the crew on the correct unit, but the crew never showed back up. The person who portrayed himself as the crew leader then falsified his statement to Zachary supervision and said "Someone in a full brim yellow hardhat told him to go to the unit they was working on". Zachary supervision dismissed his story as false and agreed that the crew walked to the incorrect unit where no tags or locks were present and they did not verify the line was drained prior to removing the bolts. | Anthony Gillespie | Melton Morris |  | River Valley | FALSE |  | TRUE | Operations |  | Ricky Welch | Melton Morris |  | Timothy Chancellor | Approved | Timothy Chancellor | Jesse Murray | High | [8 empty] | 9.06 Inadequate work planning or programming | [7 empty] | Zachary TSA (Zachary Pre Job Safety Form) was not adequate in addressing the job steps and associated hazards. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. Jesse Murray 2/5/20 | Corrective actions listed should greatly reduce the likelihood of a similar incident reoccurring once completed. |  |  |  | Clearance / LOTO |  | Melton Morris | [5 empty] | 9. Abnormal Operation | Ricky Welch | Zachry | Aaron Hall |  |  |  | Brian Hillebrand
9125 | River Valley | 2019-11-02 08:25 | Zachry contractors removed the bolts form the wrong unit condensate pump. The crew was supposed to be working on unit 1 and went to unit 2 and began removing bolts on the running unit's condensate pump suction expansion joint. | Level 3 |  | TRUE | Contractor | Donnie Jones | Jesse Murray | Jesse, I would like for Lee Morris to be on this team for sure. I would like to include Travis Morgan as well (our newly named LOTO coord.). Regards, Andy | 2019-11-12 11:39 | Power Supply | Melton Morris |  | 2019-11-02 15:32 | 2019-11-02 15:32 | 2019-12-13 10:21 | 2019-11-16 08:25 | 2019-11-02 08:30 | 2020-01-14 16:28 | 2020-02-05 12:11 | 2019-12-20 11:19 | River Valley Unit 2 Condensate pump suction expansion joint. |  |  |  |  | Power Supply |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Melton Morris |  | A crew of contractors were assigned a task to remove the expansion joint on a condensate pump to inspect the strainer and the joint. The person who portrayed himself as the Zachary crew leader to OG&E contact was walked through the job. This individual then went and got the tools and the rest of his crew, but they went to the incorrect unit when they returned to go to work. The individual lead the crew back to the wrong unit, the actual crew leader stopped off to use the restroom while the crew proceeded to work.. The TSA that the Zachary supervision completed was inadequate and the crew leader did not verify the job location prior to the crew removing bolts. The OG&E contact member was waiting for the crew on the correct unit, but the crew never showed back up. The person who portrayed himself as the crew leader then falsified his statement to Zachary supervision and said "Someone in a full brim yellow hardhat told him to go to the unit they was working on". Zachary supervision dismissed his story as false and agreed that the crew walked to the incorrect unit where no tags or locks were present and they did not verify the line was drained prior to removing the bolts. | Anthony Gillespie | Melton Morris |  | River Valley | FALSE |  | TRUE | Operations |  | Ricky Welch | Melton Morris |  | Timothy Chancellor | Approved | Timothy Chancellor | Jesse Murray | High |  |  |  |  | 5.01 Lack of experience |  | 7.08 Improper attempt to gain attention | [9 empty] | A crew of contractors were assigned a task to remove the expansion joint on a condensate pump to inspect the strainer and the joint. The person who portrayed himself as the crew leader to OG&E contact was walked through the job. This individual then went and got the tools and the rest of his crew, but they went to the incorrect unit when they returned to go to work. | 17. Failure to Identify Hazard, Risk | 9. Abnormal Operation | Approved. Jesse Murray 2/5/20 | Corrective actions listed should greatly reduce the likelihood of a similar incident reoccurring once completed. |  |  |  | Clearance / LOTO |  | Melton Morris | [5 empty] | 9. Abnormal Operation | Ricky Welch | Zachry | Aaron Hall |  |  |  | Brian Hillebrand
9125 | River Valley | 2019-11-02 08:25 | Zachry contractors removed the bolts form the wrong unit condensate pump. The crew was supposed to be working on unit 1 and went to unit 2 and began removing bolts on the running unit's condensate pump suction expansion joint. | Level 3 |  | TRUE | Contractor | Donnie Jones | Jesse Murray | Jesse, I would like for Lee Morris to be on this team for sure. I would like to include Travis Morgan as well (our newly named LOTO coord.). Regards, Andy | 2019-11-12 11:39 | Power Supply | Melton Morris |  | 2019-11-02 15:32 | 2019-11-02 15:32 | 2019-12-13 10:21 | 2019-11-16 08:25 | 2019-11-02 08:30 | 2020-01-14 16:28 | 2020-02-05 12:11 | 2019-12-20 11:19 | River Valley Unit 2 Condensate pump suction expansion joint. |  |  |  |  | Power Supply |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Melton Morris |  | A crew of contractors were assigned a task to remove the expansion joint on a condensate pump to inspect the strainer and the joint. The person who portrayed himself as the Zachary crew leader to OG&E contact was walked through the job. This individual then went and got the tools and the rest of his crew, but they went to the incorrect unit when they returned to go to work. The individual lead the crew back to the wrong unit, the actual crew leader stopped off to use the restroom while the crew proceeded to work.. The TSA that the Zachary supervision completed was inadequate and the crew leader did not verify the job location prior to the crew removing bolts. The OG&E contact member was waiting for the crew on the correct unit, but the crew never showed back up. The person who portrayed himself as the crew leader then falsified his statement to Zachary supervision and said "Someone in a full brim yellow hardhat told him to go to the unit they was working on". Zachary supervision dismissed his story as false and agreed that the crew walked to the incorrect unit where no tags or locks were present and they did not verify the line was drained prior to removing the bolts. | Anthony Gillespie | Melton Morris |  | River Valley | FALSE |  | TRUE | Operations |  | Ricky Welch | Melton Morris |  | Timothy Chancellor | Approved | Timothy Chancellor | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness |  | 7.08 Improper attempt to gain attention | [9 empty] | A crew of contractors were assigned a task to remove the expansion joint on a condensate pump to inspect the strainer and the joint. The person who portrayed himself as the crew leader to OG&E contact was walked through the job. This individual then went and got the tools and the rest of his crew, but they went to the incorrect unit when they returned to go to work. | 17. Failure to Identify Hazard, Risk | 9. Abnormal Operation | Approved. Jesse Murray 2/5/20 | Corrective actions listed should greatly reduce the likelihood of a similar incident reoccurring once completed. |  |  |  | Clearance / LOTO |  | Melton Morris | [5 empty] | 9. Abnormal Operation | Ricky Welch | Zachry | Aaron Hall |  |  |  | Brian Hillebrand
9125 | River Valley | 2019-11-02 08:25 | Zachry contractors removed the bolts form the wrong unit condensate pump. The crew was supposed to be working on unit 1 and went to unit 2 and began removing bolts on the running unit's condensate pump suction expansion joint. | Level 3 |  | TRUE | Contractor | Donnie Jones | Jesse Murray | Jesse, I would like for Lee Morris to be on this team for sure. I would like to include Travis Morgan as well (our newly named LOTO coord.). Regards, Andy | 2019-11-12 11:39 | Power Supply | Melton Morris |  | 2019-11-02 15:32 | 2019-11-02 15:32 | 2019-12-13 10:21 | 2019-11-16 08:25 | 2019-11-02 08:30 | 2020-01-14 16:28 | 2020-02-05 12:11 | 2019-12-20 11:19 | River Valley Unit 2 Condensate pump suction expansion joint. |  |  |  |  | Power Supply |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Melton Morris |  | A crew of contractors were assigned a task to remove the expansion joint on a condensate pump to inspect the strainer and the joint. The person who portrayed himself as the Zachary crew leader to OG&E contact was walked through the job. This individual then went and got the tools and the rest of his crew, but they went to the incorrect unit when they returned to go to work. The individual lead the crew back to the wrong unit, the actual crew leader stopped off to use the restroom while the crew proceeded to work.. The TSA that the Zachary supervision completed was inadequate and the crew leader did not verify the job location prior to the crew removing bolts. The OG&E contact member was waiting for the crew on the correct unit, but the crew never showed back up. The person who portrayed himself as the crew leader then falsified his statement to Zachary supervision and said "Someone in a full brim yellow hardhat told him to go to the unit they was working on". Zachary supervision dismissed his story as false and agreed that the crew walked to the incorrect unit where no tags or locks were present and they did not verify the line was drained prior to removing the bolts. | Anthony Gillespie | Melton Morris |  | River Valley | FALSE |  | TRUE | Operations |  | Ricky Welch | Melton Morris |  | Timothy Chancellor | Approved | Timothy Chancellor | Jesse Murray | High |  |  |  |  | 5.01 Lack of experience | [11 empty] | Failure to verify zero energy on running equipment. | 12. Servicing Equipment in Operation | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. Jesse Murray 2/5/20 | Corrective actions listed should greatly reduce the likelihood of a similar incident reoccurring once completed. |  |  |  | Clearance / LOTO |  | Melton Morris | [5 empty] | 9. Abnormal Operation | Ricky Welch | Zachry | Aaron Hall |  |  |  | Brian Hillebrand
9125 | River Valley | 2019-11-02 08:25 | Zachry contractors removed the bolts form the wrong unit condensate pump. The crew was supposed to be working on unit 1 and went to unit 2 and began removing bolts on the running unit's condensate pump suction expansion joint. | Level 3 |  | TRUE | Contractor | Donnie Jones | Jesse Murray | Jesse, I would like for Lee Morris to be on this team for sure. I would like to include Travis Morgan as well (our newly named LOTO coord.). Regards, Andy | 2019-11-12 11:39 | Power Supply | Melton Morris |  | 2019-11-02 15:32 | 2019-11-02 15:32 | 2019-12-13 10:21 | 2019-11-16 08:25 | 2019-11-02 08:30 | 2020-01-14 16:28 | 2020-02-05 12:11 | 2019-12-20 11:19 | River Valley Unit 2 Condensate pump suction expansion joint. |  |  |  |  | Power Supply |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Melton Morris |  | A crew of contractors were assigned a task to remove the expansion joint on a condensate pump to inspect the strainer and the joint. The person who portrayed himself as the Zachary crew leader to OG&E contact was walked through the job. This individual then went and got the tools and the rest of his crew, but they went to the incorrect unit when they returned to go to work. The individual lead the crew back to the wrong unit, the actual crew leader stopped off to use the restroom while the crew proceeded to work.. The TSA that the Zachary supervision completed was inadequate and the crew leader did not verify the job location prior to the crew removing bolts. The OG&E contact member was waiting for the crew on the correct unit, but the crew never showed back up. The person who portrayed himself as the crew leader then falsified his statement to Zachary supervision and said "Someone in a full brim yellow hardhat told him to go to the unit they was working on". Zachary supervision dismissed his story as false and agreed that the crew walked to the incorrect unit where no tags or locks were present and they did not verify the line was drained prior to removing the bolts. | Anthony Gillespie | Melton Morris |  | River Valley | FALSE |  | TRUE | Operations |  | Ricky Welch | Melton Morris |  | Timothy Chancellor | Approved | Timothy Chancellor | Jesse Murray | High |  |  |  |  | 5.05 Misunderstood directions | [11 empty] | Failure to verify zero energy on running equipment. | 12. Servicing Equipment in Operation | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. Jesse Murray 2/5/20 | Corrective actions listed should greatly reduce the likelihood of a similar incident reoccurring once completed. |  |  |  | Clearance / LOTO |  | Melton Morris | [5 empty] | 9. Abnormal Operation | Ricky Welch | Zachry | Aaron Hall |  |  |  | Brian Hillebrand
9125 | River Valley | 2019-11-02 08:25 | Zachry contractors removed the bolts form the wrong unit condensate pump. The crew was supposed to be working on unit 1 and went to unit 2 and began removing bolts on the running unit's condensate pump suction expansion joint. | Level 3 |  | TRUE | Contractor | Donnie Jones | Jesse Murray | Jesse, I would like for Lee Morris to be on this team for sure. I would like to include Travis Morgan as well (our newly named LOTO coord.). Regards, Andy | 2019-11-12 11:39 | Power Supply | Melton Morris |  | 2019-11-02 15:32 | 2019-11-02 15:32 | 2019-12-13 10:21 | 2019-11-16 08:25 | 2019-11-02 08:30 | 2020-01-14 16:28 | 2020-02-05 12:11 | 2019-12-20 11:19 | River Valley Unit 2 Condensate pump suction expansion joint. |  |  |  |  | Power Supply |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Melton Morris |  | A crew of contractors were assigned a task to remove the expansion joint on a condensate pump to inspect the strainer and the joint. The person who portrayed himself as the Zachary crew leader to OG&E contact was walked through the job. This individual then went and got the tools and the rest of his crew, but they went to the incorrect unit when they returned to go to work. The individual lead the crew back to the wrong unit, the actual crew leader stopped off to use the restroom while the crew proceeded to work.. The TSA that the Zachary supervision completed was inadequate and the crew leader did not verify the job location prior to the crew removing bolts. The OG&E contact member was waiting for the crew on the correct unit, but the crew never showed back up. The person who portrayed himself as the crew leader then falsified his statement to Zachary supervision and said "Someone in a full brim yellow hardhat told him to go to the unit they was working on". Zachary supervision dismissed his story as false and agreed that the crew walked to the incorrect unit where no tags or locks were present and they did not verify the line was drained prior to removing the bolts. | Anthony Gillespie | Melton Morris |  | River Valley | FALSE |  | TRUE | Operations |  | Ricky Welch | Melton Morris |  | Timothy Chancellor | Approved | Timothy Chancellor | Jesse Murray | High |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Failure to verify zero energy on running equipment. | 12. Servicing Equipment in Operation | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. Jesse Murray 2/5/20 | Corrective actions listed should greatly reduce the likelihood of a similar incident reoccurring once completed. |  |  |  | Clearance / LOTO |  | Melton Morris | [5 empty] | 9. Abnormal Operation | Ricky Welch | Zachry | Aaron Hall |  |  |  | Brian Hillebrand
9126 | Sooner Power Plant | 2019-11-03 11:00 | Vendor (Howden) dropped small flashlight off 2A ID Fan. Flashlight fell approximately 8-10 feet. No injuries. | Level 1 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services | Ashley Harris | 2019-11-25 16:17 | 2019-11-04 09:09 | 2019-11-04 09:08 | 2019-11-15 09:09 | 2019-11-17 11:00 | 2019-11-04 08:35 | 2019-11-19 11:09 |  |  | Sooner Power Plant- 2A ID Fan |  |  | Marcus Huddleston | No additional comments. MLH 11/25/19 | UTS |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Ashley Harris |  | Vendor from Howden, Chuck Seagle dropped a small flashlight white taking pictures of OB fan shaft RENK bearing. The flashlight fell one floor between concrete pedestal and grating opening on the concrete below. No injuries. Tool Tethers were not being utilized. To minimize the potential for dropped objects all tools utilized by a contractor working at heights higher than four feet are required to be tethered. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | UTS - Capital Projects |  | Richard Wood | Ashley Harris |  | Robert Weaver | Agree with the assessment | Robert Weaver |  | Low |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming | [7 empty] | Vendor from Howden, Chuck Seagle dropped a small flashlight white taking pictures of OB fan shaft RENK bearing. The flashlight fell one floor between concrete pedestal and grating opening on the concrete below. No injuries. Tool Tethers were not being utilized. To minimize the potential for dropped objects all tools utilized by a contractor working at heights higher than four feet are required to be tethered. | 16. Failure to Follow Procedure, Policy, Practice | 2. Struck By (Hit By Moving Object) | [5 empty] | Injury / Illness |  | Ashley Harris | [5 empty] | 2. Struck By (Hit By Moving Object) | Richard Wood | Howden | Chuck Seagle |  |  |  | Ashley Harris
9127 | Crossroads Wind Farm | 2019-11-03 14:00 | While assembling crane boom, contractor lacerated finger on pin puller. Contractor taken to regional medical center for treatment. Contractor was bandaged and referred to a specialist for reconstructive surgery. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Patrick Townsley | 2019-12-05 10:14 | 2019-11-04 09:43 | 2019-11-04 09:43 | 2019-11-20 06:45 | 2019-11-17 14:00 | 2019-11-03 14:00 | 2019-11-22 12:56 |  | 2019-11-22 10:12 | Crossroads Wind Turbine S51 |  |  | Jesse Murray | I Approve. Jesse Murray 12/5/19 | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Patrick Townsley |  | While assembling crane boom at turbine S51, boom butt was installed onto crane base when it was identified that a shim that was required to be installed was missing. Pins, operated hydraulically by the crane operator, were unset to allow shim to be inserted. The shim is held in place by metal fingers resting on the boom and once placed in the correct position does not require further adjustment. At about 1400 on Sunday the 3rd of November, the contractor had their finger lacerated and a piece of skin came off. Exact position of the hand at the time of injury is unclear, it is my contention that their finger was trapped against a pin guide and that the damage was caused by a cotter pin as it passed by. The other working theory is that the finger was pinched between the arm and the locking pin base. Contractor was wearing a glove at the time, stitching on the glove was torn. Contractor was taken to Seiling Regional Medical Center for treatment and will be seeing a specialist as the damage to the thumb is extensive. Contractor company was behind schedule but crew was not rushed. Injured contractor was an AD (Assembly/Disassembly Director) and has significant experience assembling the model of crane, some complacency may have been involved. The pin was operated from the cab of the crane which is located on the opposite side of the boom butt and the crane operator communicated with the injured contractor through a window. |  |  |  | Crossroads Wind Farm | FALSE |  | FALSE | Renewable Energy |  | Patrick Townsley | Patrick Townsley |  | Jason Thomas | Reviewed | Jason Thomas |  | Medium | [12 empty] | 13.02 Inadequate human factors/ergonomics considerations |  |  |  | Improper placement of hand/thumb during work procedure. Contractor hand was exposed to a pinch point. | 11. Improper Position for Task | 5. Caught In (Pinch and Nip Points) |  | 11/22/19 - Still reviewing. Have reviewed and discussed with Patrick (investigation and corrective actions). |  |  |  | Injury / Illness |  | Patrick Townsley |  | Laceration/Crush of Thumb | FALSE |  |  | 7. Caught Between or Under (Crushed or Amputated) | Patrick Townsley | TNT Crane & Rigging | Eric Chavers | Laceration |  | Hand | Patrick Townsley | Right | TRUE | Company Vehicle
9128 | Metro Service Center | 2019-11-01 11:30 | Contractor OESCO was working on re-routing the primary underground feeder on bank three for the new reactors location last Friday @ Draper. In the process of digging out the old riser foundation the operator dug into the control cable going to bank four. Which cause the bank four to trip off and losing station power into the control house. | Level 2 |  | FALSE | Property Damage |  |  |  |  | OG&E Corp Services | Timothy Carter | 2020-02-25 11:05 | 2019-11-04 14:45 | 2019-11-04 14:45 | 2019-12-18 13:39 | 2019-11-15 11:30 | 2019-11-01 11:36 | 2020-02-07 07:38 |  | 2020-01-13 07:46 | Draper Lake substation Oklahoma City, Oklahoma, replacing FIS reactor R073 |  |  | William Young | Reviewed and approved. WCY 2/25/2020 | UTS |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Timothy Carter |  | Contractor OESCO was working on re-routing the primary underground feeder on bank three for the new reactors location last Friday @ Draper. In the process of digging out the old riser foundation the operator dug into the control cable going to bank four. Which cause the bank four to trip off and losing station power into the control house. |  |  |  | Metro Service Center | FALSE |  | FALSE | UTS - Project Mgmt |  | Roy Hoffman | Timothy Carter |  | William Young | Not sure how the first CA is actually implemented. It does not seem to me to address the lapses and oversights. The CA would appear to me to state what they should have been doing in the first place so how does restating it in a CA change anything. What are they going to do to ensure compliance with their procedures? How will be know with the operator training has been done. Have they or will they provide a copy of the training documentation? We need more rigor around the training requirement. WCY 12-9-2019. Reviewed with Mark. He is working with Tim Carter. Suggested that they develop specific program requirement and/or policy to require spotter while digging. Returning for further investigation and revised CA. 12-16-2019 WCY. 2/7/2020 Reviewed updates. OK WCY | William Young |  | Medium | [6 empty] | 7.09 Inadequate discipline | [9 empty] | Digging around control ditch without a spotter. Spotter got sick and left job site. Excavator operator continued to dig without spotter. Excavator operator should have stop digging or found another spotter. | 16. Failure to Follow Procedure, Policy, Practice | 6. Caught On (Snagged, Hung) |  | Approved. In future, please list the corrective actions out individually. MLH 11/25/19 |  |  |  | Property Damage |  | Timothy Carter | Contractor OESCO was working on re-routing the primary underground feeder on bank three for the new reactors location last Friday @ Draper. In the process of digging out the old riser foundation the operator dug into the control cable going to bank four. Which cause the bank four to trip off and losing station power into the control house. This cable will have to be replaced. |  |  |  |  | 6. Caught On (Snagged, Hung) | Roy Hoffman | OESCO | Chris McBride |  | 3rd Party Property/Equipment |  | Roy Hoffman |  |  |  |  | FALSE | [42 empty] | One 8/C and two 1/C 4/0 relay cables were damaged. | 10000 | OESCO | 3rd Party Property/Equipment |  | Mini Ex | [18 empty] | 1647285
9129 | Northeast District Service Cen | 2019-10-24 13:00 | While member was emptying sweeper it got stuck causing damage to the machine on the right side. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Delivery | Donald Melson | 2019-11-12 11:49 | 2019-11-05 08:47 | 2019-11-05 08:47 | 2019-11-05 09:42 | 2019-11-07 13:00 | 2019-11-04 11:00 | 2019-11-08 11:29 |  |  | Northeast District pole yard |  |  | Hannah Everett | Approved. | T&D Ops |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Donald Melson |  | Member swept the dock area and drove down to the north end of pole yard to empty it. Before emptying, member struck steel beam that is used to level gravel in pole yard. This caused damage to the belt and right side fender area of the sweeper. The sweeper was stuck after striking the beam. The member had another member assist to move the steel beam and extract the sweeper. -The member reported to material handler three days later, but did not report to supervisor -Member had reviewed incident reporting SSOP September 9th of 2018. |  |  |  | Northeast District Service Cen | FALSE |  | FALSE | Construction Services |  | Jordan Holt | Donald Melson |  | Chad Inman | I approve of the corrective action listed above. Local leadership and I had a through conversation with all members involved regarding OGE's Values, Beliefs, and Safety Principals, we also discussed leaderships expectations of them. CI | Chad Inman |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Member not identifying hazard while operating sweeper. | 11. Improper Position for Task | 1. Struck Against (Running or Bumping Into) | [68 empty] | bottom right fender area bent | 1000 | Jordan Holt | Industrial/Heavy Equipment |  | F32-666
9130 | Sooner Power Plant | 2019-10-31 17:30 | Contractor impacted guard shack bollard located on the west side of the building outside the gate with his truck while exiting facility. | Level 1 |  | FALSE | Contractor |  |  |  |  | OGE Energy Corp | Adrian Little | 2019-12-02 10:45 | 2019-11-06 08:12 | 2019-11-06 08:12 | 2019-11-22 15:04 | 2019-11-14 17:30 | 2019-11-06 07:53 | 2019-12-02 08:53 |  |  | Sooner PP guard shack exit bollard |  |  | Cody Vinyard | not approved, cody vinyard. Need to take incident back to draft stage and select contractor as the incident type. Approved, Cody Vinyard 12/2/19 Need to complete the incident description Need to list the corrective action that the coordinator re emphasized the need to notify OGE of any incident that occurs during the project. As we were not notified promptly when this occurred. | Enterprise Services |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Adrian Little |  | Contractor impacted guard shack bollard located on the west side of the building outside the gate with his truck while exiting facility. OGE contact was not notified after this incident occurred. SNPP personnel brought the incident up to SNPP safety on 11/5/2019. When OGE contacted contractor, driver admitted to being distracted handling badges while exiting and impacted the bollard with the tool box of his truck. See Supreme's incident investigation attached below. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Other |  | Brady Sowell | Adrian Little |  | Terry Brown | I have reviewed this document and I am sending for final approval. Thanks, Terry Brown | Terry Brown |  | Low |  | 2.07 Slow reaction time | [14 empty] | Driver was not paying attention. Was distracted by handling ID badges. | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Adrian Little | Paint damage / scrape |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Brady Sowell | Supreme Roofing | David Cornejo |  | Fixed Equipment |  | Adrian Little |  |  |  |  | FALSE | [48 empty] | FALSE |  | Red Rock | Struck Fixed Object | Drove Forward Into Object |  |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Clear
9131 | Muskogee Service Center | 2019-10-24 17:00 | Member working call about low wire, noticed bad primary insulator. Member checked voltage at primary neutral to pole and had 800 volts. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Delivery | Randell Gilbert | 2019-11-08 12:02 | 2019-11-06 09:18 | 2019-11-06 09:18 | 2019-11-06 09:41 | 2019-11-07 17:00 | 2019-10-30 07:30 | 2019-11-08 11:35 |  | 2019-11-07 15:29 | 905 SW 2nd, Checotah, Ok |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Randell Gilbert |  | On 10/24/2019 after a storm, Service tech Member received trouble call about low hanging wire. When he arrived he noticed the primary insulator had gotten struck by lightning and was damaged. Member then checked voltage at primary neutral to pole and had 800 volts. The service dead-end was broke causing service to hang low. After getting a better look from the bucket, he noticed it had burnt into the neutral from the bad primary insulator. Member proceeded to check voltage from pole to neutral and also checked voltage at bottom of pole to ground and had 41 volts. |  |  |  | Muskogee Service Center | FALSE |  | TRUE | Construction Services |  | Nicholas Selvidge | Randell Gilbert |  | Chad Inman | I approve the corrective action listed above. This close call will be discussed in detail during our 11/13 weekly safety call. I'm thankful that our member went above and beyond. CI | Chad Inman |  | Medium | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | Lightning struck primary insulator causing primary to track through pin. | 40. Weather Conditions | 12. Equipment Failure |  | Reviewed | [90 empty] | 8859154
9132 | Sooner Power Plant | 2019-11-04 13:00 | Zachry base crew was removing windows from the east end of TG building to install new overhead doors. While removing the old windows part of the window actuator slid out and fell approx. 90 ft. to the ground. The area was red barricaded and no one was inside the barricaded area. There were no injuries and no other damages. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Lance Lantz | 2019-12-04 10:50 | 2019-11-06 10:10 | 2019-11-06 10:10 | 2019-11-20 15:11 | 2019-11-18 13:00 | 2019-11-06 09:57 | 2019-11-25 13:06 |  |  | Sooner Power Plant Unit 1 TG Crane Bay |  |  | Brady Sowell | approved by Sowell on 11/27/19 | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Lance Lantz |  | The Zachry base crew was assigned with replacing the two(2) upper east T/G windows. They would be removing the old fold out style windows and installing glass roll up overhead doors. These windows are located on the East end of the turbine floor over the crane bay approximately 85’ from the ground. Scaffolding was used to gain access to the windows. The crew was in the process of removing the old windows from the north set when the incident occurred. The crew was using a crane with a skid pan to haul off the debris from the old windows. The crane and the skid pan was set up on the outside of the building. The windows were removed in sections and passed through the window opening and into the skid pan. A few pieces of the old actuator assemblies were too long or cumbersome to pass through the window opening so the pieces were cut down. It was found during the investigation the crew had already removed the south set of windows using the same procedure without incident. It was determined that the actuator arm had been cut from the window on one end. This would allow the arm to roll out of the gears if turned upside down. It also appeared the gearbox this actuator ran through was stripped out. This allowed the gears to turn freely. It was determined that after the section was cut free the members had rotated the section to pass it out the window opening into the skid pan. As the section was rotated the actuator arm slid out of the gearbox falling between the wall and the scaffolding. The scaffold did have orange barricade netting around the handrails. The area between the wall and the scaffold had fire blanket on it, but the fire blanket was not stretched all the way across. It was only installed in areas where cutting and grinding was being performed. The actuator arm weighed approximately 2 lbs. and fell approximately 85’ to the ground. The arm landed with in the crews red barricaded area below. No members were in the barricaded area. There were no injuries and no equipment was damaged. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Lance Lantz | Lance Lantz |  | Frank Brixey | Kris what is the action item to insure there are no more actuator arms come loose and fall? Are they securing them differently? Approve - Brixey 11/25/19 | Frank Brixey |  | Low |  |  |  |  | 5.01 Lack of experience | [11 empty] | member cut arm to where it would have the ability to slide out of the gears and member turned the piece in a manner that allowed the arm to slide out | 03. Failure to Secure | 3. Fall from Elevation to Lower Level | [5 empty] | Injury / Illness |  | Lance Lantz | [5 empty] | 2. Struck By (Hit By Moving Object) | Lance Lantz | Zachry | Tyler Bohon |  |  |  | Lance Lantz | [71 empty] | 615603
9132 | Sooner Power Plant | 2019-11-04 13:00 | Zachry base crew was removing windows from the east end of TG building to install new overhead doors. While removing the old windows part of the window actuator slid out and fell approx. 90 ft. to the ground. The area was red barricaded and no one was inside the barricaded area. There were no injuries and no other damages. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Lance Lantz | 2019-12-04 10:50 | 2019-11-06 10:10 | 2019-11-06 10:10 | 2019-11-20 15:11 | 2019-11-18 13:00 | 2019-11-06 09:57 | 2019-11-25 13:06 |  |  | Sooner Power Plant Unit 1 TG Crane Bay |  |  | Brady Sowell | approved by Sowell on 11/27/19 | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Lance Lantz |  | The Zachry base crew was assigned with replacing the two(2) upper east T/G windows. They would be removing the old fold out style windows and installing glass roll up overhead doors. These windows are located on the East end of the turbine floor over the crane bay approximately 85’ from the ground. Scaffolding was used to gain access to the windows. The crew was in the process of removing the old windows from the north set when the incident occurred. The crew was using a crane with a skid pan to haul off the debris from the old windows. The crane and the skid pan was set up on the outside of the building. The windows were removed in sections and passed through the window opening and into the skid pan. A few pieces of the old actuator assemblies were too long or cumbersome to pass through the window opening so the pieces were cut down. It was found during the investigation the crew had already removed the south set of windows using the same procedure without incident. It was determined that the actuator arm had been cut from the window on one end. This would allow the arm to roll out of the gears if turned upside down. It also appeared the gearbox this actuator ran through was stripped out. This allowed the gears to turn freely. It was determined that after the section was cut free the members had rotated the section to pass it out the window opening into the skid pan. As the section was rotated the actuator arm slid out of the gearbox falling between the wall and the scaffolding. The scaffold did have orange barricade netting around the handrails. The area between the wall and the scaffold had fire blanket on it, but the fire blanket was not stretched all the way across. It was only installed in areas where cutting and grinding was being performed. The actuator arm weighed approximately 2 lbs. and fell approximately 85’ to the ground. The arm landed with in the crews red barricaded area below. No members were in the barricaded area. There were no injuries and no equipment was damaged. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Lance Lantz | Lance Lantz |  | Frank Brixey | Kris what is the action item to insure there are no more actuator arms come loose and fall? Are they securing them differently? Approve - Brixey 11/25/19 | Frank Brixey |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | member cut arm to where it would have the ability to slide out of the gears and member turned the piece in a manner that allowed the arm to slide out | 03. Failure to Secure | 3. Fall from Elevation to Lower Level | [5 empty] | Injury / Illness |  | Lance Lantz | [5 empty] | 2. Struck By (Hit By Moving Object) | Lance Lantz | Zachry | Tyler Bohon |  |  |  | Lance Lantz | [71 empty] | 615603
9133 | Muskogee Power Plant | 2019-11-05 17:00 | Fleet mechanic was performing a pm on a pickup at Muskogee PP. The air compressor in the fleet service truck was running. A member that was walking by seen a fire in the truck and notified the mechanic. They used a fire extinguisher and put the fire out. After the fire was extinguished they found an air filter box had fallen against the exhaust of the air compressor and caught on fire. | Level 2 |  | FALSE | Property Damage |  |  |  |  | OG&E Corp Services | Nathan Gooch | 2019-12-09 16:55 | 2019-11-06 13:43 | 2019-11-06 13:43 | 2019-11-18 16:34 | 2019-11-19 17:00 | 2019-11-06 13:29 | 2019-11-29 13:25 |  | 2019-11-18 16:37 | In the building on the South east side of Muskogee PP. |  |  | William Young | Reviewed and approved. WCY 12-9-2019 | UTS |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Nathan Gooch |  | Fleet mechanic was performing a pm on a pickup at Muskogee PP. Fleet service truck F08-412 has an enclosed bed housing the air compressor, oil bulk tank and large tools. The air compressor in the fleet service truck was running. A member that was walking by seen a fire in the truck and notified the mechanic who was servicing a vehicle close by. They used a fire extinguisher and put the fire out. After the fire was extinguished they found an air filter box had fallen against the exhaust of the air compressor and caught on fire. From time to time material such as filters are transported in the back of the truck. Upon investigation filter boxes were store in close proximity of the air compressor exhaust. Found the exhaust pipe header lose and missing screws at the muffler. Found a 2 foot section of exhaust pipe uninsulated. Possible ignition come from contact to pipe or from a spark from the muffler. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | UTS - Fleet Services |  | Kristoffer Schaffler | Nathan Gooch |  | Paul Jefferson | I approve corrective actions. | Paul Jefferson |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance | [10 empty] | Filter Box came into contact with air compressor exhaust. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved, Cody Vinyard | [66 empty] | A new air filter got burnt and is now unusable. No damage to the truck or any other equipment. | 100 | Kristoffer Schaffler | Fire |  | F08-412
9134 | Horseshoe Lake Power Plant | 2019-11-05 20:00 | Member returning to plant from Tinker Air Force Base struck a deer. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Michael Kennedy | 2019-12-13 09:17 | 2019-11-06 14:17 | 2019-11-06 14:17 | 2019-11-18 11:18 | 2019-11-19 20:00 | 2019-11-06 13:57 | 2019-12-09 07:50 |  | 2019-11-22 10:04 | Horseshoe Lake entrance road before security gate on NE 36th street. |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Michael Kennedy |  | On 11/15/2019 member was coming back from Tinker Air Force Base and returning to the plant. He was traveling East on NE 36th st. It was dark and as the member drove past the turnpike construction in truck # FO3-1233 a deer jumped out in front of him so fast although he caught a glimpse of the deer prior to impact he didn't have time to apply brakes. He notified the control room immediately by radio about the incident. Damage to the vehicle was cosmetic grill and bumper. Members contacted the Oklahoma County Sheriffs Office and the wildlife department. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Operations |  | Nathan Loesch | Michael Kennedy |  | Robert Doupe | RDD Approved | Robert Doupe |  | Medium | [9 empty] | 10.04 Inadequate monitoring of construction | [6 empty] | Member hit deer while it attempted to run across the road. | 39. Road Conditions | 1. Struck Against (Running or Bumping Into) |  | I agree with the overall risk ranking but I believe it should be a C2 minor due to the cost of the damage and L3 possible due to the fact that the location is highly trafficked by wildlife. | [66 empty] | Hole in grill and bent bumper due to driver side impact from Deer. | 1000 | Nathan Loesch | Vehicle (not related to operation of vehicle) |  | FO3-1233
9135 | Sooner Power Plant | 2019-11-06 12:30 | While replacing the T/G crane bay windows with glass overhead doors. One glass panes was found to be broke after returning from lunch. All the glass fell to the outside and was on the window seal. Area was barricaded of and no glass fell into the barricaded area. No injuries or other property damage. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Lance Lantz | 2019-11-22 11:17 | 2019-11-06 16:38 | 2019-11-06 16:38 | 2019-11-14 11:09 | 2019-11-20 12:30 | 2019-11-06 16:17 | 2019-11-18 10:39 |  |  | Sooner Power Plant Unit 1 T/G Crane Bay |  |  | Tanner Brady | Reviewed and approve for Brady while he is on vacation. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Lance Lantz |  | The Zachry base crew was assigned with replacing the two(2) upper east T/G windows. They would be removing the old fold out style windows and installing glass roll up overhead doors. These windows are located on the East end of the turbine floor over the crane bay approximately 85’ from the ground. Scaffolding was used to gain access to the windows. The crew had installed the tracks and the door panels on the south window. They were in the process of installing the tension spring/rod assembly when the incident occurred. It was found during the investigation that the crew needed to weld a support bracket in place to support the tension spring/rod assembly. The members rolled the upper door section out to create space between the area where the support bracket would be welded to the header frame and the aluminum frame of the door. The crew also draped fire blanket over the top of the door. Then over to the scaffolding. This was mainly done to prevent sparks from falling to lower levels. The crew finished welding the support bracket and installing the tension spring/rod assembly. It was close to lunch so the crew left the fire blanket in place and exited the scaffolding. After returning from lunch and climbing up the scaffold the crew members could see under the fire blanket noticed that one of the panes of glass was broke out. It is believed that welding slag hit the glass and caused the tempered glass to shatter. The crew did not realize the glass was shattered since the window pane was covered by the fire blanket. The wind was blowing this particular day and the door was moving a little bit in the tracks due to being rolled out to create a space between the header frame and the door frame. This movement caused the small pieces of the shattered glass to fall out. All the glass fell to the outside and landed on the window seal. The area to the outside was over the admin office roof. There were a few pieces of glass found on the roof. The area below in the T/G crane bay was barricaded off due to the overhead work. The area was inspected and no glass was found in the crane bay. The remainder of the glass was removed and plastic was put over the opening to prevent rain from entering the building. All rest of the glass was cleaned up. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Maintenance |  | Lance Lantz | Lance Lantz |  | Frank Brixey | Approve - Brixey 11/18/2019 | Frank Brixey |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | weld slag coming into contact with tempered glass. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Property Damage |  | Lance Lantz | Broken Window |  |  |  |  | 2. Struck By (Hit By Moving Object) | Lance Lantz | Zachry | Tyler Bohon |  | Fixed Equipment |  | Lance Lantz |  |  |  |  | FALSE | [66 empty] | 615603
9136 | Metro Service Center | 2019-11-06 09:30 | While performing switching members completed steps of switching before being directed to do so. | Level 1 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Joseph Manseau | 2020-01-20 16:24 | 2019-11-07 10:22 |  | 2020-01-20 13:19 | 2019-12-18 09:30 | 2019-11-06 13:00 | 2020-01-20 13:31 |  |  | Draper Lake substation |  |  | Cody Magby | approved cm | T&D Ops |  | Level 1 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Joseph Manseau |  | Members were performing switching to return Draper Lake Bank 4 to service following relay testing. While performing live trip relay testing, Bank 4 was trip offline. Alternate station power was being carried through Bank 4 at the time because Bank 3 (Primary station power) was offline due to construction work. When power was lost related to the trip of Bank 4 a state of confusion began. In the confusion team members performing the testing misunderstood the operating authority that they should continue with switching completing steps 19-24 of switching order S1631. When members contacted TCC to relay times the operating authority then advised them of the error. |  |  |  | Metro Service Center | FALSE |  | FALSE | PD Operations Services |  | Clay Dildine | Joseph Manseau |  | James Hutchison | I have reviewed this incident and approve the report and it's findings. The corrective action will also include clarifying each of the steps so each person performing the communication will have full understanding before moving forward. | James Hutchison |  | Low
9137 | Metro Service Center | 2019-10-29 11:00 | Closed transformer lid on secondary | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Delivery | Garrett Bernethy | 2019-11-25 16:19 | 2019-11-07 11:21 | 2019-11-07 11:21 | 2019-11-07 11:40 | 2019-11-12 11:00 | 2019-11-07 11:16 | 2019-11-20 10:40 |  |  | 11700 SW 54th |  |  | Marcus Huddleston | No additional comments. MLH 11-25-19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Garrett Bernethy |  | . The crew was given the assignment to install an UG service at 11700 SW 54th in OKC. Jeremy put on his rubber gloves and lifted the UG transformer lid, to check if there was room on the transformer lugs for another service. When he went to shut the lid of the transformer one of the energized service leads moved into the opening of the transformer lid. The transformer lid was dropped approximately 18 inches. When the lid hit the energized cable the lid punctured the insulation causing a direct phase to ground flash which burnt the cable in the clear. There was a partial light event due to this incident. The crew notified their foreman and the safety department to report this incident. No injuries resulted from this near miss. Additional Information: The weather was dry when the incident occurred, the transformer had a lot of dirt inside where the lugs are located, gophers were digging in the area, the foreman was contacted, the cable was repaired, had a 3 ½ hr outage to make repairs. |  |  |  | Metro Service Center | FALSE |  | FALSE | Resource Planning & Coord |  | Garrett Bernethy | Garrett Bernethy |  | John Legg | Contractor has discussed incident in safety meeting. no further comments | John Legg |  | Low | [9 empty] | 10.03 Inadequate standards, specifications and/or design criteria | [6 empty] | . The crew was given the assignment to install an UG service at 11700 SW 54th in OKC. Jeremy put on his rubber gloves and lifted the UG transformer lid, to check if there was room on the transformer lugs for another service. When he went to shut the lid of the transformer one of the energized service leads moved into the opening of the transformer lid. The transformer lid was dropped approximately 18 inches. When the lid hit the energized cable the lid punctured the insulation causing a direct phase to ground flash which burnt the cable in the clear. There was a partial light event due to this incident. The crew notified their foreman and the safety department to report this incident. No injuries resulted from this near miss. Additional Information: The weather was dry when the incident occurred, the transformer had a lot of dirt inside where the lugs are located, gophers were digging in the area, the foreman was contacted, the cable was repaired, had a 3 ½ hr outage to make repairs. | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Garrett Bernethy | Transformer lid hit secondary |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Garrett Bernethy | Imperium | Jeremy Morris |  | Utility Strike |  | Garrett Bernethy |  |  |  |  | FALSE | [66 empty] | 000800776083
9137 | Metro Service Center | 2019-10-29 11:00 | Closed transformer lid on secondary | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Delivery | Garrett Bernethy | 2019-11-25 16:19 | 2019-11-07 11:21 | 2019-11-07 11:21 | 2019-11-07 11:40 | 2019-11-12 11:00 | 2019-11-07 11:16 | 2019-11-20 10:40 |  |  | 11700 SW 54th |  |  | Marcus Huddleston | No additional comments. MLH 11-25-19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Garrett Bernethy |  | . The crew was given the assignment to install an UG service at 11700 SW 54th in OKC. Jeremy put on his rubber gloves and lifted the UG transformer lid, to check if there was room on the transformer lugs for another service. When he went to shut the lid of the transformer one of the energized service leads moved into the opening of the transformer lid. The transformer lid was dropped approximately 18 inches. When the lid hit the energized cable the lid punctured the insulation causing a direct phase to ground flash which burnt the cable in the clear. There was a partial light event due to this incident. The crew notified their foreman and the safety department to report this incident. No injuries resulted from this near miss. Additional Information: The weather was dry when the incident occurred, the transformer had a lot of dirt inside where the lugs are located, gophers were digging in the area, the foreman was contacted, the cable was repaired, had a 3 ½ hr outage to make repairs. |  |  |  | Metro Service Center | FALSE |  | FALSE | Resource Planning & Coord |  | Garrett Bernethy | Garrett Bernethy |  | John Legg | Contractor has discussed incident in safety meeting. no further comments | John Legg |  | Low | [9 empty] | 10.03 Inadequate standards, specifications and/or design criteria | [6 empty] | . The crew was given the assignment to install an UG service at 11700 SW 54th in OKC. Jeremy put on his rubber gloves and lifted the UG transformer lid, to check if there was room on the transformer lugs for another service. When he went to shut the lid of the transformer one of the energized service leads moved into the opening of the transformer lid. The transformer lid was dropped approximately 18 inches. When the lid hit the energized cable the lid punctured the insulation causing a direct phase to ground flash which burnt the cable in the clear. There was a partial light event due to this incident. The crew notified their foreman and the safety department to report this incident. No injuries resulted from this near miss. Additional Information: The weather was dry when the incident occurred, the transformer had a lot of dirt inside where the lugs are located, gophers were digging in the area, the foreman was contacted, the cable was repaired, had a 3 ½ hr outage to make repairs. | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) | [5 empty] | System Outage |  | Garrett Bernethy | Transformer lid hit secondary |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Garrett Bernethy | Imperium | Jeremy Morris |  | Utility Strike |  | Garrett Bernethy |  |  |  |  | FALSE | [66 empty] | 000800776083
9138 | Northeast District Service Cen | 2019-11-05 12:30 | Crew had loaded power dolly and was going to unload pad mount off the machine. Member swung boom to the left for the line truck to pick up pad mount and machine leaned over on the boom. Crew removed pad mount and used outriggers to set the machine up right. There was no damage to the trailer or power dolly. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Delivery | Donald Melson | 2019-11-18 15:49 | 2019-11-07 13:25 | 2019-11-07 13:25 | 2019-11-08 07:04 | 2019-11-19 12:30 | 2019-11-05 13:15 | 2019-11-18 11:31 |  | 2019-11-13 08:53 | N. Moccasin St. and Terrill Cir. in Sapulpa |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Donald Melson |  | Crew had pad mount on power dolly from previous location and was going to unload old pad mount and load new pad mount. Foreman went to check jobsite when member operated power dolly and swung boom to the left causing the power dolly to lean over on the boom tip contacting the ground. Crew stopped the job and contacted supervisor. Crew then unloaded pad mount and used outriggers to lean power dolly over and swing boom back straight. -Equipment was checked by fleet and verified there was no damage to the power dolly or trailer 11/5/19. -"Communicate while using power dolly" was documented in the tailboard. -Member operating power dolly at the time did not have a completed FPR for the Power Dolly. -Stickers and labels are present on the machine warning that "All outriggers must be extended and set firmly on ground and machine leveled before crane operation" |  |  |  | Northeast District Service Cen | FALSE |  | TRUE | Construction Services |  | Dwayne Fox | Donald Melson |  | Chad Inman | I agree with the Corrective Actions listed above. Our leaders and members must understand that our SOP's and FPR's engage us and keep us informed, but the users must be intentional and do their due diligence to remain familiar with the equipment they use. DON'T ASSUME! | Chad Inman |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.05 Inadequate review instruction |  |  | 9.03 Improper or insufficient delegation | [7 empty] | The immediate investigation was that the tracks had not been extracted after two of the members had gone out the backyard gate to load the machine on the trailer. The members had set up power dolly to lift the pad mount up and over the gate due to it being to big to get through the gate. After loading the pad mount back on the machine the tracks were not extended back out when they tracked to the trailer and loaded. This caused instability when the member swung to boom over to get the pad mount unloaded at the next location. The members realized the mistake after the event and had been utilizing the tracks prior to this event. | 15. Using Equipment Improperly | 9. Abnormal Operation |  | The learnings from this close call should include encouraging members to communicate competencies in operating heavy equipment during the tailboard. Approved. | [90 empty] | 7963302
9138 | Northeast District Service Cen | 2019-11-05 12:30 | Crew had loaded power dolly and was going to unload pad mount off the machine. Member swung boom to the left for the line truck to pick up pad mount and machine leaned over on the boom. Crew removed pad mount and used outriggers to set the machine up right. There was no damage to the trailer or power dolly. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Delivery | Donald Melson | 2019-11-18 15:49 | 2019-11-07 13:25 | 2019-11-07 13:25 | 2019-11-08 07:04 | 2019-11-19 12:30 | 2019-11-05 13:15 | 2019-11-18 11:31 |  | 2019-11-13 08:53 | N. Moccasin St. and Terrill Cir. in Sapulpa |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Donald Melson |  | Crew had pad mount on power dolly from previous location and was going to unload old pad mount and load new pad mount. Foreman went to check jobsite when member operated power dolly and swung boom to the left causing the power dolly to lean over on the boom tip contacting the ground. Crew stopped the job and contacted supervisor. Crew then unloaded pad mount and used outriggers to lean power dolly over and swing boom back straight. -Equipment was checked by fleet and verified there was no damage to the power dolly or trailer 11/5/19. -"Communicate while using power dolly" was documented in the tailboard. -Member operating power dolly at the time did not have a completed FPR for the Power Dolly. -Stickers and labels are present on the machine warning that "All outriggers must be extended and set firmly on ground and machine leveled before crane operation" |  |  |  | Northeast District Service Cen | FALSE |  | TRUE | Construction Services |  | Dwayne Fox | Donald Melson |  | Chad Inman | I agree with the Corrective Actions listed above. Our leaders and members must understand that our SOP's and FPR's engage us and keep us informed, but the users must be intentional and do their due diligence to remain familiar with the equipment they use. DON'T ASSUME! | Chad Inman |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.05 Inadequate review instruction |  |  | 9.11 Inadequate matching of individual qualifications and job/task requirements | [7 empty] | The immediate investigation was that the tracks had not been extracted after two of the members had gone out the backyard gate to load the machine on the trailer. The members had set up power dolly to lift the pad mount up and over the gate due to it being to big to get through the gate. After loading the pad mount back on the machine the tracks were not extended back out when they tracked to the trailer and loaded. This caused instability when the member swung to boom over to get the pad mount unloaded at the next location. The members realized the mistake after the event and had been utilizing the tracks prior to this event. | 15. Using Equipment Improperly | 9. Abnormal Operation |  | The learnings from this close call should include encouraging members to communicate competencies in operating heavy equipment during the tailboard. Approved. | [90 empty] | 7963302
9138 | Northeast District Service Cen | 2019-11-05 12:30 | Crew had loaded power dolly and was going to unload pad mount off the machine. Member swung boom to the left for the line truck to pick up pad mount and machine leaned over on the boom. Crew removed pad mount and used outriggers to set the machine up right. There was no damage to the trailer or power dolly. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Delivery | Donald Melson | 2019-11-18 15:49 | 2019-11-07 13:25 | 2019-11-07 13:25 | 2019-11-08 07:04 | 2019-11-19 12:30 | 2019-11-05 13:15 | 2019-11-18 11:31 |  | 2019-11-13 08:53 | N. Moccasin St. and Terrill Cir. in Sapulpa |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Donald Melson |  | Crew had pad mount on power dolly from previous location and was going to unload old pad mount and load new pad mount. Foreman went to check jobsite when member operated power dolly and swung boom to the left causing the power dolly to lean over on the boom tip contacting the ground. Crew stopped the job and contacted supervisor. Crew then unloaded pad mount and used outriggers to lean power dolly over and swing boom back straight. -Equipment was checked by fleet and verified there was no damage to the power dolly or trailer 11/5/19. -"Communicate while using power dolly" was documented in the tailboard. -Member operating power dolly at the time did not have a completed FPR for the Power Dolly. -Stickers and labels are present on the machine warning that "All outriggers must be extended and set firmly on ground and machine leveled before crane operation" |  |  |  | Northeast District Service Cen | FALSE |  | TRUE | Construction Services |  | Dwayne Fox | Donald Melson |  | Chad Inman | I agree with the Corrective Actions listed above. Our leaders and members must understand that our SOP's and FPR's engage us and keep us informed, but the users must be intentional and do their due diligence to remain familiar with the equipment they use. DON'T ASSUME! | Chad Inman |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.05 Inadequate review instruction |  |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | The immediate investigation was that the tracks had not been extracted after two of the members had gone out the backyard gate to load the machine on the trailer. The members had set up power dolly to lift the pad mount up and over the gate due to it being to big to get through the gate. After loading the pad mount back on the machine the tracks were not extended back out when they tracked to the trailer and loaded. This caused instability when the member swung to boom over to get the pad mount unloaded at the next location. The members realized the mistake after the event and had been utilizing the tracks prior to this event. | 15. Using Equipment Improperly | 9. Abnormal Operation |  | The learnings from this close call should include encouraging members to communicate competencies in operating heavy equipment during the tailboard. Approved. | [90 empty] | 7963302
9138 | Northeast District Service Cen | 2019-11-05 12:30 | Crew had loaded power dolly and was going to unload pad mount off the machine. Member swung boom to the left for the line truck to pick up pad mount and machine leaned over on the boom. Crew removed pad mount and used outriggers to set the machine up right. There was no damage to the trailer or power dolly. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Delivery | Donald Melson | 2019-11-18 15:49 | 2019-11-07 13:25 | 2019-11-07 13:25 | 2019-11-08 07:04 | 2019-11-19 12:30 | 2019-11-05 13:15 | 2019-11-18 11:31 |  | 2019-11-13 08:53 | N. Moccasin St. and Terrill Cir. in Sapulpa |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Donald Melson |  | Crew had pad mount on power dolly from previous location and was going to unload old pad mount and load new pad mount. Foreman went to check jobsite when member operated power dolly and swung boom to the left causing the power dolly to lean over on the boom tip contacting the ground. Crew stopped the job and contacted supervisor. Crew then unloaded pad mount and used outriggers to lean power dolly over and swing boom back straight. -Equipment was checked by fleet and verified there was no damage to the power dolly or trailer 11/5/19. -"Communicate while using power dolly" was documented in the tailboard. -Member operating power dolly at the time did not have a completed FPR for the Power Dolly. -Stickers and labels are present on the machine warning that "All outriggers must be extended and set firmly on ground and machine leveled before crane operation" |  |  |  | Northeast District Service Cen | FALSE |  | TRUE | Construction Services |  | Dwayne Fox | Donald Melson |  | Chad Inman | I agree with the Corrective Actions listed above. Our leaders and members must understand that our SOP's and FPR's engage us and keep us informed, but the users must be intentional and do their due diligence to remain familiar with the equipment they use. DON'T ASSUME! | Chad Inman |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.02 Inadequate practice |  |  | 9.03 Improper or insufficient delegation | [7 empty] | The immediate investigation was that the tracks had not been extracted after two of the members had gone out the backyard gate to load the machine on the trailer. The members had set up power dolly to lift the pad mount up and over the gate due to it being to big to get through the gate. After loading the pad mount back on the machine the tracks were not extended back out when they tracked to the trailer and loaded. This caused instability when the member swung to boom over to get the pad mount unloaded at the next location. The members realized the mistake after the event and had been utilizing the tracks prior to this event. | 15. Using Equipment Improperly | 9. Abnormal Operation |  | The learnings from this close call should include encouraging members to communicate competencies in operating heavy equipment during the tailboard. Approved. | [90 empty] | 7963302
9138 | Northeast District Service Cen | 2019-11-05 12:30 | Crew had loaded power dolly and was going to unload pad mount off the machine. Member swung boom to the left for the line truck to pick up pad mount and machine leaned over on the boom. Crew removed pad mount and used outriggers to set the machine up right. There was no damage to the trailer or power dolly. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Delivery | Donald Melson | 2019-11-18 15:49 | 2019-11-07 13:25 | 2019-11-07 13:25 | 2019-11-08 07:04 | 2019-11-19 12:30 | 2019-11-05 13:15 | 2019-11-18 11:31 |  | 2019-11-13 08:53 | N. Moccasin St. and Terrill Cir. in Sapulpa |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Donald Melson |  | Crew had pad mount on power dolly from previous location and was going to unload old pad mount and load new pad mount. Foreman went to check jobsite when member operated power dolly and swung boom to the left causing the power dolly to lean over on the boom tip contacting the ground. Crew stopped the job and contacted supervisor. Crew then unloaded pad mount and used outriggers to lean power dolly over and swing boom back straight. -Equipment was checked by fleet and verified there was no damage to the power dolly or trailer 11/5/19. -"Communicate while using power dolly" was documented in the tailboard. -Member operating power dolly at the time did not have a completed FPR for the Power Dolly. -Stickers and labels are present on the machine warning that "All outriggers must be extended and set firmly on ground and machine leveled before crane operation" |  |  |  | Northeast District Service Cen | FALSE |  | TRUE | Construction Services |  | Dwayne Fox | Donald Melson |  | Chad Inman | I agree with the Corrective Actions listed above. Our leaders and members must understand that our SOP's and FPR's engage us and keep us informed, but the users must be intentional and do their due diligence to remain familiar with the equipment they use. DON'T ASSUME! | Chad Inman |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.02 Inadequate practice |  |  | 9.11 Inadequate matching of individual qualifications and job/task requirements | [7 empty] | The immediate investigation was that the tracks had not been extracted after two of the members had gone out the backyard gate to load the machine on the trailer. The members had set up power dolly to lift the pad mount up and over the gate due to it being to big to get through the gate. After loading the pad mount back on the machine the tracks were not extended back out when they tracked to the trailer and loaded. This caused instability when the member swung to boom over to get the pad mount unloaded at the next location. The members realized the mistake after the event and had been utilizing the tracks prior to this event. | 15. Using Equipment Improperly | 9. Abnormal Operation |  | The learnings from this close call should include encouraging members to communicate competencies in operating heavy equipment during the tailboard. Approved. | [90 empty] | 7963302
9138 | Northeast District Service Cen | 2019-11-05 12:30 | Crew had loaded power dolly and was going to unload pad mount off the machine. Member swung boom to the left for the line truck to pick up pad mount and machine leaned over on the boom. Crew removed pad mount and used outriggers to set the machine up right. There was no damage to the trailer or power dolly. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Delivery | Donald Melson | 2019-11-18 15:49 | 2019-11-07 13:25 | 2019-11-07 13:25 | 2019-11-08 07:04 | 2019-11-19 12:30 | 2019-11-05 13:15 | 2019-11-18 11:31 |  | 2019-11-13 08:53 | N. Moccasin St. and Terrill Cir. in Sapulpa |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Donald Melson |  | Crew had pad mount on power dolly from previous location and was going to unload old pad mount and load new pad mount. Foreman went to check jobsite when member operated power dolly and swung boom to the left causing the power dolly to lean over on the boom tip contacting the ground. Crew stopped the job and contacted supervisor. Crew then unloaded pad mount and used outriggers to lean power dolly over and swing boom back straight. -Equipment was checked by fleet and verified there was no damage to the power dolly or trailer 11/5/19. -"Communicate while using power dolly" was documented in the tailboard. -Member operating power dolly at the time did not have a completed FPR for the Power Dolly. -Stickers and labels are present on the machine warning that "All outriggers must be extended and set firmly on ground and machine leveled before crane operation" |  |  |  | Northeast District Service Cen | FALSE |  | TRUE | Construction Services |  | Dwayne Fox | Donald Melson |  | Chad Inman | I agree with the Corrective Actions listed above. Our leaders and members must understand that our SOP's and FPR's engage us and keep us informed, but the users must be intentional and do their due diligence to remain familiar with the equipment they use. DON'T ASSUME! | Chad Inman |  | Medium |  |  |  |  | 5.03 Inadequate initial training | 6.02 Inadequate practice |  |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | The immediate investigation was that the tracks had not been extracted after two of the members had gone out the backyard gate to load the machine on the trailer. The members had set up power dolly to lift the pad mount up and over the gate due to it being to big to get through the gate. After loading the pad mount back on the machine the tracks were not extended back out when they tracked to the trailer and loaded. This caused instability when the member swung to boom over to get the pad mount unloaded at the next location. The members realized the mistake after the event and had been utilizing the tracks prior to this event. | 15. Using Equipment Improperly | 9. Abnormal Operation |  | The learnings from this close call should include encouraging members to communicate competencies in operating heavy equipment during the tailboard. Approved. | [90 empty] | 7963302
9138 | Northeast District Service Cen | 2019-11-05 12:30 | Crew had loaded power dolly and was going to unload pad mount off the machine. Member swung boom to the left for the line truck to pick up pad mount and machine leaned over on the boom. Crew removed pad mount and used outriggers to set the machine up right. There was no damage to the trailer or power dolly. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Delivery | Donald Melson | 2019-11-18 15:49 | 2019-11-07 13:25 | 2019-11-07 13:25 | 2019-11-08 07:04 | 2019-11-19 12:30 | 2019-11-05 13:15 | 2019-11-18 11:31 |  | 2019-11-13 08:53 | N. Moccasin St. and Terrill Cir. in Sapulpa |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Donald Melson |  | Crew had pad mount on power dolly from previous location and was going to unload old pad mount and load new pad mount. Foreman went to check jobsite when member operated power dolly and swung boom to the left causing the power dolly to lean over on the boom tip contacting the ground. Crew stopped the job and contacted supervisor. Crew then unloaded pad mount and used outriggers to lean power dolly over and swing boom back straight. -Equipment was checked by fleet and verified there was no damage to the power dolly or trailer 11/5/19. -"Communicate while using power dolly" was documented in the tailboard. -Member operating power dolly at the time did not have a completed FPR for the Power Dolly. -Stickers and labels are present on the machine warning that "All outriggers must be extended and set firmly on ground and machine leveled before crane operation" |  |  |  | Northeast District Service Cen | FALSE |  | TRUE | Construction Services |  | Dwayne Fox | Donald Melson |  | Chad Inman | I agree with the Corrective Actions listed above. Our leaders and members must understand that our SOP's and FPR's engage us and keep us informed, but the users must be intentional and do their due diligence to remain familiar with the equipment they use. DON'T ASSUME! | Chad Inman |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction |  |  | 9.03 Improper or insufficient delegation | [7 empty] | The immediate investigation was that the tracks had not been extracted after two of the members had gone out the backyard gate to load the machine on the trailer. The members had set up power dolly to lift the pad mount up and over the gate due to it being to big to get through the gate. After loading the pad mount back on the machine the tracks were not extended back out when they tracked to the trailer and loaded. This caused instability when the member swung to boom over to get the pad mount unloaded at the next location. The members realized the mistake after the event and had been utilizing the tracks prior to this event. | 15. Using Equipment Improperly | 9. Abnormal Operation |  | The learnings from this close call should include encouraging members to communicate competencies in operating heavy equipment during the tailboard. Approved. | [90 empty] | 7963302
9138 | Northeast District Service Cen | 2019-11-05 12:30 | Crew had loaded power dolly and was going to unload pad mount off the machine. Member swung boom to the left for the line truck to pick up pad mount and machine leaned over on the boom. Crew removed pad mount and used outriggers to set the machine up right. There was no damage to the trailer or power dolly. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Delivery | Donald Melson | 2019-11-18 15:49 | 2019-11-07 13:25 | 2019-11-07 13:25 | 2019-11-08 07:04 | 2019-11-19 12:30 | 2019-11-05 13:15 | 2019-11-18 11:31 |  | 2019-11-13 08:53 | N. Moccasin St. and Terrill Cir. in Sapulpa |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Donald Melson |  | Crew had pad mount on power dolly from previous location and was going to unload old pad mount and load new pad mount. Foreman went to check jobsite when member operated power dolly and swung boom to the left causing the power dolly to lean over on the boom tip contacting the ground. Crew stopped the job and contacted supervisor. Crew then unloaded pad mount and used outriggers to lean power dolly over and swing boom back straight. -Equipment was checked by fleet and verified there was no damage to the power dolly or trailer 11/5/19. -"Communicate while using power dolly" was documented in the tailboard. -Member operating power dolly at the time did not have a completed FPR for the Power Dolly. -Stickers and labels are present on the machine warning that "All outriggers must be extended and set firmly on ground and machine leveled before crane operation" |  |  |  | Northeast District Service Cen | FALSE |  | TRUE | Construction Services |  | Dwayne Fox | Donald Melson |  | Chad Inman | I agree with the Corrective Actions listed above. Our leaders and members must understand that our SOP's and FPR's engage us and keep us informed, but the users must be intentional and do their due diligence to remain familiar with the equipment they use. DON'T ASSUME! | Chad Inman |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction |  |  | 9.11 Inadequate matching of individual qualifications and job/task requirements | [7 empty] | The immediate investigation was that the tracks had not been extracted after two of the members had gone out the backyard gate to load the machine on the trailer. The members had set up power dolly to lift the pad mount up and over the gate due to it being to big to get through the gate. After loading the pad mount back on the machine the tracks were not extended back out when they tracked to the trailer and loaded. This caused instability when the member swung to boom over to get the pad mount unloaded at the next location. The members realized the mistake after the event and had been utilizing the tracks prior to this event. | 15. Using Equipment Improperly | 9. Abnormal Operation |  | The learnings from this close call should include encouraging members to communicate competencies in operating heavy equipment during the tailboard. Approved. | [90 empty] | 7963302
9138 | Northeast District Service Cen | 2019-11-05 12:30 | Crew had loaded power dolly and was going to unload pad mount off the machine. Member swung boom to the left for the line truck to pick up pad mount and machine leaned over on the boom. Crew removed pad mount and used outriggers to set the machine up right. There was no damage to the trailer or power dolly. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Delivery | Donald Melson | 2019-11-18 15:49 | 2019-11-07 13:25 | 2019-11-07 13:25 | 2019-11-08 07:04 | 2019-11-19 12:30 | 2019-11-05 13:15 | 2019-11-18 11:31 |  | 2019-11-13 08:53 | N. Moccasin St. and Terrill Cir. in Sapulpa |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Donald Melson |  | Crew had pad mount on power dolly from previous location and was going to unload old pad mount and load new pad mount. Foreman went to check jobsite when member operated power dolly and swung boom to the left causing the power dolly to lean over on the boom tip contacting the ground. Crew stopped the job and contacted supervisor. Crew then unloaded pad mount and used outriggers to lean power dolly over and swing boom back straight. -Equipment was checked by fleet and verified there was no damage to the power dolly or trailer 11/5/19. -"Communicate while using power dolly" was documented in the tailboard. -Member operating power dolly at the time did not have a completed FPR for the Power Dolly. -Stickers and labels are present on the machine warning that "All outriggers must be extended and set firmly on ground and machine leveled before crane operation" |  |  |  | Northeast District Service Cen | FALSE |  | TRUE | Construction Services |  | Dwayne Fox | Donald Melson |  | Chad Inman | I agree with the Corrective Actions listed above. Our leaders and members must understand that our SOP's and FPR's engage us and keep us informed, but the users must be intentional and do their due diligence to remain familiar with the equipment they use. DON'T ASSUME! | Chad Inman |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction |  |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | The immediate investigation was that the tracks had not been extracted after two of the members had gone out the backyard gate to load the machine on the trailer. The members had set up power dolly to lift the pad mount up and over the gate due to it being to big to get through the gate. After loading the pad mount back on the machine the tracks were not extended back out when they tracked to the trailer and loaded. This caused instability when the member swung to boom over to get the pad mount unloaded at the next location. The members realized the mistake after the event and had been utilizing the tracks prior to this event. | 15. Using Equipment Improperly | 9. Abnormal Operation |  | The learnings from this close call should include encouraging members to communicate competencies in operating heavy equipment during the tailboard. Approved. | [90 empty] | 7963302
9138 | Northeast District Service Cen | 2019-11-05 12:30 | Crew had loaded power dolly and was going to unload pad mount off the machine. Member swung boom to the left for the line truck to pick up pad mount and machine leaned over on the boom. Crew removed pad mount and used outriggers to set the machine up right. There was no damage to the trailer or power dolly. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Delivery | Donald Melson | 2019-11-18 15:49 | 2019-11-07 13:25 | 2019-11-07 13:25 | 2019-11-08 07:04 | 2019-11-19 12:30 | 2019-11-05 13:15 | 2019-11-18 11:31 |  | 2019-11-13 08:53 | N. Moccasin St. and Terrill Cir. in Sapulpa |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Donald Melson |  | Crew had pad mount on power dolly from previous location and was going to unload old pad mount and load new pad mount. Foreman went to check jobsite when member operated power dolly and swung boom to the left causing the power dolly to lean over on the boom tip contacting the ground. Crew stopped the job and contacted supervisor. Crew then unloaded pad mount and used outriggers to lean power dolly over and swing boom back straight. -Equipment was checked by fleet and verified there was no damage to the power dolly or trailer 11/5/19. -"Communicate while using power dolly" was documented in the tailboard. -Member operating power dolly at the time did not have a completed FPR for the Power Dolly. -Stickers and labels are present on the machine warning that "All outriggers must be extended and set firmly on ground and machine leveled before crane operation" |  |  |  | Northeast District Service Cen | FALSE |  | TRUE | Construction Services |  | Dwayne Fox | Donald Melson |  | Chad Inman | I agree with the Corrective Actions listed above. Our leaders and members must understand that our SOP's and FPR's engage us and keep us informed, but the users must be intentional and do their due diligence to remain familiar with the equipment they use. DON'T ASSUME! | Chad Inman |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.02 Inadequate practice |  |  | 9.03 Improper or insufficient delegation | [7 empty] | The immediate investigation was that the tracks had not been extracted after two of the members had gone out the backyard gate to load the machine on the trailer. The members had set up power dolly to lift the pad mount up and over the gate due to it being to big to get through the gate. After loading the pad mount back on the machine the tracks were not extended back out when they tracked to the trailer and loaded. This caused instability when the member swung to boom over to get the pad mount unloaded at the next location. The members realized the mistake after the event and had been utilizing the tracks prior to this event. | 15. Using Equipment Improperly | 9. Abnormal Operation |  | The learnings from this close call should include encouraging members to communicate competencies in operating heavy equipment during the tailboard. Approved. | [90 empty] | 7963302
9138 | Northeast District Service Cen | 2019-11-05 12:30 | Crew had loaded power dolly and was going to unload pad mount off the machine. Member swung boom to the left for the line truck to pick up pad mount and machine leaned over on the boom. Crew removed pad mount and used outriggers to set the machine up right. There was no damage to the trailer or power dolly. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Delivery | Donald Melson | 2019-11-18 15:49 | 2019-11-07 13:25 | 2019-11-07 13:25 | 2019-11-08 07:04 | 2019-11-19 12:30 | 2019-11-05 13:15 | 2019-11-18 11:31 |  | 2019-11-13 08:53 | N. Moccasin St. and Terrill Cir. in Sapulpa |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Donald Melson |  | Crew had pad mount on power dolly from previous location and was going to unload old pad mount and load new pad mount. Foreman went to check jobsite when member operated power dolly and swung boom to the left causing the power dolly to lean over on the boom tip contacting the ground. Crew stopped the job and contacted supervisor. Crew then unloaded pad mount and used outriggers to lean power dolly over and swing boom back straight. -Equipment was checked by fleet and verified there was no damage to the power dolly or trailer 11/5/19. -"Communicate while using power dolly" was documented in the tailboard. -Member operating power dolly at the time did not have a completed FPR for the Power Dolly. -Stickers and labels are present on the machine warning that "All outriggers must be extended and set firmly on ground and machine leveled before crane operation" |  |  |  | Northeast District Service Cen | FALSE |  | TRUE | Construction Services |  | Dwayne Fox | Donald Melson |  | Chad Inman | I agree with the Corrective Actions listed above. Our leaders and members must understand that our SOP's and FPR's engage us and keep us informed, but the users must be intentional and do their due diligence to remain familiar with the equipment they use. DON'T ASSUME! | Chad Inman |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.02 Inadequate practice |  |  | 9.11 Inadequate matching of individual qualifications and job/task requirements | [7 empty] | The immediate investigation was that the tracks had not been extracted after two of the members had gone out the backyard gate to load the machine on the trailer. The members had set up power dolly to lift the pad mount up and over the gate due to it being to big to get through the gate. After loading the pad mount back on the machine the tracks were not extended back out when they tracked to the trailer and loaded. This caused instability when the member swung to boom over to get the pad mount unloaded at the next location. The members realized the mistake after the event and had been utilizing the tracks prior to this event. | 15. Using Equipment Improperly | 9. Abnormal Operation |  | The learnings from this close call should include encouraging members to communicate competencies in operating heavy equipment during the tailboard. Approved. | [90 empty] | 7963302
9138 | Northeast District Service Cen | 2019-11-05 12:30 | Crew had loaded power dolly and was going to unload pad mount off the machine. Member swung boom to the left for the line truck to pick up pad mount and machine leaned over on the boom. Crew removed pad mount and used outriggers to set the machine up right. There was no damage to the trailer or power dolly. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Delivery | Donald Melson | 2019-11-18 15:49 | 2019-11-07 13:25 | 2019-11-07 13:25 | 2019-11-08 07:04 | 2019-11-19 12:30 | 2019-11-05 13:15 | 2019-11-18 11:31 |  | 2019-11-13 08:53 | N. Moccasin St. and Terrill Cir. in Sapulpa |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Donald Melson |  | Crew had pad mount on power dolly from previous location and was going to unload old pad mount and load new pad mount. Foreman went to check jobsite when member operated power dolly and swung boom to the left causing the power dolly to lean over on the boom tip contacting the ground. Crew stopped the job and contacted supervisor. Crew then unloaded pad mount and used outriggers to lean power dolly over and swing boom back straight. -Equipment was checked by fleet and verified there was no damage to the power dolly or trailer 11/5/19. -"Communicate while using power dolly" was documented in the tailboard. -Member operating power dolly at the time did not have a completed FPR for the Power Dolly. -Stickers and labels are present on the machine warning that "All outriggers must be extended and set firmly on ground and machine leveled before crane operation" |  |  |  | Northeast District Service Cen | FALSE |  | TRUE | Construction Services |  | Dwayne Fox | Donald Melson |  | Chad Inman | I agree with the Corrective Actions listed above. Our leaders and members must understand that our SOP's and FPR's engage us and keep us informed, but the users must be intentional and do their due diligence to remain familiar with the equipment they use. DON'T ASSUME! | Chad Inman |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.02 Inadequate practice |  |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | The immediate investigation was that the tracks had not been extracted after two of the members had gone out the backyard gate to load the machine on the trailer. The members had set up power dolly to lift the pad mount up and over the gate due to it being to big to get through the gate. After loading the pad mount back on the machine the tracks were not extended back out when they tracked to the trailer and loaded. This caused instability when the member swung to boom over to get the pad mount unloaded at the next location. The members realized the mistake after the event and had been utilizing the tracks prior to this event. | 15. Using Equipment Improperly | 9. Abnormal Operation |  | The learnings from this close call should include encouraging members to communicate competencies in operating heavy equipment during the tailboard. Approved. | [90 empty] | 7963302
9139 | Sooner Power Plant | 2019-11-06 17:00 | Member removed abandoned intercom system by cutting wires. When cutting wiring member noticed a small arc. Wiring was tested and found to have an induced voltage. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Michael Dowell | 2019-12-05 10:20 | 2019-11-07 16:54 | 2019-11-07 16:54 | 2019-11-20 10:54 | 2019-11-20 17:00 | 2019-11-07 16:47 | 2019-11-25 13:11 |  | 2019-11-22 09:09 | Sooner PP Garage Office |  |  | Jesse Murray | Approved. Jesse Murray 12/5/19 | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Michael Dowell |  | On Wednesday, November 6th, member was given instruction to paint the office in the garage/carpentry shop. The garage has been part of our 5S efforts and the office was being painted to improve its appearance. The member began the day by masking areas of the room that were not to be painted. After completing a large part of the room, the member decided that by removing the GAI Tronics intercom, which had not been in used for several years , he could further improve the look of the room. The member was standing on a fiberglass ladder, about 2 feet off the ground, and unbolted the system from the wall. After the hardware(bolts) were removed, the member removed the cover to the LB that was attached to the intercom junction box and cut the wiring. When the member cut the wires, he notice a sizzling sound. He did not see an arc or feel and electrical contact. Member taped up the wires and reported incident to supervisor. After being notified of the incident, the wiring was test with a non-contact voltage detector. This device did not indicate, positively that the wiring was energized. A digital multi-meter was used and 120 vac was detected. When first tested the amperage of the wiring appeared to be .74 amps, the voltage was assumed to be induced and the first report was submitted. However, we were not completely happy with our testing methods and retested the wiring the next day. Upon our retest we discover that the voltage present had the potential to produce 54 amps. When the prints for the system were pulled it was discovered that the intercom system in the main building (admin, weld shop, i&C shop. elec shop) was indeed disconnected, the stations mounted in the outlying buildings were fed from other outlying buildings. When discussing this system with the senior electrical members at the plant, the consensus was that the system was dead and power had been disconnected. The member "knew" that the system had not been used in many years and understood that it was "dead". Member was wearing company approved safety shoes, standing on a fiberglass ladder 2' off of the ground, wearing gloves, using side cutters with vinyl handles and cut all the conductors in one action. All of these things helped to reduce the risk of this incident. The member did not actively take these steps to reduce risk. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Michael Gibbs | Michael Dowell |  | Frank Brixey | Approved - Brixey 11/25/2019 | Frank Brixey |  | Medium |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Member thought that intercom system was dead. The system has not been used in many years and it was his understanding that the system had no power. | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | I have reviewed while Brady is on vacation. | [90 empty] | 18850712
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Jackson Dale | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [8 empty] | 9.09 Inadequate identification and evaluation of loss exposures | 10.03 Inadequate standards, specifications and/or design criteria | [6 empty] | Fire system isolated | 23. Defective Tools, Equipment or Materials | 9. Abnormal Operation | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Jackson Dale | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [8 empty] | 9.09 Inadequate identification and evaluation of loss exposures | 10.01 Inadequate assessment of loss exposures |  |  |  |  | 15.03 Inadequate inspection and/or monitoring |  | Ducting failed in an uncontrolled way | 26. Fire & Explosion Hazards | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Jackson Dale | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [8 empty] | 9.09 Inadequate identification and evaluation of loss exposures | 10.01 Inadequate assessment of loss exposures |  |  |  |  | 15.02 Improper extension of service life |  | Ducting failed in an uncontrolled way | 26. Fire & Explosion Hazards | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Jackson Dale | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [8 empty] | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.01 Inadequate assessment of loss exposures |  |  |  |  | 15.03 Inadequate inspection and/or monitoring |  | Ducting failed in an uncontrolled way | 26. Fire & Explosion Hazards | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Jackson Dale | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [8 empty] | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.01 Inadequate assessment of loss exposures |  |  |  |  | 15.02 Improper extension of service life |  | Ducting failed in an uncontrolled way | 26. Fire & Explosion Hazards | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Jackson Dale | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | plugged chute | 40. Weather Conditions | 12. Equipment Failure | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Jackson Dale | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [12 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | plugged chute | 40. Weather Conditions | 12. Equipment Failure | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Jackson Dale | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [12 empty] | 13.03 Inadequate standards or specifications |  |  |  | plugged chute | 40. Weather Conditions | 12. Equipment Failure | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Jackson Dale | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [8 empty] | 9.06 Inadequate work planning or programming |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Failure to monitor pyrite flow | 36. Inadequate Preparation, Planning | 9. Abnormal Operation | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Robert Wright | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [8 empty] | 9.09 Inadequate identification and evaluation of loss exposures | 10.03 Inadequate standards, specifications and/or design criteria | [6 empty] | Fire system isolated | 23. Defective Tools, Equipment or Materials | 9. Abnormal Operation | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Robert Wright | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [8 empty] | 9.09 Inadequate identification and evaluation of loss exposures | 10.01 Inadequate assessment of loss exposures |  |  |  |  | 15.03 Inadequate inspection and/or monitoring |  | Ducting failed in an uncontrolled way | 26. Fire & Explosion Hazards | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Robert Wright | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [8 empty] | 9.09 Inadequate identification and evaluation of loss exposures | 10.01 Inadequate assessment of loss exposures |  |  |  |  | 15.02 Improper extension of service life |  | Ducting failed in an uncontrolled way | 26. Fire & Explosion Hazards | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Robert Wright | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [8 empty] | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.01 Inadequate assessment of loss exposures |  |  |  |  | 15.03 Inadequate inspection and/or monitoring |  | Ducting failed in an uncontrolled way | 26. Fire & Explosion Hazards | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Robert Wright | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [8 empty] | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.01 Inadequate assessment of loss exposures |  |  |  |  | 15.02 Improper extension of service life |  | Ducting failed in an uncontrolled way | 26. Fire & Explosion Hazards | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Robert Wright | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | plugged chute | 40. Weather Conditions | 12. Equipment Failure | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Robert Wright | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [12 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | plugged chute | 40. Weather Conditions | 12. Equipment Failure | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Robert Wright | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [12 empty] | 13.03 Inadequate standards or specifications |  |  |  | plugged chute | 40. Weather Conditions | 12. Equipment Failure | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Robert Wright | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [8 empty] | 9.06 Inadequate work planning or programming |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Failure to monitor pyrite flow | 36. Inadequate Preparation, Planning | 9. Abnormal Operation | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Rodney Hyslope | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [8 empty] | 9.09 Inadequate identification and evaluation of loss exposures | 10.03 Inadequate standards, specifications and/or design criteria | [6 empty] | Fire system isolated | 23. Defective Tools, Equipment or Materials | 9. Abnormal Operation | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Rodney Hyslope | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [8 empty] | 9.09 Inadequate identification and evaluation of loss exposures | 10.01 Inadequate assessment of loss exposures |  |  |  |  | 15.03 Inadequate inspection and/or monitoring |  | Ducting failed in an uncontrolled way | 26. Fire & Explosion Hazards | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Rodney Hyslope | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [8 empty] | 9.09 Inadequate identification and evaluation of loss exposures | 10.01 Inadequate assessment of loss exposures |  |  |  |  | 15.02 Improper extension of service life |  | Ducting failed in an uncontrolled way | 26. Fire & Explosion Hazards | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Rodney Hyslope | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [8 empty] | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.01 Inadequate assessment of loss exposures |  |  |  |  | 15.03 Inadequate inspection and/or monitoring |  | Ducting failed in an uncontrolled way | 26. Fire & Explosion Hazards | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Rodney Hyslope | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [8 empty] | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.01 Inadequate assessment of loss exposures |  |  |  |  | 15.02 Improper extension of service life |  | Ducting failed in an uncontrolled way | 26. Fire & Explosion Hazards | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Rodney Hyslope | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | plugged chute | 40. Weather Conditions | 12. Equipment Failure | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Rodney Hyslope | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [12 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | plugged chute | 40. Weather Conditions | 12. Equipment Failure | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Rodney Hyslope | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [12 empty] | 13.03 Inadequate standards or specifications |  |  |  | plugged chute | 40. Weather Conditions | 12. Equipment Failure | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Rodney Hyslope | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [8 empty] | 9.06 Inadequate work planning or programming |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Failure to monitor pyrite flow | 36. Inadequate Preparation, Planning | 9. Abnormal Operation | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Raleigh Hetherington | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [8 empty] | 9.09 Inadequate identification and evaluation of loss exposures | 10.03 Inadequate standards, specifications and/or design criteria | [6 empty] | Fire system isolated | 23. Defective Tools, Equipment or Materials | 9. Abnormal Operation | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Raleigh Hetherington | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [8 empty] | 9.09 Inadequate identification and evaluation of loss exposures | 10.01 Inadequate assessment of loss exposures |  |  |  |  | 15.03 Inadequate inspection and/or monitoring |  | Ducting failed in an uncontrolled way | 26. Fire & Explosion Hazards | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Raleigh Hetherington | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [8 empty] | 9.09 Inadequate identification and evaluation of loss exposures | 10.01 Inadequate assessment of loss exposures |  |  |  |  | 15.02 Improper extension of service life |  | Ducting failed in an uncontrolled way | 26. Fire & Explosion Hazards | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Raleigh Hetherington | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [8 empty] | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.01 Inadequate assessment of loss exposures |  |  |  |  | 15.03 Inadequate inspection and/or monitoring |  | Ducting failed in an uncontrolled way | 26. Fire & Explosion Hazards | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Raleigh Hetherington | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [8 empty] | 9.04 Giving inadequate policy, procedure, practices or guidelines | 10.01 Inadequate assessment of loss exposures |  |  |  |  | 15.02 Improper extension of service life |  | Ducting failed in an uncontrolled way | 26. Fire & Explosion Hazards | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Raleigh Hetherington | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | plugged chute | 40. Weather Conditions | 12. Equipment Failure | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Raleigh Hetherington | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [12 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | plugged chute | 40. Weather Conditions | 12. Equipment Failure | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Raleigh Hetherington | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [12 empty] | 13.03 Inadequate standards or specifications |  |  |  | plugged chute | 40. Weather Conditions | 12. Equipment Failure | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9140 | Muskogee Power Plant | 2019-11-07 23:00 | While fighting wet coal on unit 6 the 6F feeder started to plug up. When it did so the pulverizer got hot and we puffed the pulverizer causing damage to the hot air duct and expansion joint. | Level 3 |  | TRUE | Property Damage | Donnie Jones | Jesse Murray | I assigned this team because 2 of them were on shift that night. I also wanted a safety professional on the team. Jesse, Please assign Carol Rollins (lead), Darcey Hayes, Rodney Hyslope, and Bob Wright. Thanks for the reminder. Also, Steve is out until his last day so send any operations items my way until we name the new MPO. Thanks, Jon. | 2019-11-20 19:34 | Power Supply | Darcey Hayes | 2020-02-10 07:38 | 2019-11-08 18:34 | 2019-11-08 18:34 | 2019-12-16 15:36 | 2019-11-21 23:00 | 2019-11-07 23:00 | 2019-12-30 11:09 | 2020-02-05 12:24 | 2019-12-18 13:30 | Muskogee PP Unit 6 boiler basement and mill bay area |  |  | Donnie Jones | I would like to see a final version of the wet coal plan that is mentioned in the corrective actions. I would like to also ensure this plan has been developed through collaboration between Muskogee and Sooner members. One plan for both plants if applicable. If that is not possible I would like a summary of why when the plan is presented to me once complete. Thank you, Donnie Jones | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Carol Rollins |  | Wet coal plan was put into effect on 11/6/2019. Mills A,B,C,E were in service. All mills were experiencing intermittent plugging. Plugging on B mill caused a gearbox failure and F mill was placed into service 11/7 at 1820. F mill began to plug at 1830 and was washed at put back into service at 1834. Duct work was damaged at 2258. Wet coal causes plugging at the inlet piping to the feeder at the mill. The mill outlet temperature begins to climb as coal acts as a coolant in the pulverization process. The plug is relieved by washing the coal out of the feeder. The water and coal are drained through the mill's pyrite system. If the water flow outruns the drain system, the coal laden water will back-flow into the hot air duct coming into the mill. When the hot air duct temp rises combustion of the fuel in the duct can occur. An interim wet coal strategy was in place while the wet coal OI is being updated. The strategy, attached, was printed and available during the wet coal event. It was covered in the turnover and on the SWP. In the wet coal strategy the outlet temps, air flow are trended and monitored. The data from unit 6 is slower than 4 and 5 were previously. A planned DCS evergreen update will provide better trending for 6 mills. The outlet temperature was noted to be climbing at 2212. Operations washed down the inlet to unplug and cool the mill at that time. Pyrite system was not in automatic operation. The outlet temperature was starting to rise about 10 seconds before the explosion occurred. Operators were notified to return to the area as soon as the outlet temp started to rise. The duct blew out before they could reach the area. The explosion can be seen on the trend by the furnace differential pressure spike and the under bowl air flow dropped out. The cold air, hot air, and feeder rejected to manual due to the air flow reading bad quality. The feeder tripped on a plugged discharge chute switch within 10 seconds. The outlet temperature continues to climb due to a fire in the duct. The fire suppression in the system did automatically fire but the header was isolated due to freeze protection. The unit was taken off line after the mill was tripped due to inadequate fuel supply to the boiler. The PA duct and the hot air damper were damaged. The hot air expansion joint required minor repair and the cold air expansion joint was patched until a new one is received. The hot air gate had no damage. This resulted in a forced outage to return mills A and B to service. A maintenance outage was then entered to repair the duct work and damper. All ducts were inspected and cleaned for fuel spillage in the outage as well. | Raleigh Hetherington | Carol Rollins |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Kirby Haynes | Darcey Hayes |  | Jonathan Stogsdill | Reviewed w/ no additional comments. JHS | Jonathan Stogsdill | Jesse Murray | High | [8 empty] | 9.06 Inadequate work planning or programming |  |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Failure to monitor pyrite flow | 36. Inadequate Preparation, Planning | 9. Abnormal Operation | Approved. Jesse Murray | Good Investigation Reviewed Bob Wright
9141 | Ardmore Service Center | 2019-11-11 14:00 | This is a First Aid. While member was on pole changing pin and insulator a gust of wind blew member causing member to reposition feeling discomfort in lower back. | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Terry Looney | 2019-11-19 14:45 | 2019-11-12 07:45 | 2019-11-12 07:45 | 2019-11-12 07:57 | 2019-11-25 14:00 | 2019-11-12 07:36 |  |  |  | Ratliff City 6 miles north 1 mile east |  |  | Terry Hackett | Member was operating within the parameters of our safety policies and practices and experienced a minor strain. TMH | T&D Ops |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | [5 empty] | FALSE | Ardmore Service Center | FALSE |  | FALSE | Construction Services |  | Keith McMillan | Terry Looney |  |  |  | Kenneth McKinzie |  | Low | [45 empty] | FALSE |  |  | 2016-02-08 | 1979-06-05 |  | 2019-11-11 07:00 | 0 | 0 |  | FALSE |  | While member was on pole changing pin and insulator a gust of wind blew member causing member to reposition feeling discomfort in lower back. |  | FALSE | Keith McMillan |  | First Aid | Keith McMillan |  |  |  |  | Sprain/Strain |  | FALSE |  | Area Service Technician | Back |  | Lower |  | Terry Looney |  |  | 11/11/2019 7:00:00 AM |  | FALSE |  |  | Wind | Climbing wood pole
9142 | Sooner Power Plant | 2019-11-12 15:00 | Contractor (GBI) was driving forklift carrying short timbers. As they were going up inclined road West of intake channel toward the coal yard the short timbers fell off forklift. No damage or injuries. | Level 1 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services | Ashley Harris | 2019-11-25 16:20 | 2019-11-12 16:42 | 2019-11-12 16:42 | 2019-11-20 11:54 | 2019-11-26 15:00 | 2019-11-12 16:11 | 2019-11-20 13:46 |  |  | Sooner Power Plant- inclined road leading to coal yard. |  |  | Marcus Huddleston | No additional comments. MLH 11/25/19 | UTS |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Ashley Harris |  | Contractor (GBI) was driving forklift carrying a pallet of two foot cross ties. As they were going up inclined road West of intake channel toward the coal yard a 2 foot piece of cross tie fell off due to a low depression in the road. The cross tie hit the roadway and forklift tire. No injury or damage. Immediate corrective action taken was to restack material in a more stable way. Future corrective action to prevent reoccurrence would be to strap down material when needed to forklift. Load was not secured/ tied down. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | UTS - Capital Projects |  | Ashley Harris | Ashley Harris |  | Robert Weaver | Agree with assessment above. | Robert Weaver |  | Low | [6 empty] | 7.06 Improper attempt to save time or effort |  | 9.06 Inadequate work planning or programming | [7 empty] | Contractor (GBI) was driving forklift carrying a pallet of two foot cross ties. As they were going up inclined road West of intake channel toward the coal yard a 2 foot piece of cross tie fell off due to a low depression in the road. | 08. Improper Loading | 2. Struck By (Hit By Moving Object) | [5 empty] | Injury / Illness |  | Ashley Harris | [5 empty] | 2. Struck By (Hit By Moving Object) | Ashley Harris | Great Basin Industrial | Great Basin Industial |  |  |  | Ashley Harris
9143 | Ft Smith Service Center | 2019-11-14 12:00 | Foreman trimming tree adjacent to gas meter, after making cut on limb, it caught on lower limbs while falling to the ground, causing it to swing out of drop zone and strike the regulator of a gas meter, damaging it in the process. AOG was notified and made necessary repairs. | Level 1 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services | Elizabeth Mason-Reynolds | 2019-12-04 13:22 | 2019-11-15 13:28 | 2019-11-15 13:28 | 2019-11-27 16:57 | 2019-11-28 12:00 | 2019-11-15 13:15 | 2019-12-02 10:47 |  |  | 1505 S 37th St , Ft. Smith Arkansas |  |  | Jerrie Looney | West Tree fully investigated incident and described corrective action as "Retraining on proper trimming techniques". Jerrie Looney, 12/4/19 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Elizabeth Mason-Reynolds |  | Jason Rich stated he was in the process of cutting several limbs, some of which had grown in-between the fiber optic cable wire and the Neutral wire, when a limb, approximately 4 ft in length, 2 to 3 inches in diameter got caught on some lower hanging limbs as it was falling to the ground. As a result, the limb swung out of the intended fall zone, striking the regulator of gas meter in the process |  |  |  | Ft Smith Service Center | FALSE |  | TRUE | PD - Resource Planning & Coord |  | Elizabeth Mason-Reynolds | Elizabeth Mason-Reynolds |  | Danny Coffey | Incident has been reviewed by OG&E Forester in conjunction with West Tree Safety Representative and West Tree Supervisor. As this was designated a Close Call, no further investigation is needed. | Danny Coffey |  | Low |  |  |  | 4.04 Routine, monotony, demand for uneventful vigilance | [12 empty] | Foreman was trimming a Mulberry tree in the back yard of a residence located at 1505 S. 37th Street in Fort Smith, a falling limb struck a gas meter, damaging it as a result. Human Factor: Team member failed to properly analyze tree, failing to clear all lower limbs before cutting upper limbs. | 17. Failure to Identify Hazard, Risk | 6. Caught On (Snagged, Hung) | [5 empty] | Property Damage |  | Elizabeth Mason-Reynolds | [5 empty] | 7. Caught Between or Under (Crushed or Amputated) | Elizabeth Mason-Reynolds | West Tree Service | Jason Rich |  |  |  | Elizabeth Mason-Reynolds | [71 empty] | 82942151
9144 | Seminole PP; EGX Gath/Trans | 2019-11-19 14:00 | insulation and lagging fell off piping and landed on boiler roof | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Leslie Henderson | 2020-01-20 14:41 | 2019-11-19 15:00 | 2019-11-19 15:00 | 2019-12-06 14:18 | 2019-12-03 14:00 | 2019-11-19 14:51 | 2020-01-10 15:08 |  | 2019-12-19 16:14 | Seminole pp unit 3 boiler roof north side |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Leslie Henderson |  | Lagging and Insulation fell off of abandon piping. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | Operations |  | Roy Hicks | Leslie Henderson |  | Paul Schoelen | Review complete | Paul Schoelen |  | Medium | [12 empty] | 13.06 Inadequate salvage and reclamation |  |  |  | Lagging and Insulation fell from a height of approximately twenty feet | 40. Weather Conditions | 3. Fall from Elevation to Lower Level |  | Reviewed | [66 empty] | Lagging and insulation on abandon piping | 5000 | Terry Bunch | Fixed Equipment
9145 | Metro Service Center | 2019-11-18 16:30 | Public vehicle made contact with company vehicle. Minor damage was sustained to the rear bumper. Member was going approximately 20 MPH due to traffic congestion. | Level 2 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Kenny La Ferney | 2019-11-21 12:10 | 2019-11-19 15:31 | 2019-11-19 15:31 | 2019-11-19 15:48 | 2019-12-02 16:30 | 2019-11-19 15:26 | 2019-11-21 09:23 |  | 2019-11-20 08:23 | I-35 North Bound between 10th and 23rd St |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Kenny La Ferney |  | Member was traveling home from work on I-35 Northbound. Traffic was moving slowly due to congestion. A pile up occurred behind the company vehicle. Public vehicle that was involved in the pile up made contact with the rear bumper of company truck on the driver side, resulting in minor damage. Member did not realize or notice that the public vehicle had made contact with the company vehicle until arriving home. Member was not at fault. |  |  |  | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Wayne Adams | Kenny La Ferney |  | Gary Lassley | Member was aware of the pending situation and had slowed down due to the traffic congestion. After the pile up occurred (behind the members vehicle) Member exited the vehicle to check on the welfare of the vehicles behind him. Member did everything possible to avoid being involved in this incident. | Gary Lassley |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Public vehicle struck company vehicle 5.06 is referring to the public drivers who were at fault. | 16. Failure to Follow Procedure, Policy, Practice | 2. Struck By (Hit By Moving Object) |  | Reviewed/Approved. Member was not at fault for the incident | [72 empty] | FALSE |  | Oklahoma City | Public Vehicle Struck OGE | Both Vehicles Moving | 1985-04-21 19:00 |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Clear
9146 | Metro Service Center | 2019-11-20 14:00 | Company vehicle was sitting at stop light and got rear-ended by a public vehicle. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Jeffrey Gleim | 2019-11-26 08:24 | 2019-11-21 09:21 | 2019-11-21 09:21 | 2019-11-21 09:24 | 2019-12-04 14:00 | 2019-11-21 09:13 |  |  |  | East bound 12th street at North Moore Ave. |  |  | Brent Perdue | our vehicle was setting still. I approve of the incident analysis due to the circumstances. | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | [6 empty] | Metro Service Center | FALSE |  | FALSE | PD Operations Services |  | Michael Jennings | Jeffrey Gleim |  |  |  | Steve Watkins |  | Low | [93 empty] | FALSE |  | Moore | Public Vehicle Struck OGE | OGE Vehicle Stopped/Parked | 2012-03-11 19:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
9147 | Metro Service Center | 2019-11-21 09:52 | TCC System Operator was performing switching order S1739 with field personnel on location at Draper Lake sub. Step 26 was to open Draper Lake 345kV PCB 303 by SCADA. Operator incorrectly opened Draper Lake 302 instead of 303. | Level 2 |  | FALSE | System Operational Incident |  |  |  |  | Transco | Drew Walker | 2020-02-05 12:01 | 2019-11-21 12:24 |  | 2020-01-31 12:06 | 2020-01-02 09:52 | 2019-11-21 10:20 | 2020-02-05 10:42 |  | 2020-02-03 08:19 | TCC System Operator at the Metro Transmission Control Center performing remote SCADA switching at Draper Lake Substation |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Drew Walker |  | TCC System Operator was performing switching order S1739 with field personnel on location at Draper Lake sub. Step 26 was to open Draper Lake 345kV PCB 303 by SCADA. Operator incorrectly opened Draper Lake 302 instead of 303. Field switchman heard relay operate but did not verify the correct PCB opened. TCC operator gave steps to close disconnects on bus-tie transformer bank #3, field switchman closed high side switch which energized bank #3 since PCB 303 was still closed. |  |  |  | Metro Service Center | FALSE |  | FALSE | System Operations |  | Craig Daniel | Drew Walker |  | Darrell Fuller | I agree with all corrective actions outlined above. It is important, all operators know and understand the importance of making sure they are always operating the correct device when conducting switching. The redesigned SCADA One Line will be a big help's provide clarity on what was a congested or busy screen. Jim's review with his field members is a significant piece as well. Not only are they the eyes in the filed, they must make sure the desired device was operated and is in the proper position for everyone safety. | Darrell Fuller |  | Medium |  | 2.10 Memory failure |  |  | 5.06 Lack of situational awareness | [11 empty] | Failure to select proper PCB on SCADA screen, failure to read and comprehend correctly both dialog boxes indicating which PCB was selected, failure to verify correct PCB opened. | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation |  | review and approve cm
9147 | Metro Service Center | 2019-11-21 09:52 | TCC System Operator was performing switching order S1739 with field personnel on location at Draper Lake sub. Step 26 was to open Draper Lake 345kV PCB 303 by SCADA. Operator incorrectly opened Draper Lake 302 instead of 303. | Level 2 |  | FALSE | System Operational Incident |  |  |  |  | Transco | Drew Walker | 2020-02-05 12:01 | 2019-11-21 12:24 |  | 2020-01-31 12:06 | 2020-01-02 09:52 | 2019-11-21 10:20 | 2020-02-05 10:42 |  | 2020-02-03 08:19 | TCC System Operator at the Metro Transmission Control Center performing remote SCADA switching at Draper Lake Substation |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Drew Walker |  | TCC System Operator was performing switching order S1739 with field personnel on location at Draper Lake sub. Step 26 was to open Draper Lake 345kV PCB 303 by SCADA. Operator incorrectly opened Draper Lake 302 instead of 303. Field switchman heard relay operate but did not verify the correct PCB opened. TCC operator gave steps to close disconnects on bus-tie transformer bank #3, field switchman closed high side switch which energized bank #3 since PCB 303 was still closed. |  |  |  | Metro Service Center | FALSE |  | FALSE | System Operations |  | Craig Daniel | Drew Walker |  | Darrell Fuller | I agree with all corrective actions outlined above. It is important, all operators know and understand the importance of making sure they are always operating the correct device when conducting switching. The redesigned SCADA One Line will be a big help's provide clarity on what was a congested or busy screen. Jim's review with his field members is a significant piece as well. Not only are they the eyes in the filed, they must make sure the desired device was operated and is in the proper position for everyone safety. | Darrell Fuller |  | Medium |  | 2.05 Inability to comprehend |  |  | 5.06 Lack of situational awareness | [11 empty] | Failure to select proper PCB on SCADA screen, failure to read and comprehend correctly both dialog boxes indicating which PCB was selected, failure to verify correct PCB opened. | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation |  | review and approve cm
9148 | Sooner Power Plant | 2019-11-21 14:30 | Sparks from a piece of steel that was being prepped for a new pipe support contacted some old insulation that had some coal dust on it. After contact at some point the coal and old insulation started smoldering. Welder and fire watch noted the smell but had to locate where the smoke was coming from. After finding the smoldering insulation it was doused with a bottle of water to put out the fire. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | David Willis | 2019-12-19 11:42 | 2019-11-21 16:02 | 2019-11-21 16:02 | 2019-12-09 09:04 | 2019-12-05 14:30 | 2019-11-21 15:37 | 2019-12-11 11:37 |  |  | Sooner PP Coal Yard Service Water Booster Pump Room |  |  | Brady Sowell | David, I am returning this incident because I do not believe we have addressed how they missed the flammable material that was within their hotwork area. If they have a hotwork permit and are performing hotwork, there should be no combustibles within 35ft. Please address how this was missed. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | David Willis |  | Employees were doing hot work installing pipe and brackets in the booster pump room at the coal yard. Employees smelled something burning and found a piece of torn insulation about six feet up on the east wall smoldering. Employees took a bottle of water and poured it onto the insulation to put out the smoldering embers. Employees then reported the incident. During initial set up for the welding and the hot work permit the workers noted that everything in the booster pump room was coated in dust and was generally dirty but did not realize that some of the dust was actually coal dust mixed in with the silica dust and was flammable. This allowed them to complete the hot work permit with out identifying the flammable material. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Engineering & Planning |  | David Willis | Donald Wyckoff |  | Donald Wyckoff | Contractor did not take into account presence of coal dust in area, therefore proper enclosure/cutting technics were not used to prevent sparks from being contained. Contractor is not identifying the hazards in coal handling areas as necessary. This may be from a lack of knowledge of the potential danger a combustible dust incident can be. Contractors need to be more aware of this energy source when performing hot work in a coal facility. The action item to communicate hazard in the beginning of execution phase is a must but also mitigation of hazards also must be taken to prevent ignition of any remaining dust in the immediate work area. I approve incident investigation findings. | Donald Wyckoff |  | Low |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming | [7 empty] | Sparks from grinding a steel support in preparation for welding contacted flammable material, in this case coal dust, that had accumulated in a torn section of insulation and started smoldering. | 17. Failure to Identify Hazard, Risk | 9. Abnormal Operation | [5 empty] | Property Damage |  | David Willis | [5 empty] | 9. Abnormal Operation | David Willis | Zachry | Vernon King |  |  |  | David Willis | [71 empty] | 9590552
9149 | South District Service Center | 2019-11-22 09:00 | While positioning bucket trucks, working arm of bucket 2 tipped canvas working bag to the side causing battery cutter to fall out. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Delivery | Gary Parks | 2019-12-11 08:50 | 2019-11-22 10:41 | 2019-11-22 10:41 | 2019-12-05 13:06 | 2019-12-06 09:00 | 2019-11-22 09:00 | 2019-12-06 10:12 |  |  | 222 E. Gray, Norman, Ok |  |  | Luke Kennedy | Further investigation into tool securement will be completed via the corrective actions from this investigation. Approved | T&D Ops |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Gary Parks |  | Crew was building an alley structure and hanging 3 large transformers. While working, bag that was holding the press, tipped and the press fell striking the right side of the front windshield. This caused a spider web of the windshield. |  |  |  | South District Service Center | FALSE |  | FALSE | Construction Services |  | Cameron Allen | Gary Parks |  | Terry Garrett | I approve | Terry Garrett |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | bag was contacted by bucket causing the cutter to fall onto the windshield causing minor damage | 03. Failure to Secure | 3. Fall from Elevation to Lower Level | [68 empty] | Cracked passenger side windshield | 300 |  | Vehicle (not related to operation of vehicle)
9150 | River Valley | 2019-11-21 22:30 | Fuel Supply Operators went to manually change the position of a Limestone silo gate. During the operation one members hand was placed between the cylinder housing and the handle smashing the tip of his right hand ring finger. | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Supply | Jeffrey Monks | 2019-12-02 07:42 | 2019-11-22 15:33 | 2019-11-22 15:33 | 2019-11-22 16:28 | 2019-12-05 22:30 | 2019-11-22 15:00 |  |  |  | Unit 2 Limestone silo flop gate |  |  | Anthony Gillespie | Incident closed. | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | [5 empty] | FALSE | River Valley | FALSE |  | FALSE | Fuel Supply |  | Robert Williamson | Jeffrey Monks |  |  |  | Jeremiah Perryman |  | Low | [45 empty] | FALSE |  |  | 2019-05-28 | 1970-10-11 |  | 2019-11-21 22:00 | 0 | 0 | Cleaned the area and placed bandage the finger. | FALSE |  | Fuel Supply Operators went to manually change the position of a Limestone silo gate. During the operation one members hand was placed between the cylinder housing and the handle smashing the tip of his right hand ring finger. |  | TRUE | Robert Williamson |  | First Aid | Robert Williamson |  |  |  |  | Crush/Smash |  | FALSE |  | Fuel Supply Tech Senior | Finger |  | Right |  | Jeffrey Monks |  |  | 11/21/2019 10:00:00 PM | 6 months | FALSE |  |  | During the operation one members hand was placed between the cylinder housing and the handle. | Fuel Supply Operators went to manually change the position of a Limestone silo gate
9151 | Muskogee Service Center | 2019-11-26 12:15 | Company member was in left turning lane when public vehicle struck company vehicle passenger side. No injuries. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Jeffery Walker | 2019-12-02 07:52 | 2019-11-27 13:52 | 2019-11-27 13:52 | 2019-11-27 13:58 | 2019-12-10 12:15 | 2019-11-26 13:45 |  |  |  | 32nd Street & Okmulgee Muskogee, ok |  |  | Hannah Everett | Reviewed | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE |  |  | Member in company vehicle was turning east onto west Okmulgee from North 32nd St, when public vehicle came into turning lane making contact with company vehicle rear passenger side. Supervisor were notified and there were no injuries. |  |  |  | Muskogee Service Center | FALSE |  | FALSE | PD Operations Services |  | Jeffery Walker | Don Mantooth |  |  |  | James Hutchison |  | Low | [93 empty] | FALSE |  | Muskogee | Public Vehicle Struck OGE | Public Driver Failed To Yield | 1985-11-03 18:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
9152 | Sooner Power Plant | 2019-11-27 00:30 | At about 0004 hours on 11/27, security notified SS office that he had called 911 to report a fire along HWY 177. Fire spread into the pasture to the south of the guard shack towards the lay down yard (best we could tell is that it did not make all the way to the yard) then traveled to the east about half way to the bean field. Estimate that it may have burnt 15-20 acres. Fire was deem extinguished at 0100 hours. | Level 1 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Marc Hodgson | 2019-12-12 07:16 | 2019-11-27 19:40 | 2019-11-27 19:40 | 2019-12-02 16:04 | 2019-12-11 00:30 | 2019-11-27 18:40 | 2019-12-06 21:38 |  |  | Sooner PP south of main entrance road |  |  | Brady Sowell | approved and learnings shared on 12/11 incident call. per sowell | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Marc Hodgson |  | At about 0004 hours on 11/27, John with security notified SS office that he had called 911 to report a fire along HWY 177 that at the time fire was thought to be on the west side of the HWY. He called back at 0016 hours stating that the fire was on the east side (OGE land). S.S. called Red Rock again to make sure they had been dispatched and fireman stated that they had been dispatched and were in route arrived at 0030 hours. Operators were at the gate to assist when fire department arrived. Operators opened the gate to the pasture by removing some wire. Fire spread into the pasture to the south of the guard shack towards the lay down yard (best we could tell is that it did not make all the way to the yard) then traveled to the east about half way to the bean field. Estimate that it may have burnt 15-20 acres. Fire was deem extinguished at 0100 hours. According to the fire department the fire was more than likely started by a cigarette butt or a spark from a vehicle. Battery on the backhoe was dead used jumper cables to get started. When backhoe arrived to pull out trucks fire department was able to get them unstuck using their own equipment. All trucks were unstuck and leaving property at 0235 hours. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Operations |  | Marc Hodgson | Marc Hodgson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Low | [8 empty] | 9.09 Inadequate identification and evaluation of loss exposures | [7 empty] | high winds/dry conditions and a ignition source caused fire | 40. Weather Conditions | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise)
9153 | Metro Service Center | 2019-11-27 12:00 | OGE Member was exiting I240 going North bound onto to I35 on ramp, when merging private vehicle ahead of OGE Member stopped abruptly causing OGE vehicle to hit Private vehicle | Level 2 |  | FALSE | Vehicle |  |  |  |  | OGE Energy Corp | Phillip Messer | 2020-01-06 17:01 | 2019-11-28 08:48 | 2019-11-28 08:48 | 2019-12-16 14:36 | 2019-12-11 12:00 | 2019-11-28 08:29 | 2020-01-03 10:34 |  | 2019-12-30 13:17 | I240 on ramp to I35 |  |  | William Young | Reviewed and approved. WCY 1-6-2020 | Enterprise Services |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Phillip Messer |  | Member was exiting I240 going North bound onto to I35 on ramp, when merging private vehicle ahead of OGE Member stopped member failed to merge, abruptly causing OGE vehicle to hit Private vehicle |  |  |  | Metro Service Center | FALSE |  | FALSE | Real Estate |  | Tyler Watkins | Phillip Messer |  | Vance Krebs | I am satisfied with the recommendation to attend OSU driver training. | Vance Krebs |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | failure to merge to private vehicle | 02. Failure to Warn | 1. Struck Against (Running or Bumping Into) |  | approved | [72 empty] | FALSE |  | OKC | OGE Vehicle Struck Other Vehicle | OGE Driver Failed To Yield | 2019-09-15 19:00 |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Clear
9154 | Ardmore Service Center | 2019-11-28 12:30 | Company was west bound on Sam Noble Parkway Public driver was headed south on P street and failed to stop at a red light and vehicles collided. | Level 2 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Terry Looney | 2019-12-05 14:14 | 2019-11-28 19:49 | 2019-11-28 19:48 | 2019-12-02 09:49 | 2019-12-12 12:30 | 2019-11-28 12:45 | 2019-12-05 10:42 |  | 2019-12-03 15:24 | P street & Sam Noble Parkway |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Terry Looney |  | OGE member was travelling south on Sam Noble Parkway when he approached the P Street intersection. The traffic light was green so member started crossing intersection and noticed a public driver travelling south who did not appear to be slowing down for the red light. OGE member tried to get as far left as possible to avoid the public vehicle but was not able to miss the vehicle. Public driver had ran the red light, never slowed down or attempted to miss OGE vehicle. Public vehicle struck OGE trucks right front tire/fender with their left front end. OGE vehicle came to a stop and member was okay so got out to check on public driver who's vehicle ended up in a culvert. Once public driver was out OGE member notified his supervisor of the accident. Ardmore PD investigated the accident and cited public driver for failure to obey traffic signals. Public driver was transported by ambulance and both vehicles were towed from the scene. OGE driver attempted to miss the other driver but was unsuccessful due to public driver never slowing or yielding. |  |  |  | Ardmore Service Center | FALSE |  | FALSE | Construction Services |  | Randal Callaway | Terry Looney |  | Kenneth McKinzie | I Agree with comments | Kenneth McKinzie |  | Medium |  | 2.07 Slow reaction time | [14 empty] | public driver failed to stop at red light which caused a collision with OGE vehicle | 19. Failure to React, Correct | 2. Struck By (Hit By Moving Object) |  | After completing the investigation with Mr. Looney we concluded the OGE driver was not at fault in any way. The member did all he could to avoid the collision while not endangering himself. Had he not moved over the collision could have been much worse. I commend him for his attentiveness and having sense to not "jerk" to miss the driver, possibly causing a roll over situation. cm | [72 empty] | FALSE |  | Ardmore | Public Vehicle Struck OGE | Both Vehicles Moving | 2010-08-29 19:00 |  | TRUE |  |  | Day Light | 0 | 0 | Asphalt |  | Rain | TRUE | FALSE | 8859682
9155 | Sooner Power Plant | 2019-12-03 09:30 | Contractor (FCI) was compacting ground with remote controlled roller compactor. The ground they were trying to compact was unstable and caused the equipment to roll over on its side. No injuries or damage. | Level 1 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services | Ashley Harris | 2020-01-07 13:16 | 2019-12-03 14:51 | 2019-12-03 14:51 | 2019-12-17 09:43 | 2019-12-17 09:30 | 2019-12-03 14:37 | 2019-12-19 10:22 |  |  | Sooner Power Plant- North of EER building |  |  | Marcus Huddleston | No additional comments. MLH 1-7-20 | UTS |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Ashley Harris |  | Contractor Frank Polanco was compacting backfill around the EER building. The roller got into the mud beside the trench that was being backfilled. The roller was North of the EER building when it rolled over on its left side. The roller was in remote mode. The operator did not see the muddy area since he was at a distance operating roller. There was no injuries or damage to the equipment. Immediate Corrective Action: FCI got rigging to hook to the roller and lifted roller back up right with backhoe. Investigation: Per the Operating Instructions (https://static.bidadoo.com/PDF/Bomag/Bomag%20BMP%208500%20Trench%20Compactor.pdf) If an operator is between 2 machines in both safety fields, both corresponding travel directions of the associated machines will be stopped. The operator must leave the safety field to be able to move the machine again. The minimum distance between operator and machine must be 2 m (approx. 6.5 feet). When falling short of a distance of 1.2 m (approx. 4 feet), the corresponding travel direction will be stopped. Only operators carrying the associated remote control are protected in the safety field. Any members working around the area should be notified by the operator to stay outside of this safety field and situationally aware that this equipment is in operation. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | UTS - Capital Projects |  | Richard Wood | Ashley Harris |  | Robert Weaver | agree with above assessment. | Robert Weaver |  | Low |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance | [6 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | Contractor (FCI) was compacting ground with remote controlled roller compactor. The ground they were trying to compact was unstable and caused the equipment to roll over on its side. No injuries or damage. | 18. Failure to Check, Monitor | 7. Caught Between or Under (Crushed or Amputated) | [5 empty] | Injury / Illness |  | Ashley Harris | [5 empty] | 7. Caught Between or Under (Crushed or Amputated) | Richard Wood | Wolf Point Engineers | WPE |  |  |  | Ashley Harris
9156 | Central District Office | 2019-10-23 09:00 | This is a previous first aid incident that is now requiring medical attention. Member was assisting in traffic control for heavy haulers. He was walking at an accelerated pace and turned to look back at the traffic. When he did he twisted his left knee causing minor discomfort | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Gerald Smith | 2019-12-20 10:31 | 2019-12-04 11:04 | 2019-12-04 11:04 | 2019-12-16 13:17 | 2019-11-06 09:00 | 2019-12-04 10:53 | 2019-12-18 09:00 |  | 2019-12-18 08:37 | .Park Place Substation, OKC, OK |  |  | Lindle Coleman | 12/20/19 approved, also discussed with manager 12/13/19 pushing this incident back to get more clarity on the action items. Can we separate the current action item into two items. 1. LMS review on backing specifically around proper positioning, hazard identification when backing. 2. review sprain & strain presentation and industrial athlete program. | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Gerald Smith |  | Member was assisting in traffic control for heavy haulers. He was walking at an accelerated pace and turned to look back at the traffic. When he did he twisted his left knee causing minor discomfort |  |  | TRUE | Central District Office | FALSE |  | FALSE | PD Operations Services | 9108 | Terry Collins | Gerald Smith |  | James Hutchison | I have reviewed this incident investigation and concur with the report and corrective actions. | James Hutchison |  | Medium | 1.03 Limited ability to sustain body positions |  |  | 4.06 "Meaningless" or "degrading" activities | [12 empty] | immediate stop and turn while walking | 09. Improper Placement | 11. Overstress, Overpressure, Overexertion, Ergonomic |  | The corrective actions were updated to reflect more specific information on the intended benefits of the actions assigned to this incident. Additional actions have already been addressed and are in the process of being implemented prior to this incident. The management of this group is taking steps to increase the emphasis on preventing strain and sprain type incidents. | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2005-05-23 | 1962-12-31 |  | 2019-10-23 07:00 | 0 | 0 |  | FALSE |  | Member stopped while walking and turned to stop oncoming traffic. member felt the discomfort when he turned. |  |  | Terry Collins |  | Recordable | Terry Collins | FALSE |  |  |  | Sprain/Strain |  | TRUE |  | Foreman Maintenance | Knee | Injury | Left | TRUE | Gerald Smith | TRUE | 2019 | 10/23/2019 7:00:00 AM | 4 | TRUE |  |  | turning while standing on dry paved road | acting as a "backer" for crane operator that was backing into an empty lot.
9157 | Sooner Power Plant | 2019-12-03 08:00 | While contractors were removing two control valves that had been verified dead and all piping and controls had been removed, they bumped a cut heat trace line and it arced. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | David Willis | 2020-01-22 14:08 | 2019-12-04 13:42 | 2019-12-04 13:42 | 2020-01-13 12:17 | 2019-12-17 08:00 | 2019-12-04 13:01 | 2020-01-15 15:37 |  | 2020-01-14 09:35 | Sooner 1A Bottom Ash Dewatering Bin Upper Walk Way |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | David Willis |  | In October a 3" line was being demolished in preparation for installing a new service water supply line to the de-watering bins. The old line had insulation and heat trace visible where the line had been cut and abandoned in place adjacent to #1 recirculation basin. Due to the exposed heat trace wires and cut piping the heat trace system and line was presumed to be de-energized. An operation was written on the work order to verify power source and if circuit is still in use. After tracing the power conduits and looking at the heat trace drawing E-1569A the electrician incorrectly identified the Dewatering Bin Freeze Protection panel (FP 2B). In the Freeze Protection Light Panel B, which is located in the #1 Marketable Fly Ash Tower, all power sources that fed FP-2B were lifted. Therefor, no LOTO was issued because the power supply appeared to be lifted already. After this Zachry demolished the 3" line including cutting heat trace box conduit power supplies. The only thing left in the rack were two large 3" control valves that the contractor did not feel comfortable removing with the smaller 80' manlift available at the time. On December 3rd after acquiring a 120' manlift Zachry returned to remove the two 3" control valves and while maneuvering these out of the rack the contractors bumped the heat trace power cable that had been cut in October and it sparked. Electricians were called to investigate and traced the power back to the 1A Dewatering Bin Freeze Protection panel (FP 1A) not FB 2B as was originally thought. The mis-identification of the power source was do partly to poor heat trace drawings that haven't been kept up to date. The electrical craft member that originally verified there was no power active has since retired between the time originally identified in October and the incident date in December. We can speculate that our findings are accurate to the point of the facts we know without actually interviewing the retired member. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Engineering & Planning |  | David Willis | David Willis |  | Donald Wyckoff | I have reviewed the investigation findings and deem adequate diligence has been taken to identify the root cause and develop corrective actions to eliminate future incidents. DEW 1/15/2020. | Donald Wyckoff |  | Medium | [8 empty] | 9.09 Inadequate identification and evaluation of loss exposures | 10.06 Inadequate or improper controls | [6 empty] | Mis-Identifying the power source for heat trace on old 3" Dewatering Bin circulating water supply line. | 35. Inadequate Information, Data | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell |  |  |  | Injury / Illness |  | David Willis | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | David Willis | Zachry | Vernon King |  |  |  | David Willis | [71 empty] | 9590552
9158 | River Valley | 2019-12-04 07:00 | Contractor entering the plant drove into the security gate. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Michael Smith | 2020-01-06 16:43 | 2019-12-05 12:40 | 2019-12-05 12:40 | 2019-12-19 10:07 | 2019-12-18 07:00 | 2019-12-05 12:34 | 2020-01-06 14:55 |  |  | River Valley PP Security Gate |  |  | Anthony Gillespie | There were 3 incidents of a vehicle striking our main gate arms in 2019. Very good opportunity to coordinate with facilities to determine if a more visible option is appropriate. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Michael Smith |  | Employee was entering the plant by way of the main guard gate. He exited the vehicle to have his badge scanned. Upon returning to the vehicle he drove forward striking the gate arm causing damage. |  |  |  | River Valley | FALSE |  | FALSE | Other |  | Larry Hammons | Michael Smith |  | Timothy Chancellor | Agreed. While it would seem obvious that you must wait for gate to lift to proceed, this gate has been hit multiple times. At other plants, a stop light was added to indicate that the gate was open or closed as a secondary check as well. | Timothy Chancellor |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Employee was entering the plant by way of the main guard gate. He exited the vehicle to have his badge scanned. Upon returning to the vehicle he drove forward striking the gate arm causing damage. | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Michael Smith | Bent exit gate |  |  |  |  | 1. Struck Against (Running or Bumping Into) | Larry Hammons | Zachary | Aaron Hall |  | Fixed Equipment |  | Michael Smith |  |  |  |  | FALSE
9159 | Sooner Power Plant | 2019-12-05 15:30 | Brock employees were dismantling a scaffold on the lower concrete level of the transfer tower. A piece of #9 wire fell out of an open window and went approximately 150’ hitting the roof of a deluge house below then bouncing over and landing in close proximity to an OG&E crew that was working on the ground. No members were injured and no property was damaged. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Lance Lantz | 2020-01-09 07:06 | 2019-12-05 17:04 | 2019-12-05 17:04 | 2019-12-17 11:29 | 2019-12-19 15:30 | 2019-12-05 16:50 | 2019-12-20 08:05 |  |  | Sooner Power Plant Transfer Tower |  |  | Brady Sowell | approved by Brady Sowell. Waiting to be placed on the call or the hotsheet. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Lance Lantz |  | It was found during the investigation into the incident. The Brock crew had completed the dismantling of the work deck and was in the process of passing material up the stairs to the upper concrete level. This was so the material could be loaded into a rack then lowered down with the crane. One Brock member had grabbed the orange barricade netting, a small 2”x4” board, and some wire that had been removed and was laying on the floor. As the member started up the up the stairs and got just past the window he felt a tug against his hand. The member stopped and looked, but did not see anything drop or hear anything drop. The member continued up the stairs with the materials in hand. At the same time the Brock crew was dismantling the scaffold an OG&E crew was cleaning up after a job on the ground at the base of the transfer tower. One OG&E member was standing next to a pick-up about 20’ away from the deluge house at the base of the transfer tower. He heard something hit the roof of the deluge house and as he looked up seen a piece of #9 wire come off the roof and land approximately 10’ away from where he was standing. It is believed that when the Brock employee was going up the stairs with the materials in hand. The wire had fell out of his hand and deflected out the window that is located next to the stairs and fell to the ground landing in close proximity to the OG&E crew working below. No one was injured in this event and no equipment was damaged. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Kevin Ferguson | Lance Lantz |  | Frank Brixey | Approved - Keith Brixey 12/20/2019 | Frank Brixey |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [7 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | material not secured properly before transporting. | 08. Improper Loading | 2. Struck By (Hit By Moving Object) | [5 empty] | Injury / Illness |  | Lance Lantz | [5 empty] | 2. Struck By (Hit By Moving Object) | Kevin Ferguson | Brock | Alfredo Solis |  |  |  | Lance Lantz
9160 | Seminole PP; EGX Gath/Trans | 2019-12-06 06:30 | Failure of boiler skin on header vestibule resulting in flue gas exposure. Lagging was damaged as well. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Leslie Henderson | 2020-02-24 13:44 | 2019-12-06 14:27 | 2019-12-06 14:26 | 2020-02-10 16:47 | 2019-12-20 06:30 | 2019-12-06 14:20 | 2020-02-11 09:29 |  | 2020-02-10 17:11 | Unit #1 sw corner of boiler 4 1/2 landing |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Leslie Henderson |  | Background information: The refractory is possibly original install. There was no information to suggest otherwise. The LowNOX project conducted in 2016 changed the way the boiler operates. The fire in the boiler is located approximately one level higher inside the boiler. The blow out occurred ½ level above where the new overfire airports were installed due to the LowNOX project. The unit has increased in the number of starts and stops since the LowNOX project. There have been 68 starts and stops, which may be contributing to refractory degradation from expansion/contraction and vibration. The last official thermography report was completed on Unit 1 on 04/27/2018. However, thermography was conducted again on 08/06/2019 and the SW corner of the 4.5 level did not show any changes from the official report conducted on 04/27/2018. There is not currently a documented process on how to conduct thermographic testing; however, the Reliability group is currently working on a documented process. The last boiler inspection was conducted from 11/26/2018 to 11/30/2018. The boiler inspection report was sent 12/11/2018 and did not show any major issues. However, the area in question was not specifically checked as there is no way to check the area without cutting into the area. Incident: On 12/06/2019 at 6:30 am, Operations noted hole in the boiler. Area was barricaded (above and below) hole opening. The unit remained online until 12/11/2019. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | Operations |  | Arthur Deatherage | Leslie Henderson |  | Paul Schoelen | Review complete | Paul Schoelen |  | Medium | [9 empty] | 10.03 Inadequate standards, specifications and/or design criteria | [6 empty] | Firing boiler to place unit on line blew hole in side of boiler | 30. Temperature Extremes | 12. Equipment Failure |  | Please see workflow comments for reasons being returned. Leslie, get with me and I will explain in person why these are being sent back. Chrysty UPDATED: Approved. | [66 empty] | Failure of boiler skin on header vestibule resulting in flue gas exposure. Lagging was damaged as well. | 15000 | Terry Bunch | Structural
9160 | Seminole PP; EGX Gath/Trans | 2019-12-06 06:30 | Failure of boiler skin on header vestibule resulting in flue gas exposure. Lagging was damaged as well. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Leslie Henderson | 2020-02-24 13:44 | 2019-12-06 14:27 | 2019-12-06 14:26 | 2020-02-10 16:47 | 2019-12-20 06:30 | 2019-12-06 14:20 | 2020-02-11 09:29 |  | 2020-02-10 17:11 | Unit #1 sw corner of boiler 4 1/2 landing |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Leslie Henderson |  | Background information: The refractory is possibly original install. There was no information to suggest otherwise. The LowNOX project conducted in 2016 changed the way the boiler operates. The fire in the boiler is located approximately one level higher inside the boiler. The blow out occurred ½ level above where the new overfire airports were installed due to the LowNOX project. The unit has increased in the number of starts and stops since the LowNOX project. There have been 68 starts and stops, which may be contributing to refractory degradation from expansion/contraction and vibration. The last official thermography report was completed on Unit 1 on 04/27/2018. However, thermography was conducted again on 08/06/2019 and the SW corner of the 4.5 level did not show any changes from the official report conducted on 04/27/2018. There is not currently a documented process on how to conduct thermographic testing; however, the Reliability group is currently working on a documented process. The last boiler inspection was conducted from 11/26/2018 to 11/30/2018. The boiler inspection report was sent 12/11/2018 and did not show any major issues. However, the area in question was not specifically checked as there is no way to check the area without cutting into the area. Incident: On 12/06/2019 at 6:30 am, Operations noted hole in the boiler. Area was barricaded (above and below) hole opening. The unit remained online until 12/11/2019. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | Operations |  | Arthur Deatherage | Leslie Henderson |  | Paul Schoelen | Review complete | Paul Schoelen |  | Medium | [9 empty] | 10.08 Inadequate evaluation of changes | [6 empty] | Firing boiler to place unit on line blew hole in side of boiler | 30. Temperature Extremes | 12. Equipment Failure |  | Please see workflow comments for reasons being returned. Leslie, get with me and I will explain in person why these are being sent back. Chrysty UPDATED: Approved. | [66 empty] | Failure of boiler skin on header vestibule resulting in flue gas exposure. Lagging was damaged as well. | 15000 | Terry Bunch | Structural
9160 | Seminole PP; EGX Gath/Trans | 2019-12-06 06:30 | Failure of boiler skin on header vestibule resulting in flue gas exposure. Lagging was damaged as well. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Leslie Henderson | 2020-02-24 13:44 | 2019-12-06 14:27 | 2019-12-06 14:26 | 2020-02-10 16:47 | 2019-12-20 06:30 | 2019-12-06 14:20 | 2020-02-11 09:29 |  | 2020-02-10 17:11 | Unit #1 sw corner of boiler 4 1/2 landing |  |  | Jesse Murray | Approved, Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Leslie Henderson |  | Background information: The refractory is possibly original install. There was no information to suggest otherwise. The LowNOX project conducted in 2016 changed the way the boiler operates. The fire in the boiler is located approximately one level higher inside the boiler. The blow out occurred ½ level above where the new overfire airports were installed due to the LowNOX project. The unit has increased in the number of starts and stops since the LowNOX project. There have been 68 starts and stops, which may be contributing to refractory degradation from expansion/contraction and vibration. The last official thermography report was completed on Unit 1 on 04/27/2018. However, thermography was conducted again on 08/06/2019 and the SW corner of the 4.5 level did not show any changes from the official report conducted on 04/27/2018. There is not currently a documented process on how to conduct thermographic testing; however, the Reliability group is currently working on a documented process. The last boiler inspection was conducted from 11/26/2018 to 11/30/2018. The boiler inspection report was sent 12/11/2018 and did not show any major issues. However, the area in question was not specifically checked as there is no way to check the area without cutting into the area. Incident: On 12/06/2019 at 6:30 am, Operations noted hole in the boiler. Area was barricaded (above and below) hole opening. The unit remained online until 12/11/2019. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | Operations |  | Arthur Deatherage | Leslie Henderson |  | Paul Schoelen | Review complete | Paul Schoelen |  | Medium | [9 empty] | 10.08 Inadequate evaluation of changes |  |  |  |  | 15.03 Inadequate inspection and/or monitoring |  | Hole one boiler 4 1/2 level SW corner of Unit #1 | 18. Failure to Check, Monitor | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Please see workflow comments for reasons being returned. Leslie, get with me and I will explain in person why these are being sent back. Chrysty UPDATED: Approved. | [66 empty] | Failure of boiler skin on header vestibule resulting in flue gas exposure. Lagging was damaged as well. | 15000 | Terry Bunch | Structural
9161 | Metro Service Center | 2019-12-06 08:30 | While driving down interstate a red tailed hawk flew into the front of company vehicle. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Gary Lassley | 2019-12-11 07:32 | 2019-12-09 08:02 | 2019-12-09 08:02 | 2019-12-09 08:06 | 2019-12-20 08:30 | 2019-12-09 07:57 |  |  |  | West Bound I-40, Exit 185 |  |  | Terry Hackett | Reviewed/Approved TMH. Watched Dash Cam video that showed bird flying into vehicle, impact was unavoidable, and ticket has been submitted to fleet. | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | [6 empty] | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Gary Lassley | Gary Lassley |  |  |  | Robert Gottshall |  | Low | [93 empty] | FALSE |  | Shawnee | Animal-related |  | 1983-01-30 18:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
9162 | Sooner Power Plant | 2019-12-06 09:30 | Looked at a job east of water treatment. Grabbed a red nylon rope used for barricade. Rope twisted in hand and left nylon fiber splinters in hand. | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Supply | Tony Mena | 2019-12-19 11:41 | 2019-12-10 09:41 | 2019-12-10 09:41 | 2019-12-10 09:48 | 2019-12-20 09:30 | 2019-12-10 09:33 |  |  |  | East of Water Treatment |  |  | Brady Sowell | approved | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | [5 empty] | FALSE | Sooner Power Plant | FALSE |  | FALSE | Engineering & Planning |  | Tony Mena | Jerry Bocox |  |  |  | Donald Wyckoff |  | Low | [45 empty] | FALSE |  |  | 1983-07-18 | 1959-09-06 |  | 2019-12-06 06:30 | 0 | 0 | Alcohol swab, splinter removal removal kit, tweezers | FALSE |  | Nylon rope twisted in bare hands. |  | TRUE | Tony Mena |  | First Aid | Tony Mena |  |  |  |  | Foreign Body |  | FALSE |  | Sr Crew Planner | Hand |  | Left |  | Jerry Bocox |  |  | 12/6/2019 6:30:00 AM | 36 | FALSE |  |  | nylon rope | Looking at job.
9163 | Muskogee Power Plant | 2019-12-09 14:00 | Member was inspecting equipment and rolled ankle on uneven door threshold. | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Supply | Carol Rollins | 2020-01-22 09:23 | 2019-12-10 12:30 | 2019-12-10 12:30 | 2020-01-16 14:58 | 2019-12-23 14:00 | 2019-12-09 14:30 | 2020-01-17 15:15 |  |  | Machine shop south overhead door |  |  | Robert Wright | The pictures of the thresh hold have been added approved Bob Wright | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Jeffrey Mackey |  | Member rolled left ankle as he was inspecting parts on the machine shop floor. Member stepped around a pallet while doing his inspection. As he stepped around the pallet his left foot came in contact with an uneven over head door thresh hold causing him to roll his left ankle Findings: the member was not in a rush or felt hurried in any way. Member revealed that he had had ankle problems since his high school days. The lighting in the area was adequate for this task The concentration of the member was focused on completing his task. His focus was not on the thresh hold. In this case it was a lack of awareness combined with focus on the task at hand On Monday December 9th at 200pm at Muskogee Power Plant MK Planner, was inspecting equipment in the machine shop and rolled ankle on uneven door threshold (South roll up door). He immediately reported to his supervisor and they huddled up with the safety coordinator. Member stated he's had ankle problems for 12 plus years and that this has happened before. He refused any medical treatment but wanted the first aid reported. *note* Tuesday December 10th. All supervisors are at Norman for Annual Management Meeting. Tuesday December 10th 7:00am the safety coordinator calls member to follow up on how he's doing from first aid occurring the afternoon prior. Injured member states he is staying home and had made his own appointment for 1000am at Med Now; without notifying supervision or safety. The Safety coordinator asked him why, Member states he's still in pain and wanted to confirm his ankle was not broken by completing an x ray. The safety coordinator says we do not need an appointment and told injured member to go to Med Now and he would meet him there. The safety coordinator notifies MK leadership and power supply safety manager that the injured member is requesting treatment and safety coordinator and injured member met at Med Now MK (approved clinic) for Medical Evaluation. Safety coordinator and injured member go to Med Now together. During the Clinic Visit member was wearing a Ridged Boot he had acquired in years past from previous injury. He stated he was wearing it because it helped with mobility due to pain he was feeling. member is evaluated at Med Now. At the end of evaluation Doctor says that boot looks pretty ragged do you want another one, member says yes. Member was giving full release paperwork and no treatment. Follow up requested for 12/16/19. Med Now sends OGE paperwork with full details. In details it states that patient was prescribed a ridged boot and crutches. -----Making this recordable. Weds December 11th MK Leadership and Murray debrief. We decided that injured member should get an opinion from Doctor Estep. Friday Dec 13th the injured member traveled to OKC to be evaluated by Doctor Estep. Estep reviews member's history and does a full evaluation. Doctor Estep reports out the he's released to full duty and with no restrictions. He also noted -- that in his medical opinion he would not have prescribed the Ridged Boot or the Crutches. He provided these details to Moser for the Recordability Decision. Member is at work now, a little sore but getting around, and preforming he job as required. |  |  | FALSE | Muskogee Power Plant | FALSE |  | FALSE | Engineering & Planning |  | Rowdy Lindsey | Jeffrey Mackey |  | Jonathan Stogsdill | ………. | Jonathan Stogsdill |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Member sprained left ankle from stepping on an uneven surface | 11. Improper Position for Task | 9. Abnormal Operation | [26 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2015-04-06 | 1979-12-15 |  | 2019-12-09 07:00 | 0 | 0 | The member was prescribed a rigid ankle support or boot and crutches | FALSE |  | Member walked around pallet of parts sitting in the floor and stepped on an uneven overhead door thresh hold causing him to roll his left ankle |  | TRUE | Rowdy Lindsey |  | Recordable | Rowdy Lindsey | FALSE |  | Med Now in Muskogee | Holsopple | Sprain/Strain |  | TRUE |  | System Planner | Ankle | Injury | Left | TRUE | Jeffrey Mackey | TRUE | 2019 | 12/9/2019 7:00:00 AM | 4 months | TRUE | FALSE | FALSE | The weight of his body and the uneven thresh hold | He was inspecting equipment in the machine shop
9164 | North Service Center | 2019-12-09 18:30 | Member was removing pitman arm with a hammer, on F10-232, and stuck the left hand on the pinky finger. First aid was applied and member reported incident. No prelesional medical attention needed. | Level 1 |  | FALSE | Member Injury |  |  |  |  | OG&E Corp Services | Jamie Clark | 2019-12-12 08:02 | 2019-12-11 09:44 | 2019-12-11 09:44 | 2019-12-11 11:16 | 2019-12-23 18:30 | 2019-12-11 09:36 |  |  |  | North end of shop on work bench between the first and second bay |  |  | Cody Vinyard | approved | UTS |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | [5 empty] | FALSE | North Service Center | FALSE |  | FALSE | UTS - Fleet Services |  |  | Jamie Clark |  |  |  | Nathan Gooch |  | Low | [45 empty] | FALSE |  |  | 2019-03-18 | 1979-06-19 |  | 2019-12-09 13:00 | 0 | 0 | Put Band aid on finger | FALSE |  | Member was striking the pitman arm with hammer and hit pinky finger. |  | TRUE | Carlo Dixon |  | First Aid | Carlo Dixon |  |  |  |  | Contusion |  | FALSE |  | Sr Mechanic Fleet Srvcs | Finger |  | Left |  | Jamie Clark |  |  | 12/9/2019 1:00:00 PM |  | FALSE |  |  | Hammer | Removed steering gear box from F10-232.
9165 | Muskogee Power Plant | 2019-12-13 16:00 | While installing new potable water line piping for eyewash stations contractor was cutting new piping from man lift for installation. Contractor was using tubing cutter and when tubing was cut the contractor lost control of the cut end (approximately 14" piece of tubing) and it fell from the single pod man lift striking a pvc valve below causing it to break and leak. Contractors had to use the one man pod lift for restricted area work and barricades and spotters were being used on the ground. Leak was immediately reported and operations confirmed source was demin water. Tank was drained overnight and repairs made the next shift. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2020-02-05 12:16 | 2019-12-14 08:24 | 2019-12-14 08:24 | 2020-01-09 07:37 | 2019-12-27 16:00 | 2019-12-13 16:00 | 2020-01-21 08:04 |  | 2020-01-14 10:01 | Muskogee PP Demin building |  |  | Jesse Murray | Approved. Jesse Murray. | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Zachary contractors were installing new copper potable water line piping for eyewash stations. Contractor was elevated in a single pod manlift, using a tubing cutter to cut tubing to length when tubing the contractor lost control of the cut end (approximately 14" piece of tubing) and it slipped from his hand striking a pvc valve below causing it to break and leak. Contractors had to use the one man pod lift for restricted area work and barricades and spotters were being used on the ground. Leak was immediately reported and operations confirmed source was demin water. Tank was drained overnight and repairs made the next shift. Investigation findings: 1) Demin building was congested and limited areas to work at elevation to install piping. Lift was positioned directly under work, where contractor was not reaching or stretched out when doing work. 2) Member was using lanyard on tools, discussed opportunity to lanyard tail piece. Discussion identified potential of greater hazards. ( securing, weight, control when piece came loose). 3) Barricades and spotters were being used while elevated. 4) Contractors SWP identified lanyards and dropped object prevention and use of spotters. Zachary's SWP identified the use of netting, buckets and plywood to eliminate dropped objects but discussion or use of these potentially would not have affected dropped object but could have eliminated the broken valve. We are in discussion with plant chemist about use of PVC if other more durable material could be used to prevent broken components / piping. 5) Post incident reporting and hazard identification through multiple members worked well. Zachary and OGE have taken this incident to use at all OGE sites where the same project is ongoing. ( HL, Tinker, McClain, Sooner, and MK) to identify steps taken and hazards identified that could be easier to break, crack or cause potential for leaks. Zachary leadership was going to present this incident investigation to their leadership as a discussion point and risk identification at their next leadership meeting. 6) Gloves worn? Yes, wet? slippery? No Member did not feel that the wrong gloves were worn for the task. They were not bulky or welding type common leather work gloves. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | Special Services |  | Randy Ellis | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Medium |  | 2.07 Slow reaction time | [14 empty] | pipe slipped from grasp | 03. Failure to Secure | 3. Fall from Elevation to Lower Level |  | See workflow comments for reason being returned. |  |  |  | Environmental |  | Kelly Casey | broken pvc valve / piping |  |  |  |  | 3. Fall from Elevation to Lower Level | Randy Ellis | Zachary | William Ramsey |  | Fixed Equipment |  | Randy Ellis |  |  |  |  | FALSE | [66 empty] | 9592018
9165 | Muskogee Power Plant | 2019-12-13 16:00 | While installing new potable water line piping for eyewash stations contractor was cutting new piping from man lift for installation. Contractor was using tubing cutter and when tubing was cut the contractor lost control of the cut end (approximately 14" piece of tubing) and it fell from the single pod man lift striking a pvc valve below causing it to break and leak. Contractors had to use the one man pod lift for restricted area work and barricades and spotters were being used on the ground. Leak was immediately reported and operations confirmed source was demin water. Tank was drained overnight and repairs made the next shift. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2020-02-05 12:16 | 2019-12-14 08:24 | 2019-12-14 08:24 | 2020-01-09 07:37 | 2019-12-27 16:00 | 2019-12-13 16:00 | 2020-01-21 08:04 |  | 2020-01-14 10:01 | Muskogee PP Demin building |  |  | Jesse Murray | Approved. Jesse Murray. | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Zachary contractors were installing new copper potable water line piping for eyewash stations. Contractor was elevated in a single pod manlift, using a tubing cutter to cut tubing to length when tubing the contractor lost control of the cut end (approximately 14" piece of tubing) and it slipped from his hand striking a pvc valve below causing it to break and leak. Contractors had to use the one man pod lift for restricted area work and barricades and spotters were being used on the ground. Leak was immediately reported and operations confirmed source was demin water. Tank was drained overnight and repairs made the next shift. Investigation findings: 1) Demin building was congested and limited areas to work at elevation to install piping. Lift was positioned directly under work, where contractor was not reaching or stretched out when doing work. 2) Member was using lanyard on tools, discussed opportunity to lanyard tail piece. Discussion identified potential of greater hazards. ( securing, weight, control when piece came loose). 3) Barricades and spotters were being used while elevated. 4) Contractors SWP identified lanyards and dropped object prevention and use of spotters. Zachary's SWP identified the use of netting, buckets and plywood to eliminate dropped objects but discussion or use of these potentially would not have affected dropped object but could have eliminated the broken valve. We are in discussion with plant chemist about use of PVC if other more durable material could be used to prevent broken components / piping. 5) Post incident reporting and hazard identification through multiple members worked well. Zachary and OGE have taken this incident to use at all OGE sites where the same project is ongoing. ( HL, Tinker, McClain, Sooner, and MK) to identify steps taken and hazards identified that could be easier to break, crack or cause potential for leaks. Zachary leadership was going to present this incident investigation to their leadership as a discussion point and risk identification at their next leadership meeting. 6) Gloves worn? Yes, wet? slippery? No Member did not feel that the wrong gloves were worn for the task. They were not bulky or welding type common leather work gloves. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | Special Services |  | Randy Ellis | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Medium |  | 2.07 Slow reaction time | [14 empty] | pipe slipped from grasp | 03. Failure to Secure | 3. Fall from Elevation to Lower Level |  | See workflow comments for reason being returned. |  |  |  | Property Damage |  | Kelly Casey | broken pvc valve / piping |  |  |  |  | 3. Fall from Elevation to Lower Level | Randy Ellis | Zachary | William Ramsey |  | Fixed Equipment |  | Randy Ellis |  |  |  |  | FALSE | [66 empty] | 9592018
9165 | Muskogee Power Plant | 2019-12-13 16:00 | While installing new potable water line piping for eyewash stations contractor was cutting new piping from man lift for installation. Contractor was using tubing cutter and when tubing was cut the contractor lost control of the cut end (approximately 14" piece of tubing) and it fell from the single pod man lift striking a pvc valve below causing it to break and leak. Contractors had to use the one man pod lift for restricted area work and barricades and spotters were being used on the ground. Leak was immediately reported and operations confirmed source was demin water. Tank was drained overnight and repairs made the next shift. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2020-02-05 12:16 | 2019-12-14 08:24 | 2019-12-14 08:24 | 2020-01-09 07:37 | 2019-12-27 16:00 | 2019-12-13 16:00 | 2020-01-21 08:04 |  | 2020-01-14 10:01 | Muskogee PP Demin building |  |  | Jesse Murray | Approved. Jesse Murray. | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Zachary contractors were installing new copper potable water line piping for eyewash stations. Contractor was elevated in a single pod manlift, using a tubing cutter to cut tubing to length when tubing the contractor lost control of the cut end (approximately 14" piece of tubing) and it slipped from his hand striking a pvc valve below causing it to break and leak. Contractors had to use the one man pod lift for restricted area work and barricades and spotters were being used on the ground. Leak was immediately reported and operations confirmed source was demin water. Tank was drained overnight and repairs made the next shift. Investigation findings: 1) Demin building was congested and limited areas to work at elevation to install piping. Lift was positioned directly under work, where contractor was not reaching or stretched out when doing work. 2) Member was using lanyard on tools, discussed opportunity to lanyard tail piece. Discussion identified potential of greater hazards. ( securing, weight, control when piece came loose). 3) Barricades and spotters were being used while elevated. 4) Contractors SWP identified lanyards and dropped object prevention and use of spotters. Zachary's SWP identified the use of netting, buckets and plywood to eliminate dropped objects but discussion or use of these potentially would not have affected dropped object but could have eliminated the broken valve. We are in discussion with plant chemist about use of PVC if other more durable material could be used to prevent broken components / piping. 5) Post incident reporting and hazard identification through multiple members worked well. Zachary and OGE have taken this incident to use at all OGE sites where the same project is ongoing. ( HL, Tinker, McClain, Sooner, and MK) to identify steps taken and hazards identified that could be easier to break, crack or cause potential for leaks. Zachary leadership was going to present this incident investigation to their leadership as a discussion point and risk identification at their next leadership meeting. 6) Gloves worn? Yes, wet? slippery? No Member did not feel that the wrong gloves were worn for the task. They were not bulky or welding type common leather work gloves. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | Special Services |  | Randy Ellis | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Medium |  | 2.06 Poor coordination | [14 empty] | pipe slipped from grasp | 03. Failure to Secure | 3. Fall from Elevation to Lower Level |  | See workflow comments for reason being returned. |  |  |  | Environmental |  | Kelly Casey | broken pvc valve / piping |  |  |  |  | 3. Fall from Elevation to Lower Level | Randy Ellis | Zachary | William Ramsey |  | Fixed Equipment |  | Randy Ellis |  |  |  |  | FALSE | [66 empty] | 9592018
9165 | Muskogee Power Plant | 2019-12-13 16:00 | While installing new potable water line piping for eyewash stations contractor was cutting new piping from man lift for installation. Contractor was using tubing cutter and when tubing was cut the contractor lost control of the cut end (approximately 14" piece of tubing) and it fell from the single pod man lift striking a pvc valve below causing it to break and leak. Contractors had to use the one man pod lift for restricted area work and barricades and spotters were being used on the ground. Leak was immediately reported and operations confirmed source was demin water. Tank was drained overnight and repairs made the next shift. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2020-02-05 12:16 | 2019-12-14 08:24 | 2019-12-14 08:24 | 2020-01-09 07:37 | 2019-12-27 16:00 | 2019-12-13 16:00 | 2020-01-21 08:04 |  | 2020-01-14 10:01 | Muskogee PP Demin building |  |  | Jesse Murray | Approved. Jesse Murray. | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Zachary contractors were installing new copper potable water line piping for eyewash stations. Contractor was elevated in a single pod manlift, using a tubing cutter to cut tubing to length when tubing the contractor lost control of the cut end (approximately 14" piece of tubing) and it slipped from his hand striking a pvc valve below causing it to break and leak. Contractors had to use the one man pod lift for restricted area work and barricades and spotters were being used on the ground. Leak was immediately reported and operations confirmed source was demin water. Tank was drained overnight and repairs made the next shift. Investigation findings: 1) Demin building was congested and limited areas to work at elevation to install piping. Lift was positioned directly under work, where contractor was not reaching or stretched out when doing work. 2) Member was using lanyard on tools, discussed opportunity to lanyard tail piece. Discussion identified potential of greater hazards. ( securing, weight, control when piece came loose). 3) Barricades and spotters were being used while elevated. 4) Contractors SWP identified lanyards and dropped object prevention and use of spotters. Zachary's SWP identified the use of netting, buckets and plywood to eliminate dropped objects but discussion or use of these potentially would not have affected dropped object but could have eliminated the broken valve. We are in discussion with plant chemist about use of PVC if other more durable material could be used to prevent broken components / piping. 5) Post incident reporting and hazard identification through multiple members worked well. Zachary and OGE have taken this incident to use at all OGE sites where the same project is ongoing. ( HL, Tinker, McClain, Sooner, and MK) to identify steps taken and hazards identified that could be easier to break, crack or cause potential for leaks. Zachary leadership was going to present this incident investigation to their leadership as a discussion point and risk identification at their next leadership meeting. 6) Gloves worn? Yes, wet? slippery? No Member did not feel that the wrong gloves were worn for the task. They were not bulky or welding type common leather work gloves. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | Special Services |  | Randy Ellis | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Medium |  | 2.06 Poor coordination | [14 empty] | pipe slipped from grasp | 03. Failure to Secure | 3. Fall from Elevation to Lower Level |  | See workflow comments for reason being returned. |  |  |  | Property Damage |  | Kelly Casey | broken pvc valve / piping |  |  |  |  | 3. Fall from Elevation to Lower Level | Randy Ellis | Zachary | William Ramsey |  | Fixed Equipment |  | Randy Ellis |  |  |  |  | FALSE | [66 empty] | 9592018
9166 | Horseshoe Lake Power Plant | 2019-12-15 03:00 | Performing unit rounds a wood fire smell was evident on TR floor. FPO and operator investigated around #8 which was on for testing. An incipient fire was detected under the 8 Turbine. 2x10 scaffolding boards and insulation blankets were smoldering and flaming up when air when fan the embers. | Level 3 |  | FALSE | System Operational Incident | Donnie Jones | Jesse Murray | Assigning per Doupe and Murray. | 2019-12-18 10:35 | Power Supply | Peter Nowakowski |  | 2019-12-15 18:17 | 2019-12-15 18:17 |  | 2019-12-29 03:00 | 2019-12-15 04:30 |  |  |  | Horseshoe Lake PP mezzanine level, under HP/IP section of turbine. |  |  |  |  | Power Supply |  | Level 3 | System Operational Incident |  | FALSE | FALSE | TRUE |  | TRUE | FALSE |  |  |  | Jeffrey Guinn | Daniel Perry |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Operations |  | Peter Nowakowski | Michael Kennedy |  |  |  | Daniel Perry |  | High | [87 empty] | Multiple burnt treated 2x10 scaffolding boards and multiple insulation blankets around steam piping. | 2000 | Peter Nowakowski | Fire | Terry Patterson | [19 empty] | 9581777
9166 | Horseshoe Lake Power Plant | 2019-12-15 03:00 | Performing unit rounds a wood fire smell was evident on TR floor. FPO and operator investigated around #8 which was on for testing. An incipient fire was detected under the 8 Turbine. 2x10 scaffolding boards and insulation blankets were smoldering and flaming up when air when fan the embers. | Level 3 |  | FALSE | System Operational Incident | Donnie Jones | Jesse Murray | Assigning per Doupe and Murray. | 2019-12-18 10:35 | Power Supply | Peter Nowakowski |  | 2019-12-15 18:17 | 2019-12-15 18:17 |  | 2019-12-29 03:00 | 2019-12-15 04:30 |  |  |  | Horseshoe Lake PP mezzanine level, under HP/IP section of turbine. |  |  |  |  | Power Supply |  | Level 3 | System Operational Incident |  | FALSE | FALSE | TRUE |  | TRUE | FALSE |  |  |  | Jeffrey Guinn | Daniel Perry |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Operations |  | Peter Nowakowski | Michael Kennedy |  |  |  | Daniel Perry |  | High | [87 empty] | Multiple burnt treated 2x10 scaffolding boards and multiple insulation blankets around steam piping. | 2000 | Peter Nowakowski | Fire | Johnny Jonas | [19 empty] | 9581777
9166 | Horseshoe Lake Power Plant | 2019-12-15 03:00 | Performing unit rounds a wood fire smell was evident on TR floor. FPO and operator investigated around #8 which was on for testing. An incipient fire was detected under the 8 Turbine. 2x10 scaffolding boards and insulation blankets were smoldering and flaming up when air when fan the embers. | Level 3 |  | FALSE | System Operational Incident | Donnie Jones | Jesse Murray | Assigning per Doupe and Murray. | 2019-12-18 10:35 | Power Supply | Peter Nowakowski |  | 2019-12-15 18:17 | 2019-12-15 18:17 |  | 2019-12-29 03:00 | 2019-12-15 04:30 |  |  |  | Horseshoe Lake PP mezzanine level, under HP/IP section of turbine. |  |  |  |  | Power Supply |  | Level 3 | System Operational Incident |  | FALSE | FALSE | TRUE |  | TRUE | FALSE |  |  |  | Benjamin Dickinson | Daniel Perry |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Operations |  | Peter Nowakowski | Michael Kennedy |  |  |  | Daniel Perry |  | High | [87 empty] | Multiple burnt treated 2x10 scaffolding boards and multiple insulation blankets around steam piping. | 2000 | Peter Nowakowski | Fire | Terry Patterson | [19 empty] | 9581777
9166 | Horseshoe Lake Power Plant | 2019-12-15 03:00 | Performing unit rounds a wood fire smell was evident on TR floor. FPO and operator investigated around #8 which was on for testing. An incipient fire was detected under the 8 Turbine. 2x10 scaffolding boards and insulation blankets were smoldering and flaming up when air when fan the embers. | Level 3 |  | FALSE | System Operational Incident | Donnie Jones | Jesse Murray | Assigning per Doupe and Murray. | 2019-12-18 10:35 | Power Supply | Peter Nowakowski |  | 2019-12-15 18:17 | 2019-12-15 18:17 |  | 2019-12-29 03:00 | 2019-12-15 04:30 |  |  |  | Horseshoe Lake PP mezzanine level, under HP/IP section of turbine. |  |  |  |  | Power Supply |  | Level 3 | System Operational Incident |  | FALSE | FALSE | TRUE |  | TRUE | FALSE |  |  |  | Benjamin Dickinson | Daniel Perry |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Operations |  | Peter Nowakowski | Michael Kennedy |  |  |  | Daniel Perry |  | High | [87 empty] | Multiple burnt treated 2x10 scaffolding boards and multiple insulation blankets around steam piping. | 2000 | Peter Nowakowski | Fire | Johnny Jonas | [19 empty] | 9581777
9166 | Horseshoe Lake Power Plant | 2019-12-15 03:00 | Performing unit rounds a wood fire smell was evident on TR floor. FPO and operator investigated around #8 which was on for testing. An incipient fire was detected under the 8 Turbine. 2x10 scaffolding boards and insulation blankets were smoldering and flaming up when air when fan the embers. | Level 3 |  | FALSE | Property Damage | Donnie Jones | Jesse Murray | Assigning per Doupe and Murray. | 2019-12-18 10:35 | Power Supply | Peter Nowakowski |  | 2019-12-15 18:17 | 2019-12-15 18:17 |  | 2019-12-29 03:00 | 2019-12-15 04:30 |  |  |  | Horseshoe Lake PP mezzanine level, under HP/IP section of turbine. |  |  |  |  | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | TRUE | FALSE |  |  |  | Jeffrey Guinn | Daniel Perry |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Operations |  | Peter Nowakowski | Michael Kennedy |  |  |  | Daniel Perry |  | High | [87 empty] | Multiple burnt treated 2x10 scaffolding boards and multiple insulation blankets around steam piping. | 2000 | Peter Nowakowski | Fire | Terry Patterson | [19 empty] | 9581777
9166 | Horseshoe Lake Power Plant | 2019-12-15 03:00 | Performing unit rounds a wood fire smell was evident on TR floor. FPO and operator investigated around #8 which was on for testing. An incipient fire was detected under the 8 Turbine. 2x10 scaffolding boards and insulation blankets were smoldering and flaming up when air when fan the embers. | Level 3 |  | FALSE | Property Damage | Donnie Jones | Jesse Murray | Assigning per Doupe and Murray. | 2019-12-18 10:35 | Power Supply | Peter Nowakowski |  | 2019-12-15 18:17 | 2019-12-15 18:17 |  | 2019-12-29 03:00 | 2019-12-15 04:30 |  |  |  | Horseshoe Lake PP mezzanine level, under HP/IP section of turbine. |  |  |  |  | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | TRUE | FALSE |  |  |  | Jeffrey Guinn | Daniel Perry |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Operations |  | Peter Nowakowski | Michael Kennedy |  |  |  | Daniel Perry |  | High | [87 empty] | Multiple burnt treated 2x10 scaffolding boards and multiple insulation blankets around steam piping. | 2000 | Peter Nowakowski | Fire | Johnny Jonas | [19 empty] | 9581777
9166 | Horseshoe Lake Power Plant | 2019-12-15 03:00 | Performing unit rounds a wood fire smell was evident on TR floor. FPO and operator investigated around #8 which was on for testing. An incipient fire was detected under the 8 Turbine. 2x10 scaffolding boards and insulation blankets were smoldering and flaming up when air when fan the embers. | Level 3 |  | FALSE | Property Damage | Donnie Jones | Jesse Murray | Assigning per Doupe and Murray. | 2019-12-18 10:35 | Power Supply | Peter Nowakowski |  | 2019-12-15 18:17 | 2019-12-15 18:17 |  | 2019-12-29 03:00 | 2019-12-15 04:30 |  |  |  | Horseshoe Lake PP mezzanine level, under HP/IP section of turbine. |  |  |  |  | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | TRUE | FALSE |  |  |  | Benjamin Dickinson | Daniel Perry |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Operations |  | Peter Nowakowski | Michael Kennedy |  |  |  | Daniel Perry |  | High | [87 empty] | Multiple burnt treated 2x10 scaffolding boards and multiple insulation blankets around steam piping. | 2000 | Peter Nowakowski | Fire | Terry Patterson | [19 empty] | 9581777
9166 | Horseshoe Lake Power Plant | 2019-12-15 03:00 | Performing unit rounds a wood fire smell was evident on TR floor. FPO and operator investigated around #8 which was on for testing. An incipient fire was detected under the 8 Turbine. 2x10 scaffolding boards and insulation blankets were smoldering and flaming up when air when fan the embers. | Level 3 |  | FALSE | Property Damage | Donnie Jones | Jesse Murray | Assigning per Doupe and Murray. | 2019-12-18 10:35 | Power Supply | Peter Nowakowski |  | 2019-12-15 18:17 | 2019-12-15 18:17 |  | 2019-12-29 03:00 | 2019-12-15 04:30 |  |  |  | Horseshoe Lake PP mezzanine level, under HP/IP section of turbine. |  |  |  |  | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | TRUE | FALSE |  |  |  | Benjamin Dickinson | Daniel Perry |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Operations |  | Peter Nowakowski | Michael Kennedy |  |  |  | Daniel Perry |  | High | [87 empty] | Multiple burnt treated 2x10 scaffolding boards and multiple insulation blankets around steam piping. | 2000 | Peter Nowakowski | Fire | Johnny Jonas | [19 empty] | 9581777
9167 | Metro Service Center | 2019-12-16 17:00 | Member was entering door with roll around file cart and the cart got hung up on the door frame. In the process of trying to get the cart inside the door, member lost footing and fell down. Member reports they are a little sore but not injured and no first aid is required. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Transco | Drew Walker | 2020-01-06 07:39 | 2019-12-16 18:14 | 2019-12-16 18:14 | 2019-12-30 14:29 | 2019-12-30 17:00 | 2019-12-16 17:47 | 2020-01-01 10:17 |  |  | North District Operating Center |  |  | Cody Magby | I agree with review. cm | T&D Ops |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Drew Walker |  | Member was entering doorway at the North District Operating Center. Member was starting their shift and was bringing in their lunchbox and the roll around cart that we use to transfer files between control centers. Member stopped at Metro on their way to work for nightshift, loaded the cart with proper items, then drove to the North District Operating Center. When member attempted to go through the second door that opens into a large hallway, the cart got hung up on the door and member lost footing trying to get it through the door. Member fell down. He believed he may have got his foot hung up on the rug also, but wasn't for sure. No injury or first aid required. |  |  |  | Metro Service Center | FALSE |  | TRUE | System Operations |  | Eric Bramel | Drew Walker |  | Darrell Fuller | I agree with the actions taken in making all TCC members aware of the incident involving the TCC bug out box. This is a job task that isn't performed very often. Members should recognize the potential hazards when performing out of the ordinary tasks. | Darrell Fuller |  | Low |  | 2.06 Poor coordination | [14 empty] | Member was entering doorway with roll-around file cart. While trying to pull the cart through the doorway, cart got hung up on door frame and member lost footing and fell down. | 11. Improper Position for Task | 4. Fall on Same Level (Slip and Fall, Trip Over)
9168 | Muskogee Power Plant | 2019-12-17 15:00 | Contractor set 1" conduit on chemical tote to put on his fall harness and conduit rolled off of tote approximately 3' and struck a 1/2" pvc pipe and broke it releasing chemical onto floor. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2020-02-05 12:52 | 2019-12-17 20:20 | 2019-12-17 20:20 | 2020-01-21 08:44 | 2019-12-31 15:00 | 2019-12-17 14:30 | 2020-01-21 09:39 |  | 2020-01-21 08:53 | Muskogee PP Demin Building |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | ECA contractor was installing conduit in ceiling of MK Demin building and was preparing to go up in manlift with material. Contractor set down a 10' stick of 1" conduit on a chemical tote beside the manlift while putting on his fall protection harness. The chemical tote had a wire support rack around the tote and as he was donning his PPE the conduit rolled to the back side of the tote and to the floor striking a 1/2" PVC valve and nipple with a hose attatched, breaking the nipple off at the valve releasing sodium bisulfite A onto floor. Inspector was notified by contractor and demin was evacuated for hazard. Inspector notified plant chemist (Harry Byrne) who addressed spill containment and clean-up. This system had a check valve and isolation to minimize loss and spill. Once area was cleaned up and secure repair was made to broken valve. Investigation findings: This was the second incident of falling objects to a lower level on this project by two separate contract crews in three days. Some potential causal factors that we witnessed: 1) Congested area. Demin has small tight aisles and limited room for ceiling access with manlifts. 2) High traffic area. Two separate contract crews working at times in the area with sub contractors excavating outside building. OGE chemist and operations crew also needed access to area at times. 3) Limited amount of floor or staging room for material and equipment. Contract crew was stopped and a stand down held with crew members and supervisor by construction inspector. Inspector went over proper means of material laydown and dropped object prevention with crew. Solutions were discussed to stage material and how to prevent dropped objects. The OGE inspector walked area with contractors to identify other potential pvc valves and piping that could be damaged or broken and put out cones or flags to make visible, and if possible to place protection over or around valves and piping that stuck out in the walkways. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | Special Services |  | Randy Ellis | Kelly Casey |  | Brian Huckabay | Approved with addition of additional corrective action. | Brian Huckabay |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | pipe fell on pvc valve | 03. Failure to Secure | 3. Fall from Elevation to Lower Level |  | Reviewed. Updated: Added SDS 01-20-2020. |  |  |  | Property Damage |  | Kelly Casey | broken pvc piping |  |  |  |  | 3. Fall from Elevation to Lower Level | Randy Ellis | ECA | channing black |  | Fixed Equipment |  | Randy Ellis |  |  |  |  | FALSE | [66 empty] | 9592018
9169 | Ft Smith Service Center | 2019-12-17 13:00 | BJs Oilfield Services was contracted to remove contaminated gravel from Third Street Substation and replace it with fresh gravel. During the process, BJs had one of their skid-steers back into a breaker control cable plastic conduit and break it. The breakers (82 and 86) did not operate however the conduit will have to be repaired and the control cable may have been nicked. Further investigation will be required. BJs did not follow the 5' exclusion rule about operating heavy equipment near substation equipment or structures. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | John Burns | 2020-02-25 11:55 | 2019-12-18 12:59 | 2019-12-18 12:59 | 2020-01-09 09:21 | 2019-12-31 13:00 | 2019-12-18 12:44 | 2020-02-25 10:49 |  | 2020-01-13 07:47 | Third Street Substation - Fort Smith, Arkansas |  |  | William Young | Reviewed and approved. WCY 2/25/2020 | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | John Burns |  | Site Manager Trader Horn contacted Project Manager to inform him that contractor BJs Oilfield Services had backed into a breaker control cable conduit at Third Street Sub in Fort Smith, Arkansas. The control cable inside the conduit was not damaged and the breakers did not operate. The conduit is old and brittle and will need to be repaired. It is also possible that some of the control cables might have been nicked. The breakers cannot be taken out of service until Spring of 2020. Until then, the conduit will be patched. In the spring a more thorough examination of the cable will be performed to determine if it needs to be replaced. |  |  |  | Ft Smith Service Center | FALSE |  | FALSE | UTS - Capital Projects |  | John Burns | John Burns |  | William Young | Reviewed and approved. WCY 2/25/2020 | William Young |  | Medium | [8 empty] | 9.07 Inadequate instructions, orientation and/or training | [7 empty] | Contractor was operating bobcat loader inside substation while removing contaminated gravel and replacing with fresh gravel. Operator backed into concrete support pad and damage control cable conduit that controls two main breakers inside substation. Contractor should have had spotter in place to prevent contact between bobcat and conduit | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) |  | no additional comments. MLH 1/13 |  |  |  | Property Damage |  | John Burns | Damage to substation control cable conduit |  |  |  |  | 1. Struck Against (Running or Bumping Into) | John Burns | BJs Oilfield Services | BJs Oilfield Services |  | Structural |  | John Burns |  |  |  |  | FALSE
9169 | Ft Smith Service Center | 2019-12-17 13:00 | BJs Oilfield Services was contracted to remove contaminated gravel from Third Street Substation and replace it with fresh gravel. During the process, BJs had one of their skid-steers back into a breaker control cable plastic conduit and break it. The breakers (82 and 86) did not operate however the conduit will have to be repaired and the control cable may have been nicked. Further investigation will be required. BJs did not follow the 5' exclusion rule about operating heavy equipment near substation equipment or structures. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | John Burns | 2020-02-25 11:55 | 2019-12-18 12:59 | 2019-12-18 12:59 | 2020-01-09 09:21 | 2019-12-31 13:00 | 2019-12-18 12:44 | 2020-02-25 10:49 |  | 2020-01-13 07:47 | Third Street Substation - Fort Smith, Arkansas |  |  | William Young | Reviewed and approved. WCY 2/25/2020 | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | John Burns |  | Site Manager Trader Horn contacted Project Manager to inform him that contractor BJs Oilfield Services had backed into a breaker control cable conduit at Third Street Sub in Fort Smith, Arkansas. The control cable inside the conduit was not damaged and the breakers did not operate. The conduit is old and brittle and will need to be repaired. It is also possible that some of the control cables might have been nicked. The breakers cannot be taken out of service until Spring of 2020. Until then, the conduit will be patched. In the spring a more thorough examination of the cable will be performed to determine if it needs to be replaced. |  |  |  | Ft Smith Service Center | FALSE |  | FALSE | UTS - Capital Projects |  | John Burns | John Burns |  | William Young | Reviewed and approved. WCY 2/25/2020 | William Young |  | Medium | [8 empty] | 9.04 Giving inadequate policy, procedure, practices or guidelines | [7 empty] | Contractor was operating bobcat loader inside substation while removing contaminated gravel and replacing with fresh gravel. Operator backed into concrete support pad and damage control cable conduit that controls two main breakers inside substation. Contractor should have had spotter in place to prevent contact between bobcat and conduit | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) |  | no additional comments. MLH 1/13 |  |  |  | Property Damage |  | John Burns | Damage to substation control cable conduit |  |  |  |  | 1. Struck Against (Running or Bumping Into) | John Burns | BJs Oilfield Services | BJs Oilfield Services |  | Structural |  | John Burns |  |  |  |  | FALSE
9169 | Ft Smith Service Center | 2019-12-17 13:00 | BJs Oilfield Services was contracted to remove contaminated gravel from Third Street Substation and replace it with fresh gravel. During the process, BJs had one of their skid-steers back into a breaker control cable plastic conduit and break it. The breakers (82 and 86) did not operate however the conduit will have to be repaired and the control cable may have been nicked. Further investigation will be required. BJs did not follow the 5' exclusion rule about operating heavy equipment near substation equipment or structures. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | John Burns | 2020-02-25 11:55 | 2019-12-18 12:59 | 2019-12-18 12:59 | 2020-01-09 09:21 | 2019-12-31 13:00 | 2019-12-18 12:44 | 2020-02-25 10:49 |  | 2020-01-13 07:47 | Third Street Substation - Fort Smith, Arkansas |  |  | William Young | Reviewed and approved. WCY 2/25/2020 | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | John Burns |  | Site Manager Trader Horn contacted Project Manager to inform him that contractor BJs Oilfield Services had backed into a breaker control cable conduit at Third Street Sub in Fort Smith, Arkansas. The control cable inside the conduit was not damaged and the breakers did not operate. The conduit is old and brittle and will need to be repaired. It is also possible that some of the control cables might have been nicked. The breakers cannot be taken out of service until Spring of 2020. Until then, the conduit will be patched. In the spring a more thorough examination of the cable will be performed to determine if it needs to be replaced. |  |  |  | Ft Smith Service Center | FALSE |  | FALSE | UTS - Capital Projects |  | John Burns | John Burns |  | William Young | Reviewed and approved. WCY 2/25/2020 | William Young |  | Medium | [8 empty] | 9.11 Inadequate matching of individual qualifications and job/task requirements | [7 empty] | Contractor was operating bobcat loader inside substation while removing contaminated gravel and replacing with fresh gravel. Operator backed into concrete support pad and damage control cable conduit that controls two main breakers inside substation. Contractor should have had spotter in place to prevent contact between bobcat and conduit | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) |  | no additional comments. MLH 1/13 |  |  |  | Property Damage |  | John Burns | Damage to substation control cable conduit |  |  |  |  | 1. Struck Against (Running or Bumping Into) | John Burns | BJs Oilfield Services | BJs Oilfield Services |  | Structural |  | John Burns |  |  |  |  | FALSE
9169 | Ft Smith Service Center | 2019-12-17 13:00 | BJs Oilfield Services was contracted to remove contaminated gravel from Third Street Substation and replace it with fresh gravel. During the process, BJs had one of their skid-steers back into a breaker control cable plastic conduit and break it. The breakers (82 and 86) did not operate however the conduit will have to be repaired and the control cable may have been nicked. Further investigation will be required. BJs did not follow the 5' exclusion rule about operating heavy equipment near substation equipment or structures. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | John Burns | 2020-02-25 11:55 | 2019-12-18 12:59 | 2019-12-18 12:59 | 2020-01-09 09:21 | 2019-12-31 13:00 | 2019-12-18 12:44 | 2020-02-25 10:49 |  | 2020-01-13 07:47 | Third Street Substation - Fort Smith, Arkansas |  |  | William Young | Reviewed and approved. WCY 2/25/2020 | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | John Burns |  | Site Manager Trader Horn contacted Project Manager to inform him that contractor BJs Oilfield Services had backed into a breaker control cable conduit at Third Street Sub in Fort Smith, Arkansas. The control cable inside the conduit was not damaged and the breakers did not operate. The conduit is old and brittle and will need to be repaired. It is also possible that some of the control cables might have been nicked. The breakers cannot be taken out of service until Spring of 2020. Until then, the conduit will be patched. In the spring a more thorough examination of the cable will be performed to determine if it needs to be replaced. |  |  |  | Ft Smith Service Center | FALSE |  | FALSE | UTS - Capital Projects |  | John Burns | John Burns |  | William Young | Reviewed and approved. WCY 2/25/2020 | William Young |  | Medium | [8 empty] | 9.06 Inadequate work planning or programming | [7 empty] | Contractor was operating bobcat loader inside substation while removing contaminated gravel and replacing with fresh gravel. Operator backed into concrete support pad and damage control cable conduit that controls two main breakers inside substation. Contractor should have had spotter in place to prevent contact between bobcat and conduit | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) |  | no additional comments. MLH 1/13 |  |  |  | Property Damage |  | John Burns | Damage to substation control cable conduit |  |  |  |  | 1. Struck Against (Running or Bumping Into) | John Burns | BJs Oilfield Services | BJs Oilfield Services |  | Structural |  | John Burns |  |  |  |  | FALSE
9169 | Ft Smith Service Center | 2019-12-17 13:00 | BJs Oilfield Services was contracted to remove contaminated gravel from Third Street Substation and replace it with fresh gravel. During the process, BJs had one of their skid-steers back into a breaker control cable plastic conduit and break it. The breakers (82 and 86) did not operate however the conduit will have to be repaired and the control cable may have been nicked. Further investigation will be required. BJs did not follow the 5' exclusion rule about operating heavy equipment near substation equipment or structures. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | John Burns | 2020-02-25 11:55 | 2019-12-18 12:59 | 2019-12-18 12:59 | 2020-01-09 09:21 | 2019-12-31 13:00 | 2019-12-18 12:44 | 2020-02-25 10:49 |  | 2020-01-13 07:47 | Third Street Substation - Fort Smith, Arkansas |  |  | William Young | Reviewed and approved. WCY 2/25/2020 | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | John Burns |  | Site Manager Trader Horn contacted Project Manager to inform him that contractor BJs Oilfield Services had backed into a breaker control cable conduit at Third Street Sub in Fort Smith, Arkansas. The control cable inside the conduit was not damaged and the breakers did not operate. The conduit is old and brittle and will need to be repaired. It is also possible that some of the control cables might have been nicked. The breakers cannot be taken out of service until Spring of 2020. Until then, the conduit will be patched. In the spring a more thorough examination of the cable will be performed to determine if it needs to be replaced. |  |  |  | Ft Smith Service Center | FALSE |  | FALSE | UTS - Capital Projects |  | John Burns | John Burns |  | William Young | Reviewed and approved. WCY 2/25/2020 | William Young |  | Medium |  |  | 3.09 Constrained movement |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction |  |  | 9.09 Inadequate identification and evaluation of loss exposures | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | The basic cause of this accident was inattention while changing out gravel inside substation. Contractor failed to observe 5 foot exclusion zone surrounding equipment and substation supports. No safety observer was present during the accident. | 11. Improper Position for Task | 1. Struck Against (Running or Bumping Into) |  | no additional comments. MLH 1/13 |  |  |  | Property Damage |  | John Burns | Damage to substation control cable conduit |  |  |  |  | 1. Struck Against (Running or Bumping Into) | John Burns | BJs Oilfield Services | BJs Oilfield Services |  | Structural |  | John Burns |  |  |  |  | FALSE
9169 | Ft Smith Service Center | 2019-12-17 13:00 | BJs Oilfield Services was contracted to remove contaminated gravel from Third Street Substation and replace it with fresh gravel. During the process, BJs had one of their skid-steers back into a breaker control cable plastic conduit and break it. The breakers (82 and 86) did not operate however the conduit will have to be repaired and the control cable may have been nicked. Further investigation will be required. BJs did not follow the 5' exclusion rule about operating heavy equipment near substation equipment or structures. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | John Burns | 2020-02-25 11:55 | 2019-12-18 12:59 | 2019-12-18 12:59 | 2020-01-09 09:21 | 2019-12-31 13:00 | 2019-12-18 12:44 | 2020-02-25 10:49 |  | 2020-01-13 07:47 | Third Street Substation - Fort Smith, Arkansas |  |  | William Young | Reviewed and approved. WCY 2/25/2020 | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | John Burns |  | Site Manager Trader Horn contacted Project Manager to inform him that contractor BJs Oilfield Services had backed into a breaker control cable conduit at Third Street Sub in Fort Smith, Arkansas. The control cable inside the conduit was not damaged and the breakers did not operate. The conduit is old and brittle and will need to be repaired. It is also possible that some of the control cables might have been nicked. The breakers cannot be taken out of service until Spring of 2020. Until then, the conduit will be patched. In the spring a more thorough examination of the cable will be performed to determine if it needs to be replaced. |  |  |  | Ft Smith Service Center | FALSE |  | FALSE | UTS - Capital Projects |  | John Burns | John Burns |  | William Young | Reviewed and approved. WCY 2/25/2020 | William Young |  | Medium |  |  | 3.09 Constrained movement |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction |  |  | 9.09 Inadequate identification and evaluation of loss exposures | [6 empty] | 16.01 Inadequate horizontal communication between peers | The basic cause of this accident was inattention while changing out gravel inside substation. Contractor failed to observe 5 foot exclusion zone surrounding equipment and substation supports. No safety observer was present during the accident. | 11. Improper Position for Task | 1. Struck Against (Running or Bumping Into) |  | no additional comments. MLH 1/13 |  |  |  | Property Damage |  | John Burns | Damage to substation control cable conduit |  |  |  |  | 1. Struck Against (Running or Bumping Into) | John Burns | BJs Oilfield Services | BJs Oilfield Services |  | Structural |  | John Burns |  |  |  |  | FALSE
9169 | Ft Smith Service Center | 2019-12-17 13:00 | BJs Oilfield Services was contracted to remove contaminated gravel from Third Street Substation and replace it with fresh gravel. During the process, BJs had one of their skid-steers back into a breaker control cable plastic conduit and break it. The breakers (82 and 86) did not operate however the conduit will have to be repaired and the control cable may have been nicked. Further investigation will be required. BJs did not follow the 5' exclusion rule about operating heavy equipment near substation equipment or structures. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | John Burns | 2020-02-25 11:55 | 2019-12-18 12:59 | 2019-12-18 12:59 | 2020-01-09 09:21 | 2019-12-31 13:00 | 2019-12-18 12:44 | 2020-02-25 10:49 |  | 2020-01-13 07:47 | Third Street Substation - Fort Smith, Arkansas |  |  | William Young | Reviewed and approved. WCY 2/25/2020 | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | John Burns |  | Site Manager Trader Horn contacted Project Manager to inform him that contractor BJs Oilfield Services had backed into a breaker control cable conduit at Third Street Sub in Fort Smith, Arkansas. The control cable inside the conduit was not damaged and the breakers did not operate. The conduit is old and brittle and will need to be repaired. It is also possible that some of the control cables might have been nicked. The breakers cannot be taken out of service until Spring of 2020. Until then, the conduit will be patched. In the spring a more thorough examination of the cable will be performed to determine if it needs to be replaced. |  |  |  | Ft Smith Service Center | FALSE |  | FALSE | UTS - Capital Projects |  | John Burns | John Burns |  | William Young | Reviewed and approved. WCY 2/25/2020 | William Young |  | Medium |  |  | 3.09 Constrained movement |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction |  |  | 9.06 Inadequate work planning or programming | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | The basic cause of this accident was inattention while changing out gravel inside substation. Contractor failed to observe 5 foot exclusion zone surrounding equipment and substation supports. No safety observer was present during the accident. | 11. Improper Position for Task | 1. Struck Against (Running or Bumping Into) |  | no additional comments. MLH 1/13 |  |  |  | Property Damage |  | John Burns | Damage to substation control cable conduit |  |  |  |  | 1. Struck Against (Running or Bumping Into) | John Burns | BJs Oilfield Services | BJs Oilfield Services |  | Structural |  | John Burns |  |  |  |  | FALSE
9169 | Ft Smith Service Center | 2019-12-17 13:00 | BJs Oilfield Services was contracted to remove contaminated gravel from Third Street Substation and replace it with fresh gravel. During the process, BJs had one of their skid-steers back into a breaker control cable plastic conduit and break it. The breakers (82 and 86) did not operate however the conduit will have to be repaired and the control cable may have been nicked. Further investigation will be required. BJs did not follow the 5' exclusion rule about operating heavy equipment near substation equipment or structures. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | John Burns | 2020-02-25 11:55 | 2019-12-18 12:59 | 2019-12-18 12:59 | 2020-01-09 09:21 | 2019-12-31 13:00 | 2019-12-18 12:44 | 2020-02-25 10:49 |  | 2020-01-13 07:47 | Third Street Substation - Fort Smith, Arkansas |  |  | William Young | Reviewed and approved. WCY 2/25/2020 | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | John Burns |  | Site Manager Trader Horn contacted Project Manager to inform him that contractor BJs Oilfield Services had backed into a breaker control cable conduit at Third Street Sub in Fort Smith, Arkansas. The control cable inside the conduit was not damaged and the breakers did not operate. The conduit is old and brittle and will need to be repaired. It is also possible that some of the control cables might have been nicked. The breakers cannot be taken out of service until Spring of 2020. Until then, the conduit will be patched. In the spring a more thorough examination of the cable will be performed to determine if it needs to be replaced. |  |  |  | Ft Smith Service Center | FALSE |  | FALSE | UTS - Capital Projects |  | John Burns | John Burns |  | William Young | Reviewed and approved. WCY 2/25/2020 | William Young |  | Medium |  |  | 3.09 Constrained movement |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction |  |  | 9.06 Inadequate work planning or programming | [6 empty] | 16.01 Inadequate horizontal communication between peers | The basic cause of this accident was inattention while changing out gravel inside substation. Contractor failed to observe 5 foot exclusion zone surrounding equipment and substation supports. No safety observer was present during the accident. | 11. Improper Position for Task | 1. Struck Against (Running or Bumping Into) |  | no additional comments. MLH 1/13 |  |  |  | Property Damage |  | John Burns | Damage to substation control cable conduit |  |  |  |  | 1. Struck Against (Running or Bumping Into) | John Burns | BJs Oilfield Services | BJs Oilfield Services |  | Structural |  | John Burns |  |  |  |  | FALSE
9169 | Ft Smith Service Center | 2019-12-17 13:00 | BJs Oilfield Services was contracted to remove contaminated gravel from Third Street Substation and replace it with fresh gravel. During the process, BJs had one of their skid-steers back into a breaker control cable plastic conduit and break it. The breakers (82 and 86) did not operate however the conduit will have to be repaired and the control cable may have been nicked. Further investigation will be required. BJs did not follow the 5' exclusion rule about operating heavy equipment near substation equipment or structures. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | John Burns | 2020-02-25 11:55 | 2019-12-18 12:59 | 2019-12-18 12:59 | 2020-01-09 09:21 | 2019-12-31 13:00 | 2019-12-18 12:44 | 2020-02-25 10:49 |  | 2020-01-13 07:47 | Third Street Substation - Fort Smith, Arkansas |  |  | William Young | Reviewed and approved. WCY 2/25/2020 | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | John Burns |  | Site Manager Trader Horn contacted Project Manager to inform him that contractor BJs Oilfield Services had backed into a breaker control cable conduit at Third Street Sub in Fort Smith, Arkansas. The control cable inside the conduit was not damaged and the breakers did not operate. The conduit is old and brittle and will need to be repaired. It is also possible that some of the control cables might have been nicked. The breakers cannot be taken out of service until Spring of 2020. Until then, the conduit will be patched. In the spring a more thorough examination of the cable will be performed to determine if it needs to be replaced. |  |  |  | Ft Smith Service Center | FALSE |  | FALSE | UTS - Capital Projects |  | John Burns | John Burns |  | William Young | Reviewed and approved. WCY 2/25/2020 | William Young |  | Medium |  |  | 3.09 Constrained movement |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction |  |  | 9.02 Unclear or conflicting assignment of responsibility | [6 empty] | 16.02 Inadequate vertical communication between supervisor and person | The basic cause of this accident was inattention while changing out gravel inside substation. Contractor failed to observe 5 foot exclusion zone surrounding equipment and substation supports. No safety observer was present during the accident. | 11. Improper Position for Task | 1. Struck Against (Running or Bumping Into) |  | no additional comments. MLH 1/13 |  |  |  | Property Damage |  | John Burns | Damage to substation control cable conduit |  |  |  |  | 1. Struck Against (Running or Bumping Into) | John Burns | BJs Oilfield Services | BJs Oilfield Services |  | Structural |  | John Burns |  |  |  |  | FALSE
9169 | Ft Smith Service Center | 2019-12-17 13:00 | BJs Oilfield Services was contracted to remove contaminated gravel from Third Street Substation and replace it with fresh gravel. During the process, BJs had one of their skid-steers back into a breaker control cable plastic conduit and break it. The breakers (82 and 86) did not operate however the conduit will have to be repaired and the control cable may have been nicked. Further investigation will be required. BJs did not follow the 5' exclusion rule about operating heavy equipment near substation equipment or structures. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | John Burns | 2020-02-25 11:55 | 2019-12-18 12:59 | 2019-12-18 12:59 | 2020-01-09 09:21 | 2019-12-31 13:00 | 2019-12-18 12:44 | 2020-02-25 10:49 |  | 2020-01-13 07:47 | Third Street Substation - Fort Smith, Arkansas |  |  | William Young | Reviewed and approved. WCY 2/25/2020 | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | John Burns |  | Site Manager Trader Horn contacted Project Manager to inform him that contractor BJs Oilfield Services had backed into a breaker control cable conduit at Third Street Sub in Fort Smith, Arkansas. The control cable inside the conduit was not damaged and the breakers did not operate. The conduit is old and brittle and will need to be repaired. It is also possible that some of the control cables might have been nicked. The breakers cannot be taken out of service until Spring of 2020. Until then, the conduit will be patched. In the spring a more thorough examination of the cable will be performed to determine if it needs to be replaced. |  |  |  | Ft Smith Service Center | FALSE |  | FALSE | UTS - Capital Projects |  | John Burns | John Burns |  | William Young | Reviewed and approved. WCY 2/25/2020 | William Young |  | Medium |  |  | 3.09 Constrained movement |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction |  |  | 9.02 Unclear or conflicting assignment of responsibility | [6 empty] | 16.01 Inadequate horizontal communication between peers | The basic cause of this accident was inattention while changing out gravel inside substation. Contractor failed to observe 5 foot exclusion zone surrounding equipment and substation supports. No safety observer was present during the accident. | 11. Improper Position for Task | 1. Struck Against (Running or Bumping Into) |  | no additional comments. MLH 1/13 |  |  |  | Property Damage |  | John Burns | Damage to substation control cable conduit |  |  |  |  | 1. Struck Against (Running or Bumping Into) | John Burns | BJs Oilfield Services | BJs Oilfield Services |  | Structural |  | John Burns |  |  |  |  | FALSE
9170 | Sooner Power Plant | 2019-12-18 14:00 | member removing firehose fitting from piping. This piping was touching a light fixture conduit, the movement caused the glass globe covering the light bulb to fall to the grating and break apart. The glass then fell through the grating and approx. 100 feet to the ground. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Daniel Dickinson | 2020-01-09 07:07 | 2019-12-18 15:49 | 2019-12-18 15:49 | 2019-12-27 00:22 | 2020-01-01 14:00 | 2019-12-18 15:32 | 2019-12-27 15:25 |  |  | Sooner PP-on top of bottom ash dewatering bins at silo area |  |  | Brady Sowell | approved by brady sowell | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Daniel Dickinson |  | Sooner PP dewatering bins are filled with bottom ash, a by-product of burning coal, from both boilers every shift and then the bins are dumped (emptied) twice a week. After the dewatering bins are dumped, a firehose is used from the top to clean the inside of the bins to remove any ash stuck on the sides of the bins. This process is necessary to keep the dewatering bins in working order. The system has recently been upgraded and a new higher pressure service water line has been installed to the top of both dewatering bins. This upgrade took some of the load off of the plant firewater system and also provided more system pressure at the top of the dewatering bins because it comes from the coal yard service water booster pumps. Operations members went to the top of the dewatering bin to check out how well the new water supply was working by running all of the screen nozzles and to check how much better pressure was available at firehose connections. When members went to hook up fire hose, he noticed that the fitting was not present to allow a firehose to be hooked up at the new station, so he saw the fitting he needed at the old fire water station in between the bins on the walkway. Member had a pair of Knipex pliers on him and placed them on the fitting and when he pulled on the pliers the glass globe from the light fixture next to him fell to the grating and busted, the pieces of glass then fell through grating and landed on the ground, approximately 100 feet below. The member stopped what he was doing and reported near miss to supervisor. No one was in the area on the ground level where the glass fell. The area underneath was not barricaded. The process of dumping the dewatering bins requires a coal yard scrapper to be driven through this area, filled, and then driven out to be emptied. After further investigation, the firewater piping (1-1/2” pipe) runs right next to and makes contact with the electrical conduit (1-1/2”) holding the light fixture. The light fixture conduit is approx. 9 feet in length and the vertical run is attached to the handrail midrail with a u-bolt. Any movement of the handrail amplifies the movement at the light fixture due to height of the fixture and distance it is away from the support. Essentially the light fixture was “whipped” when the handrail and the firewater piping was moved or shaken. The broken glass globe is threaded into the light fixture, from the broken glass it appears to have only been held by 1 thread. After reporting to supervisor, members checked the remaining lights in the area that were accessible for loose globes and found 5 others that were slightly loose and tightened them up. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Other |  | Curtis Tweedy | Daniel Dickinson |  | Alexander Taybah | There is already a project to upgrade the light fixtures. I approve. | Alexander Taybah |  | Low | [14 empty] | 15.03 Inadequate inspection and/or monitoring |  | overhead light glass globe was loose and fell when handrail and conduit that light was attached to was moved. glass globe was not tight in light fixture. | 23. Defective Tools, Equipment or Materials | 2. Struck By (Hit By Moving Object)
9171 | River Valley | 2019-12-18 09:30 | Maintenance team member did not unplug electric cart and drove away. Pulling receptacle away from wall. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Michael Smith | 2020-02-24 06:58 | 2019-12-19 11:13 | 2019-12-19 11:13 | 2020-01-14 08:50 | 2020-01-01 09:30 | 2019-12-18 09:30 | 2020-02-18 06:55 |  |  | River Valley PP Maintenance Shop |  |  | Anthony Gillespie | Corrective actions should eliminate the potential of incident occurring in the future. | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Michael Smith |  | Maintenance team member did not unplug electric cart and drove away. Pulling receptacle away from wall. |  |  |  | River Valley | FALSE |  | FALSE | Maintenance |  | Richard Evans | Michael Smith |  | Timothy Chancellor | Approved. Corrective actions are appropriate. | Timothy Chancellor |  | Low |  |  |  | 4.09 Preoccupation with problems | [12 empty] | Member did not unplug cart and drove away pulling the conduit from the wall. | 18. Failure to Check, Monitor | 6. Caught On (Snagged, Hung) | [68 empty] | Conduit pulled apart. | 100 | Richard Evans | Structural
9172 | Shawnee Service Center | 2019-12-23 12:00 | An OGE vehicle was traveling east on MacArthur Street in Shawnee OK. Company vehicle was approaching Harrison in right lane getting ready to turn right. The light was yellow as company vehicle approached intersection but turned red as company vehicle stopped in right turn lane at intersection. Public Vehicle hit Company vehicle in the driver side rear bumper. | Level 3 |  | FALSE | Vehicle | Jean Leger | William Young | Change risk ranking to medium. Low speed collision. Public vehicle struck company vehicle. Non chargeable vehicle incident. WCY 2/25/2020 |  | OG&E Corp Services | Ronald Madron |  | 2019-12-23 20:34 | 2019-12-23 20:34 |  | 2020-01-06 12:00 | 2019-12-23 19:54 |  |  |  | Shawnee Oklahoma, MacArthur Street and Harrison Street intersection. |  |  |  |  | UTS |  | Level 3 | Vehicle |  | FALSE | FALSE | TRUE |  | FALSE | TRUE | [6 empty] | Shawnee Service Center | FALSE |  | FALSE | UTS - Envir. & Process Chem |  | Nathaniel Shepherd | Ronald Madron |  |  |  | Thomas Leach |  | High | [87 empty] | Left rear quarter panel and rear bumper. | 3000 | Nathaniel Shepherd | Vehicle (not related to operation of vehicle) |  | FO-1122 | FALSE |  | Shawnee | Public Vehicle Struck OGE | OGE Vehicle Stopped/Parked | 2017-12-11 |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Clear
9172 | Shawnee Service Center | 2019-12-23 12:00 | An OGE vehicle was traveling east on MacArthur Street in Shawnee OK. Company vehicle was approaching Harrison in right lane getting ready to turn right. The light was yellow as company vehicle approached intersection but turned red as company vehicle stopped in right turn lane at intersection. Public Vehicle hit Company vehicle in the driver side rear bumper. | Level 3 |  | FALSE | Property Damage | Jean Leger | William Young | Change risk ranking to medium. Low speed collision. Public vehicle struck company vehicle. Non chargeable vehicle incident. WCY 2/25/2020 |  | OG&E Corp Services | Ronald Madron |  | 2019-12-23 20:34 | 2019-12-23 20:34 |  | 2020-01-06 12:00 | 2019-12-23 19:54 |  |  |  | Shawnee Oklahoma, MacArthur Street and Harrison Street intersection. |  |  |  |  | UTS |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | TRUE | [6 empty] | Shawnee Service Center | FALSE |  | FALSE | UTS - Envir. & Process Chem |  | Nathaniel Shepherd | Ronald Madron |  |  |  | Thomas Leach |  | High | [87 empty] | Left rear quarter panel and rear bumper. | 3000 | Nathaniel Shepherd | Vehicle (not related to operation of vehicle) |  | FO-1122 | FALSE |  | Shawnee | Public Vehicle Struck OGE | OGE Vehicle Stopped/Parked | 2017-12-11 |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Clear
9173 | Redbud Plant | 2019-12-26 09:30 | Member was offloading bleach to Cooling Towers, but it would not fit full load. Member asked control room for Demin Tank Full Level. Control Room checked the "Chemical Offload Calculator" sheet. It listed the available level to offload at 160". Member began offloading bleach to the demin building tank. Starting tank level was 118". The tank overflowed at 140" and was immediately caught by the operations member. Offload was stopped, onsite chemist notified, and control room notified. All chemical was contained in the berm, and chemist neutralized chemical. No member injury of spill out of berm. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Benjamin Dickinson | 2020-01-29 10:43 | 2019-12-26 11:11 | 2019-12-26 11:11 | 2020-01-14 10:10 | 2020-01-09 08:30 | 2019-12-26 10:52 | 2020-01-24 09:47 |  |  | Redbud Power Plant Water Demin Chemical Unloading Station. |  |  | Guillermo Sarmiento | Reviewed incident and discussed with Ben Dickinson. Incident was covered on the incident call on 29JAN20. No additional action items were concluded from the call. I agree and approve he incident findings and action items. | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Benjamin Dickinson |  | Operations Member started sodium hypochlorite offload at unit 3 cooling tower. The cooling tower tank available space was slightly less than the bleach tanker had brought. The member radioed the control room to see where else bleach could be offloaded. This is a common occurrence. The Operations Member reviewed the "Offload Calculator" sheet on the "Operations Turnover" Worksheet. This sheet listed the "Available Level to Off Load" for the Raw Water Demineralized Building Sodium Hypochlorite Tank at 160". The current level was at 118". The operations member began offloading bleach to the Raw Water Demin Tank (29X-WR-MT-006). The Raw Water Demin Building Sodium Hypochlorite tank has a local digital level readout, but it was not working at the time. No notification found for the digital readout not working. There is no visual tank level reading on the tank, i.e. no sight glass and the tank is not transparent. At 140" on the DCS Readout, the tank began overflowing and was immediately noticed by the member. The offload was stopped, and the plant chemist was notified. All overflowed chemical was safely contained in the berm. All members are outside the berm during an offload, and the fill station is located outside the building. Truck driver and operations member were wearing proper PPE and were outside the affected area during offload. The plant chemist was able to dilute the chemical and neutralize the water. The remaining bleach was loaded into unit 4 cooling tower with no incident. The Demin tank had received bleach on 12/20 and went from 97" to 118". On 12/20, an alarm was noted at 110", but this was thought to be incorrectly loaded from our DCS upgrade in 2018. The operators noted the alarm at that time to be updated. The chemical offload SOP lists the max tank level of 120”. The operations member did have the SOP with them and had checked all boxes. Step 3 is “Verify the available tank capacity is adequate”. The member did this by radioing the control room and did not notice the “note” above listing max tank level. The procedure also lists “46.5 gallons per inch” and a “working volume of 6700 gallons”. At 46.5 gallons per inch, 6700 gallons would equal 144”. This does not align with the working level of 120”. The tank capacity is posted by the fill station, but it is listed as 7,500 gallons, and does not include a max level in inches. According to the drawing, the volume per height is 48.9 gallons per inch (10’-0” ID). At a working volume of 6700 gallons, this would equal 137”. The overflow is also shown at 149”, with the level transmitter connection at 12”. The tank volume at overflow level is 7,286 gallons. The listed tank capacity is 7,500 gallons. Assuming the level transmitter is calibrated to read 0” when the level falls below the level transmitter connection, the reading at the max working level would be 132” at 6,700 gallons. The reading at the actual overflow would be 137”. It is also worth noting that the level transmitter and isolation valve had numerous issues within the past 18 months. The valve and level transmitter were replaced in April 2019 due to these issues. Prior to the replacement, the level indication read above 140” consistently, and was likely calibrated incorrectly. On more than one occasion, the level transmitter read above 160” without overflowing. Regardless of the above information, the operations members relied on the excel worksheet that was developed to help with chemical offloading. This worksheet did not align with the SOP as written. The additional information is added to show possible confusion and inconsistencies which may have led to issues in the past, and likely led to a low confidence in the SOP. Consequence state as C1 due to no members being allowed inside the berm during an offload. Therefore, they cannot be harmed by the bleach. Also, berm is designed to contain the full tanks work of chemical without causing property damage. Some chemical was lost but did not total cost to greater than $1000. Probability of any first aid or minor injury is very low due to reasoning above. |  |  |  | Redbud Plant | FALSE |  | TRUE | Operations |  | Anthony Gatto | Benjamin Dickinson |  | Thomas Ward | Have reviewed the incident and have no further comments. | Thomas Ward |  | Low | [9 empty] | 10.03 Inadequate standards, specifications and/or design criteria | [6 empty] | Tank Max Level incorrectly labeled. | 34. Inadequate Instructions, Procedures | 13. Environmental Release
9174 | Muskogee Power Plant | 2019-12-26 14:00 | Member had the job of replacing the wash down line on the conveyor 15/16. Job location was about 100 feet off the ground. Small grass fire under conveyor 15/16 belt. Fire watch spotted fire and extinguished fire. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Jerry Knight | 2020-01-22 14:02 | 2019-12-27 07:51 | 2019-12-27 07:51 | 2019-12-30 14:51 | 2020-01-09 14:00 | 2019-12-27 07:41 | 2020-01-14 16:45 |  | 2020-01-08 06:28 | Under belt 15/16 |  |  | Jesse Murray | Jesse Murray Approved. | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Jerry Knight |  | A crew of four people were tasked to replace the wash down water line from head of conveyor to tail. Members were welding the new line in place. Fire blanket was used (See pics). The fire watch was stationed at the site of the welding. There was not a fire watch on the ground (100 ft below). The grass in the area below was dried out and dead. Some slag from the weld made it's way to the ground and caused a small fire. The member acting as fire watch noticed the grass smoldering and immediately went to extinguish the grass. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | Maintenance |  | Daniel Wafford | Jerry Knight |  | Andy Hedge | Reviewed. Andy Hedge 1/14/2020 | Andy Hedge |  | Medium | [12 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | Welding slag fell 100 feet causing dead grass to smolder. | 26. Fire & Explosion Hazards | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Reviewed Bob Wright | [66 empty] | incipient fire in the grass under 15/16 belt. | 1 | James Greathouse | Fire | [20 empty] | 9583355
9175 | Metro Service Center | 2019-12-26 22:16 | TCC Operator did not state two of the four boundaries when issuing clearance to field member. Field member accepted boundaries and clearance. All four boundaries were properly isolated and tagged in the field and no personnel were in harm. Problem was caught later in the shift and boundaries were correctly given to field member. | Level 1 |  | FALSE | System Operational Incident |  |  |  |  | Transco | Drew Walker |  | 2019-12-27 11:40 |  | 2020-02-28 11:58 | 2020-02-06 22:16 | 2019-12-27 05:15 | 2020-02-28 12:15 |  |  | TCC Operator in the Metro Transmission Control Center issuing transmission line clearance to field member |  |  |  |  | T&D Ops |  | Level 1 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Drew Walker |  | Member was working forced transmission line outage on nightshift 12-26-19. Switching S1940 was conducted to isolate the trouble area. Jason wrote switching and senior operator Matthew Bratvold reviewed it. Both missed that the "header" of the switching and the clearance left off both PT disconnect boundaries. These were in the switching and were opened and hold tagged. Jason issued the clearance to Scott Holt at 2016 12-26-19, who accepted the clearance, and began work. Later on in Jason's shift, after working a completely unrelated outage, he checked over the original switching and noticed that he left two boundaries (PTs) unstated. After a quick discussion with his supervisor, Jason called Scott Holt and told him that he failed to mention two boundaries, gave them to Scott, who repeated his understanding. The clearance had 4 boundaries all together, 2 line switches and 2 PTs. |  |  |  | Metro Service Center | FALSE |  | FALSE | System Operations |  | Jason Weil | Drew Walker |  | Darrell Fuller | I am in agreement with the actions to be undertaken by the TCC Control Center and Transmission Construction. I believe it's important that the field members identify all boundaries when possible. This serves as a self check for both departments. TCC operators should verify among themselves the boundaries and discuss those with the field members before issuing clearances. Nowhere is this more apparent than with emergency work is required. | Darrell Fuller |  | Low |  | 2.10 Memory failure | [14 empty] | Failure to properly write switching and clearance, failure to properly review switching and clearance | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation
9175 | Metro Service Center | 2019-12-26 22:16 | TCC Operator did not state two of the four boundaries when issuing clearance to field member. Field member accepted boundaries and clearance. All four boundaries were properly isolated and tagged in the field and no personnel were in harm. Problem was caught later in the shift and boundaries were correctly given to field member. | Level 1 |  | FALSE | System Operational Incident |  |  |  |  | Transco | Drew Walker |  | 2019-12-27 11:40 |  | 2020-02-28 11:58 | 2020-02-06 22:16 | 2019-12-27 05:15 | 2020-02-28 12:15 |  |  | TCC Operator in the Metro Transmission Control Center issuing transmission line clearance to field member |  |  |  |  | T&D Ops |  | Level 1 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Drew Walker |  | Member was working forced transmission line outage on nightshift 12-26-19. Switching S1940 was conducted to isolate the trouble area. Jason wrote switching and senior operator Matthew Bratvold reviewed it. Both missed that the "header" of the switching and the clearance left off both PT disconnect boundaries. These were in the switching and were opened and hold tagged. Jason issued the clearance to Scott Holt at 2016 12-26-19, who accepted the clearance, and began work. Later on in Jason's shift, after working a completely unrelated outage, he checked over the original switching and noticed that he left two boundaries (PTs) unstated. After a quick discussion with his supervisor, Jason called Scott Holt and told him that he failed to mention two boundaries, gave them to Scott, who repeated his understanding. The clearance had 4 boundaries all together, 2 line switches and 2 PTs. |  |  |  | Metro Service Center | FALSE |  | FALSE | System Operations |  | Jason Weil | Drew Walker |  | Darrell Fuller | I am in agreement with the actions to be undertaken by the TCC Control Center and Transmission Construction. I believe it's important that the field members identify all boundaries when possible. This serves as a self check for both departments. TCC operators should verify among themselves the boundaries and discuss those with the field members before issuing clearances. Nowhere is this more apparent than with emergency work is required. | Darrell Fuller |  | Low |  | 2.10 Memory failure | [14 empty] | Member failed to properly review all boundaries in the header section of the switching and clearance. | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation
9176 | Sooner Power Plant | 2019-12-27 16:30 | After returning LOTO on newly installed overhead door and operator, contractor pushed close button to operate the door and the breaker feeding the door operator immediately tripped. Contract members standing near the overhead door saw a flash come from the operator. Operator was found to be wired incorrectly. No injuries occurred due to all panels being closed and operator mounted 16 ft off the ground. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Michael Dowell | 2020-01-29 12:38 | 2019-12-28 10:17 | 2019-12-28 10:17 | 2020-01-21 11:50 | 2020-01-10 16:30 | 2019-12-28 10:10 | 2020-01-22 14:55 |  |  | Sooner PP Fuel Supply Heavy Equipment Shop |  |  | Brady Sowell | Approved and waiting to be placed on the Incident Call or Hot Sheet - Brady Sowell | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Michael Dowell |  | Contract company DH Pace was tasked with replacing overhead door and operator on the Heavy Equipment(HE) Shop at the Coal Yard. The project manager explained at the time that the power was 480 Volts, 3 phase. Collins electric was the contract company tasked with connecting electrical power. The project manager explained to Collins that the power source was 480 volt, 3 phase. Collins electric has worked at Sooner PP many times in the past and is at least familiar with our electrical system. The Door and Operator were installed by DH Pace and Collins was contacted to connect the electrical power. DH Pace wanted to leave the plant while the power was connect and return on Monday and operate the door. The plant contact asked them to stay so that the door could be returned to service that day and not remain out over the weekend. After completing connections Collins asked DH Pace if they approved of the connections. DH Pace allowed that they did and the LOTO was returned. When DH Pace tired to operate the door after power was restored a flash of light was seen in the operator followed by a release of smoke. After trouble shooting the problem it was noticed that the electrical power was connected to the 240 volt section of the operator and not the 480 volt section. The door operator was installed on an overhead door that was replacing a horizontal door. This job was completed on a Friday. DH Pace had completed their work by 3:00 and wanted to leave the plant and return the following Monday to finish setting up the operator (set limits). They were instructed to stay until the electricians work was complete so the door would not be out of service during the weekend. This door could have been operated manually, but due to its size manually opening or closing it can take more than 15 minutes. The new operator is designed to work with multiple voltages, this is common with many electrical devices (welders,motors). The incoming wiring is connected to a common termination point and then a molex plug is inserted into a receptacle that is labeled for the system voltage. This operator two different receptacles, one for 208/240 volt, 3 phase power and one for 480/575 volt, 3 phase power. Typically DH Pace makes the field terminations on operators that they install. Collins Electric was used to make electrical connections because the conduit that attached to the operator had to be modified. The new operator was in a different location than the one it replaced. Both DH Pace and Collins Electric were notified by the Project Manager that incoming voltage was 480 volt, 3 phase. Collins verified the incoming voltage prior to work beginning. Collins was not given electrical prints or drawings for the new operator and relied solely on verbal instructions from DH Pace. When Collins completed the electrical work and before the LOTO was returned, Collins asked DH Pace if the wiring was correct. DH Pace acknowledged it was. The representative from Collins' that walked the job with the Project Manager was aware that the system was 480 volt, 3 phase. There was a communication breakdown between DH Pace and Collins. Collins was only tasked with the electrical part of the installation and any conduilt that needed to be modified or added. Collins also wired the control switches for the doors as well and this was supposed to be done by DH Pace. The Project Manager had clear communications with the representatives from from Collins and DH Pace. Neither representative was present while the actual work was being done. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Maintenance |  | Brian St Andrews | Michael Dowell |  | Frank Brixey | I am having trouble seeing where the cause and corrective action correlate with the incident. Please clarify. The write up from Collins has some good information as well. Keith Brixey - 1/14/2020 Approved - Brixey | Frank Brixey |  | Low | [6 empty] | 7.04 Excessive frustration | [8 empty] | 16.04 Inadequate communication between work groups | Contractors did not have appropriate discussion before returning equipment to service | 38. Inadequate Communications Hardware, Software, Process | 12. Equipment Failure | [5 empty] | Property Damage |  | Michael Dowell | Shorted electrical components |  |  |  |  | 12. Equipment Failure | Brian St Andrews | DH Pace Door Company | Robert Guynes |  | Fixed Equipment |  | Michael Dowell |  |  |  |  | FALSE | [66 empty] | 9589787
9176 | Sooner Power Plant | 2019-12-27 16:30 | After returning LOTO on newly installed overhead door and operator, contractor pushed close button to operate the door and the breaker feeding the door operator immediately tripped. Contract members standing near the overhead door saw a flash come from the operator. Operator was found to be wired incorrectly. No injuries occurred due to all panels being closed and operator mounted 16 ft off the ground. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Michael Dowell | 2020-01-29 12:38 | 2019-12-28 10:17 | 2019-12-28 10:17 | 2020-01-21 11:50 | 2020-01-10 16:30 | 2019-12-28 10:10 | 2020-01-22 14:55 |  |  | Sooner PP Fuel Supply Heavy Equipment Shop |  |  | Brady Sowell | Approved and waiting to be placed on the Incident Call or Hot Sheet - Brady Sowell | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Michael Dowell |  | Contract company DH Pace was tasked with replacing overhead door and operator on the Heavy Equipment(HE) Shop at the Coal Yard. The project manager explained at the time that the power was 480 Volts, 3 phase. Collins electric was the contract company tasked with connecting electrical power. The project manager explained to Collins that the power source was 480 volt, 3 phase. Collins electric has worked at Sooner PP many times in the past and is at least familiar with our electrical system. The Door and Operator were installed by DH Pace and Collins was contacted to connect the electrical power. DH Pace wanted to leave the plant while the power was connect and return on Monday and operate the door. The plant contact asked them to stay so that the door could be returned to service that day and not remain out over the weekend. After completing connections Collins asked DH Pace if they approved of the connections. DH Pace allowed that they did and the LOTO was returned. When DH Pace tired to operate the door after power was restored a flash of light was seen in the operator followed by a release of smoke. After trouble shooting the problem it was noticed that the electrical power was connected to the 240 volt section of the operator and not the 480 volt section. The door operator was installed on an overhead door that was replacing a horizontal door. This job was completed on a Friday. DH Pace had completed their work by 3:00 and wanted to leave the plant and return the following Monday to finish setting up the operator (set limits). They were instructed to stay until the electricians work was complete so the door would not be out of service during the weekend. This door could have been operated manually, but due to its size manually opening or closing it can take more than 15 minutes. The new operator is designed to work with multiple voltages, this is common with many electrical devices (welders,motors). The incoming wiring is connected to a common termination point and then a molex plug is inserted into a receptacle that is labeled for the system voltage. This operator two different receptacles, one for 208/240 volt, 3 phase power and one for 480/575 volt, 3 phase power. Typically DH Pace makes the field terminations on operators that they install. Collins Electric was used to make electrical connections because the conduit that attached to the operator had to be modified. The new operator was in a different location than the one it replaced. Both DH Pace and Collins Electric were notified by the Project Manager that incoming voltage was 480 volt, 3 phase. Collins verified the incoming voltage prior to work beginning. Collins was not given electrical prints or drawings for the new operator and relied solely on verbal instructions from DH Pace. When Collins completed the electrical work and before the LOTO was returned, Collins asked DH Pace if the wiring was correct. DH Pace acknowledged it was. The representative from Collins' that walked the job with the Project Manager was aware that the system was 480 volt, 3 phase. There was a communication breakdown between DH Pace and Collins. Collins was only tasked with the electrical part of the installation and any conduilt that needed to be modified or added. Collins also wired the control switches for the doors as well and this was supposed to be done by DH Pace. The Project Manager had clear communications with the representatives from from Collins and DH Pace. Neither representative was present while the actual work was being done. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Maintenance |  | Brian St Andrews | Michael Dowell |  | Frank Brixey | I am having trouble seeing where the cause and corrective action correlate with the incident. Please clarify. The write up from Collins has some good information as well. Keith Brixey - 1/14/2020 Approved - Brixey | Frank Brixey |  | Low | [6 empty] | 7.04 Excessive frustration | [8 empty] | 16.01 Inadequate horizontal communication between peers | Contractors did not have appropriate discussion before returning equipment to service | 38. Inadequate Communications Hardware, Software, Process | 12. Equipment Failure | [5 empty] | Property Damage |  | Michael Dowell | Shorted electrical components |  |  |  |  | 12. Equipment Failure | Brian St Andrews | DH Pace Door Company | Robert Guynes |  | Fixed Equipment |  | Michael Dowell |  |  |  |  | FALSE | [66 empty] | 9589787
9176 | Sooner Power Plant | 2019-12-27 16:30 | After returning LOTO on newly installed overhead door and operator, contractor pushed close button to operate the door and the breaker feeding the door operator immediately tripped. Contract members standing near the overhead door saw a flash come from the operator. Operator was found to be wired incorrectly. No injuries occurred due to all panels being closed and operator mounted 16 ft off the ground. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Michael Dowell | 2020-01-29 12:38 | 2019-12-28 10:17 | 2019-12-28 10:17 | 2020-01-21 11:50 | 2020-01-10 16:30 | 2019-12-28 10:10 | 2020-01-22 14:55 |  |  | Sooner PP Fuel Supply Heavy Equipment Shop |  |  | Brady Sowell | Approved and waiting to be placed on the Incident Call or Hot Sheet - Brady Sowell | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Michael Dowell |  | Contract company DH Pace was tasked with replacing overhead door and operator on the Heavy Equipment(HE) Shop at the Coal Yard. The project manager explained at the time that the power was 480 Volts, 3 phase. Collins electric was the contract company tasked with connecting electrical power. The project manager explained to Collins that the power source was 480 volt, 3 phase. Collins electric has worked at Sooner PP many times in the past and is at least familiar with our electrical system. The Door and Operator were installed by DH Pace and Collins was contacted to connect the electrical power. DH Pace wanted to leave the plant while the power was connect and return on Monday and operate the door. The plant contact asked them to stay so that the door could be returned to service that day and not remain out over the weekend. After completing connections Collins asked DH Pace if they approved of the connections. DH Pace allowed that they did and the LOTO was returned. When DH Pace tired to operate the door after power was restored a flash of light was seen in the operator followed by a release of smoke. After trouble shooting the problem it was noticed that the electrical power was connected to the 240 volt section of the operator and not the 480 volt section. The door operator was installed on an overhead door that was replacing a horizontal door. This job was completed on a Friday. DH Pace had completed their work by 3:00 and wanted to leave the plant and return the following Monday to finish setting up the operator (set limits). They were instructed to stay until the electricians work was complete so the door would not be out of service during the weekend. This door could have been operated manually, but due to its size manually opening or closing it can take more than 15 minutes. The new operator is designed to work with multiple voltages, this is common with many electrical devices (welders,motors). The incoming wiring is connected to a common termination point and then a molex plug is inserted into a receptacle that is labeled for the system voltage. This operator two different receptacles, one for 208/240 volt, 3 phase power and one for 480/575 volt, 3 phase power. Typically DH Pace makes the field terminations on operators that they install. Collins Electric was used to make electrical connections because the conduit that attached to the operator had to be modified. The new operator was in a different location than the one it replaced. Both DH Pace and Collins Electric were notified by the Project Manager that incoming voltage was 480 volt, 3 phase. Collins verified the incoming voltage prior to work beginning. Collins was not given electrical prints or drawings for the new operator and relied solely on verbal instructions from DH Pace. When Collins completed the electrical work and before the LOTO was returned, Collins asked DH Pace if the wiring was correct. DH Pace acknowledged it was. The representative from Collins' that walked the job with the Project Manager was aware that the system was 480 volt, 3 phase. There was a communication breakdown between DH Pace and Collins. Collins was only tasked with the electrical part of the installation and any conduilt that needed to be modified or added. Collins also wired the control switches for the doors as well and this was supposed to be done by DH Pace. The Project Manager had clear communications with the representatives from from Collins and DH Pace. Neither representative was present while the actual work was being done. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Maintenance |  | Brian St Andrews | Michael Dowell |  | Frank Brixey | I am having trouble seeing where the cause and corrective action correlate with the incident. Please clarify. The write up from Collins has some good information as well. Keith Brixey - 1/14/2020 Approved - Brixey | Frank Brixey |  | Low | [6 empty] | 7.06 Improper attempt to save time or effort | [8 empty] | 16.04 Inadequate communication between work groups | Contractors did not have appropriate discussion before returning equipment to service | 38. Inadequate Communications Hardware, Software, Process | 12. Equipment Failure | [5 empty] | Property Damage |  | Michael Dowell | Shorted electrical components |  |  |  |  | 12. Equipment Failure | Brian St Andrews | DH Pace Door Company | Robert Guynes |  | Fixed Equipment |  | Michael Dowell |  |  |  |  | FALSE | [66 empty] | 9589787
9176 | Sooner Power Plant | 2019-12-27 16:30 | After returning LOTO on newly installed overhead door and operator, contractor pushed close button to operate the door and the breaker feeding the door operator immediately tripped. Contract members standing near the overhead door saw a flash come from the operator. Operator was found to be wired incorrectly. No injuries occurred due to all panels being closed and operator mounted 16 ft off the ground. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Michael Dowell | 2020-01-29 12:38 | 2019-12-28 10:17 | 2019-12-28 10:17 | 2020-01-21 11:50 | 2020-01-10 16:30 | 2019-12-28 10:10 | 2020-01-22 14:55 |  |  | Sooner PP Fuel Supply Heavy Equipment Shop |  |  | Brady Sowell | Approved and waiting to be placed on the Incident Call or Hot Sheet - Brady Sowell | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Michael Dowell |  | Contract company DH Pace was tasked with replacing overhead door and operator on the Heavy Equipment(HE) Shop at the Coal Yard. The project manager explained at the time that the power was 480 Volts, 3 phase. Collins electric was the contract company tasked with connecting electrical power. The project manager explained to Collins that the power source was 480 volt, 3 phase. Collins electric has worked at Sooner PP many times in the past and is at least familiar with our electrical system. The Door and Operator were installed by DH Pace and Collins was contacted to connect the electrical power. DH Pace wanted to leave the plant while the power was connect and return on Monday and operate the door. The plant contact asked them to stay so that the door could be returned to service that day and not remain out over the weekend. After completing connections Collins asked DH Pace if they approved of the connections. DH Pace allowed that they did and the LOTO was returned. When DH Pace tired to operate the door after power was restored a flash of light was seen in the operator followed by a release of smoke. After trouble shooting the problem it was noticed that the electrical power was connected to the 240 volt section of the operator and not the 480 volt section. The door operator was installed on an overhead door that was replacing a horizontal door. This job was completed on a Friday. DH Pace had completed their work by 3:00 and wanted to leave the plant and return the following Monday to finish setting up the operator (set limits). They were instructed to stay until the electricians work was complete so the door would not be out of service during the weekend. This door could have been operated manually, but due to its size manually opening or closing it can take more than 15 minutes. The new operator is designed to work with multiple voltages, this is common with many electrical devices (welders,motors). The incoming wiring is connected to a common termination point and then a molex plug is inserted into a receptacle that is labeled for the system voltage. This operator two different receptacles, one for 208/240 volt, 3 phase power and one for 480/575 volt, 3 phase power. Typically DH Pace makes the field terminations on operators that they install. Collins Electric was used to make electrical connections because the conduit that attached to the operator had to be modified. The new operator was in a different location than the one it replaced. Both DH Pace and Collins Electric were notified by the Project Manager that incoming voltage was 480 volt, 3 phase. Collins verified the incoming voltage prior to work beginning. Collins was not given electrical prints or drawings for the new operator and relied solely on verbal instructions from DH Pace. When Collins completed the electrical work and before the LOTO was returned, Collins asked DH Pace if the wiring was correct. DH Pace acknowledged it was. The representative from Collins' that walked the job with the Project Manager was aware that the system was 480 volt, 3 phase. There was a communication breakdown between DH Pace and Collins. Collins was only tasked with the electrical part of the installation and any conduilt that needed to be modified or added. Collins also wired the control switches for the doors as well and this was supposed to be done by DH Pace. The Project Manager had clear communications with the representatives from from Collins and DH Pace. Neither representative was present while the actual work was being done. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Maintenance |  | Brian St Andrews | Michael Dowell |  | Frank Brixey | I am having trouble seeing where the cause and corrective action correlate with the incident. Please clarify. The write up from Collins has some good information as well. Keith Brixey - 1/14/2020 Approved - Brixey | Frank Brixey |  | Low | [6 empty] | 7.06 Improper attempt to save time or effort | [8 empty] | 16.01 Inadequate horizontal communication between peers | Contractors did not have appropriate discussion before returning equipment to service | 38. Inadequate Communications Hardware, Software, Process | 12. Equipment Failure | [5 empty] | Property Damage |  | Michael Dowell | Shorted electrical components |  |  |  |  | 12. Equipment Failure | Brian St Andrews | DH Pace Door Company | Robert Guynes |  | Fixed Equipment |  | Michael Dowell |  |  |  |  | FALSE | [66 empty] | 9589787
9177 | Sooner Power Plant | 2019-12-28 14:30 | Member hit light pole with personal vehicle when leaving for the day. Minor scratches to light pole. | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Frank Brixey | 2020-01-20 14:44 | 2019-12-30 09:04 | 2019-12-30 09:04 | 2020-01-11 11:56 | 2020-01-11 14:30 | 2019-12-30 08:34 | 2020-01-13 11:49 |  | 2020-01-13 11:27 | Sooner PP Employee Parking Lot |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Frank Brixey |  | Member was leaving for the day in his personal vehicle. There was a very few cars in the parking lot due to the holiday and being a Saturday so the member parked vehicle in different location than normal. He did a 360 when he arrived at his vehicle. He admitted he had a lot on his mind other than the task of driving, but did not take the time to stop and focus. As he was leaving, He was looking out the driver side window at a vehicle to be sure he cleared it and did not see the light pole. Upon clearing the vehicle the member struck the light pole. The member was driving at an appropriate speed, but there was damage to his truck. There were some scratches left on the pole, but no major damage. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Michael Dowell | Frank Brixey |  | Kent Wilson | Approved. | Kent Wilson |  | Medium |  |  |  | 4.09 Preoccupation with problems | [12 empty] | Member not looking at eyes on path while operating vehicle. | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) |  | Approved by Brady Sowell
9178 | Muskogee Service Center | 2019-12-30 09:30 | While backing out of driveway, struck old fence post with rear of truck. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Randell Gilbert | 2020-01-08 10:02 | 2019-12-31 09:35 | 2019-12-31 09:35 | 2020-01-06 15:25 | 2020-01-13 09:30 | 2019-12-30 10:00 | 2020-01-08 09:30 |  |  | 3321 E. Hancock, Muskogee, Ok |  |  | Hannah Everett | Reviewed and approve CA. | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Randell Gilbert |  | Member was working ticket at 3321 E. Hancock in Muskogee. Member pulled up the driveway to locked gate, and noticed it was congested with old fence post near driveway. After getting in gate to jobsite and finishing work, member decided there was no place to turn around and backed out the way he came in. While backing out of driveway, member struck old fence post with rear of truck. Member immediately called and notified supervisor. Damage was to flange on back of truck and weld. |  |  |  | Muskogee Service Center | FALSE |  | FALSE | Construction Services |  | James Evans | Randell Gilbert |  | Chad Inman | I approve of the corrective actions. | Chad Inman |  | Low | [9 empty] | 10.04 Inadequate monitoring of construction | [6 empty] | Member backed out of congested driveway and struck old fence post. | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) | [74 empty] | TRUE |  | Muskogee | Struck Fixed Object | Backing Related | 1993-10-03 19:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear |  |  | 800783321
9179 | Sooner Power Plant | 2019-12-31 14:00 | Contractor (Diamond) was excavating North of dumper and hit a 3 inch water service pipe. Property damage. No injuries. | Level 1 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Ashley Harris | 2020-01-20 06:39 | 2019-12-31 14:03 | 2019-12-31 14:03 | 2020-01-08 09:38 | 2020-01-14 14:00 | 2019-12-31 13:44 | 2020-01-17 10:17 |  |  | Sooner Power Plant- North of the dumper. |  |  | Marcus Huddleston | No additional comments. MLH 1/20/2020 | UTS |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Ashley Harris |  | Chad Ashlock from Diamond Services Company was digging grade for crane pad on North side of the Dumper to install pipe and backfill. While digging out subgrade with a track hoe a 3 inch poly waterline was hit. The waterline was in LOTO so there were not any leaks. This line was not marked or shown on the plans that were available to diamond. The line was repaired the next day. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | UTS - Capital Projects |  | Pete Hamby | Ashley Harris |  | Robert Weaver | no comments. | Robert Weaver |  | Low | [8 empty] | 9.06 Inadequate work planning or programming | [6 empty] | 16.03. Inadequate communication between different organizations | Diamond had the wrong revision of drawings for the area they were excavating. The waterline that was hit was not marked on these drawings. | 35. Inadequate Information, Data | 9. Abnormal Operation |  |  |  |  | Sooner 10 & 11 Conveyor | Property Damage |  | Ashley Harris | 3 inch water service plastic pipe was hit by backhoe. |  |  |  |  | 2. Struck By (Hit By Moving Object) | Pete Hamby | Diamond | Diamond |  | Utility Strike |  | Ashley Harris |  |  |  |  | FALSE | [42 empty] | A 3 inch plastic water service pipe was hit by backhoe. Picture attached. | 1000 | Diamond | Utility Strike
9180 | Sooner Power Plant | 2019-12-31 13:30 | Contractor was observed working on ladder without fall protection. | Level 3 |  | TRUE | Contractor | Donnie Jones | Jesse Murray | Assigning to Kelly Casey due to fact Josh Richardson hasn't been through incident investigation yet. Josh can shadow this for experience. Brady will provide Safety resources and Matt project experience. | 2020-01-03 09:35 | Power Supply | Matthew Phillips |  | 2020-01-02 12:48 | 2020-01-02 12:48 | 2020-01-15 08:15 | 2020-01-14 13:30 | 2020-01-02 12:42 | 2020-02-11 15:58 | 2020-02-26 13:47 | 2020-01-16 16:06 | Sooner Battery Room |  |  |  |  | Power Supply |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Incident Timeline: December 31st late morning approximately 12:30 Brady Sowell went into battery room where he witnessed a 20-foot extension ladder in place appearing to access roof of battery room and a 6 foot step ladder on top of the battery room. Brady looked to identify if a retractable or beam clamp was in place for fall protection and did not find one present. He decided to come back after lunch to verify if contractors had PPE for fall prevention established. During the investigation the question was asked if the contractors plant contact or inspector was contacted. Brady stated that the inspector was off for the day and that the back up had left early that day as well. At 1:15 Brady went back to the battery room and identified an ECA contractor was working on top of the battery room wearing fall protection but was not tied off. Brady then asked contractor to come down to discuss required PPE. During this discussion contractor realized he was not tied off and knew he should be. He knew the procedure called out above 4’ and within 6’ from an unprotected edge. He stated that he did have a beam clamp and it was on top of the battery room, but he did not install it. The discussion led to the need for 100% tie off in this situation. Brady then contacted the ECA supervisor and turned over disciplinary action to ECA. Member was sent home for 3 days without pay. During the investigation ECA provided their documentation for TRA ( Safe Work Plan ) and it called out the 4 foot requirement for fall protection and the requirement for fall protection within 6 feet of an unprotected edge. It should be noted that there is a permanent ladder with a cage to access the top of the battery room, but contractor needed access behind the duct work and that’s the reason he was using the extension ladder. Greg Fulton was the ECA supervisor onsite and his statements during the investigation are included. Greg stated his members come from the Union Hall and that all training is recorded at the Hall. He was assigned the action item to get the members training records or have his supervisor to get them. His assumption was that the member had certified training. Greg stated that he demonstrated the proper way to don and doff the PPE, adjustments for fit and reminded his members the procedure and policy required. Greg also stated that typically they are assigned in pairs, but that one member of their team had called in sick that day. The question was asked during the investigation about the contractors’ experience level and Greg stated that the member had limited industrial experience which might have some bearing on the incident. It was stated that the member knew the need had the PPE needed but chose not to utilize it. Discussion generated several action items that are good learnings for the whole fleet and our contractors. A stand down was held with all contractors onsite that day (both ECA and Zachary), OGE inspectors and safety requirements and expectations were discussed. ECA is working to identify how they can supply training records for contractors coming to work at OGE sites. |  | Kelly Casey |  | Sooner Power Plant | FALSE |  | TRUE | Other |  | Brady Sowell | Matthew Phillips |  | Brian Huckabay | Approved |  | Jesse Murray | High | [5 empty] | 6.04 Lack of coaching |  | 8.2.2 Improper conduct that is not condoned: Unintentional | [8 empty] | not utilizing fall protection while working at heights | 16. Failure to Follow Procedure, Policy, Practice | 3. Fall from Elevation to Lower Level | Approved. Jesse Murray | Approved by Brady Sowell. Thorough Job by Kelly and the investigation team. |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Jesse Murray | [5 empty] | 3. Fall from Elevation to Lower Level | Brady Sowell | Zachry | Zachry |  |  |  | Matthew Phillips | [71 empty] | 9583153
9180 | Sooner Power Plant | 2019-12-31 13:30 | Contractor was observed working on ladder without fall protection. | Level 3 |  | TRUE | Contractor | Donnie Jones | Jesse Murray | Assigning to Kelly Casey due to fact Josh Richardson hasn't been through incident investigation yet. Josh can shadow this for experience. Brady will provide Safety resources and Matt project experience. | 2020-01-03 09:35 | Power Supply | Matthew Phillips |  | 2020-01-02 12:48 | 2020-01-02 12:48 | 2020-01-15 08:15 | 2020-01-14 13:30 | 2020-01-02 12:42 | 2020-02-11 15:58 | 2020-02-26 13:47 | 2020-01-16 16:06 | Sooner Battery Room |  |  |  |  | Power Supply |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Incident Timeline: December 31st late morning approximately 12:30 Brady Sowell went into battery room where he witnessed a 20-foot extension ladder in place appearing to access roof of battery room and a 6 foot step ladder on top of the battery room. Brady looked to identify if a retractable or beam clamp was in place for fall protection and did not find one present. He decided to come back after lunch to verify if contractors had PPE for fall prevention established. During the investigation the question was asked if the contractors plant contact or inspector was contacted. Brady stated that the inspector was off for the day and that the back up had left early that day as well. At 1:15 Brady went back to the battery room and identified an ECA contractor was working on top of the battery room wearing fall protection but was not tied off. Brady then asked contractor to come down to discuss required PPE. During this discussion contractor realized he was not tied off and knew he should be. He knew the procedure called out above 4’ and within 6’ from an unprotected edge. He stated that he did have a beam clamp and it was on top of the battery room, but he did not install it. The discussion led to the need for 100% tie off in this situation. Brady then contacted the ECA supervisor and turned over disciplinary action to ECA. Member was sent home for 3 days without pay. During the investigation ECA provided their documentation for TRA ( Safe Work Plan ) and it called out the 4 foot requirement for fall protection and the requirement for fall protection within 6 feet of an unprotected edge. It should be noted that there is a permanent ladder with a cage to access the top of the battery room, but contractor needed access behind the duct work and that’s the reason he was using the extension ladder. Greg Fulton was the ECA supervisor onsite and his statements during the investigation are included. Greg stated his members come from the Union Hall and that all training is recorded at the Hall. He was assigned the action item to get the members training records or have his supervisor to get them. His assumption was that the member had certified training. Greg stated that he demonstrated the proper way to don and doff the PPE, adjustments for fit and reminded his members the procedure and policy required. Greg also stated that typically they are assigned in pairs, but that one member of their team had called in sick that day. The question was asked during the investigation about the contractors’ experience level and Greg stated that the member had limited industrial experience which might have some bearing on the incident. It was stated that the member knew the need had the PPE needed but chose not to utilize it. Discussion generated several action items that are good learnings for the whole fleet and our contractors. A stand down was held with all contractors onsite that day (both ECA and Zachary), OGE inspectors and safety requirements and expectations were discussed. ECA is working to identify how they can supply training records for contractors coming to work at OGE sites. | Matthew Phillips | Kelly Casey |  | Sooner Power Plant | FALSE |  | TRUE | Other |  | Brady Sowell | Matthew Phillips |  | Brian Huckabay | Approved |  | Jesse Murray | High | [5 empty] | 6.04 Lack of coaching |  | 8.2.2 Improper conduct that is not condoned: Unintentional | [8 empty] | not utilizing fall protection while working at heights | 16. Failure to Follow Procedure, Policy, Practice | 3. Fall from Elevation to Lower Level | Approved. Jesse Murray | Approved by Brady Sowell. Thorough Job by Kelly and the investigation team. |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Jesse Murray | [5 empty] | 3. Fall from Elevation to Lower Level | Brady Sowell | Zachry | Zachry |  |  |  | Matthew Phillips | [71 empty] | 9583153
9180 | Sooner Power Plant | 2019-12-31 13:30 | Contractor was observed working on ladder without fall protection. | Level 3 |  | TRUE | Contractor | Donnie Jones | Jesse Murray | Assigning to Kelly Casey due to fact Josh Richardson hasn't been through incident investigation yet. Josh can shadow this for experience. Brady will provide Safety resources and Matt project experience. | 2020-01-03 09:35 | Power Supply | Matthew Phillips |  | 2020-01-02 12:48 | 2020-01-02 12:48 | 2020-01-15 08:15 | 2020-01-14 13:30 | 2020-01-02 12:42 | 2020-02-11 15:58 | 2020-02-26 13:47 | 2020-01-16 16:06 | Sooner Battery Room |  |  |  |  | Power Supply |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Incident Timeline: December 31st late morning approximately 12:30 Brady Sowell went into battery room where he witnessed a 20-foot extension ladder in place appearing to access roof of battery room and a 6 foot step ladder on top of the battery room. Brady looked to identify if a retractable or beam clamp was in place for fall protection and did not find one present. He decided to come back after lunch to verify if contractors had PPE for fall prevention established. During the investigation the question was asked if the contractors plant contact or inspector was contacted. Brady stated that the inspector was off for the day and that the back up had left early that day as well. At 1:15 Brady went back to the battery room and identified an ECA contractor was working on top of the battery room wearing fall protection but was not tied off. Brady then asked contractor to come down to discuss required PPE. During this discussion contractor realized he was not tied off and knew he should be. He knew the procedure called out above 4’ and within 6’ from an unprotected edge. He stated that he did have a beam clamp and it was on top of the battery room, but he did not install it. The discussion led to the need for 100% tie off in this situation. Brady then contacted the ECA supervisor and turned over disciplinary action to ECA. Member was sent home for 3 days without pay. During the investigation ECA provided their documentation for TRA ( Safe Work Plan ) and it called out the 4 foot requirement for fall protection and the requirement for fall protection within 6 feet of an unprotected edge. It should be noted that there is a permanent ladder with a cage to access the top of the battery room, but contractor needed access behind the duct work and that’s the reason he was using the extension ladder. Greg Fulton was the ECA supervisor onsite and his statements during the investigation are included. Greg stated his members come from the Union Hall and that all training is recorded at the Hall. He was assigned the action item to get the members training records or have his supervisor to get them. His assumption was that the member had certified training. Greg stated that he demonstrated the proper way to don and doff the PPE, adjustments for fit and reminded his members the procedure and policy required. Greg also stated that typically they are assigned in pairs, but that one member of their team had called in sick that day. The question was asked during the investigation about the contractors’ experience level and Greg stated that the member had limited industrial experience which might have some bearing on the incident. It was stated that the member knew the need had the PPE needed but chose not to utilize it. Discussion generated several action items that are good learnings for the whole fleet and our contractors. A stand down was held with all contractors onsite that day (both ECA and Zachary), OGE inspectors and safety requirements and expectations were discussed. ECA is working to identify how they can supply training records for contractors coming to work at OGE sites. | Brady Sowell | Kelly Casey |  | Sooner Power Plant | FALSE |  | TRUE | Other |  | Brady Sowell | Matthew Phillips |  | Brian Huckabay | Approved |  | Jesse Murray | High | [5 empty] | 6.04 Lack of coaching |  | 8.2.2 Improper conduct that is not condoned: Unintentional | [8 empty] | not utilizing fall protection while working at heights | 16. Failure to Follow Procedure, Policy, Practice | 3. Fall from Elevation to Lower Level | Approved. Jesse Murray | Approved by Brady Sowell. Thorough Job by Kelly and the investigation team. |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Jesse Murray | [5 empty] | 3. Fall from Elevation to Lower Level | Brady Sowell | Zachry | Zachry |  |  |  | Matthew Phillips | [71 empty] | 9583153
9180 | Sooner Power Plant | 2019-12-31 13:30 | Contractor was observed working on ladder without fall protection. | Level 3 |  | TRUE | Contractor | Donnie Jones | Jesse Murray | Assigning to Kelly Casey due to fact Josh Richardson hasn't been through incident investigation yet. Josh can shadow this for experience. Brady will provide Safety resources and Matt project experience. | 2020-01-03 09:35 | Power Supply | Matthew Phillips |  | 2020-01-02 12:48 | 2020-01-02 12:48 | 2020-01-15 08:15 | 2020-01-14 13:30 | 2020-01-02 12:42 | 2020-02-11 15:58 | 2020-02-26 13:47 | 2020-01-16 16:06 | Sooner Battery Room |  |  |  |  | Power Supply |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Incident Timeline: December 31st late morning approximately 12:30 Brady Sowell went into battery room where he witnessed a 20-foot extension ladder in place appearing to access roof of battery room and a 6 foot step ladder on top of the battery room. Brady looked to identify if a retractable or beam clamp was in place for fall protection and did not find one present. He decided to come back after lunch to verify if contractors had PPE for fall prevention established. During the investigation the question was asked if the contractors plant contact or inspector was contacted. Brady stated that the inspector was off for the day and that the back up had left early that day as well. At 1:15 Brady went back to the battery room and identified an ECA contractor was working on top of the battery room wearing fall protection but was not tied off. Brady then asked contractor to come down to discuss required PPE. During this discussion contractor realized he was not tied off and knew he should be. He knew the procedure called out above 4’ and within 6’ from an unprotected edge. He stated that he did have a beam clamp and it was on top of the battery room, but he did not install it. The discussion led to the need for 100% tie off in this situation. Brady then contacted the ECA supervisor and turned over disciplinary action to ECA. Member was sent home for 3 days without pay. During the investigation ECA provided their documentation for TRA ( Safe Work Plan ) and it called out the 4 foot requirement for fall protection and the requirement for fall protection within 6 feet of an unprotected edge. It should be noted that there is a permanent ladder with a cage to access the top of the battery room, but contractor needed access behind the duct work and that’s the reason he was using the extension ladder. Greg Fulton was the ECA supervisor onsite and his statements during the investigation are included. Greg stated his members come from the Union Hall and that all training is recorded at the Hall. He was assigned the action item to get the members training records or have his supervisor to get them. His assumption was that the member had certified training. Greg stated that he demonstrated the proper way to don and doff the PPE, adjustments for fit and reminded his members the procedure and policy required. Greg also stated that typically they are assigned in pairs, but that one member of their team had called in sick that day. The question was asked during the investigation about the contractors’ experience level and Greg stated that the member had limited industrial experience which might have some bearing on the incident. It was stated that the member knew the need had the PPE needed but chose not to utilize it. Discussion generated several action items that are good learnings for the whole fleet and our contractors. A stand down was held with all contractors onsite that day (both ECA and Zachary), OGE inspectors and safety requirements and expectations were discussed. ECA is working to identify how they can supply training records for contractors coming to work at OGE sites. | William Cash | Kelly Casey |  | Sooner Power Plant | FALSE |  | TRUE | Other |  | Brady Sowell | Matthew Phillips |  | Brian Huckabay | Approved |  | Jesse Murray | High | [5 empty] | 6.04 Lack of coaching |  | 8.2.2 Improper conduct that is not condoned: Unintentional | [8 empty] | not utilizing fall protection while working at heights | 16. Failure to Follow Procedure, Policy, Practice | 3. Fall from Elevation to Lower Level | Approved. Jesse Murray | Approved by Brady Sowell. Thorough Job by Kelly and the investigation team. |  |  |  | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Jesse Murray | [5 empty] | 3. Fall from Elevation to Lower Level | Brady Sowell | Zachry | Zachry |  |  |  | Matthew Phillips | [71 empty] | 9583153
9181 | Ardmore Service Center | 2020-01-02 18:30 | While travelling home from outage at Valley View substation several deer ran out in front of vehicle. Avoided all but one that clipped the drivers side of the vehicle. No obvious damage to the vehicle at this time | Level 3 |  | TRUE | Vehicle | Andrea Dennis | Lindle Coleman | Simple investigation to include review and determine Basic facts, speed, ect. | 2020-01-03 09:56 | Power Delivery | Bradley Kosemund | 2020-01-20 15:57 | 2020-01-02 18:58 | 2020-01-02 18:58 | 2020-01-06 07:59 | 2020-01-16 18:30 | 2020-01-02 18:51 | 2020-01-14 05:09 | 2020-01-16 10:37 | 2020-01-07 12:56 | State highway 9A 6 miles north of Konawa |  |  | Andrea Dennis | I approve. | T&D Ops |  | Level 3 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Bradley Kosemund |  | While travelling home from a outage in Ada at about 67 miles per hour I topped a hill and saw, I believe 4 deer. One was already to the right side of the road and the other three were coming out of the ditch on the left side of the road. I was able to slow and then veer right, miss the deer on the right and I clipped the lead deer with the left side of the vehicle. Upon investigation in the daylight there was a small amount of deer snot on the left front fender behind the headlight. No other marks on the vehicle. Traveling around 6:30pm it was dark clear weather, good road conditions. It was on highway 9A. Speed Limit is 65mph. Asphalt hwy new paved road, no shoulders. Driving white OGE 2012 Chevy impala. speed at contact was estimated to be lower than traveling speed due to braking. no damage, no injury | Cody Magby | Bradley Kosemund |  | Ardmore Service Center | FALSE |  | TRUE | PD Operations Services |  | Bradley Kosemund | Cody Magby |  | James Hutchison | I have reviewed this report and agree with the corrective action. The Sub Ops supervisors will be instructed to cover this topic during their February safety meeting. | James Hutchison | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Driver was unable to avoid being struck by a deer. Did well to avoid the entire herd and stay on the roadway. | 39. Road Conditions | 2. Struck By (Hit By Moving Object) | Member ranked as a high due to an everyday hazard, however. Safety Prof followed up and determined could have been a low. coached member on proper risk ranking. approved | I approve cm
9182 | Enid Service Center | 2020-01-02 12:00 | Members were traveling south on 9th street in Woodward through downtown. They hit a bump in the road, heard something land on the roof of the van. They pulled over immediately and discovered the cap on the stick tube had fallen off. Nothing had slid out of the tube. They removed all the tools from the tube, glued the cap back on and left it empty for now so the glue can cure. | Level 1 |  | TRUE | Vehicle |  |  |  |  | Power Delivery | Zachary Hamen | 2020-01-13 11:26 | 2020-01-03 08:04 | 2020-01-03 08:04 | 2020-01-03 08:18 | 2020-01-16 12:00 | 2020-01-03 07:52 | 2020-01-08 07:11 |  |  | Southbound lane. 9th street downtown Woodward OK. |  |  | Luke Kennedy | approved 1/13/20 | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Zachary Hamen |  | Members were traveling south on 9th street in Woodward through downtown. They hit a bump in the road, heard something land on the roof of the van. They pulled over immediately and discovered the cap on the tube had fallen off. Nothing had slid out of the tube. They removed all the tools from the tube, glued the cap back on and left it empty for now so the glue can cure. 2008 Van. Tube has been in service for at least 12 years. Glue looked worn out. |  |  |  | Enid Service Center | FALSE |  | TRUE | PD Operations Services |  | Lee Olmstead | Zachary Hamen |  | Dustin Kingcade | Cap has been secured. | Dustin Kingcade |  | Low | [14 empty] | 15.03 Inadequate inspection and/or monitoring |  | The glue that failed allowed the cap to fall off. | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure
9183 | Sooner Power Plant | 2020-01-03 10:30 | A approximately 3 foot by 3 foot sheet metal cover that belongs on the side of 1A drum room vent fan was found on the deck grating on level 11. vent fan is located on the roof of the drum room. I am assuming the wind caught cover and tore it loose. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Daniel Dickinson | 2020-01-22 13:53 | 2020-01-03 11:56 | 2020-01-03 11:56 | 2020-01-05 14:29 | 2020-01-17 10:30 | 2020-01-03 11:47 | 2020-01-10 12:08 |  | 2020-01-09 07:09 | Sooner PP, #1 boiler level 11, east side, outside north drum room door. |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Daniel Dickinson |  | While walking down #1 boiler, a 36" X 48" piece of metal was found next to the north east drum room door on level 11. Door came from 1A drum room vent fan enclosure, which is located on top of the drum room. Door was found with 1 screw still in door, and judging from the damage to corner of the door, I assume that the wind tore door off of the enclosure and it fell to the lower level. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Operations |  | Daniel Dickinson | Daniel Dickinson |  | Alexander Taybah | I approve. | Alexander Taybah |  | Medium | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | 1A drum room vent fan door came loose and fell to a lower level. I am assuming the wind caused this, door was found on level below vent fan. | 23. Defective Tools, Equipment or Materials | 2. Struck By (Hit By Moving Object) |  | approved by brady sowell
9184 | Ardmore Service Center | 2019-12-31 | Member was traveling east on Highway 7 just east of Davis when a deer ran onto the highway. The deer made slight contact with the right front of the vehicle. There was no visible damage the member could see but a few days later he noticed the windshield wiper fluid reservoir had a small leak. He found a small crack in the reservoir. | Level 2 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Terry Looney | 2020-02-08 11:34 | 2020-01-06 11:10 | 2020-01-06 11:10 | 2020-01-06 11:24 | 2020-01-14 | 2020-01-01 11:03 | 2020-02-06 15:19 |  | 2020-01-07 12:57 | 2.5 miles east of Davis on Highway 7 |  |  | Lindle Coleman | Approved | T&D Ops |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Terry Looney |  | Mr. Beam was travelling east on highway 7 around 5:50 pm, driving approximately 45 mph when a deer ran onto the highway and made contact with right front end. There was no visible damage and the deer was not on the shoulder or highway. After a few days Bruce noticed a small crack in his window wiper fluid reservoir under the hood. |  |  |  | Ardmore Service Center | FALSE |  | FALSE | PD Operations Services |  | Bruce Beam | Terry Looney |  | Kenneth McKinzie | Reporting this just for record and we have no proof the deer caused any damage. | Kenneth McKinzie |  | Medium |  | 2.07 Slow reaction time | [14 empty] | deer ran in front of OGE vehicle making minor contact | 19. Failure to React, Correct | 2. Struck By (Hit By Moving Object) |  | I approve cm | [72 empty] | FALSE |  | Davis | Animal-related |  | 1989-12-03 18:00 |  | FALSE |  |  | Night |  |  | Concrete/Pavement |  | Clear
9185 | Sooner Power Plant | 2020-01-06 10:30 | While replacing one of the turbine floor window sets. The Zachry crew was installing an 18’ long piece of 2”x4” rectangle tubing to support the seal plate. The crew was using C-clamps to hold the tubing in place. When the members tried to adjust the tubing it slipped out of the C-clamps and fell down the wall approximately 10’ landing on the wall girt just below the turbine floor. No members were injured and no property damaged. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Lance Lantz | 2020-01-22 13:56 | 2020-01-06 16:11 | 2020-01-06 16:11 | 2020-01-13 15:54 | 2020-01-20 10:30 | 2020-01-06 15:51 | 2020-01-14 16:09 |  | 2020-01-14 09:40 | Sooner Power Plant Unit 2 Turbine Floor |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Lance Lantz |  | The Zachry base crew was tasked with replacing six(6) of the lower south T/G windows. The windows are being replaced with roll up glass overhead doors. The crew was in the process of installing the seal plate when the incident occurred. This process involves placing a 2”x4” rectangle tubing on the lower flange of the window opening. Then installing a piece of stainless steel flashing over the top to channel water away from the door seal. After further investigation into the incident. It was discovered the crew had performed this task on six(6) other window installs. On the previous installs the crew would use at least three(3) members in conjunction with the C-clamps to hold the rectangle tubing. On this day the other members from the crew were assisting the OG&E plant contact with hoisting man-lifts to the turbine floor to facilitate the rest of the window replacement. The two members had discussed the plan to place the rectangle tubing. The helper voiced concerns with doing the task with only two(2) people. The welder thought with the assistance of the C-clamps they could get the rectangle tubing tacked into place. The rectangle tubing was lifted by the two(2) members into place and the C-clamp was placed on one end. The members were attempting to get the other end in place and clamped down when the rectangle tubing slipped out of the first C-clamp. This caused the rectangle tubing to fall on the first end that was clamped and the members were unable to hold onto the other end. The rectangle tubing was being placed approximately 3’ off the turbine deck floor. When the rectangle tubing dropped it slid between the floor and the outer wall. The gap between the floor and the wall was approximately 12”. The tubing landed on a wall girt that was about 7’ below the level of the turbine floor. This area had cross braces and conduit that kept the rectangle tubing from being able to come out from against the wall. The area and the conduits were inspected and no other damage was found. The area on the floor below where the work was being performed was not barricaded off. Fire blanket was being used on turbine floor at each end of the rectangle tubing to prevent sparks from falling to lower levels. The blanket was not secured nor was it used to catch dropped objects. No members were injured and no property damaged. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Lance Lantz | Lance Lantz |  | Frank Brixey | Approved | Frank Brixey |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [10 empty] | 16.01 Inadequate horizontal communication between peers | failure to stop work until more members were available to assist with the install. | 36. Inadequate Preparation, Planning | 3. Fall from Elevation to Lower Level |  | Approved |  |  |  | Property Damage |  | Lance Lantz | [5 empty] | 2. Struck By (Hit By Moving Object) | Lance Lantz | Zachry | James Williams |  |  |  | Lance Lantz | [71 empty] | 615675
9185 | Sooner Power Plant | 2020-01-06 10:30 | While replacing one of the turbine floor window sets. The Zachry crew was installing an 18’ long piece of 2”x4” rectangle tubing to support the seal plate. The crew was using C-clamps to hold the tubing in place. When the members tried to adjust the tubing it slipped out of the C-clamps and fell down the wall approximately 10’ landing on the wall girt just below the turbine floor. No members were injured and no property damaged. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Lance Lantz | 2020-01-22 13:56 | 2020-01-06 16:11 | 2020-01-06 16:11 | 2020-01-13 15:54 | 2020-01-20 10:30 | 2020-01-06 15:51 | 2020-01-14 16:09 |  | 2020-01-14 09:40 | Sooner Power Plant Unit 2 Turbine Floor |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Lance Lantz |  | The Zachry base crew was tasked with replacing six(6) of the lower south T/G windows. The windows are being replaced with roll up glass overhead doors. The crew was in the process of installing the seal plate when the incident occurred. This process involves placing a 2”x4” rectangle tubing on the lower flange of the window opening. Then installing a piece of stainless steel flashing over the top to channel water away from the door seal. After further investigation into the incident. It was discovered the crew had performed this task on six(6) other window installs. On the previous installs the crew would use at least three(3) members in conjunction with the C-clamps to hold the rectangle tubing. On this day the other members from the crew were assisting the OG&E plant contact with hoisting man-lifts to the turbine floor to facilitate the rest of the window replacement. The two members had discussed the plan to place the rectangle tubing. The helper voiced concerns with doing the task with only two(2) people. The welder thought with the assistance of the C-clamps they could get the rectangle tubing tacked into place. The rectangle tubing was lifted by the two(2) members into place and the C-clamp was placed on one end. The members were attempting to get the other end in place and clamped down when the rectangle tubing slipped out of the first C-clamp. This caused the rectangle tubing to fall on the first end that was clamped and the members were unable to hold onto the other end. The rectangle tubing was being placed approximately 3’ off the turbine deck floor. When the rectangle tubing dropped it slid between the floor and the outer wall. The gap between the floor and the wall was approximately 12”. The tubing landed on a wall girt that was about 7’ below the level of the turbine floor. This area had cross braces and conduit that kept the rectangle tubing from being able to come out from against the wall. The area and the conduits were inspected and no other damage was found. The area on the floor below where the work was being performed was not barricaded off. Fire blanket was being used on turbine floor at each end of the rectangle tubing to prevent sparks from falling to lower levels. The blanket was not secured nor was it used to catch dropped objects. No members were injured and no property damaged. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Lance Lantz | Lance Lantz |  | Frank Brixey | Approved | Frank Brixey |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [10 empty] | 16.01 Inadequate horizontal communication between peers | failure to stop work until more members were available to assist with the install. | 36. Inadequate Preparation, Planning | 3. Fall from Elevation to Lower Level |  | Approved |  |  |  | Injury / Illness |  | Lance Lantz | [5 empty] | 2. Struck By (Hit By Moving Object) | Lance Lantz | Zachry | James Williams |  |  |  | Lance Lantz | [71 empty] | 615675
9186 | Muskogee Power Plant | 2020-01-06 17:00 | Making turn at gate the welding machine tipped over and slipped off of tommy lift. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Jerry Knight |  | 2020-01-07 12:16 | 2020-01-07 12:16 | 2020-02-18 17:25 | 2020-01-20 17:00 | 2020-01-07 12:02 |  |  |  | East of unit 6 south main gate |  |  |  |  | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Jerry Knight |  | To much lead was rolled up on machine causing the welder to be top heavy and tip over. The lead will weigh .5 lbs per feet and there was 200 feet rolled up hanging from the top of the cart the welder was setting on. That would make the cart very top heavy having 100 lbs three feet in the air hanging on the side of the cart. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | Maintenance |  | Robert Wright | Jerry Knight |  | Andy Hedge | Reviewed and returned to investigation due to more information needed in the detailed description. Andy Hedge 2/10/20 | Andy Hedge |  | Low | [10 empty] | 11.09 Improper transporting of materials | [5 empty] | Welder fell over because of pot hole in road causing the lead to fall off the back of truck and pulling the weld over with it. | 15. Using Equipment Improperly | 3. Fall from Elevation to Lower Level | [68 empty] | Welder was in cart so there was no Damage. | 1 |  | Portable Tool
9187 | Metro Service Center | 2020-01-06 07:30 | On January 6th, 2020 member was sent to Remington park tap to perform switching on S1850. When member opened the 138kv switch the switch blades opened but arcing whips did not fully open allowing load to remain on the line. TCC noticed the line still had load on it and advised the member how to proceed. With help from the transmission coordinator the member was able to get the switch to open properly and hang the hold tag. | Level 2 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Gerald Smith | 2020-01-20 07:29 | 2020-01-07 12:25 |  | 2020-01-15 10:20 | 2020-02-17 07:30 | 2020-01-06 09:00 | 2020-01-20 07:09 |  | 2020-01-16 07:55 | Remington Park Tap |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Gerald Smith |  | On January 6th, 2020 member was sent to Remington park tap to perform switching on S1850. When member opened the 138kv switch the switch blades opened but arcing whips did not fully open allowing load to remain on the line. TCC noticed the line still had load on it and advised the member how to proceed. With help from the transmission coordinator the member was able to get the switch to open properly and hang the hold tag. |  |  |  | Metro Service Center | FALSE |  | FALSE | PD Operations Services |  | Loren Hastings | Gerald Smith |  | James Hutchison | I have reviewed this incident and agree with it's finding and corrective action. | James Hutchison |  | Medium | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | Whips did not clear the switch. | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure |  | approve cm
9188 | Shawnee Service Center | 2020-01-07 06:30 | Members were attempting to close transformer lid. Upon trying to close the transformer lid it was recognized that the cable was in the way of the door. Member then used shotgun stick to move cable out of the way. While moving cable a small flash occurred. No injuries or damage occurred. Bad order elbow was discovered and replaced. 19.9 KV 1/0 cable. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Delivery | Stacy Ragan | 2020-01-16 10:54 | 2020-01-07 13:52 | 2020-01-07 13:52 | 2020-01-14 07:32 | 2020-01-21 06:30 | 2020-01-07 13:36 | 2020-01-14 15:32 |  | 2020-01-14 07:48 | 2001 Hazy Brook Dr. Pad Mount Transformer 83040 |  |  | Lindle Coleman | I had a question on CA aligning with casual factors, after follow up We found that the construction standard was adequate. equip was built more than 10 years ago, no records on who constructed could be found. We could not identify why it was constructed incorrectly. Elbow was cracked due to the cable being to long for 10 years. It was discussed on the incident call and supervisors will re-visit with members on not setting traps. No other corrective actions were entered at this time. we can control and prevent injury by continuing to follow safe work practices that are designed to protect members when equip issues like this show up. | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Stacy Ragan |  | Trouble shooter was responding to outage call on an underground loop. Trouble shooter called for another qualified member to assist, due to the job scope. Members found bad underground primary run between Trans 74086 and 74085, they then opened switch #1 and danger tagged (74085). Then they opened switch #2 and danger tagged it (Trans 74085). Then members went to N/O trans 83040 and closed in switch 1 to restore outage. Members were attempting to close transformer lid. Upon trying to close the transformer lid it was recognized that the cable was in the way of the door. Member then used shotgun stick to move cable out of the way. While moving cable a small flash occurred. No injuries or damage occurred. Bad order elbow was discovered and replaced. Facts Ascertained: - 19.9 KV - Elastimold Elbow had small crack and flashed over to the concentric bleeder to elbow - Both members were wearing class 4 Rubber gloves, safety glasses, FR Clothing, Hard Hats, Florescent Vests - Member performing switching was using a shotgun stick from the side and was approximately 6' from the transformer - Qualified observer was approximately 10' from the transformer - Tailboard was completed prior to the job and specifically discussed the voltage and using the insulated shotgun stick - Incident occurred at 6:30 AM while it was still dark outside (limited visibility) |  |  |  | Shawnee Service Center | FALSE |  | TRUE | Construction Services |  | Christopher Procell | Stacy Ragan |  | Steve Watkins | Approve | Steve Watkins |  | Medium | [9 empty] | 10.05 Inadequate assessment of operational readiness | [6 empty] | Elastimold switch was cracked. | 23. Defective Tools, Equipment or Materials | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Members implemented the proper work practices/procedures to prevent injury from a potential arc flash. Their is opportunity to share this information with our members and increase awareness of why following OGE work practices/procedures is so important. | [90 empty] | 000607074311
9188 | Shawnee Service Center | 2020-01-07 06:30 | Members were attempting to close transformer lid. Upon trying to close the transformer lid it was recognized that the cable was in the way of the door. Member then used shotgun stick to move cable out of the way. While moving cable a small flash occurred. No injuries or damage occurred. Bad order elbow was discovered and replaced. 19.9 KV 1/0 cable. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Delivery | Stacy Ragan | 2020-01-16 10:54 | 2020-01-07 13:52 | 2020-01-07 13:52 | 2020-01-14 07:32 | 2020-01-21 06:30 | 2020-01-07 13:36 | 2020-01-14 15:32 |  | 2020-01-14 07:48 | 2001 Hazy Brook Dr. Pad Mount Transformer 83040 |  |  | Lindle Coleman | I had a question on CA aligning with casual factors, after follow up We found that the construction standard was adequate. equip was built more than 10 years ago, no records on who constructed could be found. We could not identify why it was constructed incorrectly. Elbow was cracked due to the cable being to long for 10 years. It was discussed on the incident call and supervisors will re-visit with members on not setting traps. No other corrective actions were entered at this time. we can control and prevent injury by continuing to follow safe work practices that are designed to protect members when equip issues like this show up. | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Stacy Ragan |  | Trouble shooter was responding to outage call on an underground loop. Trouble shooter called for another qualified member to assist, due to the job scope. Members found bad underground primary run between Trans 74086 and 74085, they then opened switch #1 and danger tagged (74085). Then they opened switch #2 and danger tagged it (Trans 74085). Then members went to N/O trans 83040 and closed in switch 1 to restore outage. Members were attempting to close transformer lid. Upon trying to close the transformer lid it was recognized that the cable was in the way of the door. Member then used shotgun stick to move cable out of the way. While moving cable a small flash occurred. No injuries or damage occurred. Bad order elbow was discovered and replaced. Facts Ascertained: - 19.9 KV - Elastimold Elbow had small crack and flashed over to the concentric bleeder to elbow - Both members were wearing class 4 Rubber gloves, safety glasses, FR Clothing, Hard Hats, Florescent Vests - Member performing switching was using a shotgun stick from the side and was approximately 6' from the transformer - Qualified observer was approximately 10' from the transformer - Tailboard was completed prior to the job and specifically discussed the voltage and using the insulated shotgun stick - Incident occurred at 6:30 AM while it was still dark outside (limited visibility) |  |  |  | Shawnee Service Center | FALSE |  | TRUE | Construction Services |  | Christopher Procell | Stacy Ragan |  | Steve Watkins | Approve | Steve Watkins |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | During initial installation cable was termed too long | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Members implemented the proper work practices/procedures to prevent injury from a potential arc flash. Their is opportunity to share this information with our members and increase awareness of why following OGE work practices/procedures is so important. | [90 empty] | 000607074311
9189 | Enid Service Center | 2020-01-07 10:00 | member had applied cover up and was putting a dead end wrap on when the 7W3 copper broke a few feet from him and fell to the ground. | Level 1 |  | TRUE | Property Damage |  |  |  |  | Power Delivery | Tyler Scott | 2020-01-13 07:38 | 2020-01-08 09:11 | 2020-01-08 09:11 | 2020-01-08 09:21 | 2020-01-21 10:00 | 2020-01-08 08:58 | 2020-01-08 10:10 |  |  | Reed rd and Leona Mitchell Waukomis, Ok |  |  | Luke Kennedy | Approved - I believe replacing the obsolete wire is necessary to prevent further instances of this at that location going forward. | T&D Ops |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Tyler Scott |  | The crew was setting a pole down the line went to this location to cut a gap in the line to kill it out. Member applied cover up and was installing dead end bell and wraps to cut a gap when the 7W3 wire broke a few feet down the line from him causing it to fall to the ground. After the wire fell the foreman verified the 30 amp fuse was blown and repaired the wire and refused and closed the cutout. |  |  |  | Enid Service Center | FALSE |  | TRUE | Construction Services |  | Joshua Shepherd | Tyler Scott |  | Chad Inman | I'm appreciative that there were no injuries or property damages and I approve of the corrective actions listed above. This is a opportune moment for the reliability team to step into action and support our internal and external customers, by continually promoting our Beliefs through Achieving Together. | Chad Inman |  | Low | [14 empty] | 15.02 Improper extension of service life |  | wire was obsolete causing it to break | 06. Using Defective Equipment | 12. Equipment Failure
9190 | Shawnee Service Center | 2020-01-08 06:30 | Traveling South on highway 9A approximately 6:30 am and hit a raccoon crossing the highway. Damage to lower grill of OGE car. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Bradley Kosemund | 2020-01-08 12:42 | 2020-01-08 12:34 | 2020-01-08 12:34 | 2020-01-08 12:37 | 2020-01-22 06:30 | 2020-01-08 12:21 |  |  |  | 2 miles north of Konawa on Highway 9A |  |  | Cody Magby | Nothing more to investigate. Animal was in the roadway, driver was going the speed limit, in the dark animal was tough to see in time to miss it. cm | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | [6 empty] | Shawnee Service Center | FALSE |  | FALSE | PD Operations Services |  | Bradley Kosemund | Cody Magby |  |  |  | James Hutchison |  | Low | [93 empty] | FALSE |  | Konawa | Animal-related |  | 1984-01-08 18:00 |  | FALSE |  |  | Night |  |  | Concrete/Pavement |  | Clear
9191 | Muskogee Power Plant | 2020-01-08 | Fuel/Operations Multi Craft members were hauling coal with scrapers to assist with Conveyor 14 repair and putting water out for dust mitigation. Operator had emptied his load and was heading back South to retrieve another load when Operator on Water Wagon discovered the failure. CAT Coal Scraper F38-899 Rear Transmission failed. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Joel Leavell | 2020-02-26 14:22 | 2020-01-08 20:28 | 2020-01-08 20:28 | 2020-02-17 07:13 | 2020-01-22 | 2020-01-08 00:15 | 2020-02-18 10:45 |  |  | Muskogee PP Coal Pile. |  |  | Robert Wright | Approved Bob Wright | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Rodney Hyslope |  | Member was operating scraper on night shift. member had just unloaded scrapper coming around south end of coal pile , headed to get another load of coal when the water truck operator notified the scrapper operator to take his scrapper to the shop. the water truck operator was following the scraper and noticed parts laying in the roadway from the scraper. member on scraper said he never felt anything out of the norm. day shift came in and found the scraper still on the coal pile. found the drive shaft to the rear transmission had sheared the mounting bolts and busted the transmission housing. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Fuel Supply |  | Nathan Webb | Joel Leavell |  | Darcey Hayes | I feel Anthony and Rodney addressed all possible causes and told the story to the best of their knowledge and investigation. | Darcey Hayes |  | Low |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching | [7 empty] | 14.02.4 Inadequate communication of standards: training |  |  | improper training | 34. Inadequate Instructions, Procedures | 12. Equipment Failure
9191 | Muskogee Power Plant | 2020-01-08 | Fuel/Operations Multi Craft members were hauling coal with scrapers to assist with Conveyor 14 repair and putting water out for dust mitigation. Operator had emptied his load and was heading back South to retrieve another load when Operator on Water Wagon discovered the failure. CAT Coal Scraper F38-899 Rear Transmission failed. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Joel Leavell | 2020-02-26 14:22 | 2020-01-08 20:28 | 2020-01-08 20:28 | 2020-02-17 07:13 | 2020-01-22 | 2020-01-08 00:15 | 2020-02-18 10:45 |  |  | Muskogee PP Coal Pile. |  |  | Robert Wright | Approved Bob Wright | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Rodney Hyslope |  | Member was operating scraper on night shift. member had just unloaded scrapper coming around south end of coal pile , headed to get another load of coal when the water truck operator notified the scrapper operator to take his scrapper to the shop. the water truck operator was following the scraper and noticed parts laying in the roadway from the scraper. member on scraper said he never felt anything out of the norm. day shift came in and found the scraper still on the coal pile. found the drive shaft to the rear transmission had sheared the mounting bolts and busted the transmission housing. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Fuel Supply |  | Nathan Webb | Joel Leavell |  | Darcey Hayes | I feel Anthony and Rodney addressed all possible causes and told the story to the best of their knowledge and investigation. | Darcey Hayes |  | Low |  |  |  |  | 5.01 Lack of experience | 6.02 Inadequate practice | [7 empty] | 14.02.4 Inadequate communication of standards: training |  |  | improper training | 34. Inadequate Instructions, Procedures | 12. Equipment Failure
9191 | Muskogee Power Plant | 2020-01-08 | Fuel/Operations Multi Craft members were hauling coal with scrapers to assist with Conveyor 14 repair and putting water out for dust mitigation. Operator had emptied his load and was heading back South to retrieve another load when Operator on Water Wagon discovered the failure. CAT Coal Scraper F38-899 Rear Transmission failed. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Joel Leavell | 2020-02-26 14:22 | 2020-01-08 20:28 | 2020-01-08 20:28 | 2020-02-17 07:13 | 2020-01-22 | 2020-01-08 00:15 | 2020-02-18 10:45 |  |  | Muskogee PP Coal Pile. |  |  | Robert Wright | Approved Bob Wright | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Rodney Hyslope |  | Member was operating scraper on night shift. member had just unloaded scrapper coming around south end of coal pile , headed to get another load of coal when the water truck operator notified the scrapper operator to take his scrapper to the shop. the water truck operator was following the scraper and noticed parts laying in the roadway from the scraper. member on scraper said he never felt anything out of the norm. day shift came in and found the scraper still on the coal pile. found the drive shaft to the rear transmission had sheared the mounting bolts and busted the transmission housing. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Fuel Supply |  | Nathan Webb | Joel Leavell |  | Darcey Hayes | I feel Anthony and Rodney addressed all possible causes and told the story to the best of their knowledge and investigation. | Darcey Hayes |  | Low |  |  |  |  | 5.03 Inadequate initial training | 6.04 Lack of coaching | [7 empty] | 14.02.4 Inadequate communication of standards: training |  |  | improper training | 34. Inadequate Instructions, Procedures | 12. Equipment Failure
9191 | Muskogee Power Plant | 2020-01-08 | Fuel/Operations Multi Craft members were hauling coal with scrapers to assist with Conveyor 14 repair and putting water out for dust mitigation. Operator had emptied his load and was heading back South to retrieve another load when Operator on Water Wagon discovered the failure. CAT Coal Scraper F38-899 Rear Transmission failed. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Joel Leavell | 2020-02-26 14:22 | 2020-01-08 20:28 | 2020-01-08 20:28 | 2020-02-17 07:13 | 2020-01-22 | 2020-01-08 00:15 | 2020-02-18 10:45 |  |  | Muskogee PP Coal Pile. |  |  | Robert Wright | Approved Bob Wright | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Rodney Hyslope |  | Member was operating scraper on night shift. member had just unloaded scrapper coming around south end of coal pile , headed to get another load of coal when the water truck operator notified the scrapper operator to take his scrapper to the shop. the water truck operator was following the scraper and noticed parts laying in the roadway from the scraper. member on scraper said he never felt anything out of the norm. day shift came in and found the scraper still on the coal pile. found the drive shaft to the rear transmission had sheared the mounting bolts and busted the transmission housing. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Fuel Supply |  | Nathan Webb | Joel Leavell |  | Darcey Hayes | I feel Anthony and Rodney addressed all possible causes and told the story to the best of their knowledge and investigation. | Darcey Hayes |  | Low |  |  |  |  | 5.03 Inadequate initial training | 6.02 Inadequate practice | [7 empty] | 14.02.4 Inadequate communication of standards: training |  |  | improper training | 34. Inadequate Instructions, Procedures | 12. Equipment Failure
9191 | Muskogee Power Plant | 2020-01-08 | Fuel/Operations Multi Craft members were hauling coal with scrapers to assist with Conveyor 14 repair and putting water out for dust mitigation. Operator had emptied his load and was heading back South to retrieve another load when Operator on Water Wagon discovered the failure. CAT Coal Scraper F38-899 Rear Transmission failed. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Joel Leavell | 2020-02-26 14:22 | 2020-01-08 20:28 | 2020-01-08 20:28 | 2020-02-17 07:13 | 2020-01-22 | 2020-01-08 00:15 | 2020-02-18 10:45 |  |  | Muskogee PP Coal Pile. |  |  | Robert Wright | Approved Bob Wright | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Rodney Hyslope |  | Member was operating scraper on night shift. member had just unloaded scrapper coming around south end of coal pile , headed to get another load of coal when the water truck operator notified the scrapper operator to take his scrapper to the shop. the water truck operator was following the scraper and noticed parts laying in the roadway from the scraper. member on scraper said he never felt anything out of the norm. day shift came in and found the scraper still on the coal pile. found the drive shaft to the rear transmission had sheared the mounting bolts and busted the transmission housing. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Fuel Supply |  | Nathan Webb | Joel Leavell |  | Darcey Hayes | I feel Anthony and Rodney addressed all possible causes and told the story to the best of their knowledge and investigation. | Darcey Hayes |  | Low |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching | [7 empty] | 14.02.4 Inadequate communication of standards: training |  |  | during operation of this equipt. if not operated properly, coming in at too high of a speed or trying to dig ( scrap ) in too high of gear, or not pushing with the rear engine properly, can cause the rear wheels to skip or slip and grab which causes a lot of torque on the drive shaft. There is a transmission lock on the hydraulic control lever that should be used during digging, this locks in the transmissions in gear where they are unable to shift. While not digging this transmission lock should be unlocked, which in turn lets the transmissions shift through each sequence. The bolts that mount the yoke of the drive shaft to the transmission housing were found to have been sheared completely off. Once this happened the drive shaft continued to spin and break anything it came in contact with, such as the transmission housing etc. | 15. Using Equipment Improperly | 9. Abnormal Operation
9191 | Muskogee Power Plant | 2020-01-08 | Fuel/Operations Multi Craft members were hauling coal with scrapers to assist with Conveyor 14 repair and putting water out for dust mitigation. Operator had emptied his load and was heading back South to retrieve another load when Operator on Water Wagon discovered the failure. CAT Coal Scraper F38-899 Rear Transmission failed. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Joel Leavell | 2020-02-26 14:22 | 2020-01-08 20:28 | 2020-01-08 20:28 | 2020-02-17 07:13 | 2020-01-22 | 2020-01-08 00:15 | 2020-02-18 10:45 |  |  | Muskogee PP Coal Pile. |  |  | Robert Wright | Approved Bob Wright | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Rodney Hyslope |  | Member was operating scraper on night shift. member had just unloaded scrapper coming around south end of coal pile , headed to get another load of coal when the water truck operator notified the scrapper operator to take his scrapper to the shop. the water truck operator was following the scraper and noticed parts laying in the roadway from the scraper. member on scraper said he never felt anything out of the norm. day shift came in and found the scraper still on the coal pile. found the drive shaft to the rear transmission had sheared the mounting bolts and busted the transmission housing. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Fuel Supply |  | Nathan Webb | Joel Leavell |  | Darcey Hayes | I feel Anthony and Rodney addressed all possible causes and told the story to the best of their knowledge and investigation. | Darcey Hayes |  | Low |  |  |  |  | 5.03 Inadequate initial training | 6.04 Lack of coaching | [7 empty] | 14.02.4 Inadequate communication of standards: training |  |  | during operation of this equipt. if not operated properly, coming in at too high of a speed or trying to dig ( scrap ) in too high of gear, or not pushing with the rear engine properly, can cause the rear wheels to skip or slip and grab which causes a lot of torque on the drive shaft. There is a transmission lock on the hydraulic control lever that should be used during digging, this locks in the transmissions in gear where they are unable to shift. While not digging this transmission lock should be unlocked, which in turn lets the transmissions shift through each sequence. The bolts that mount the yoke of the drive shaft to the transmission housing were found to have been sheared completely off. Once this happened the drive shaft continued to spin and break anything it came in contact with, such as the transmission housing etc. | 15. Using Equipment Improperly | 9. Abnormal Operation
9191 | Muskogee Power Plant | 2020-01-08 | Fuel/Operations Multi Craft members were hauling coal with scrapers to assist with Conveyor 14 repair and putting water out for dust mitigation. Operator had emptied his load and was heading back South to retrieve another load when Operator on Water Wagon discovered the failure. CAT Coal Scraper F38-899 Rear Transmission failed. | Level 1 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Joel Leavell | 2020-02-26 14:22 | 2020-01-08 20:28 | 2020-01-08 20:28 | 2020-02-17 07:13 | 2020-01-22 | 2020-01-08 00:15 | 2020-02-18 10:45 |  |  | Muskogee PP Coal Pile. |  |  | Robert Wright | Approved Bob Wright | Power Supply |  | Level 1 | Property Damage |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Rodney Hyslope |  | Member was operating scraper on night shift. member had just unloaded scrapper coming around south end of coal pile , headed to get another load of coal when the water truck operator notified the scrapper operator to take his scrapper to the shop. the water truck operator was following the scraper and noticed parts laying in the roadway from the scraper. member on scraper said he never felt anything out of the norm. day shift came in and found the scraper still on the coal pile. found the drive shaft to the rear transmission had sheared the mounting bolts and busted the transmission housing. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Fuel Supply |  | Nathan Webb | Joel Leavell |  | Darcey Hayes | I feel Anthony and Rodney addressed all possible causes and told the story to the best of their knowledge and investigation. | Darcey Hayes |  | Low |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching | [7 empty] | 14.02.4 Inadequate communication of standards: training |  |  | improper training | 34. Inadequate Instructions, Procedures | 12. Equipment Failure
9191 | Muskogee Power Plant | 2020-01-08 | Fuel/Operations Multi Craft members were hauling coal with scrapers to assist with Conveyor 14 repair and putting water out for dust mitigation. Operator had emptied his load and was heading back South to retrieve another load when Operator on Water Wagon discovered the failure. CAT Coal Scraper F38-899 Rear Transmission failed. | Level 1 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Joel Leavell | 2020-02-26 14:22 | 2020-01-08 20:28 | 2020-01-08 20:28 | 2020-02-17 07:13 | 2020-01-22 | 2020-01-08 00:15 | 2020-02-18 10:45 |  |  | Muskogee PP Coal Pile. |  |  | Robert Wright | Approved Bob Wright | Power Supply |  | Level 1 | Property Damage |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Rodney Hyslope |  | Member was operating scraper on night shift. member had just unloaded scrapper coming around south end of coal pile , headed to get another load of coal when the water truck operator notified the scrapper operator to take his scrapper to the shop. the water truck operator was following the scraper and noticed parts laying in the roadway from the scraper. member on scraper said he never felt anything out of the norm. day shift came in and found the scraper still on the coal pile. found the drive shaft to the rear transmission had sheared the mounting bolts and busted the transmission housing. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Fuel Supply |  | Nathan Webb | Joel Leavell |  | Darcey Hayes | I feel Anthony and Rodney addressed all possible causes and told the story to the best of their knowledge and investigation. | Darcey Hayes |  | Low |  |  |  |  | 5.01 Lack of experience | 6.02 Inadequate practice | [7 empty] | 14.02.4 Inadequate communication of standards: training |  |  | improper training | 34. Inadequate Instructions, Procedures | 12. Equipment Failure
9191 | Muskogee Power Plant | 2020-01-08 | Fuel/Operations Multi Craft members were hauling coal with scrapers to assist with Conveyor 14 repair and putting water out for dust mitigation. Operator had emptied his load and was heading back South to retrieve another load when Operator on Water Wagon discovered the failure. CAT Coal Scraper F38-899 Rear Transmission failed. | Level 1 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Joel Leavell | 2020-02-26 14:22 | 2020-01-08 20:28 | 2020-01-08 20:28 | 2020-02-17 07:13 | 2020-01-22 | 2020-01-08 00:15 | 2020-02-18 10:45 |  |  | Muskogee PP Coal Pile. |  |  | Robert Wright | Approved Bob Wright | Power Supply |  | Level 1 | Property Damage |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Rodney Hyslope |  | Member was operating scraper on night shift. member had just unloaded scrapper coming around south end of coal pile , headed to get another load of coal when the water truck operator notified the scrapper operator to take his scrapper to the shop. the water truck operator was following the scraper and noticed parts laying in the roadway from the scraper. member on scraper said he never felt anything out of the norm. day shift came in and found the scraper still on the coal pile. found the drive shaft to the rear transmission had sheared the mounting bolts and busted the transmission housing. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Fuel Supply |  | Nathan Webb | Joel Leavell |  | Darcey Hayes | I feel Anthony and Rodney addressed all possible causes and told the story to the best of their knowledge and investigation. | Darcey Hayes |  | Low |  |  |  |  | 5.03 Inadequate initial training | 6.04 Lack of coaching | [7 empty] | 14.02.4 Inadequate communication of standards: training |  |  | improper training | 34. Inadequate Instructions, Procedures | 12. Equipment Failure
9191 | Muskogee Power Plant | 2020-01-08 | Fuel/Operations Multi Craft members were hauling coal with scrapers to assist with Conveyor 14 repair and putting water out for dust mitigation. Operator had emptied his load and was heading back South to retrieve another load when Operator on Water Wagon discovered the failure. CAT Coal Scraper F38-899 Rear Transmission failed. | Level 1 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Joel Leavell | 2020-02-26 14:22 | 2020-01-08 20:28 | 2020-01-08 20:28 | 2020-02-17 07:13 | 2020-01-22 | 2020-01-08 00:15 | 2020-02-18 10:45 |  |  | Muskogee PP Coal Pile. |  |  | Robert Wright | Approved Bob Wright | Power Supply |  | Level 1 | Property Damage |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Rodney Hyslope |  | Member was operating scraper on night shift. member had just unloaded scrapper coming around south end of coal pile , headed to get another load of coal when the water truck operator notified the scrapper operator to take his scrapper to the shop. the water truck operator was following the scraper and noticed parts laying in the roadway from the scraper. member on scraper said he never felt anything out of the norm. day shift came in and found the scraper still on the coal pile. found the drive shaft to the rear transmission had sheared the mounting bolts and busted the transmission housing. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Fuel Supply |  | Nathan Webb | Joel Leavell |  | Darcey Hayes | I feel Anthony and Rodney addressed all possible causes and told the story to the best of their knowledge and investigation. | Darcey Hayes |  | Low |  |  |  |  | 5.03 Inadequate initial training | 6.02 Inadequate practice | [7 empty] | 14.02.4 Inadequate communication of standards: training |  |  | improper training | 34. Inadequate Instructions, Procedures | 12. Equipment Failure
9191 | Muskogee Power Plant | 2020-01-08 | Fuel/Operations Multi Craft members were hauling coal with scrapers to assist with Conveyor 14 repair and putting water out for dust mitigation. Operator had emptied his load and was heading back South to retrieve another load when Operator on Water Wagon discovered the failure. CAT Coal Scraper F38-899 Rear Transmission failed. | Level 1 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Joel Leavell | 2020-02-26 14:22 | 2020-01-08 20:28 | 2020-01-08 20:28 | 2020-02-17 07:13 | 2020-01-22 | 2020-01-08 00:15 | 2020-02-18 10:45 |  |  | Muskogee PP Coal Pile. |  |  | Robert Wright | Approved Bob Wright | Power Supply |  | Level 1 | Property Damage |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Rodney Hyslope |  | Member was operating scraper on night shift. member had just unloaded scrapper coming around south end of coal pile , headed to get another load of coal when the water truck operator notified the scrapper operator to take his scrapper to the shop. the water truck operator was following the scraper and noticed parts laying in the roadway from the scraper. member on scraper said he never felt anything out of the norm. day shift came in and found the scraper still on the coal pile. found the drive shaft to the rear transmission had sheared the mounting bolts and busted the transmission housing. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Fuel Supply |  | Nathan Webb | Joel Leavell |  | Darcey Hayes | I feel Anthony and Rodney addressed all possible causes and told the story to the best of their knowledge and investigation. | Darcey Hayes |  | Low |  |  |  |  | 5.01 Lack of experience | 6.04 Lack of coaching | [7 empty] | 14.02.4 Inadequate communication of standards: training |  |  | during operation of this equipt. if not operated properly, coming in at too high of a speed or trying to dig ( scrap ) in too high of gear, or not pushing with the rear engine properly, can cause the rear wheels to skip or slip and grab which causes a lot of torque on the drive shaft. There is a transmission lock on the hydraulic control lever that should be used during digging, this locks in the transmissions in gear where they are unable to shift. While not digging this transmission lock should be unlocked, which in turn lets the transmissions shift through each sequence. The bolts that mount the yoke of the drive shaft to the transmission housing were found to have been sheared completely off. Once this happened the drive shaft continued to spin and break anything it came in contact with, such as the transmission housing etc. | 15. Using Equipment Improperly | 9. Abnormal Operation
9191 | Muskogee Power Plant | 2020-01-08 | Fuel/Operations Multi Craft members were hauling coal with scrapers to assist with Conveyor 14 repair and putting water out for dust mitigation. Operator had emptied his load and was heading back South to retrieve another load when Operator on Water Wagon discovered the failure. CAT Coal Scraper F38-899 Rear Transmission failed. | Level 1 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Joel Leavell | 2020-02-26 14:22 | 2020-01-08 20:28 | 2020-01-08 20:28 | 2020-02-17 07:13 | 2020-01-22 | 2020-01-08 00:15 | 2020-02-18 10:45 |  |  | Muskogee PP Coal Pile. |  |  | Robert Wright | Approved Bob Wright | Power Supply |  | Level 1 | Property Damage |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Rodney Hyslope |  | Member was operating scraper on night shift. member had just unloaded scrapper coming around south end of coal pile , headed to get another load of coal when the water truck operator notified the scrapper operator to take his scrapper to the shop. the water truck operator was following the scraper and noticed parts laying in the roadway from the scraper. member on scraper said he never felt anything out of the norm. day shift came in and found the scraper still on the coal pile. found the drive shaft to the rear transmission had sheared the mounting bolts and busted the transmission housing. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Fuel Supply |  | Nathan Webb | Joel Leavell |  | Darcey Hayes | I feel Anthony and Rodney addressed all possible causes and told the story to the best of their knowledge and investigation. | Darcey Hayes |  | Low |  |  |  |  | 5.03 Inadequate initial training | 6.04 Lack of coaching | [7 empty] | 14.02.4 Inadequate communication of standards: training |  |  | during operation of this equipt. if not operated properly, coming in at too high of a speed or trying to dig ( scrap ) in too high of gear, or not pushing with the rear engine properly, can cause the rear wheels to skip or slip and grab which causes a lot of torque on the drive shaft. There is a transmission lock on the hydraulic control lever that should be used during digging, this locks in the transmissions in gear where they are unable to shift. While not digging this transmission lock should be unlocked, which in turn lets the transmissions shift through each sequence. The bolts that mount the yoke of the drive shaft to the transmission housing were found to have been sheared completely off. Once this happened the drive shaft continued to spin and break anything it came in contact with, such as the transmission housing etc. | 15. Using Equipment Improperly | 9. Abnormal Operation
9192 | Metro Service Center | 2020-01-09 08:30 | While walking through wooded area member was pushing tree limbs out of way when a tree limb snapped back and hit member on right side of head, causing puncture to right ear drum. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Daniel Godwin | 2020-01-23 14:53 | 2020-01-09 13:44 | 2020-01-09 13:44 | 2020-01-23 08:03 | 2020-01-23 08:30 | 2020-01-09 13:16 | 2020-01-23 13:33 |  | 2020-01-23 13:11 | NE 63rd and Grand Blvd, Oklahoma City in the distribution line right of way |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Daniel Godwin |  | Employee was inspecting a pole with a broken cross arm. He was trying to see if a crew would be able to gain access to base of pole with a bucket truck. While walking down the right of way he pushed some small tree limbs out of his way. One of the limbs snapped back and entered into his ear canal. The limb punctured his ear drum. The member evaluated 3 different options to walk down the line. There was a concrete water way he could have traveled but it was wet and covered in moss. The concrete was very slick. The opposing bank was covered 4 to 5 feet grass with a steep slope. The path he chose appeared to be the safest method of approach. Additional Information: • What is the original job to be performed? o Performing switching order M1898 • Why did you deviate from the job of switching order M1898? o Noticed that a cross arm was broken while on the way to perform switching.  This is common practice when this group spots defects on circuits.  The broken crossarm was on a double circuit switch pole. • The broken crossarm could cause additional system issues if not promptly fixed.  Member stopped to get the correct information for creating a ticket for line crew to repair the arm. • Information needed to create a ticket: o Location o Affected equipment/parts o Types of damage o Notes on damage o Notes on additional safety hazards. o Notes for truck access to the affected parts  The member was trying to find the best access path for a line crew, when they come to make repairs to the crossarm when his ear was injured. • Why was the specific path to the crossarm chosen? o It was the path of least resistance to the assess a path for equipment to reach the broken crossarm. o There were additional paths, but each alternative was more hazardous than the path taken. o The member did not feel that the path he chose provided an unnecessary risk. • What was member doing at the time of incident? o The member had pinned limbs back with his hands to pass by a tree. • What harmed the member? o A limb that he was holding came loose. A piece of the limb entered the ear canal and punctured the members eardrum. • What immediate action was taken at the time of the incident? o Member experienced pain and dizziness. o Member called foreman. o Foreman called Supervisor. o Supervisor notified managers and safety professional o Safety professional notified company nurse, and requested that she see the affected member before being seen by an outside medical. o Company nurse assessed the member and referred him to the McBride Clinic o |  |  | FALSE | Metro Service Center | FALSE |  | FALSE | PD Operations Services |  | Gary Watson | Daniel Godwin |  | Jeffrey Gleim | I approve | Jeffrey Gleim |  | Medium |  |  |  | 4.06 "Meaningless" or "degrading" activities | [12 empty] | stored energy in a tree limb that has been moved from its natural state | 03. Failure to Secure | 11. Overstress, Overpressure, Overexertion, Ergonomic |  | this incident had a highly unexpected outcome, but the investigation lead towards a look at hazard awareness, risk assessment, and risk tolerance. I agree with the risk ranking of this incident and applaud the supervisors for the work that was put in towards the investigation. The corrective action assigned to this incident shows an effort by the supervision to set expectations by inspecting by what they are expecting. the measurement of this corrective action will be difficult but i believe can be managed through our compliance tool and self assessment requirements. | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 1984-04-09 | 1963-12-30 |  | 2020-01-09 07:00 | 0 | 0 |  | FALSE |  | Making way thru brush and tree limbs, to access the damaged pole, a very small limb snapped back and entered into workers ear canal, puncturing the ear drum. |  | FALSE | Gary Watson |  | Recordable | Gary Watson | TRUE |  | McBride Occupational Clinic |  | Puncture |  | TRUE |  | Power Quality Tech | Ear | Injury | Right | TRUE | Daniel Godwin | TRUE | 2020 | 1/9/2020 7:00:00 AM |  | TRUE | FALSE | FALSE | tree limb | Trying to determine how best to approach a pole with equipment to fix a broke x-arm on a double circuit switch pole.
9193 | Muskogee Power Plant | 2019-12-23 09:22 | While performing SPCC Transformer inspections the East U5 B bank transformer was reported as a very small leak was identified. Upon further investigation it is apparent it was "struck by" a object bending the radiator cooler some stressing the weld attachment. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Daniel Moffett | 2020-01-22 09:04 | 2020-01-09 13:47 | 2020-01-09 13:47 | 2020-01-09 14:51 | 2020-01-06 09:22 | 2020-01-09 12:53 | 2020-01-14 16:36 |  |  | East U5 Precipitator Transformer banks |  |  | Robert Wright | Approved Bob Wright | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Daniel Moffett |  | While performing the quarterly SPCC transformer inspection Calvin Shackleford noticed a slight oil smudge on the bottom south transformer radiator on U5B1 precipitator transformer. He wrote order 9595096 to repair the leak. Upon looking at the scope and how to repair it was noticed that this radiator has been struck by something. The electrical planner notified me and I concurred this has happened. Based by the photograph evidence it appears a Industrial motor driven piece of equipment was traveling east and turned north by this transformer and some part of the load managed to get between the handrail barricade and struck the oil cooler as there was a fresh paint scar on the outboard fin. The bollard is leaning but upon further looking the feet are corroded away and there is no evidence of damage or fresh tears at the foot of the bollard. The oil level has not changed and there is only a dust smudge on the base of the cooler. The containment is very large and there is little risk of a release. Our plan is to de energize this transformer today and feed the lights and welding receptacles from the west most transformer and make plans to replace this with one of the other transformers for the precipitator proper and dispose of this damaged equipment. I asked the inspector for Brock who is demobilizing if they reported this and the answer was no, I also mention it in the morning meeting today in the maintenance breakroom and no one came forward. As this was not identified and reported I have no idea who was involved. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | Maintenance |  | Lawrence Shackelford | Daniel Moffett |  | Andy Hedge | Read and approved. Andy Hedge 1/14/20 | Andy Hedge |  | Low | [8 empty] | 9.12 Inadequate performance measurement and evaluation | [7 empty] | By review of the area and pictures it appears a fork truck was being operated in a restricted area and turned north by the transformer pad and material being transported went between the handrails and barricade and struck the transformer oil cooler. This transformer is for the no longer utilized U5 precipitator. | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) | [68 empty] | crack in a weld seeping oil | 1500 | unknown | Fixed Equipment | [20 empty] | 9595096
9194 | West Service Center | 2020-01-10 23:30 | while member was replacing open wire service from service pole to house pole broke 15 inches below ground level and fell slowly to the ground. No personal injuries and no damage to customer property. | Level 3 |  | TRUE | Member Injury | Andrea Dennis | Lindle Coleman | Assigned Per discussion with ops leaders | 2020-01-16 09:54 | Power Delivery | Joshua Robertson | 2020-01-27 15:12 | 2020-01-13 09:20 | 2020-01-13 09:20 | 2020-01-20 15:18 | 2020-01-24 23:30 | 2020-01-13 09:08 | 2020-01-23 14:46 | 2020-01-23 15:15 | 2020-01-21 15:51 | 1631 NW 13 street, OKC, OK |  |  | Andrea Dennis | I approve. | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Mark Martin |  | While crew was changing out bad open wire service the 30’6 service pole broke 15 inches below ground line and slowly fell to the ground while member was at the top of pole. Member sound checked the pole with his hammer and deemed the pole safe to climb, the member also stated that he checked the pole with his gaffs and the pole felt and sounded solid. Member climbed to the top of the 30’6 service pole and proceeded to cut the open wire service down. He checked the bottom leg of the service for tension before he cut it and let it to the ground. He did the same with the top hot leg and verified no tension. He proceeded to check the neutral wire for tension and verified that there was no tension on it before he cut it and let it down as well. After he let the neutral down to the ground the pole slowly started to fall toward the way the pole was naturally leaning. When the pole came to rest with the head of the pole approximately 2 feet from the ground the member was able to remove his safety from the pole and step away from the pole. Once the Foreman had made sure that the member climbing the service pole was OK he noticed that a 30’9 street light pole to the South of the service pole was broken and laying on the ground as well. Facts Ascertained: o Member stated he rapped 30’ class 6 service pole with hammer and was confident in it’s condition o Member also mentioned that his gaffs felt and sounded good and solid o Member then climbed pole cut bottom two legs (approximately 50’ span) and dropped them to the ground. o After cutting the neutral the pole began to slowly fall WNW to the ground (towards the direction the pole was leaning and the direction of the 3/0 triplex) o Service legs and neutral were not under tension o Service pole had 3/0 wrapped secondary coming to the pole, 3 services coming off of the pole, and a service for light pole. o Pole was leaning to the west. o Member was on the eastside of the pole o Member tried to slow pole with his left foot as it neared the ground. The pole scraped his left knee o All other crew members were out of the line of fire (3 at the house near the weatherhead and 1 at the truck in the front) o 30’ class 9 Light pole in front yard fell as well (unable to confirm if it was before or after service pole) o Service pole stopped a couple of feet from the ground due to the 3/0 secondary triplex which was caught up in tree limbs and a long service span remaining tied in. o Secondaries remained energized o Once pole came to a stop the crew assisted member in unbelting and getting off of the pole o They then cleared the services from the pole allowing it to go to the ground o After investigation it was determined the service pole broke approximately 15” from the ground level o Soil around pole hole was disturbed indicating it broke below ground level and ground line was visible on the pole 15” up from the lowest point. o Soil inclined across the back yard indicating the soil level may have been changed at some. This also resulted in a divot were the pole is that may allow water to pool o OGE Meteorologist (Matt Chatelain) provided wind and temperature conditions for the location at the time of the incident.  29 degrees Fahrenheit  NNW 35MPH Sustained  47 MPH Gusts o Crew held an initial tailboard that covered the leaning pole and need to check and another tailboard after the incident occurred o Initial tailboard was not signed by the member on the pole (both Foreman and Member on the pole confirmed he was a part of the initial tailboard). o Initial tailboard noted leaning pole needed to be checked o Crew did not dig down at least 12" in depth to probe pole. SOP Requires you to dig a minimum of 12 inches in depth and probe the suspect pole with at least a 5” screw driver. There is indication that this is a gap across T&D. o If deterioration is found below ground line, determine if the pole can be secured by other means before climbing or performing work. o Anytime you are adding, removing, or changing pole tension you must also visually inspect the adjacent poles to ensure they are capable of withstanding the stress. o Dark during the duration of the job o Remaining Services was caught in tree which provided resistance o On Site at time of occurrence: Streber, Jesse Philler, Josh H, Mason Shetley, Derrick Davis o On the call prior to this one crew secured pole with a rope. o Crew had been working since 7 AM that morning (16.5 hours at the time of incident) o Member on pole is a step 24-10 apprentice o Foreman had been in position for 9 months | Matthew Stanley | Mark Martin |  | West Service Center | FALSE |  | TRUE | Construction Services |  | Brandon Streber | Joshua Robertson |  | Terry Garrett | I agree with the corrective action...TG | Terry Garrett | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction | [10 empty] | Crew did not dig down and probe pole nor check adjacent poles | 16. Failure to Follow Procedure, Policy, Practice | 7. Caught Between or Under (Crushed or Amputated) | approved | Upon assessing the corrective actions determined by the investigation team. I believe these controls would prevent similar exposures such as this one in the future. Approved 1/21/20 | [90 empty] | 8590781
9194 | West Service Center | 2020-01-10 23:30 | while member was replacing open wire service from service pole to house pole broke 15 inches below ground level and fell slowly to the ground. No personal injuries and no damage to customer property. | Level 3 |  | TRUE | Member Injury | Andrea Dennis | Lindle Coleman | Assigned Per discussion with ops leaders | 2020-01-16 09:54 | Power Delivery | Joshua Robertson | 2020-01-27 15:12 | 2020-01-13 09:20 | 2020-01-13 09:20 | 2020-01-20 15:18 | 2020-01-24 23:30 | 2020-01-13 09:08 | 2020-01-23 14:46 | 2020-01-23 15:15 | 2020-01-21 15:51 | 1631 NW 13 street, OKC, OK |  |  | Andrea Dennis | I approve. | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Mark Martin |  | While crew was changing out bad open wire service the 30’6 service pole broke 15 inches below ground line and slowly fell to the ground while member was at the top of pole. Member sound checked the pole with his hammer and deemed the pole safe to climb, the member also stated that he checked the pole with his gaffs and the pole felt and sounded solid. Member climbed to the top of the 30’6 service pole and proceeded to cut the open wire service down. He checked the bottom leg of the service for tension before he cut it and let it to the ground. He did the same with the top hot leg and verified no tension. He proceeded to check the neutral wire for tension and verified that there was no tension on it before he cut it and let it down as well. After he let the neutral down to the ground the pole slowly started to fall toward the way the pole was naturally leaning. When the pole came to rest with the head of the pole approximately 2 feet from the ground the member was able to remove his safety from the pole and step away from the pole. Once the Foreman had made sure that the member climbing the service pole was OK he noticed that a 30’9 street light pole to the South of the service pole was broken and laying on the ground as well. Facts Ascertained: o Member stated he rapped 30’ class 6 service pole with hammer and was confident in it’s condition o Member also mentioned that his gaffs felt and sounded good and solid o Member then climbed pole cut bottom two legs (approximately 50’ span) and dropped them to the ground. o After cutting the neutral the pole began to slowly fall WNW to the ground (towards the direction the pole was leaning and the direction of the 3/0 triplex) o Service legs and neutral were not under tension o Service pole had 3/0 wrapped secondary coming to the pole, 3 services coming off of the pole, and a service for light pole. o Pole was leaning to the west. o Member was on the eastside of the pole o Member tried to slow pole with his left foot as it neared the ground. The pole scraped his left knee o All other crew members were out of the line of fire (3 at the house near the weatherhead and 1 at the truck in the front) o 30’ class 9 Light pole in front yard fell as well (unable to confirm if it was before or after service pole) o Service pole stopped a couple of feet from the ground due to the 3/0 secondary triplex which was caught up in tree limbs and a long service span remaining tied in. o Secondaries remained energized o Once pole came to a stop the crew assisted member in unbelting and getting off of the pole o They then cleared the services from the pole allowing it to go to the ground o After investigation it was determined the service pole broke approximately 15” from the ground level o Soil around pole hole was disturbed indicating it broke below ground level and ground line was visible on the pole 15” up from the lowest point. o Soil inclined across the back yard indicating the soil level may have been changed at some. This also resulted in a divot were the pole is that may allow water to pool o OGE Meteorologist (Matt Chatelain) provided wind and temperature conditions for the location at the time of the incident.  29 degrees Fahrenheit  NNW 35MPH Sustained  47 MPH Gusts o Crew held an initial tailboard that covered the leaning pole and need to check and another tailboard after the incident occurred o Initial tailboard was not signed by the member on the pole (both Foreman and Member on the pole confirmed he was a part of the initial tailboard). o Initial tailboard noted leaning pole needed to be checked o Crew did not dig down at least 12" in depth to probe pole. SOP Requires you to dig a minimum of 12 inches in depth and probe the suspect pole with at least a 5” screw driver. There is indication that this is a gap across T&D. o If deterioration is found below ground line, determine if the pole can be secured by other means before climbing or performing work. o Anytime you are adding, removing, or changing pole tension you must also visually inspect the adjacent poles to ensure they are capable of withstanding the stress. o Dark during the duration of the job o Remaining Services was caught in tree which provided resistance o On Site at time of occurrence: Streber, Jesse Philler, Josh H, Mason Shetley, Derrick Davis o On the call prior to this one crew secured pole with a rope. o Crew had been working since 7 AM that morning (16.5 hours at the time of incident) o Member on pole is a step 24-10 apprentice o Foreman had been in position for 9 months | Matthew Stanley | Mark Martin |  | West Service Center | FALSE |  | TRUE | Construction Services |  | Brandon Streber | Joshua Robertson |  | Terry Garrett | I agree with the corrective action...TG | Terry Garrett | Lindle Coleman | High | [6 empty] | 7.01 Improper performance is rewarded (tolerated) | [9 empty] | Member sounded and gaff checked the pole but was unable to identify the deteriorated section of pole below the ground line. Must dig down at least 12" on suspect poles and probe. 7.01: There is indication that this is a gap across T&D. | 17. Failure to Identify Hazard, Risk | 7. Caught Between or Under (Crushed or Amputated) | approved | Upon assessing the corrective actions determined by the investigation team. I believe these controls would prevent similar exposures such as this one in the future. Approved 1/21/20 | [90 empty] | 8590781
9194 | West Service Center | 2020-01-10 23:30 | while member was replacing open wire service from service pole to house pole broke 15 inches below ground level and fell slowly to the ground. No personal injuries and no damage to customer property. | Level 3 |  | TRUE | Member Injury | Andrea Dennis | Lindle Coleman | Assigned Per discussion with ops leaders | 2020-01-16 09:54 | Power Delivery | Joshua Robertson | 2020-01-27 15:12 | 2020-01-13 09:20 | 2020-01-13 09:20 | 2020-01-20 15:18 | 2020-01-24 23:30 | 2020-01-13 09:08 | 2020-01-23 14:46 | 2020-01-23 15:15 | 2020-01-21 15:51 | 1631 NW 13 street, OKC, OK |  |  | Andrea Dennis | I approve. | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Mark Martin |  | While crew was changing out bad open wire service the 30’6 service pole broke 15 inches below ground line and slowly fell to the ground while member was at the top of pole. Member sound checked the pole with his hammer and deemed the pole safe to climb, the member also stated that he checked the pole with his gaffs and the pole felt and sounded solid. Member climbed to the top of the 30’6 service pole and proceeded to cut the open wire service down. He checked the bottom leg of the service for tension before he cut it and let it to the ground. He did the same with the top hot leg and verified no tension. He proceeded to check the neutral wire for tension and verified that there was no tension on it before he cut it and let it down as well. After he let the neutral down to the ground the pole slowly started to fall toward the way the pole was naturally leaning. When the pole came to rest with the head of the pole approximately 2 feet from the ground the member was able to remove his safety from the pole and step away from the pole. Once the Foreman had made sure that the member climbing the service pole was OK he noticed that a 30’9 street light pole to the South of the service pole was broken and laying on the ground as well. Facts Ascertained: o Member stated he rapped 30’ class 6 service pole with hammer and was confident in it’s condition o Member also mentioned that his gaffs felt and sounded good and solid o Member then climbed pole cut bottom two legs (approximately 50’ span) and dropped them to the ground. o After cutting the neutral the pole began to slowly fall WNW to the ground (towards the direction the pole was leaning and the direction of the 3/0 triplex) o Service legs and neutral were not under tension o Service pole had 3/0 wrapped secondary coming to the pole, 3 services coming off of the pole, and a service for light pole. o Pole was leaning to the west. o Member was on the eastside of the pole o Member tried to slow pole with his left foot as it neared the ground. The pole scraped his left knee o All other crew members were out of the line of fire (3 at the house near the weatherhead and 1 at the truck in the front) o 30’ class 9 Light pole in front yard fell as well (unable to confirm if it was before or after service pole) o Service pole stopped a couple of feet from the ground due to the 3/0 secondary triplex which was caught up in tree limbs and a long service span remaining tied in. o Secondaries remained energized o Once pole came to a stop the crew assisted member in unbelting and getting off of the pole o They then cleared the services from the pole allowing it to go to the ground o After investigation it was determined the service pole broke approximately 15” from the ground level o Soil around pole hole was disturbed indicating it broke below ground level and ground line was visible on the pole 15” up from the lowest point. o Soil inclined across the back yard indicating the soil level may have been changed at some. This also resulted in a divot were the pole is that may allow water to pool o OGE Meteorologist (Matt Chatelain) provided wind and temperature conditions for the location at the time of the incident.  29 degrees Fahrenheit  NNW 35MPH Sustained  47 MPH Gusts o Crew held an initial tailboard that covered the leaning pole and need to check and another tailboard after the incident occurred o Initial tailboard was not signed by the member on the pole (both Foreman and Member on the pole confirmed he was a part of the initial tailboard). o Initial tailboard noted leaning pole needed to be checked o Crew did not dig down at least 12" in depth to probe pole. SOP Requires you to dig a minimum of 12 inches in depth and probe the suspect pole with at least a 5” screw driver. There is indication that this is a gap across T&D. o If deterioration is found below ground line, determine if the pole can be secured by other means before climbing or performing work. o Anytime you are adding, removing, or changing pole tension you must also visually inspect the adjacent poles to ensure they are capable of withstanding the stress. o Dark during the duration of the job o Remaining Services was caught in tree which provided resistance o On Site at time of occurrence: Streber, Jesse Philler, Josh H, Mason Shetley, Derrick Davis o On the call prior to this one crew secured pole with a rope. o Crew had been working since 7 AM that morning (16.5 hours at the time of incident) o Member on pole is a step 24-10 apprentice o Foreman had been in position for 9 months | Matthew Stanley | Mark Martin |  | West Service Center | FALSE |  | TRUE | Construction Services |  | Brandon Streber | Joshua Robertson |  | Terry Garrett | I agree with the corrective action...TG | Terry Garrett | Lindle Coleman | High | [6 empty] | 7.07 Improper attempt to avoid discomfort | [9 empty] | Pole broke 15" below ground level | 03. Failure to Secure | 7. Caught Between or Under (Crushed or Amputated) | approved | Upon assessing the corrective actions determined by the investigation team. I believe these controls would prevent similar exposures such as this one in the future. Approved 1/21/20 | [90 empty] | 8590781
9194 | West Service Center | 2020-01-10 23:30 | while member was replacing open wire service from service pole to house pole broke 15 inches below ground level and fell slowly to the ground. No personal injuries and no damage to customer property. | Level 3 |  | TRUE | Member Injury | Andrea Dennis | Lindle Coleman | Assigned Per discussion with ops leaders | 2020-01-16 09:54 | Power Delivery | Joshua Robertson | 2020-01-27 15:12 | 2020-01-13 09:20 | 2020-01-13 09:20 | 2020-01-20 15:18 | 2020-01-24 23:30 | 2020-01-13 09:08 | 2020-01-23 14:46 | 2020-01-23 15:15 | 2020-01-21 15:51 | 1631 NW 13 street, OKC, OK |  |  | Andrea Dennis | I approve. | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Mark Martin |  | While crew was changing out bad open wire service the 30’6 service pole broke 15 inches below ground line and slowly fell to the ground while member was at the top of pole. Member sound checked the pole with his hammer and deemed the pole safe to climb, the member also stated that he checked the pole with his gaffs and the pole felt and sounded solid. Member climbed to the top of the 30’6 service pole and proceeded to cut the open wire service down. He checked the bottom leg of the service for tension before he cut it and let it to the ground. He did the same with the top hot leg and verified no tension. He proceeded to check the neutral wire for tension and verified that there was no tension on it before he cut it and let it down as well. After he let the neutral down to the ground the pole slowly started to fall toward the way the pole was naturally leaning. When the pole came to rest with the head of the pole approximately 2 feet from the ground the member was able to remove his safety from the pole and step away from the pole. Once the Foreman had made sure that the member climbing the service pole was OK he noticed that a 30’9 street light pole to the South of the service pole was broken and laying on the ground as well. Facts Ascertained: o Member stated he rapped 30’ class 6 service pole with hammer and was confident in it’s condition o Member also mentioned that his gaffs felt and sounded good and solid o Member then climbed pole cut bottom two legs (approximately 50’ span) and dropped them to the ground. o After cutting the neutral the pole began to slowly fall WNW to the ground (towards the direction the pole was leaning and the direction of the 3/0 triplex) o Service legs and neutral were not under tension o Service pole had 3/0 wrapped secondary coming to the pole, 3 services coming off of the pole, and a service for light pole. o Pole was leaning to the west. o Member was on the eastside of the pole o Member tried to slow pole with his left foot as it neared the ground. The pole scraped his left knee o All other crew members were out of the line of fire (3 at the house near the weatherhead and 1 at the truck in the front) o 30’ class 9 Light pole in front yard fell as well (unable to confirm if it was before or after service pole) o Service pole stopped a couple of feet from the ground due to the 3/0 secondary triplex which was caught up in tree limbs and a long service span remaining tied in. o Secondaries remained energized o Once pole came to a stop the crew assisted member in unbelting and getting off of the pole o They then cleared the services from the pole allowing it to go to the ground o After investigation it was determined the service pole broke approximately 15” from the ground level o Soil around pole hole was disturbed indicating it broke below ground level and ground line was visible on the pole 15” up from the lowest point. o Soil inclined across the back yard indicating the soil level may have been changed at some. This also resulted in a divot were the pole is that may allow water to pool o OGE Meteorologist (Matt Chatelain) provided wind and temperature conditions for the location at the time of the incident.  29 degrees Fahrenheit  NNW 35MPH Sustained  47 MPH Gusts o Crew held an initial tailboard that covered the leaning pole and need to check and another tailboard after the incident occurred o Initial tailboard was not signed by the member on the pole (both Foreman and Member on the pole confirmed he was a part of the initial tailboard). o Initial tailboard noted leaning pole needed to be checked o Crew did not dig down at least 12" in depth to probe pole. SOP Requires you to dig a minimum of 12 inches in depth and probe the suspect pole with at least a 5” screw driver. There is indication that this is a gap across T&D. o If deterioration is found below ground line, determine if the pole can be secured by other means before climbing or performing work. o Anytime you are adding, removing, or changing pole tension you must also visually inspect the adjacent poles to ensure they are capable of withstanding the stress. o Dark during the duration of the job o Remaining Services was caught in tree which provided resistance o On Site at time of occurrence: Streber, Jesse Philler, Josh H, Mason Shetley, Derrick Davis o On the call prior to this one crew secured pole with a rope. o Crew had been working since 7 AM that morning (16.5 hours at the time of incident) o Member on pole is a step 24-10 apprentice o Foreman had been in position for 9 months | Matthew Stanley | Mark Martin |  | West Service Center | FALSE |  | TRUE | Construction Services |  | Brandon Streber | Joshua Robertson |  | Terry Garrett | I agree with the corrective action...TG | Terry Garrett | Lindle Coleman | High | [13 empty] | 14.04 Inadequate monitoring of compliance |  |  | Member on pole did not sign tailboard | 16. Failure to Follow Procedure, Policy, Practice | 7. Caught Between or Under (Crushed or Amputated) | approved | Upon assessing the corrective actions determined by the investigation team. I believe these controls would prevent similar exposures such as this one in the future. Approved 1/21/20 | [90 empty] | 8590781
9194 | West Service Center | 2020-01-10 23:30 | while member was replacing open wire service from service pole to house pole broke 15 inches below ground level and fell slowly to the ground. No personal injuries and no damage to customer property. | Level 3 |  | TRUE | Member Injury | Andrea Dennis | Lindle Coleman | Assigned Per discussion with ops leaders | 2020-01-16 09:54 | Power Delivery | Joshua Robertson | 2020-01-27 15:12 | 2020-01-13 09:20 | 2020-01-13 09:20 | 2020-01-20 15:18 | 2020-01-24 23:30 | 2020-01-13 09:08 | 2020-01-23 14:46 | 2020-01-23 15:15 | 2020-01-21 15:51 | 1631 NW 13 street, OKC, OK |  |  | Andrea Dennis | I approve. | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Mark Martin |  | While crew was changing out bad open wire service the 30’6 service pole broke 15 inches below ground line and slowly fell to the ground while member was at the top of pole. Member sound checked the pole with his hammer and deemed the pole safe to climb, the member also stated that he checked the pole with his gaffs and the pole felt and sounded solid. Member climbed to the top of the 30’6 service pole and proceeded to cut the open wire service down. He checked the bottom leg of the service for tension before he cut it and let it to the ground. He did the same with the top hot leg and verified no tension. He proceeded to check the neutral wire for tension and verified that there was no tension on it before he cut it and let it down as well. After he let the neutral down to the ground the pole slowly started to fall toward the way the pole was naturally leaning. When the pole came to rest with the head of the pole approximately 2 feet from the ground the member was able to remove his safety from the pole and step away from the pole. Once the Foreman had made sure that the member climbing the service pole was OK he noticed that a 30’9 street light pole to the South of the service pole was broken and laying on the ground as well. Facts Ascertained: o Member stated he rapped 30’ class 6 service pole with hammer and was confident in it’s condition o Member also mentioned that his gaffs felt and sounded good and solid o Member then climbed pole cut bottom two legs (approximately 50’ span) and dropped them to the ground. o After cutting the neutral the pole began to slowly fall WNW to the ground (towards the direction the pole was leaning and the direction of the 3/0 triplex) o Service legs and neutral were not under tension o Service pole had 3/0 wrapped secondary coming to the pole, 3 services coming off of the pole, and a service for light pole. o Pole was leaning to the west. o Member was on the eastside of the pole o Member tried to slow pole with his left foot as it neared the ground. The pole scraped his left knee o All other crew members were out of the line of fire (3 at the house near the weatherhead and 1 at the truck in the front) o 30’ class 9 Light pole in front yard fell as well (unable to confirm if it was before or after service pole) o Service pole stopped a couple of feet from the ground due to the 3/0 secondary triplex which was caught up in tree limbs and a long service span remaining tied in. o Secondaries remained energized o Once pole came to a stop the crew assisted member in unbelting and getting off of the pole o They then cleared the services from the pole allowing it to go to the ground o After investigation it was determined the service pole broke approximately 15” from the ground level o Soil around pole hole was disturbed indicating it broke below ground level and ground line was visible on the pole 15” up from the lowest point. o Soil inclined across the back yard indicating the soil level may have been changed at some. This also resulted in a divot were the pole is that may allow water to pool o OGE Meteorologist (Matt Chatelain) provided wind and temperature conditions for the location at the time of the incident.  29 degrees Fahrenheit  NNW 35MPH Sustained  47 MPH Gusts o Crew held an initial tailboard that covered the leaning pole and need to check and another tailboard after the incident occurred o Initial tailboard was not signed by the member on the pole (both Foreman and Member on the pole confirmed he was a part of the initial tailboard). o Initial tailboard noted leaning pole needed to be checked o Crew did not dig down at least 12" in depth to probe pole. SOP Requires you to dig a minimum of 12 inches in depth and probe the suspect pole with at least a 5” screw driver. There is indication that this is a gap across T&D. o If deterioration is found below ground line, determine if the pole can be secured by other means before climbing or performing work. o Anytime you are adding, removing, or changing pole tension you must also visually inspect the adjacent poles to ensure they are capable of withstanding the stress. o Dark during the duration of the job o Remaining Services was caught in tree which provided resistance o On Site at time of occurrence: Streber, Jesse Philler, Josh H, Mason Shetley, Derrick Davis o On the call prior to this one crew secured pole with a rope. o Crew had been working since 7 AM that morning (16.5 hours at the time of incident) o Member on pole is a step 24-10 apprentice o Foreman had been in position for 9 months | Terry Hackett | Mark Martin |  | West Service Center | FALSE |  | TRUE | Construction Services |  | Brandon Streber | Joshua Robertson |  | Terry Garrett | I agree with the corrective action...TG | Terry Garrett | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction | [10 empty] | Crew did not dig down and probe pole nor check adjacent poles | 16. Failure to Follow Procedure, Policy, Practice | 7. Caught Between or Under (Crushed or Amputated) | approved | Upon assessing the corrective actions determined by the investigation team. I believe these controls would prevent similar exposures such as this one in the future. Approved 1/21/20 | [90 empty] | 8590781
9194 | West Service Center | 2020-01-10 23:30 | while member was replacing open wire service from service pole to house pole broke 15 inches below ground level and fell slowly to the ground. No personal injuries and no damage to customer property. | Level 3 |  | TRUE | Member Injury | Andrea Dennis | Lindle Coleman | Assigned Per discussion with ops leaders | 2020-01-16 09:54 | Power Delivery | Joshua Robertson | 2020-01-27 15:12 | 2020-01-13 09:20 | 2020-01-13 09:20 | 2020-01-20 15:18 | 2020-01-24 23:30 | 2020-01-13 09:08 | 2020-01-23 14:46 | 2020-01-23 15:15 | 2020-01-21 15:51 | 1631 NW 13 street, OKC, OK |  |  | Andrea Dennis | I approve. | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Mark Martin |  | While crew was changing out bad open wire service the 30’6 service pole broke 15 inches below ground line and slowly fell to the ground while member was at the top of pole. Member sound checked the pole with his hammer and deemed the pole safe to climb, the member also stated that he checked the pole with his gaffs and the pole felt and sounded solid. Member climbed to the top of the 30’6 service pole and proceeded to cut the open wire service down. He checked the bottom leg of the service for tension before he cut it and let it to the ground. He did the same with the top hot leg and verified no tension. He proceeded to check the neutral wire for tension and verified that there was no tension on it before he cut it and let it down as well. After he let the neutral down to the ground the pole slowly started to fall toward the way the pole was naturally leaning. When the pole came to rest with the head of the pole approximately 2 feet from the ground the member was able to remove his safety from the pole and step away from the pole. Once the Foreman had made sure that the member climbing the service pole was OK he noticed that a 30’9 street light pole to the South of the service pole was broken and laying on the ground as well. Facts Ascertained: o Member stated he rapped 30’ class 6 service pole with hammer and was confident in it’s condition o Member also mentioned that his gaffs felt and sounded good and solid o Member then climbed pole cut bottom two legs (approximately 50’ span) and dropped them to the ground. o After cutting the neutral the pole began to slowly fall WNW to the ground (towards the direction the pole was leaning and the direction of the 3/0 triplex) o Service legs and neutral were not under tension o Service pole had 3/0 wrapped secondary coming to the pole, 3 services coming off of the pole, and a service for light pole. o Pole was leaning to the west. o Member was on the eastside of the pole o Member tried to slow pole with his left foot as it neared the ground. The pole scraped his left knee o All other crew members were out of the line of fire (3 at the house near the weatherhead and 1 at the truck in the front) o 30’ class 9 Light pole in front yard fell as well (unable to confirm if it was before or after service pole) o Service pole stopped a couple of feet from the ground due to the 3/0 secondary triplex which was caught up in tree limbs and a long service span remaining tied in. o Secondaries remained energized o Once pole came to a stop the crew assisted member in unbelting and getting off of the pole o They then cleared the services from the pole allowing it to go to the ground o After investigation it was determined the service pole broke approximately 15” from the ground level o Soil around pole hole was disturbed indicating it broke below ground level and ground line was visible on the pole 15” up from the lowest point. o Soil inclined across the back yard indicating the soil level may have been changed at some. This also resulted in a divot were the pole is that may allow water to pool o OGE Meteorologist (Matt Chatelain) provided wind and temperature conditions for the location at the time of the incident.  29 degrees Fahrenheit  NNW 35MPH Sustained  47 MPH Gusts o Crew held an initial tailboard that covered the leaning pole and need to check and another tailboard after the incident occurred o Initial tailboard was not signed by the member on the pole (both Foreman and Member on the pole confirmed he was a part of the initial tailboard). o Initial tailboard noted leaning pole needed to be checked o Crew did not dig down at least 12" in depth to probe pole. SOP Requires you to dig a minimum of 12 inches in depth and probe the suspect pole with at least a 5” screw driver. There is indication that this is a gap across T&D. o If deterioration is found below ground line, determine if the pole can be secured by other means before climbing or performing work. o Anytime you are adding, removing, or changing pole tension you must also visually inspect the adjacent poles to ensure they are capable of withstanding the stress. o Dark during the duration of the job o Remaining Services was caught in tree which provided resistance o On Site at time of occurrence: Streber, Jesse Philler, Josh H, Mason Shetley, Derrick Davis o On the call prior to this one crew secured pole with a rope. o Crew had been working since 7 AM that morning (16.5 hours at the time of incident) o Member on pole is a step 24-10 apprentice o Foreman had been in position for 9 months | Terry Hackett | Mark Martin |  | West Service Center | FALSE |  | TRUE | Construction Services |  | Brandon Streber | Joshua Robertson |  | Terry Garrett | I agree with the corrective action...TG | Terry Garrett | Lindle Coleman | High | [6 empty] | 7.01 Improper performance is rewarded (tolerated) | [9 empty] | Member sounded and gaff checked the pole but was unable to identify the deteriorated section of pole below the ground line. Must dig down at least 12" on suspect poles and probe. 7.01: There is indication that this is a gap across T&D. | 17. Failure to Identify Hazard, Risk | 7. Caught Between or Under (Crushed or Amputated) | approved | Upon assessing the corrective actions determined by the investigation team. I believe these controls would prevent similar exposures such as this one in the future. Approved 1/21/20 | [90 empty] | 8590781
9194 | West Service Center | 2020-01-10 23:30 | while member was replacing open wire service from service pole to house pole broke 15 inches below ground level and fell slowly to the ground. No personal injuries and no damage to customer property. | Level 3 |  | TRUE | Member Injury | Andrea Dennis | Lindle Coleman | Assigned Per discussion with ops leaders | 2020-01-16 09:54 | Power Delivery | Joshua Robertson | 2020-01-27 15:12 | 2020-01-13 09:20 | 2020-01-13 09:20 | 2020-01-20 15:18 | 2020-01-24 23:30 | 2020-01-13 09:08 | 2020-01-23 14:46 | 2020-01-23 15:15 | 2020-01-21 15:51 | 1631 NW 13 street, OKC, OK |  |  | Andrea Dennis | I approve. | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Mark Martin |  | While crew was changing out bad open wire service the 30’6 service pole broke 15 inches below ground line and slowly fell to the ground while member was at the top of pole. Member sound checked the pole with his hammer and deemed the pole safe to climb, the member also stated that he checked the pole with his gaffs and the pole felt and sounded solid. Member climbed to the top of the 30’6 service pole and proceeded to cut the open wire service down. He checked the bottom leg of the service for tension before he cut it and let it to the ground. He did the same with the top hot leg and verified no tension. He proceeded to check the neutral wire for tension and verified that there was no tension on it before he cut it and let it down as well. After he let the neutral down to the ground the pole slowly started to fall toward the way the pole was naturally leaning. When the pole came to rest with the head of the pole approximately 2 feet from the ground the member was able to remove his safety from the pole and step away from the pole. Once the Foreman had made sure that the member climbing the service pole was OK he noticed that a 30’9 street light pole to the South of the service pole was broken and laying on the ground as well. Facts Ascertained: o Member stated he rapped 30’ class 6 service pole with hammer and was confident in it’s condition o Member also mentioned that his gaffs felt and sounded good and solid o Member then climbed pole cut bottom two legs (approximately 50’ span) and dropped them to the ground. o After cutting the neutral the pole began to slowly fall WNW to the ground (towards the direction the pole was leaning and the direction of the 3/0 triplex) o Service legs and neutral were not under tension o Service pole had 3/0 wrapped secondary coming to the pole, 3 services coming off of the pole, and a service for light pole. o Pole was leaning to the west. o Member was on the eastside of the pole o Member tried to slow pole with his left foot as it neared the ground. The pole scraped his left knee o All other crew members were out of the line of fire (3 at the house near the weatherhead and 1 at the truck in the front) o 30’ class 9 Light pole in front yard fell as well (unable to confirm if it was before or after service pole) o Service pole stopped a couple of feet from the ground due to the 3/0 secondary triplex which was caught up in tree limbs and a long service span remaining tied in. o Secondaries remained energized o Once pole came to a stop the crew assisted member in unbelting and getting off of the pole o They then cleared the services from the pole allowing it to go to the ground o After investigation it was determined the service pole broke approximately 15” from the ground level o Soil around pole hole was disturbed indicating it broke below ground level and ground line was visible on the pole 15” up from the lowest point. o Soil inclined across the back yard indicating the soil level may have been changed at some. This also resulted in a divot were the pole is that may allow water to pool o OGE Meteorologist (Matt Chatelain) provided wind and temperature conditions for the location at the time of the incident.  29 degrees Fahrenheit  NNW 35MPH Sustained  47 MPH Gusts o Crew held an initial tailboard that covered the leaning pole and need to check and another tailboard after the incident occurred o Initial tailboard was not signed by the member on the pole (both Foreman and Member on the pole confirmed he was a part of the initial tailboard). o Initial tailboard noted leaning pole needed to be checked o Crew did not dig down at least 12" in depth to probe pole. SOP Requires you to dig a minimum of 12 inches in depth and probe the suspect pole with at least a 5” screw driver. There is indication that this is a gap across T&D. o If deterioration is found below ground line, determine if the pole can be secured by other means before climbing or performing work. o Anytime you are adding, removing, or changing pole tension you must also visually inspect the adjacent poles to ensure they are capable of withstanding the stress. o Dark during the duration of the job o Remaining Services was caught in tree which provided resistance o On Site at time of occurrence: Streber, Jesse Philler, Josh H, Mason Shetley, Derrick Davis o On the call prior to this one crew secured pole with a rope. o Crew had been working since 7 AM that morning (16.5 hours at the time of incident) o Member on pole is a step 24-10 apprentice o Foreman had been in position for 9 months | Terry Hackett | Mark Martin |  | West Service Center | FALSE |  | TRUE | Construction Services |  | Brandon Streber | Joshua Robertson |  | Terry Garrett | I agree with the corrective action...TG | Terry Garrett | Lindle Coleman | High | [6 empty] | 7.07 Improper attempt to avoid discomfort | [9 empty] | Pole broke 15" below ground level | 03. Failure to Secure | 7. Caught Between or Under (Crushed or Amputated) | approved | Upon assessing the corrective actions determined by the investigation team. I believe these controls would prevent similar exposures such as this one in the future. Approved 1/21/20 | [90 empty] | 8590781
9194 | West Service Center | 2020-01-10 23:30 | while member was replacing open wire service from service pole to house pole broke 15 inches below ground level and fell slowly to the ground. No personal injuries and no damage to customer property. | Level 3 |  | TRUE | Member Injury | Andrea Dennis | Lindle Coleman | Assigned Per discussion with ops leaders | 2020-01-16 09:54 | Power Delivery | Joshua Robertson | 2020-01-27 15:12 | 2020-01-13 09:20 | 2020-01-13 09:20 | 2020-01-20 15:18 | 2020-01-24 23:30 | 2020-01-13 09:08 | 2020-01-23 14:46 | 2020-01-23 15:15 | 2020-01-21 15:51 | 1631 NW 13 street, OKC, OK |  |  | Andrea Dennis | I approve. | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Mark Martin |  | While crew was changing out bad open wire service the 30’6 service pole broke 15 inches below ground line and slowly fell to the ground while member was at the top of pole. Member sound checked the pole with his hammer and deemed the pole safe to climb, the member also stated that he checked the pole with his gaffs and the pole felt and sounded solid. Member climbed to the top of the 30’6 service pole and proceeded to cut the open wire service down. He checked the bottom leg of the service for tension before he cut it and let it to the ground. He did the same with the top hot leg and verified no tension. He proceeded to check the neutral wire for tension and verified that there was no tension on it before he cut it and let it down as well. After he let the neutral down to the ground the pole slowly started to fall toward the way the pole was naturally leaning. When the pole came to rest with the head of the pole approximately 2 feet from the ground the member was able to remove his safety from the pole and step away from the pole. Once the Foreman had made sure that the member climbing the service pole was OK he noticed that a 30’9 street light pole to the South of the service pole was broken and laying on the ground as well. Facts Ascertained: o Member stated he rapped 30’ class 6 service pole with hammer and was confident in it’s condition o Member also mentioned that his gaffs felt and sounded good and solid o Member then climbed pole cut bottom two legs (approximately 50’ span) and dropped them to the ground. o After cutting the neutral the pole began to slowly fall WNW to the ground (towards the direction the pole was leaning and the direction of the 3/0 triplex) o Service legs and neutral were not under tension o Service pole had 3/0 wrapped secondary coming to the pole, 3 services coming off of the pole, and a service for light pole. o Pole was leaning to the west. o Member was on the eastside of the pole o Member tried to slow pole with his left foot as it neared the ground. The pole scraped his left knee o All other crew members were out of the line of fire (3 at the house near the weatherhead and 1 at the truck in the front) o 30’ class 9 Light pole in front yard fell as well (unable to confirm if it was before or after service pole) o Service pole stopped a couple of feet from the ground due to the 3/0 secondary triplex which was caught up in tree limbs and a long service span remaining tied in. o Secondaries remained energized o Once pole came to a stop the crew assisted member in unbelting and getting off of the pole o They then cleared the services from the pole allowing it to go to the ground o After investigation it was determined the service pole broke approximately 15” from the ground level o Soil around pole hole was disturbed indicating it broke below ground level and ground line was visible on the pole 15” up from the lowest point. o Soil inclined across the back yard indicating the soil level may have been changed at some. This also resulted in a divot were the pole is that may allow water to pool o OGE Meteorologist (Matt Chatelain) provided wind and temperature conditions for the location at the time of the incident.  29 degrees Fahrenheit  NNW 35MPH Sustained  47 MPH Gusts o Crew held an initial tailboard that covered the leaning pole and need to check and another tailboard after the incident occurred o Initial tailboard was not signed by the member on the pole (both Foreman and Member on the pole confirmed he was a part of the initial tailboard). o Initial tailboard noted leaning pole needed to be checked o Crew did not dig down at least 12" in depth to probe pole. SOP Requires you to dig a minimum of 12 inches in depth and probe the suspect pole with at least a 5” screw driver. There is indication that this is a gap across T&D. o If deterioration is found below ground line, determine if the pole can be secured by other means before climbing or performing work. o Anytime you are adding, removing, or changing pole tension you must also visually inspect the adjacent poles to ensure they are capable of withstanding the stress. o Dark during the duration of the job o Remaining Services was caught in tree which provided resistance o On Site at time of occurrence: Streber, Jesse Philler, Josh H, Mason Shetley, Derrick Davis o On the call prior to this one crew secured pole with a rope. o Crew had been working since 7 AM that morning (16.5 hours at the time of incident) o Member on pole is a step 24-10 apprentice o Foreman had been in position for 9 months | Terry Hackett | Mark Martin |  | West Service Center | FALSE |  | TRUE | Construction Services |  | Brandon Streber | Joshua Robertson |  | Terry Garrett | I agree with the corrective action...TG | Terry Garrett | Lindle Coleman | High | [13 empty] | 14.04 Inadequate monitoring of compliance |  |  | Member on pole did not sign tailboard | 16. Failure to Follow Procedure, Policy, Practice | 7. Caught Between or Under (Crushed or Amputated) | approved | Upon assessing the corrective actions determined by the investigation team. I believe these controls would prevent similar exposures such as this one in the future. Approved 1/21/20 | [90 empty] | 8590781
9195 | Northeast District Service Cen | 2020-01-12 13:00 | Member was driving South on Hwy 48 and struck public vehicle that was turning left. There were no injuries involved company vehicle was towed from site. | Level 2 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Donald Melson | 2020-01-21 10:51 | 2020-01-13 09:45 | 2020-01-13 09:45 | 2020-01-17 12:56 | 2020-01-26 13:00 | 2020-01-12 13:00 | 2020-01-21 10:48 |  | 2020-01-21 07:18 | .25 mile south of Hwy 48 and Hwy 51 West of Mannford |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Vehicle |  | FALSE | FALSE | TRUE |  | FALSE | TRUE | Donald Melson |  | The on call foreman driving F04-526 was on his way home from Mannford after going to church on January 12, 2020. He was traveling West on Hwy 51 at the intersection of Hwy 48 he turned South. He had traveled approximately an 1/8 of a mile at that time he took his attention off the road looking to the West at an empty lot proposed to be the site of a new building which took around 4-5 seconds. When he turned his attention back to the road a Ford Explorer was stopped turning left into the IN and OUT convenience store. He slammed on his brakes and turned his wheels to the right trying to divert F04-526. He could not get stopped and hit the right rear with left front causing damage to both vehicles. He was able to pull over to the shoulder and check on the public driver where she stated "that she was okay". Member then called 911 and Mannford Police responded to the seen, shortly after he called his supervisor. F04-526 had to be towed from the seen and public vehicle was able drive away from the seen. There were no citations given to the member. Investigation Findings: Member was not engaged while driving, after turning South he should have been aware of traffic in front of him. Weather was clear and highway was flat. Telematric's was reviewed and showed member going approximately 14 and 4 at the time of impact. Member took defensive driving in July 2017 and in compliance. |  |  |  | Northeast District Service Cen | FALSE |  | FALSE | Construction Services |  | Norris Carrier | Donald Melson |  | Chad Inman | Approved of initial Corrective Actions, but I also added an additional Corrective Action to be completed by the direct supervisor within 30 days. | Chad Inman |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Member was distracted and looked to his right as he looked back to the road a public driver was stopped turning left into a convenience store. | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) |  | Approved | [66 empty] | Public vehicle had damage to the right rear | 4000 | Norris Carrier | Vehicle (not related to operation of vehicle) |  |  | TRUE |  | Mannford | OGE Vehicle Struck Other Vehicle | Struck Stopped/Parked Vehicle | 1983-08-14 19:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
9195 | Northeast District Service Cen | 2020-01-12 13:00 | Member was driving South on Hwy 48 and struck public vehicle that was turning left. There were no injuries involved company vehicle was towed from site. | Level 2 |  | FALSE | Property Damage |  |  |  |  | Power Delivery | Donald Melson | 2020-01-21 10:51 | 2020-01-13 09:45 | 2020-01-13 09:45 | 2020-01-17 12:56 | 2020-01-26 13:00 | 2020-01-12 13:00 | 2020-01-21 10:48 |  | 2020-01-21 07:18 | .25 mile south of Hwy 48 and Hwy 51 West of Mannford |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | TRUE | Donald Melson |  | The on call foreman driving F04-526 was on his way home from Mannford after going to church on January 12, 2020. He was traveling West on Hwy 51 at the intersection of Hwy 48 he turned South. He had traveled approximately an 1/8 of a mile at that time he took his attention off the road looking to the West at an empty lot proposed to be the site of a new building which took around 4-5 seconds. When he turned his attention back to the road a Ford Explorer was stopped turning left into the IN and OUT convenience store. He slammed on his brakes and turned his wheels to the right trying to divert F04-526. He could not get stopped and hit the right rear with left front causing damage to both vehicles. He was able to pull over to the shoulder and check on the public driver where she stated "that she was okay". Member then called 911 and Mannford Police responded to the seen, shortly after he called his supervisor. F04-526 had to be towed from the seen and public vehicle was able drive away from the seen. There were no citations given to the member. Investigation Findings: Member was not engaged while driving, after turning South he should have been aware of traffic in front of him. Weather was clear and highway was flat. Telematric's was reviewed and showed member going approximately 14 and 4 at the time of impact. Member took defensive driving in July 2017 and in compliance. |  |  |  | Northeast District Service Cen | FALSE |  | FALSE | Construction Services |  | Norris Carrier | Donald Melson |  | Chad Inman | Approved of initial Corrective Actions, but I also added an additional Corrective Action to be completed by the direct supervisor within 30 days. | Chad Inman |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Member was distracted and looked to his right as he looked back to the road a public driver was stopped turning left into a convenience store. | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) |  | Approved | [66 empty] | Public vehicle had damage to the right rear | 4000 | Norris Carrier | Vehicle (not related to operation of vehicle) |  |  | TRUE |  | Mannford | OGE Vehicle Struck Other Vehicle | Struck Stopped/Parked Vehicle | 1983-08-14 19:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
9196 | Metro Service Center | 2020-01-13 06:30 | Member was Opening a box with a box knife and lacerated thumb. | Level 2 |  | FALSE | Member Injury |  |  |  |  | OGE Energy Corp | Willis Jones | 2020-02-05 10:52 | 2020-01-13 13:44 | 2020-01-13 13:44 | 2020-01-28 08:36 | 2020-01-27 06:30 | 2020-01-13 13:18 | 2020-01-30 09:57 |  | 2020-01-30 06:57 | Metro SC/Print Shop |  |  | William Young | Reviewed and approved. WCY 2/5/2020 | Enterprise Services |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Willis Jones |  | Removing the top of boxes, prepping for daily production of utility statements printing and mailing. using a Box knife ( safe cutter (sc1160), remove the top of box requires member to hold down one side of the box with left hand and cut the immediate top of box with right hand, this procedure is done to remove envelopes out of boxes and load into envelope inserter for mailing. member was not wearing gloves the knife is a retractable blade box knife approved by OGE, Blade had been recently changed and member was on her third box to remove top of box member while making a cut on the long side of the box approximately 6 inches before the end of the cut, the box knife lost contact with cardboard box and due pressure being applied in a inward fashion box knife came in contact with members left thumb(blade did not retract as design). After member was cut then proceeded to notify management. after first aid was applied member sought medical attention. this function is done when we prepare to print and mail OGE utility statement, Utility bill, 48 hour cutoff notice, final letters, and smart hours statements of a estimated quantity of 630 boxes per month. see attachments to view pictures of process. Knife was tested for proper function and on two occasions blade did not retract when loosing contact with cardboard. Knife was removed from service. Training for the Print Services was reviewed and found that the WBT for Hand & Portable Power Tools was not reviewed by the member or any members in the print services group, as well as the SSOP for Hand & Portable Power Tools. |  |  | FALSE | Metro Service Center | FALSE |  | FALSE | Supply Chain |  | Karen Canary | Willis Jones |  | Sharlett Combs | As reviewing manager, I am satisfied with the analysis, the investigation and the proposed Corrective Actions. Will support actions required to ensure ongoing safety of our members. | Sharlett Combs |  | Medium | [12 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | Box knife lost contact with cardboard did not retract and cut members thumb. | 07. Failing to Use PPE Properly | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved, Cody Vinyard | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 1993-03-22 | 1961-08-22 |  | 2020-01-13 06:00 | 0 | 0 |  | FALSE |  | Cutting top of box off with retractable box Knife. |  |  | Karen Canary |  | Recordable | Karen Canary | TRUE |  |  | McBride Occupational Clinic | Laceration |  | TRUE |  | Lead Managed Printing & Mailing Services | Thumb (1) | Injury | Left | TRUE | Willis Jones | TRUE | 2020 | 1/13/2020 6:00:00 AM |  | TRUE |  |  | Blade
9197 | Horseshoe Lake Power Plant | 2020-01-13 14:30 | While making tie in for new eye wash station contractor put excessive pressure on existing isolation valve causing 2" CPVC piping to crack on top upstream of isolation valve and releasing city water pressure. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Kelly Casey | 2020-02-10 17:10 | 2020-01-13 17:44 | 2020-01-13 17:44 | 2020-01-16 11:41 | 2020-01-27 14:30 | 2020-01-13 14:30 | 2020-02-03 08:44 |  |  | Tinker Power Block potable water main North East isolation access. |  |  | Chrysty Dorsey | Approved. | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | While making tie in for new 2" HDP pipe run, contractor was removing gravel and cement from under existing valves, flow meter, and spool pieces to allow bolting removal. The flanges were 2" raised face 4 bolt and the bottom bolt were buried in the gravel. When contractor removed the gravel to expose the flange bolting the weight of these pieces and pressure from member loosening bolting caused existing 2" CPVC piping to crack above LOTO isolation valve where the threaded male adaptor glues to the CPVC. Clearance isolation had to be established on Tinker AFB water main feeding the OGE substation for repairs to be made. After the repair the contractor was asked what could have been done to avoid the incident? Contractor stated that he could have supported the piping prior to using wrenches on flanges. Replacement piping was HDPE which will help with durability and gravel was used to support the new piping and tie in. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | FALSE | Power Supply Services |  | Shanon Reich | Kelly Casey |  | Brian Huckabay | Approved | Brian Huckabay |  | Low | [11 empty] | 12.01.3 Inadequate preventative adjustment/assembly | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | excessive force on unsupported material | 03. Failure to Secure | 11. Overstress, Overpressure, Overexertion, Ergonomic | [5 empty] | Property Damage |  | Kelly Casey | broken water line |  |  |  |  | 11. Overstress, Overpressure, Overexertion, Ergonomic | Shanon Reich | Zachary | Cory Toon |  | Utility Strike |  | Shanon Reich |  |  |  |  | FALSE | [66 empty] | 9592512
9198 | Enid Service Center | 2020-01-13 19:00 | member was headed east bound on hwy11 and struck a deer on front passenger side bumper causing minimal damage to bumper | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Mark Hamm | 2020-01-17 13:53 | 2020-01-14 11:53 | 2020-01-14 11:53 | 2020-01-14 12:46 | 2020-01-27 19:00 | 2020-01-14 11:46 |  |  |  | 4 miles west of hwy132 on hwy11 |  |  | Luke Kennedy | Upon reviewing the drivers telemetrics he was travelling the speed limit for the highway he was travelling on. Due to the time of day and the highway he was on I do believe the driver was using good defensive driving habits and did the best he could to avoid the deer. Approved 1/17/20 | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | [6 empty] | Enid Service Center | FALSE |  | FALSE | Construction Services |  | Dennis Pearson | Mark Hamm |  |  |  | Chad Inman |  | Low | [93 empty] | FALSE |  | medford | Animal-related |  | 2007-09-23 19:00 |  | FALSE |  |  | Night |  |  | Asphalt |  | Clear
9198 | Enid Service Center | 2020-01-13 19:00 | member was headed east bound on hwy11 and struck a deer on front passenger side bumper causing minimal damage to bumper | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Mark Hamm | 2020-01-17 13:53 | 2020-01-14 11:53 | 2020-01-14 11:53 | 2020-01-14 12:46 | 2020-01-27 19:00 | 2020-01-14 11:46 |  |  |  | 4 miles west of hwy132 on hwy11 |  |  | Luke Kennedy | Upon reviewing the drivers telemetrics he was travelling the speed limit for the highway he was travelling on. Due to the time of day and the highway he was on I do believe the driver was using good defensive driving habits and did the best he could to avoid the deer. Approved 1/17/20 | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | [6 empty] | Enid Service Center | FALSE |  | FALSE | Construction Services |  | Dennis Pearson | Mark Hamm |  |  |  | Chad Inman |  | Low | [93 empty] | FALSE |  | medford | Animal-related |  | 2007-09-23 19:00 |  | FALSE |  |  | Night |  |  | Asphalt |  | Clear
9199 | Metro Service Center | 2020-01-16 09:30 | Issued Hot Line Hold on incorrect device | Level 2 |  | FALSE | System Operational Incident |  |  |  |  | Power Delivery | Rachel Davis |  | 2020-01-16 17:30 |  | 2020-02-24 09:21 | 2020-02-27 09:30 | 2020-01-16 17:24 |  |  |  | North District Lone Oak 863 Circuit |  |  |  |  | T&D Ops |  | Level 2 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | Rachel Davis |  | Summary Sr. Operator inadvertently issued Hot Line Hold Order on Recloser 366150 causing circuit to lock open in Madill on Russett 590764 34.5kV Timeline Friday, November 15, 2019 at 08:43 Sr. Operator received a call from Foreman to start switching order M-1695 Friday, November 15, 2019 at 08:54 Lineman called Control 2 and spoke with Sr. Operator to request for a Hot Line Hold Order (HLHO) on Lone Oak 830863 34.5kV. He advised, he was working near Switch 32787. Sr. Operator told him he needs to see how many Normal Open he has before issuing the HLHO. Sr. Operator added this is an internal loop and wants to make sure everything is covered. Sr. Operator stated there are two Recloser 336170 and Recloser 336153. Sr. Operator advised Recloser 336170 is automated because he was able to issue a Hot Line Tag. Also, Sr. Operator told Lineman second Recloser 336150 not Recloser 336153. Sr. Operator issued the Hold Orders on both of the Reclosers on the Lone Oak 863 circuit. Friday, November 15, 2019 at 09:04 Foreman called requesting to speak with Sr. Operator to be issued a clearance at 09:08 Friday, November 15, 2019 at 09:05 Foreman called to give times to Sr. Operator on M-1695 Friday, November 15, 2019 at 09:22 Sr. Operator called Lineman back and told him he was ready to issue him two HLHO’s on Reclosers 336170 and Recloser 336150. Friday, November 15, 2019 at 09:23 Sr. Operator issued HLHO on N.O Recloser 336170 Friday, November 15, 2019 at 09:25 Sr. Operator issued HLHO on Recloser 336150 Thursday, November 21, 2019 at 10:12 Recloser 366150 on Russett 590764 34.5kV circuit in Madill locked open. When the Operator pulled up the SCADA screen of Recloser 366150 he noticed the Recloser had a Close Inhibit tag installed. After further investigation it was found that Recloser 336150 never had a Hot Line Tag installed so the Linecrew was working on the line with no protection and Recloser 366150 was on one shot from 11-15-2019 until it locked open on 11-21-2019 |  |  |  | Metro Service Center | FALSE |  | FALSE | System Operations |  | Rachel Davis | Rachel Davis |  | Darrell Fuller | Check wording and recloser number. | Darrell Fuller |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | 6.05 Inadequate review instruction | [7 empty] | 14.01.2 Inadequate development of standards: coordination with process design |  |  | Sr. Operator working on other task while issue HLHO order | 16. Failure to Follow Procedure, Policy, Practice | 9. Abnormal Operation |  | I agree with corrective actions cm
9200 | McClain Power Plant | 2020-01-17 08:00 | Contractor using scissor lift to access the potable water line, upon moving the lift into place the eyewash station was in the way, they shut the valve to isolate and disconnected the union so they could turn eyewash station around making room for the lift. No LOTO was in place for them to do this. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Danny Pogue | 2020-02-24 13:49 | 2020-01-17 10:49 | 2020-01-17 10:49 | 2020-01-28 15:47 | 2020-01-31 08:00 | 2020-01-17 10:01 | 2020-02-04 14:43 |  | 2020-01-28 17:07 | McClain Power Plant Demin Building south end eyewash and shower combo # 1PWI EYWI 0116 |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Kelly Casey |  | Contractor isolated potable water line to an individual eye wash station to move a man lift into position without a LOTO in place. During questioning and investigation Contractor thought he had the authority to isolate potable water lines associated with the project if it did not interfere with plant operations. It should be noted that this contractor moved from MK plant eye wash project to MC plant eye wash project that week. The operations group at MK and the OGE inspector had agreed that the contractor could isolate his newly installed valves at any time to check for leaks and pressure test the new equipment to establish flow rates and operation of the new units, but could not isolate plant valves with out going through the OGE inspector and plant Operations group first. It should also be noted that the valve that the contractor isolated only fed the eye wash station that was interfering with the manlift location and did not interrupt potable water process to the rest of the building. |  |  |  | McClain Power Plant | FALSE |  | TRUE | Special Services |  | Danny Pogue | Kelly Casey |  | Kelly Casey | The Safety Coordinator and I have discussed the cause check list and Zachry has resubmitted the revised incident investigation that aligns with our corrective items and review is completed. | Kelly Casey |  | Medium |  |  |  | 4.03 Extreme judgment/decision demands |  |  |  |  | 9.02 Unclear or conflicting assignment of responsibility | [7 empty] | Contractor did not follow LOTO policy | 01. Operating Equipment Without Authority | 9. Abnormal Operation |  | See workflow comments for reason being returned. I also left you a voicemail. UPDATE: Reviewed. |  |  |  | Clearance / LOTO |  | Kelly Casey | [5 empty] | 9. Abnormal Operation | Danny Pogue | Zachary | Mann Self |  |  |  | Danny Pogue | [71 empty] | 9583155
9201 | Metro Service Center | 2020-01-18 12:30 | When a member opened "C" phase in a switch gear, it pulled an arc that caused a "phase to phase fault". The "phase to phase" fault caused unexpected outages due to the substation circuit opening. | Level 3 |  | FALSE | System Operational Incident | Andrea Dennis | Lindle Coleman | Per discussion with Brent Perdue, who initially responded and met with operations. | 2020-01-20 07:39 | Power Delivery | Garren Dodson |  | 2020-01-18 15:50 |  |  | 2020-02-29 12:30 | 2020-01-18 15:33 |  |  |  | Tinker Air Force Base |  |  |  |  | T&D Ops |  | Level 3 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE |  |  | The crew was assigned to complete W.O. 7937035, which was to reroute an UG cable to meet OG&E construction standards. A tailboard was held and completed, then the foreman and a crew member started the switching order for that job. When they opened "C" phase on a switching cubicle during the switching order, the fuse drew an arc. The arc spread across the top of the other 2 fuses causing a phase to phase arc. Circuit 8531 was tripped out as a result of the fault created by the arc. | Steven Chisholm | Garren Dodson |  | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Zac Barnes | Garren Dodson |  |  |  | Gary Lassley |  | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  |  |  |  | 15.02 Improper extension of service life |  | arc suppression did not operate as designed when the fuse was opened. | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure | [92 empty] | 7937035
9201 | Metro Service Center | 2020-01-18 12:30 | When a member opened "C" phase in a switch gear, it pulled an arc that caused a "phase to phase fault". The "phase to phase" fault caused unexpected outages due to the substation circuit opening. | Level 3 |  | FALSE | System Operational Incident | Andrea Dennis | Lindle Coleman | Per discussion with Brent Perdue, who initially responded and met with operations. | 2020-01-20 07:39 | Power Delivery | Garren Dodson |  | 2020-01-18 15:50 |  |  | 2020-02-29 12:30 | 2020-01-18 15:33 |  |  |  | Tinker Air Force Base |  |  |  |  | T&D Ops |  | Level 3 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE |  |  | The crew was assigned to complete W.O. 7937035, which was to reroute an UG cable to meet OG&E construction standards. A tailboard was held and completed, then the foreman and a crew member started the switching order for that job. When they opened "C" phase on a switching cubicle during the switching order, the fuse drew an arc. The arc spread across the top of the other 2 fuses causing a phase to phase arc. Circuit 8531 was tripped out as a result of the fault created by the arc. | Brent Perdue | Garren Dodson |  | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Zac Barnes | Garren Dodson |  |  |  | Gary Lassley |  | High | [9 empty] | 10.05 Inadequate assessment of operational readiness |  |  |  |  | 15.02 Improper extension of service life |  | arc suppression did not operate as designed when the fuse was opened. | 23. Defective Tools, Equipment or Materials | 12. Equipment Failure | [92 empty] | 7937035
9202 | Shawnee Service Center | 2020-01-20 16:30 | Vegetation contractor crawled into chipper to clear a jam, and did not follow LOTO procedures. (Chipper WAS NOT running) | Level 3 |  | TRUE | Contractor | Andrea Dennis | William Young | Investigate, establish causal factors and CA's. WCY 2/7/2020 | 2020-02-07 07:54 | OG&E Corp Services | Wesley Lanier |  | 2020-01-21 11:49 | 2020-01-21 11:49 | 2020-02-24 10:27 | 2020-02-03 16:30 | 2020-01-21 11:17 |  |  | 2020-02-24 12:34 | Chandler Oklahoma West of highway 18 on East 890 Rd. |  |  |  |  | T&D Ops |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Cody Vinyard |  | Monday, approx. 4:30pm, 1/20/2020, after leaving Kellyville SC, OGE member checked on Asplundh crews working in Chandler area. As member turned west off Hwy 18 on E890 there was Asplundh split dump set up on south side of road approximately 100-200 yards from Hwy 18 on E 890. Member ‘s initial observation was that crew had a sign just west of Hwy 18 on 890 Rd - truck was coned off and member could see identified work/drop zone where crew had been cutting. As member got near end of truck, could see workers standing at back of chipper. As member got past truck, chipper, and crew members, looked in rearview mirror and could see set of legs sticking out of chipper. OGE member immediately stopped and asked nearest crew member what was going on. He explained chipper was clogged and they were unclogging it. Member asked if keys were in chipper - crew member said he did not know. Alarmed, the member pulled into crew’s coned-off area on south side of road. Upon arrival, Forman, Michael Herring, who had been on chipper feed table, crawled out. OGE member asked crew member who was first Asplundh crew member spoken to about the keys and he produced them but said they had, indeed, been in the chipper and he removed them. The Foreman, Michael Herring, stated he was unsure of steps that should have been taken but knew the chipper was clogged and they needed to finish chipping brush for the day. OGE Findings: LOTO/Unclogging Procedure not followed o No Job Briefing for "unclogging" conducted o Keys left in ignition o No pinning process indicated o Rollers were jacked/lifted o Truck wheels chocked (trailer not chocked per procedure since attached) Crew Foreman, Herring, not aware of LOTO procedure (4-yr empl) o Chipper training on 5/4/18 General Forman, Lester, on job a few months as GF Asplundh Safety, Robt Brown, estimates chipper unclogging occurs every 3 months on average. Close Call report conducted by Asplundh • Lacking in detail • No formal investigation into procedure violation Overall, poor response to identify unsafe behaviors for Close Call investigation Information provided for Stand Down does not match information covered on Roster Asplundh Corrective Actions: Stand Down and retraining occurred the following day (1/21/20) for all crews reporting to this GF (roster attached) LOTO/Unclogging Procedure JHA for Chipper maintenance | Jerrie Looney | Cody Vinyard |  | Shawnee Service Center | FALSE |  | TRUE | PD - Resource Planning & Coord |  | Wesley Lanier | Wesley Lanier |  |  |  | Michael Fox |  | High |  |  |  |  | 5.03 Inadequate initial training | 6.03 Infrequent performance |  |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | Vegetation contractor crawled into chipper to clear a jam, and did not follow LOTO procedures. (Chipper WAS NOT running) | 16. Failure to Follow Procedure, Policy, Practice | 5. Caught In (Pinch and Nip Points) |  | Approved, J. Looney 2/24/20 |  |  |  | Clearance / LOTO |  | Wesley Lanier | [5 empty] | 9. Abnormal Operation | Wesley Lanier | Asplundh Tree Experts | Michael Herring |  |  |  | Wesley Lanier
9202 | Shawnee Service Center | 2020-01-20 16:30 | Vegetation contractor crawled into chipper to clear a jam, and did not follow LOTO procedures. (Chipper WAS NOT running) | Level 3 |  | TRUE | Contractor | Andrea Dennis | William Young | Investigate, establish causal factors and CA's. WCY 2/7/2020 | 2020-02-07 07:54 | OG&E Corp Services | Wesley Lanier |  | 2020-01-21 11:49 | 2020-01-21 11:49 | 2020-02-24 10:27 | 2020-02-03 16:30 | 2020-01-21 11:17 |  |  | 2020-02-24 12:34 | Chandler Oklahoma West of highway 18 on East 890 Rd. |  |  |  |  | T&D Ops |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Cody Vinyard |  | Monday, approx. 4:30pm, 1/20/2020, after leaving Kellyville SC, OGE member checked on Asplundh crews working in Chandler area. As member turned west off Hwy 18 on E890 there was Asplundh split dump set up on south side of road approximately 100-200 yards from Hwy 18 on E 890. Member ‘s initial observation was that crew had a sign just west of Hwy 18 on 890 Rd - truck was coned off and member could see identified work/drop zone where crew had been cutting. As member got near end of truck, could see workers standing at back of chipper. As member got past truck, chipper, and crew members, looked in rearview mirror and could see set of legs sticking out of chipper. OGE member immediately stopped and asked nearest crew member what was going on. He explained chipper was clogged and they were unclogging it. Member asked if keys were in chipper - crew member said he did not know. Alarmed, the member pulled into crew’s coned-off area on south side of road. Upon arrival, Forman, Michael Herring, who had been on chipper feed table, crawled out. OGE member asked crew member who was first Asplundh crew member spoken to about the keys and he produced them but said they had, indeed, been in the chipper and he removed them. The Foreman, Michael Herring, stated he was unsure of steps that should have been taken but knew the chipper was clogged and they needed to finish chipping brush for the day. OGE Findings: LOTO/Unclogging Procedure not followed o No Job Briefing for "unclogging" conducted o Keys left in ignition o No pinning process indicated o Rollers were jacked/lifted o Truck wheels chocked (trailer not chocked per procedure since attached) Crew Foreman, Herring, not aware of LOTO procedure (4-yr empl) o Chipper training on 5/4/18 General Forman, Lester, on job a few months as GF Asplundh Safety, Robt Brown, estimates chipper unclogging occurs every 3 months on average. Close Call report conducted by Asplundh • Lacking in detail • No formal investigation into procedure violation Overall, poor response to identify unsafe behaviors for Close Call investigation Information provided for Stand Down does not match information covered on Roster Asplundh Corrective Actions: Stand Down and retraining occurred the following day (1/21/20) for all crews reporting to this GF (roster attached) LOTO/Unclogging Procedure JHA for Chipper maintenance | Jerrie Looney | Cody Vinyard |  | Shawnee Service Center | FALSE |  | TRUE | PD - Resource Planning & Coord |  | Wesley Lanier | Wesley Lanier |  |  |  | Michael Fox |  | High |  |  |  |  | 5.03 Inadequate initial training | 6.03 Infrequent performance |  |  | 9.11 Inadequate matching of individual qualifications and job/task requirements |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | Vegetation contractor crawled into chipper to clear a jam, and did not follow LOTO procedures. (Chipper WAS NOT running) | 16. Failure to Follow Procedure, Policy, Practice | 5. Caught In (Pinch and Nip Points) |  | Approved, J. Looney 2/24/20 |  |  |  | Clearance / LOTO |  | Wesley Lanier | [5 empty] | 9. Abnormal Operation | Wesley Lanier | Asplundh Tree Experts | Michael Herring |  |  |  | Wesley Lanier
9202 | Shawnee Service Center | 2020-01-20 16:30 | Vegetation contractor crawled into chipper to clear a jam, and did not follow LOTO procedures. (Chipper WAS NOT running) | Level 3 |  | TRUE | Contractor | Andrea Dennis | William Young | Investigate, establish causal factors and CA's. WCY 2/7/2020 | 2020-02-07 07:54 | OG&E Corp Services | Wesley Lanier |  | 2020-01-21 11:49 | 2020-01-21 11:49 | 2020-02-24 10:27 | 2020-02-03 16:30 | 2020-01-21 11:17 |  |  | 2020-02-24 12:34 | Chandler Oklahoma West of highway 18 on East 890 Rd. |  |  |  |  | T&D Ops |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Cody Vinyard |  | Monday, approx. 4:30pm, 1/20/2020, after leaving Kellyville SC, OGE member checked on Asplundh crews working in Chandler area. As member turned west off Hwy 18 on E890 there was Asplundh split dump set up on south side of road approximately 100-200 yards from Hwy 18 on E 890. Member ‘s initial observation was that crew had a sign just west of Hwy 18 on 890 Rd - truck was coned off and member could see identified work/drop zone where crew had been cutting. As member got near end of truck, could see workers standing at back of chipper. As member got past truck, chipper, and crew members, looked in rearview mirror and could see set of legs sticking out of chipper. OGE member immediately stopped and asked nearest crew member what was going on. He explained chipper was clogged and they were unclogging it. Member asked if keys were in chipper - crew member said he did not know. Alarmed, the member pulled into crew’s coned-off area on south side of road. Upon arrival, Forman, Michael Herring, who had been on chipper feed table, crawled out. OGE member asked crew member who was first Asplundh crew member spoken to about the keys and he produced them but said they had, indeed, been in the chipper and he removed them. The Foreman, Michael Herring, stated he was unsure of steps that should have been taken but knew the chipper was clogged and they needed to finish chipping brush for the day. OGE Findings: LOTO/Unclogging Procedure not followed o No Job Briefing for "unclogging" conducted o Keys left in ignition o No pinning process indicated o Rollers were jacked/lifted o Truck wheels chocked (trailer not chocked per procedure since attached) Crew Foreman, Herring, not aware of LOTO procedure (4-yr empl) o Chipper training on 5/4/18 General Forman, Lester, on job a few months as GF Asplundh Safety, Robt Brown, estimates chipper unclogging occurs every 3 months on average. Close Call report conducted by Asplundh • Lacking in detail • No formal investigation into procedure violation Overall, poor response to identify unsafe behaviors for Close Call investigation Information provided for Stand Down does not match information covered on Roster Asplundh Corrective Actions: Stand Down and retraining occurred the following day (1/21/20) for all crews reporting to this GF (roster attached) LOTO/Unclogging Procedure JHA for Chipper maintenance | Jerrie Looney | Cody Vinyard |  | Shawnee Service Center | FALSE |  | TRUE | PD - Resource Planning & Coord |  | Wesley Lanier | Wesley Lanier |  |  |  | Michael Fox |  | High |  |  |  |  | 5.03 Inadequate initial training | 6.01 Inadequate initial instruction |  |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | Vegetation contractor crawled into chipper to clear a jam, and did not follow LOTO procedures. (Chipper WAS NOT running) | 16. Failure to Follow Procedure, Policy, Practice | 5. Caught In (Pinch and Nip Points) |  | Approved, J. Looney 2/24/20 |  |  |  | Clearance / LOTO |  | Wesley Lanier | [5 empty] | 9. Abnormal Operation | Wesley Lanier | Asplundh Tree Experts | Michael Herring |  |  |  | Wesley Lanier
9202 | Shawnee Service Center | 2020-01-20 16:30 | Vegetation contractor crawled into chipper to clear a jam, and did not follow LOTO procedures. (Chipper WAS NOT running) | Level 3 |  | TRUE | Contractor | Andrea Dennis | William Young | Investigate, establish causal factors and CA's. WCY 2/7/2020 | 2020-02-07 07:54 | OG&E Corp Services | Wesley Lanier |  | 2020-01-21 11:49 | 2020-01-21 11:49 | 2020-02-24 10:27 | 2020-02-03 16:30 | 2020-01-21 11:17 |  |  | 2020-02-24 12:34 | Chandler Oklahoma West of highway 18 on East 890 Rd. |  |  |  |  | T&D Ops |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Cody Vinyard |  | Monday, approx. 4:30pm, 1/20/2020, after leaving Kellyville SC, OGE member checked on Asplundh crews working in Chandler area. As member turned west off Hwy 18 on E890 there was Asplundh split dump set up on south side of road approximately 100-200 yards from Hwy 18 on E 890. Member ‘s initial observation was that crew had a sign just west of Hwy 18 on 890 Rd - truck was coned off and member could see identified work/drop zone where crew had been cutting. As member got near end of truck, could see workers standing at back of chipper. As member got past truck, chipper, and crew members, looked in rearview mirror and could see set of legs sticking out of chipper. OGE member immediately stopped and asked nearest crew member what was going on. He explained chipper was clogged and they were unclogging it. Member asked if keys were in chipper - crew member said he did not know. Alarmed, the member pulled into crew’s coned-off area on south side of road. Upon arrival, Forman, Michael Herring, who had been on chipper feed table, crawled out. OGE member asked crew member who was first Asplundh crew member spoken to about the keys and he produced them but said they had, indeed, been in the chipper and he removed them. The Foreman, Michael Herring, stated he was unsure of steps that should have been taken but knew the chipper was clogged and they needed to finish chipping brush for the day. OGE Findings: LOTO/Unclogging Procedure not followed o No Job Briefing for "unclogging" conducted o Keys left in ignition o No pinning process indicated o Rollers were jacked/lifted o Truck wheels chocked (trailer not chocked per procedure since attached) Crew Foreman, Herring, not aware of LOTO procedure (4-yr empl) o Chipper training on 5/4/18 General Forman, Lester, on job a few months as GF Asplundh Safety, Robt Brown, estimates chipper unclogging occurs every 3 months on average. Close Call report conducted by Asplundh • Lacking in detail • No formal investigation into procedure violation Overall, poor response to identify unsafe behaviors for Close Call investigation Information provided for Stand Down does not match information covered on Roster Asplundh Corrective Actions: Stand Down and retraining occurred the following day (1/21/20) for all crews reporting to this GF (roster attached) LOTO/Unclogging Procedure JHA for Chipper maintenance | Jerrie Looney | Cody Vinyard |  | Shawnee Service Center | FALSE |  | TRUE | PD - Resource Planning & Coord |  | Wesley Lanier | Wesley Lanier |  |  |  | Michael Fox |  | High |  |  |  |  | 5.03 Inadequate initial training | 6.01 Inadequate initial instruction |  |  | 9.11 Inadequate matching of individual qualifications and job/task requirements |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | Vegetation contractor crawled into chipper to clear a jam, and did not follow LOTO procedures. (Chipper WAS NOT running) | 16. Failure to Follow Procedure, Policy, Practice | 5. Caught In (Pinch and Nip Points) |  | Approved, J. Looney 2/24/20 |  |  |  | Clearance / LOTO |  | Wesley Lanier | [5 empty] | 9. Abnormal Operation | Wesley Lanier | Asplundh Tree Experts | Michael Herring |  |  |  | Wesley Lanier
9202 | Shawnee Service Center | 2020-01-20 16:30 | Vegetation contractor crawled into chipper to clear a jam, and did not follow LOTO procedures. (Chipper WAS NOT running) | Level 3 |  | TRUE | Contractor | Andrea Dennis | William Young | Investigate, establish causal factors and CA's. WCY 2/7/2020 | 2020-02-07 07:54 | OG&E Corp Services | Wesley Lanier |  | 2020-01-21 11:49 | 2020-01-21 11:49 | 2020-02-24 10:27 | 2020-02-03 16:30 | 2020-01-21 11:17 |  |  | 2020-02-24 12:34 | Chandler Oklahoma West of highway 18 on East 890 Rd. |  |  |  |  | T&D Ops |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Cody Vinyard |  | Monday, approx. 4:30pm, 1/20/2020, after leaving Kellyville SC, OGE member checked on Asplundh crews working in Chandler area. As member turned west off Hwy 18 on E890 there was Asplundh split dump set up on south side of road approximately 100-200 yards from Hwy 18 on E 890. Member ‘s initial observation was that crew had a sign just west of Hwy 18 on 890 Rd - truck was coned off and member could see identified work/drop zone where crew had been cutting. As member got near end of truck, could see workers standing at back of chipper. As member got past truck, chipper, and crew members, looked in rearview mirror and could see set of legs sticking out of chipper. OGE member immediately stopped and asked nearest crew member what was going on. He explained chipper was clogged and they were unclogging it. Member asked if keys were in chipper - crew member said he did not know. Alarmed, the member pulled into crew’s coned-off area on south side of road. Upon arrival, Forman, Michael Herring, who had been on chipper feed table, crawled out. OGE member asked crew member who was first Asplundh crew member spoken to about the keys and he produced them but said they had, indeed, been in the chipper and he removed them. The Foreman, Michael Herring, stated he was unsure of steps that should have been taken but knew the chipper was clogged and they needed to finish chipping brush for the day. OGE Findings: LOTO/Unclogging Procedure not followed o No Job Briefing for "unclogging" conducted o Keys left in ignition o No pinning process indicated o Rollers were jacked/lifted o Truck wheels chocked (trailer not chocked per procedure since attached) Crew Foreman, Herring, not aware of LOTO procedure (4-yr empl) o Chipper training on 5/4/18 General Forman, Lester, on job a few months as GF Asplundh Safety, Robt Brown, estimates chipper unclogging occurs every 3 months on average. Close Call report conducted by Asplundh • Lacking in detail • No formal investigation into procedure violation Overall, poor response to identify unsafe behaviors for Close Call investigation Information provided for Stand Down does not match information covered on Roster Asplundh Corrective Actions: Stand Down and retraining occurred the following day (1/21/20) for all crews reporting to this GF (roster attached) LOTO/Unclogging Procedure JHA for Chipper maintenance | Shawn Huff | Cody Vinyard |  | Shawnee Service Center | FALSE |  | TRUE | PD - Resource Planning & Coord |  | Wesley Lanier | Wesley Lanier |  |  |  | Michael Fox |  | High |  |  |  |  | 5.03 Inadequate initial training | 6.03 Infrequent performance |  |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | Vegetation contractor crawled into chipper to clear a jam, and did not follow LOTO procedures. (Chipper WAS NOT running) | 16. Failure to Follow Procedure, Policy, Practice | 5. Caught In (Pinch and Nip Points) |  | Approved, J. Looney 2/24/20 |  |  |  | Clearance / LOTO |  | Wesley Lanier | [5 empty] | 9. Abnormal Operation | Wesley Lanier | Asplundh Tree Experts | Michael Herring |  |  |  | Wesley Lanier
9202 | Shawnee Service Center | 2020-01-20 16:30 | Vegetation contractor crawled into chipper to clear a jam, and did not follow LOTO procedures. (Chipper WAS NOT running) | Level 3 |  | TRUE | Contractor | Andrea Dennis | William Young | Investigate, establish causal factors and CA's. WCY 2/7/2020 | 2020-02-07 07:54 | OG&E Corp Services | Wesley Lanier |  | 2020-01-21 11:49 | 2020-01-21 11:49 | 2020-02-24 10:27 | 2020-02-03 16:30 | 2020-01-21 11:17 |  |  | 2020-02-24 12:34 | Chandler Oklahoma West of highway 18 on East 890 Rd. |  |  |  |  | T&D Ops |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Cody Vinyard |  | Monday, approx. 4:30pm, 1/20/2020, after leaving Kellyville SC, OGE member checked on Asplundh crews working in Chandler area. As member turned west off Hwy 18 on E890 there was Asplundh split dump set up on south side of road approximately 100-200 yards from Hwy 18 on E 890. Member ‘s initial observation was that crew had a sign just west of Hwy 18 on 890 Rd - truck was coned off and member could see identified work/drop zone where crew had been cutting. As member got near end of truck, could see workers standing at back of chipper. As member got past truck, chipper, and crew members, looked in rearview mirror and could see set of legs sticking out of chipper. OGE member immediately stopped and asked nearest crew member what was going on. He explained chipper was clogged and they were unclogging it. Member asked if keys were in chipper - crew member said he did not know. Alarmed, the member pulled into crew’s coned-off area on south side of road. Upon arrival, Forman, Michael Herring, who had been on chipper feed table, crawled out. OGE member asked crew member who was first Asplundh crew member spoken to about the keys and he produced them but said they had, indeed, been in the chipper and he removed them. The Foreman, Michael Herring, stated he was unsure of steps that should have been taken but knew the chipper was clogged and they needed to finish chipping brush for the day. OGE Findings: LOTO/Unclogging Procedure not followed o No Job Briefing for "unclogging" conducted o Keys left in ignition o No pinning process indicated o Rollers were jacked/lifted o Truck wheels chocked (trailer not chocked per procedure since attached) Crew Foreman, Herring, not aware of LOTO procedure (4-yr empl) o Chipper training on 5/4/18 General Forman, Lester, on job a few months as GF Asplundh Safety, Robt Brown, estimates chipper unclogging occurs every 3 months on average. Close Call report conducted by Asplundh • Lacking in detail • No formal investigation into procedure violation Overall, poor response to identify unsafe behaviors for Close Call investigation Information provided for Stand Down does not match information covered on Roster Asplundh Corrective Actions: Stand Down and retraining occurred the following day (1/21/20) for all crews reporting to this GF (roster attached) LOTO/Unclogging Procedure JHA for Chipper maintenance | Shawn Huff | Cody Vinyard |  | Shawnee Service Center | FALSE |  | TRUE | PD - Resource Planning & Coord |  | Wesley Lanier | Wesley Lanier |  |  |  | Michael Fox |  | High |  |  |  |  | 5.03 Inadequate initial training | 6.03 Infrequent performance |  |  | 9.11 Inadequate matching of individual qualifications and job/task requirements |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | Vegetation contractor crawled into chipper to clear a jam, and did not follow LOTO procedures. (Chipper WAS NOT running) | 16. Failure to Follow Procedure, Policy, Practice | 5. Caught In (Pinch and Nip Points) |  | Approved, J. Looney 2/24/20 |  |  |  | Clearance / LOTO |  | Wesley Lanier | [5 empty] | 9. Abnormal Operation | Wesley Lanier | Asplundh Tree Experts | Michael Herring |  |  |  | Wesley Lanier
9202 | Shawnee Service Center | 2020-01-20 16:30 | Vegetation contractor crawled into chipper to clear a jam, and did not follow LOTO procedures. (Chipper WAS NOT running) | Level 3 |  | TRUE | Contractor | Andrea Dennis | William Young | Investigate, establish causal factors and CA's. WCY 2/7/2020 | 2020-02-07 07:54 | OG&E Corp Services | Wesley Lanier |  | 2020-01-21 11:49 | 2020-01-21 11:49 | 2020-02-24 10:27 | 2020-02-03 16:30 | 2020-01-21 11:17 |  |  | 2020-02-24 12:34 | Chandler Oklahoma West of highway 18 on East 890 Rd. |  |  |  |  | T&D Ops |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Cody Vinyard |  | Monday, approx. 4:30pm, 1/20/2020, after leaving Kellyville SC, OGE member checked on Asplundh crews working in Chandler area. As member turned west off Hwy 18 on E890 there was Asplundh split dump set up on south side of road approximately 100-200 yards from Hwy 18 on E 890. Member ‘s initial observation was that crew had a sign just west of Hwy 18 on 890 Rd - truck was coned off and member could see identified work/drop zone where crew had been cutting. As member got near end of truck, could see workers standing at back of chipper. As member got past truck, chipper, and crew members, looked in rearview mirror and could see set of legs sticking out of chipper. OGE member immediately stopped and asked nearest crew member what was going on. He explained chipper was clogged and they were unclogging it. Member asked if keys were in chipper - crew member said he did not know. Alarmed, the member pulled into crew’s coned-off area on south side of road. Upon arrival, Forman, Michael Herring, who had been on chipper feed table, crawled out. OGE member asked crew member who was first Asplundh crew member spoken to about the keys and he produced them but said they had, indeed, been in the chipper and he removed them. The Foreman, Michael Herring, stated he was unsure of steps that should have been taken but knew the chipper was clogged and they needed to finish chipping brush for the day. OGE Findings: LOTO/Unclogging Procedure not followed o No Job Briefing for "unclogging" conducted o Keys left in ignition o No pinning process indicated o Rollers were jacked/lifted o Truck wheels chocked (trailer not chocked per procedure since attached) Crew Foreman, Herring, not aware of LOTO procedure (4-yr empl) o Chipper training on 5/4/18 General Forman, Lester, on job a few months as GF Asplundh Safety, Robt Brown, estimates chipper unclogging occurs every 3 months on average. Close Call report conducted by Asplundh • Lacking in detail • No formal investigation into procedure violation Overall, poor response to identify unsafe behaviors for Close Call investigation Information provided for Stand Down does not match information covered on Roster Asplundh Corrective Actions: Stand Down and retraining occurred the following day (1/21/20) for all crews reporting to this GF (roster attached) LOTO/Unclogging Procedure JHA for Chipper maintenance | Shawn Huff | Cody Vinyard |  | Shawnee Service Center | FALSE |  | TRUE | PD - Resource Planning & Coord |  | Wesley Lanier | Wesley Lanier |  |  |  | Michael Fox |  | High |  |  |  |  | 5.03 Inadequate initial training | 6.01 Inadequate initial instruction |  |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | Vegetation contractor crawled into chipper to clear a jam, and did not follow LOTO procedures. (Chipper WAS NOT running) | 16. Failure to Follow Procedure, Policy, Practice | 5. Caught In (Pinch and Nip Points) |  | Approved, J. Looney 2/24/20 |  |  |  | Clearance / LOTO |  | Wesley Lanier | [5 empty] | 9. Abnormal Operation | Wesley Lanier | Asplundh Tree Experts | Michael Herring |  |  |  | Wesley Lanier
9202 | Shawnee Service Center | 2020-01-20 16:30 | Vegetation contractor crawled into chipper to clear a jam, and did not follow LOTO procedures. (Chipper WAS NOT running) | Level 3 |  | TRUE | Contractor | Andrea Dennis | William Young | Investigate, establish causal factors and CA's. WCY 2/7/2020 | 2020-02-07 07:54 | OG&E Corp Services | Wesley Lanier |  | 2020-01-21 11:49 | 2020-01-21 11:49 | 2020-02-24 10:27 | 2020-02-03 16:30 | 2020-01-21 11:17 |  |  | 2020-02-24 12:34 | Chandler Oklahoma West of highway 18 on East 890 Rd. |  |  |  |  | T&D Ops |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Cody Vinyard |  | Monday, approx. 4:30pm, 1/20/2020, after leaving Kellyville SC, OGE member checked on Asplundh crews working in Chandler area. As member turned west off Hwy 18 on E890 there was Asplundh split dump set up on south side of road approximately 100-200 yards from Hwy 18 on E 890. Member ‘s initial observation was that crew had a sign just west of Hwy 18 on 890 Rd - truck was coned off and member could see identified work/drop zone where crew had been cutting. As member got near end of truck, could see workers standing at back of chipper. As member got past truck, chipper, and crew members, looked in rearview mirror and could see set of legs sticking out of chipper. OGE member immediately stopped and asked nearest crew member what was going on. He explained chipper was clogged and they were unclogging it. Member asked if keys were in chipper - crew member said he did not know. Alarmed, the member pulled into crew’s coned-off area on south side of road. Upon arrival, Forman, Michael Herring, who had been on chipper feed table, crawled out. OGE member asked crew member who was first Asplundh crew member spoken to about the keys and he produced them but said they had, indeed, been in the chipper and he removed them. The Foreman, Michael Herring, stated he was unsure of steps that should have been taken but knew the chipper was clogged and they needed to finish chipping brush for the day. OGE Findings: LOTO/Unclogging Procedure not followed o No Job Briefing for "unclogging" conducted o Keys left in ignition o No pinning process indicated o Rollers were jacked/lifted o Truck wheels chocked (trailer not chocked per procedure since attached) Crew Foreman, Herring, not aware of LOTO procedure (4-yr empl) o Chipper training on 5/4/18 General Forman, Lester, on job a few months as GF Asplundh Safety, Robt Brown, estimates chipper unclogging occurs every 3 months on average. Close Call report conducted by Asplundh • Lacking in detail • No formal investigation into procedure violation Overall, poor response to identify unsafe behaviors for Close Call investigation Information provided for Stand Down does not match information covered on Roster Asplundh Corrective Actions: Stand Down and retraining occurred the following day (1/21/20) for all crews reporting to this GF (roster attached) LOTO/Unclogging Procedure JHA for Chipper maintenance | Shawn Huff | Cody Vinyard |  | Shawnee Service Center | FALSE |  | TRUE | PD - Resource Planning & Coord |  | Wesley Lanier | Wesley Lanier |  |  |  | Michael Fox |  | High |  |  |  |  | 5.03 Inadequate initial training | 6.01 Inadequate initial instruction |  |  | 9.11 Inadequate matching of individual qualifications and job/task requirements |  |  |  |  | 14.02.4 Inadequate communication of standards: training |  |  | Vegetation contractor crawled into chipper to clear a jam, and did not follow LOTO procedures. (Chipper WAS NOT running) | 16. Failure to Follow Procedure, Policy, Practice | 5. Caught In (Pinch and Nip Points) |  | Approved, J. Looney 2/24/20 |  |  |  | Clearance / LOTO |  | Wesley Lanier | [5 empty] | 9. Abnormal Operation | Wesley Lanier | Asplundh Tree Experts | Michael Herring |  |  |  | Wesley Lanier
9203 | Seminole PP; EGX Gath/Trans | 2020-01-22 10:00 | Wrong valve installed in sealing steam line. Valve was not the correct specification for this service. The valve was discovered before the system was returned to service. | Level 3 |  | TRUE | Member Injury | Donnie Jones | Jesse Murray | Assigned Per Matt S and Scott Lee | 2020-01-23 15:10 | Power Supply | Paul Schoelen |  | 2020-01-22 13:35 | 2020-01-22 13:35 |  | 2020-02-05 10:00 | 2020-01-22 10:00 |  |  |  | SM2 sealing steam MOV |  |  |  |  | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE |  |  |  | Chrysty Dorsey | Paul Schoelen |  | Seminole PP; EGX Gath/Trans | FALSE |  | TRUE | Maintenance |  | Terry Bunch | Paul Schoelen |  |  |  | Justin Stahl |  | High
9203 | Seminole PP; EGX Gath/Trans | 2020-01-22 10:00 | Wrong valve installed in sealing steam line. Valve was not the correct specification for this service. The valve was discovered before the system was returned to service. | Level 3 |  | TRUE | Member Injury | Donnie Jones | Jesse Murray | Assigned Per Matt S and Scott Lee | 2020-01-23 15:10 | Power Supply | Paul Schoelen |  | 2020-01-22 13:35 | 2020-01-22 13:35 |  | 2020-02-05 10:00 | 2020-01-22 10:00 |  |  |  | SM2 sealing steam MOV |  |  |  |  | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE |  |  |  | Gregory Ownby | Paul Schoelen |  | Seminole PP; EGX Gath/Trans | FALSE |  | TRUE | Maintenance |  | Terry Bunch | Paul Schoelen |  |  |  | Justin Stahl |  | High
9204 | Ft Smith Service Center | 2020-01-21 06:00 | Traveling west on the interstate towards Muskogee a racoon ran up out of the ditch into the highway in front of the vehicle before the driver could even respond, hitting the animal. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | James Hutchison | 2020-01-23 08:29 | 2020-01-23 07:40 | 2020-01-23 07:40 | 2020-01-23 07:47 | 2020-02-04 06:00 | 2020-01-21 07:29 |  |  |  | I40 westbound just east of Sallisaw Oklahoma |  |  | Cody Magby | I agree with corrective actions cm | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | [6 empty] | Ft Smith Service Center | FALSE |  | FALSE | PD Operations Services |  | Don Mantooth | James Hutchison |  |  |  | Dallas Rowley |  | Low | [93 empty] | FALSE |  | Sallisaw | Animal-related |  | 2000-10-08 19:00 |  | FALSE |  |  | Night |  |  | Concrete/Pavement |  | Clear
9205 | Muskogee Power Plant | 2020-01-23 14:20 | While positioning a stackable tote of bleach with a forklift, the tote contacted an overhead 4" PVC pipe. The PVC pipe broke at the nearest 90 degree elbow. The PVC pipe was the blower pipe for one of the UF modules and transports low pressure air to the UF module from the blower. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Charles Smithson | 2020-01-29 09:38 | 2020-01-23 14:55 | 2020-01-23 14:55 | 2020-01-24 10:30 | 2020-02-06 14:20 | 2020-01-23 14:48 | 2020-01-24 15:40 |  |  | Muskogee Unit 6 Water Treatment Building |  |  | Robert Wright | approved Bob Wright | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Charles Smithson |  | The member was positioning a tote of bleach for offloading into the permanent bleach tote. The permanent tank is located about 4 feet below the pipe that was broken. As the tote was being lifted by the forklift, the tote contacted the pipe and it broke at an elbow. This piping system handles low pressure air that is fed to the UF membranes. The air pressure in the piping system is 4 psig. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | E Chem |  | Harry Byrne | Charles Smithson |  | Robert Benham | I agree with the causes and approve the corrective actions. FB | Robert Benham |  | Low | [13 empty] | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | The forklift and load were positioned beneath the PVC pipe. When the load was lifted, the tote struck the pipe | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) | [68 empty] | A 4 inch PVC pipe in the air blow system on one of the UF modules was broken. | 1000 | Harry Byrne | Fixed Equipment
9205 | Muskogee Power Plant | 2020-01-23 14:20 | While positioning a stackable tote of bleach with a forklift, the tote contacted an overhead 4" PVC pipe. The PVC pipe broke at the nearest 90 degree elbow. The PVC pipe was the blower pipe for one of the UF modules and transports low pressure air to the UF module from the blower. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Charles Smithson | 2020-01-29 09:38 | 2020-01-23 14:55 | 2020-01-23 14:55 | 2020-01-24 10:30 | 2020-02-06 14:20 | 2020-01-23 14:48 | 2020-01-24 15:40 |  |  | Muskogee Unit 6 Water Treatment Building |  |  | Robert Wright | approved Bob Wright | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Charles Smithson |  | The member was positioning a tote of bleach for offloading into the permanent bleach tote. The permanent tank is located about 4 feet below the pipe that was broken. As the tote was being lifted by the forklift, the tote contacted the pipe and it broke at an elbow. This piping system handles low pressure air that is fed to the UF membranes. The air pressure in the piping system is 4 psig. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | E Chem |  | Harry Byrne | Charles Smithson |  | Robert Benham | I agree with the causes and approve the corrective actions. FB | Robert Benham |  | Low |  |  |  |  | 5.06 Lack of situational awareness | 6.01 Inadequate initial instruction | [7 empty] | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | The tote was positioned beneath the pipe before lifting it and struck the pipe when it was raised into position for offloading the chemical. | 11. Improper Position for Task | 1. Struck Against (Running or Bumping Into) | [68 empty] | A 4 inch PVC pipe in the air blow system on one of the UF modules was broken. | 1000 | Harry Byrne | Fixed Equipment
9206 | Ft Smith Service Center | 2020-01-23 23:00 | While closing trip saver, the end of fiberglass standoff arm broke. The trip saver fell to the ground. No injuries occurred. | Level 3 |  | TRUE | Member Injury | Andrea Dennis | Lindle Coleman | assigned per ops guidance | 2020-01-30 14:49 | Power Delivery | Terry Duvall Jr | 2020-02-20 13:06 | 2020-01-24 07:47 | 2020-01-24 07:47 | 2020-02-14 10:56 | 2020-02-06 23:00 | 2020-01-24 07:40 | 2020-02-18 13:50 | 2020-02-18 15:41 | 2020-02-17 12:27 | Hwy 71 & Graphic Rd Mountainburg |  |  | Andrea Dennis | I approve. | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Terry Duvall Jr |  | Crew received trouble call at 11:00 pm to put #4 ACSR wire back up. After repairs were made the member attempted to energize the line from the bucket and close the trip saver but failed to get the trip savor latched, he tried once more and failed. Another member went up and attempted to close the trip saver with a longer switch stick to get a better reach. He then attempted to close the trip saver and at this time the end of the fiberglass standoff arm broke causing trip saver to fall approximately 40 ft. from the top of the pole. It was 50ft pole and located off of highway 71 in Mountainburg, AR 72921. No members were injured. Quick Key learnings: -Make members aware that this equipment can break and these are heavier than a fuse. -Be sure to use the proper angles while operating trip saver with the stick from the bucket. Such as; not being directly below or parallel to the trip saver and being directly in front of trip saver not off to either side. -Continue to stay out of the line of fire. Facts: -Trip saver weighs 26.5 lbs. and fell approx. 40 ft. -Weather conditions were about 35 degrees with ice accumulation and lighting was dark. Wind was 9 MPH. - Members were clear and not below or near the pole at the time the trip saver fell. Members were observing from ground. -Tailboard covered staying clear of falling objects. -After the Equipment fell there was a part that was found to be rusted and not possible to see from the bucket. Indicating the condition had existed prior to this operation. - Store room has single support bracket for mounting lightning arresters and is not labeled for “cutouts”. -Stands and Guides (Mark Murray) confirmed the specs show that the bracket is rated for 1200 lbs. -Pole was replaced in 2013. -Trip saver job was started in December 2019. determined unit was not a part of the bad batch that the manufacture had identified bracket information HUGHES BROS CF700B-24 Maclean G1MDA124DC ALUMA-FORM F1CA-MV-A24-S1-H End Fitting • 65-45-12 Ductile Iron, hot-dipped galvanized per ASTM A153 No torque specs found on information sheet for end fitting Investigation team came to the conclusion that the bracket had been cracked previous to failure. | Jeffrey Helzer | Terry Duvall Jr |  | Ft Smith Service Center | FALSE |  | TRUE | Construction Services |  | Robert White | Terry Duvall Jr |  | Chad Inman | I approve of the corrective actions and I also appreciate the team collaboration in regards to continuing the investigation with the Manufacturer. | Chad Inman | Lindle Coleman | High | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | One point of the single stand off bracket holding the trip saver up appeared to be rusted therefore causing trip saver to fall. | 23. Defective Tools, Equipment or Materials | 3. Fall from Elevation to Lower Level | need clarification on: 1. is this the correct bracket for the trip saver? are we discontinuing the use of this bracket for trip savers? If so, what bracket is required for the trip saver? 2. Can you clarify action #9401, what does this do to prevent this from occurring in the future? 3. can you clarify the root cause, why was it rusted and cracked? clarify 9404 action item on how this tie into preventing this from reoccurrence. please call me for further discussion. | Reviewed and approved.
9206 | Ft Smith Service Center | 2020-01-23 23:00 | While closing trip saver, the end of fiberglass standoff arm broke. The trip saver fell to the ground. No injuries occurred. | Level 3 |  | TRUE | Member Injury | Andrea Dennis | Lindle Coleman | assigned per ops guidance | 2020-01-30 14:49 | Power Delivery | Terry Duvall Jr | 2020-02-20 13:06 | 2020-01-24 07:47 | 2020-01-24 07:47 | 2020-02-14 10:56 | 2020-02-06 23:00 | 2020-01-24 07:40 | 2020-02-18 13:50 | 2020-02-18 15:41 | 2020-02-17 12:27 | Hwy 71 & Graphic Rd Mountainburg |  |  | Andrea Dennis | I approve. | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Terry Duvall Jr |  | Crew received trouble call at 11:00 pm to put #4 ACSR wire back up. After repairs were made the member attempted to energize the line from the bucket and close the trip saver but failed to get the trip savor latched, he tried once more and failed. Another member went up and attempted to close the trip saver with a longer switch stick to get a better reach. He then attempted to close the trip saver and at this time the end of the fiberglass standoff arm broke causing trip saver to fall approximately 40 ft. from the top of the pole. It was 50ft pole and located off of highway 71 in Mountainburg, AR 72921. No members were injured. Quick Key learnings: -Make members aware that this equipment can break and these are heavier than a fuse. -Be sure to use the proper angles while operating trip saver with the stick from the bucket. Such as; not being directly below or parallel to the trip saver and being directly in front of trip saver not off to either side. -Continue to stay out of the line of fire. Facts: -Trip saver weighs 26.5 lbs. and fell approx. 40 ft. -Weather conditions were about 35 degrees with ice accumulation and lighting was dark. Wind was 9 MPH. - Members were clear and not below or near the pole at the time the trip saver fell. Members were observing from ground. -Tailboard covered staying clear of falling objects. -After the Equipment fell there was a part that was found to be rusted and not possible to see from the bucket. Indicating the condition had existed prior to this operation. - Store room has single support bracket for mounting lightning arresters and is not labeled for “cutouts”. -Stands and Guides (Mark Murray) confirmed the specs show that the bracket is rated for 1200 lbs. -Pole was replaced in 2013. -Trip saver job was started in December 2019. determined unit was not a part of the bad batch that the manufacture had identified bracket information HUGHES BROS CF700B-24 Maclean G1MDA124DC ALUMA-FORM F1CA-MV-A24-S1-H End Fitting • 65-45-12 Ductile Iron, hot-dipped galvanized per ASTM A153 No torque specs found on information sheet for end fitting Investigation team came to the conclusion that the bracket had been cracked previous to failure. | Hannah Everett | Terry Duvall Jr |  | Ft Smith Service Center | FALSE |  | TRUE | Construction Services |  | Robert White | Terry Duvall Jr |  | Chad Inman | I approve of the corrective actions and I also appreciate the team collaboration in regards to continuing the investigation with the Manufacturer. | Chad Inman | Lindle Coleman | High | [12 empty] | 13.05 Inadequate adjustment/repair/maintenance |  |  |  | One point of the single stand off bracket holding the trip saver up appeared to be rusted therefore causing trip saver to fall. | 23. Defective Tools, Equipment or Materials | 3. Fall from Elevation to Lower Level | need clarification on: 1. is this the correct bracket for the trip saver? are we discontinuing the use of this bracket for trip savers? If so, what bracket is required for the trip saver? 2. Can you clarify action #9401, what does this do to prevent this from occurring in the future? 3. can you clarify the root cause, why was it rusted and cracked? clarify 9404 action item on how this tie into preventing this from reoccurrence. please call me for further discussion. | Reviewed and approved.
9207 | River Valley | 2020-01-23 14:00 | A contractor crew working in the area noticed a cable arcing on the exterior building sheet metal. | Level 2 |  | FALSE | Contractor | Donnie Jones |  |  |  | Power Supply | Michael Smith |  | 2020-01-24 08:44 | 2020-01-24 08:44 |  | 2020-02-06 14:00 | 2020-01-23 14:30 |  |  |  | River Valley PP Fuel Supply Ground Floor Crusher Building |  |  |  |  | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Michael Smith |  | An electrical cable was hanging down from a overhead conduit. The ends of the cable were tapped and had wire nuts. The cable rubbed on a sheet metal screw going through the tape and causing an arc. It is believed that this cable was removed when an overhead beam was installed 20 years ago and the cable was tapped to the overhead conduit. The normal operation over the years allowed the cable to vibrate loose and fall down against the building over time wearing through the tape and causing the arc. We looked back to 2008 and did not have a clearance on this circuit. |  |  | FALSE | River Valley | FALSE |  | FALSE | Fuel Supply |  | James Brooks | Michael Smith |  |  |  | Timothy Chancellor |  | Medium | [13 empty] | 14.01.4 Inadequate development of standards: procedures/practices/rules |  | 16.09 Inadequate communication due to job turnover | An electrical cable was hanging down from a overhead conduit. The ends of the cable were tapped and had wire nuts. The cable rubbed on a sheet metal screw going through the tape and causing an arc. It is believed that this cable was removed when an overhead beam was installed 20 years ago and the cable was tapped to the overhead conduit. The normal operation over the years allowed the cable to vibrate loose and fall down against the building over time wearing through the tape and causing the arc. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Michael Smith | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | James Brooks | ECA | Brant Ridenour |  |  |  | James Brooks | [71 empty] | 750928
9208 | McClain Power Plant | 2020-01-23 09:15 | At McClain Power Plant a Frontier member was doing some training on the Diesel Generator and as he stepped down off of the bottom concrete step of the latter foundation descending from the platform of the diesel generator, he was handed a clipboard then turned around and tripped over the rain gutter deflection late and fell onto the graveled pavement and immediately popped back up. There were 6 members in the training area when the incident occurred. After reviewing with the Safety Coordinator we believe this should have been risked at a low. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | William Hunter | 2020-02-26 13:44 | 2020-01-24 13:34 | 2020-01-24 13:34 | 2020-02-10 13:01 | 2020-02-06 09:15 | 2020-01-23 15:06 | 2020-02-19 10:11 |  | 2020-02-11 13:04 | McClain Power Plant; near the Diesel Generator at the bottom concrete step of the latter foundation descending from the platform of the diesel generator where the rain gutter deflection plate is located. |  |  | Jesse Murray | Approved. Jesse Murray | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | William Hunter |  | While doing training on the Diesel Generator, the member stepped down off the bottom concrete step of the latter foundation descending from the platform of the diesel generator; he was handed a clipboard then turned around and tripped over the gutter rain deflector plate and fell onto the graveled area and immediately got back up. There were no injuries to the member and he felt no pain. The member was distracted by being handed the clip board and was not familiar with the area. |  |  |  | McClain Power Plant | FALSE |  | TRUE | Operations |  | Michael Booher | William Hunter |  | Heath Biehl | I agree with Tanner the ranking should be low. | Heath Biehl |  | Medium |  |  |  |  | 5.01 Lack of experience | [11 empty] | Member was unfamiliar with the area and was distracted when being handed a clip board. Member then tripped over the rain deflector located in the walkway. | 17. Failure to Identify Hazard, Risk | 4. Fall on Same Level (Slip and Fall, Trip Over) |  | Ranking should have been a low. Reviewed with Ops Manager. Discussed training at different plant.
9209 | Metro Service Center | 2020-01-24 11:30 | Member was attempting to close a switch and experienced a sudden pain in his left upper arm. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Team assigned per discussion with Ops Manager | 2020-02-18 14:21 | Power Delivery | Garren Dodson |  | 2020-01-24 16:57 | 2020-01-24 16:57 | 2020-02-18 14:55 | 2020-02-07 11:30 | 2020-01-24 16:43 | 2020-02-24 08:04 | 2020-02-24 11:55 | 2020-02-20 07:46 | Nw 8th and Lincoln Blvd. , OKC, OK |  |  |  |  | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Kenny La Ferney |  | Underground network crew was working on a bad transformer in medical research park. They had isolated the transformer when the coordinator and supervisor went to pick the load back up on one building by closing a switch in the ATO gear. The elastimold switch had tripped opened and needed to be reset then closed to pick up that building. The coordinator was attempting to close the switch with a 2-piece hot stick but due to the flex in the stick and the elevation of the switchman, he could not get enough leverage to close the mechanism. He asked the supervisor if he would assist him getting it closed. While trying to close it together the coordinator felt a pain in his left arm and let go of the stick. At this time the supervisor decided to wait on another crew member to help him close the switch. They ended up using a shorter extended shotgun stick to get it closed. At the time of the incident one crew was working in another area to pick up one of the buildings, the other crew was working with crane personnel to get the crane setup. The supervisor and coordinator knew they only had to close the switch to pickup the other building and was going to do that themselves. They were trying to restore power as efficiently as possible due to the sensitive nature of work performed at the facility. After investigation is was determined the switch handle angles can be adjusted but the amount of tension required to work the mechanism cannot be adjusted At the time they had three buildings without power, and they were trying to get 2 of them back on. There was a sense of urgency to restore power to the facilities because of the sensitive work done at this location. The ATO cubicle had a berm built up around it from landscapers. This put the switchman slightly above the switch he was closing. This created an awkward angle to close the switch from. It was a pulling/leverage type movement Coordinator and supervisor had participated in the tailboard before performing any work They had all done Vimocity stretching at the jobsite Supervisor last had distribution switching class May 30, 2018 Coordinator last had distribution switching class February 26, 2018 They had the stick extended fully at 10’ to stay as far away as possible in the event of arc flash After going to GSC and looking at a new (similar) gear it was determined that the handles on the switchgears could be adjusted in order to get better leverage when a switchgear is installed at a congested located The tension on the switch lever could not be measured at this time due to the switch being energized | Cody Magby | Kenny La Ferney | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Dale Allen | Garren Dodson |  | Gary Lassley | Network UG Supervisor to coach his Team on identifying hazards and stopping the job when necessary to assess/mitigate hazards. There is not job and no Customer so important that we would not take the time to do the job safely. This belief sometimes leads to a self imposed sense of urgency, and could lead to possible unforeseen hazards. Network UG Supervisor will also research to see if there is any available tech that could assist in performing this task. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance | 7.11 Improper supervisory example |  | 9.09 Inadequate identification and evaluation of loss exposures |  |  |  | 13.01 Inadequate assessment of needs and risks |  |  |  | Members did not determine there was a risk of being injured while performing this task. | 19. Failure to React, Correct | 11. Overstress, Overpressure, Overexertion, Ergonomic | approved | Based on the investigation that has been provided, I have added a couple more check marks to the immediate and basic cause topic "Members did not determine there was a risk if being injured while performing this task" to better reflect the supervisors role in the incident. I changed the "immediate/Direct cause" to Failure to React, Correct. this helped to identify these causes: • 7.01 Improper performance is rewarded (tolerated) • 7.11 Improper supervisory example • 13.01 Inadequate assessment of needs and risks I do believe that these new marks are still addressed with the current corrective actions. | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2000-06-12 | 1980-03-09 |  | 2020-01-24 07:00 | 0 | 0 | received x-ray from the clinic, | FALSE |  | while closing an ATO |  | TRUE | Dale Allen |  | Recordable | Dale Allen |  |  |  |  | Sprain/Strain |  | TRUE |  | Underground Const Coord | Arm | Injury | Left | TRUE | Garren Dodson | TRUE | 2020 | 1/24/2020 7:00:00 AM | 15 years | FALSE |  |  | stress from closing an ATO | [25 empty] | 8590250
9209 | Metro Service Center | 2020-01-24 11:30 | Member was attempting to close a switch and experienced a sudden pain in his left upper arm. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Team assigned per discussion with Ops Manager | 2020-02-18 14:21 | Power Delivery | Garren Dodson |  | 2020-01-24 16:57 | 2020-01-24 16:57 | 2020-02-18 14:55 | 2020-02-07 11:30 | 2020-01-24 16:43 | 2020-02-24 08:04 | 2020-02-24 11:55 | 2020-02-20 07:46 | Nw 8th and Lincoln Blvd. , OKC, OK |  |  |  |  | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Kenny La Ferney |  | Underground network crew was working on a bad transformer in medical research park. They had isolated the transformer when the coordinator and supervisor went to pick the load back up on one building by closing a switch in the ATO gear. The elastimold switch had tripped opened and needed to be reset then closed to pick up that building. The coordinator was attempting to close the switch with a 2-piece hot stick but due to the flex in the stick and the elevation of the switchman, he could not get enough leverage to close the mechanism. He asked the supervisor if he would assist him getting it closed. While trying to close it together the coordinator felt a pain in his left arm and let go of the stick. At this time the supervisor decided to wait on another crew member to help him close the switch. They ended up using a shorter extended shotgun stick to get it closed. At the time of the incident one crew was working in another area to pick up one of the buildings, the other crew was working with crane personnel to get the crane setup. The supervisor and coordinator knew they only had to close the switch to pickup the other building and was going to do that themselves. They were trying to restore power as efficiently as possible due to the sensitive nature of work performed at the facility. After investigation is was determined the switch handle angles can be adjusted but the amount of tension required to work the mechanism cannot be adjusted At the time they had three buildings without power, and they were trying to get 2 of them back on. There was a sense of urgency to restore power to the facilities because of the sensitive work done at this location. The ATO cubicle had a berm built up around it from landscapers. This put the switchman slightly above the switch he was closing. This created an awkward angle to close the switch from. It was a pulling/leverage type movement Coordinator and supervisor had participated in the tailboard before performing any work They had all done Vimocity stretching at the jobsite Supervisor last had distribution switching class May 30, 2018 Coordinator last had distribution switching class February 26, 2018 They had the stick extended fully at 10’ to stay as far away as possible in the event of arc flash After going to GSC and looking at a new (similar) gear it was determined that the handles on the switchgears could be adjusted in order to get better leverage when a switchgear is installed at a congested located The tension on the switch lever could not be measured at this time due to the switch being energized | Cody Magby | Kenny La Ferney | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Dale Allen | Garren Dodson |  | Gary Lassley | Network UG Supervisor to coach his Team on identifying hazards and stopping the job when necessary to assess/mitigate hazards. There is not job and no Customer so important that we would not take the time to do the job safely. This belief sometimes leads to a self imposed sense of urgency, and could lead to possible unforeseen hazards. Network UG Supervisor will also research to see if there is any available tech that could assist in performing this task. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.03 Infrequent performance | 7.01 Improper performance is rewarded (tolerated) |  | 9.09 Inadequate identification and evaluation of loss exposures |  |  |  | 13.01 Inadequate assessment of needs and risks |  |  |  | Members did not determine there was a risk of being injured while performing this task. | 19. Failure to React, Correct | 11. Overstress, Overpressure, Overexertion, Ergonomic | approved | Based on the investigation that has been provided, I have added a couple more check marks to the immediate and basic cause topic "Members did not determine there was a risk if being injured while performing this task" to better reflect the supervisors role in the incident. I changed the "immediate/Direct cause" to Failure to React, Correct. this helped to identify these causes: • 7.01 Improper performance is rewarded (tolerated) • 7.11 Improper supervisory example • 13.01 Inadequate assessment of needs and risks I do believe that these new marks are still addressed with the current corrective actions. | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2000-06-12 | 1980-03-09 |  | 2020-01-24 07:00 | 0 | 0 | received x-ray from the clinic, | FALSE |  | while closing an ATO |  | TRUE | Dale Allen |  | Recordable | Dale Allen |  |  |  |  | Sprain/Strain |  | TRUE |  | Underground Const Coord | Arm | Injury | Left | TRUE | Garren Dodson | TRUE | 2020 | 1/24/2020 7:00:00 AM | 15 years | FALSE |  |  | stress from closing an ATO | [25 empty] | 8590250
9209 | Metro Service Center | 2020-01-24 11:30 | Member was attempting to close a switch and experienced a sudden pain in his left upper arm. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Team assigned per discussion with Ops Manager | 2020-02-18 14:21 | Power Delivery | Garren Dodson |  | 2020-01-24 16:57 | 2020-01-24 16:57 | 2020-02-18 14:55 | 2020-02-07 11:30 | 2020-01-24 16:43 | 2020-02-24 08:04 | 2020-02-24 11:55 | 2020-02-20 07:46 | Nw 8th and Lincoln Blvd. , OKC, OK |  |  |  |  | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Kenny La Ferney |  | Underground network crew was working on a bad transformer in medical research park. They had isolated the transformer when the coordinator and supervisor went to pick the load back up on one building by closing a switch in the ATO gear. The elastimold switch had tripped opened and needed to be reset then closed to pick up that building. The coordinator was attempting to close the switch with a 2-piece hot stick but due to the flex in the stick and the elevation of the switchman, he could not get enough leverage to close the mechanism. He asked the supervisor if he would assist him getting it closed. While trying to close it together the coordinator felt a pain in his left arm and let go of the stick. At this time the supervisor decided to wait on another crew member to help him close the switch. They ended up using a shorter extended shotgun stick to get it closed. At the time of the incident one crew was working in another area to pick up one of the buildings, the other crew was working with crane personnel to get the crane setup. The supervisor and coordinator knew they only had to close the switch to pickup the other building and was going to do that themselves. They were trying to restore power as efficiently as possible due to the sensitive nature of work performed at the facility. After investigation is was determined the switch handle angles can be adjusted but the amount of tension required to work the mechanism cannot be adjusted At the time they had three buildings without power, and they were trying to get 2 of them back on. There was a sense of urgency to restore power to the facilities because of the sensitive work done at this location. The ATO cubicle had a berm built up around it from landscapers. This put the switchman slightly above the switch he was closing. This created an awkward angle to close the switch from. It was a pulling/leverage type movement Coordinator and supervisor had participated in the tailboard before performing any work They had all done Vimocity stretching at the jobsite Supervisor last had distribution switching class May 30, 2018 Coordinator last had distribution switching class February 26, 2018 They had the stick extended fully at 10’ to stay as far away as possible in the event of arc flash After going to GSC and looking at a new (similar) gear it was determined that the handles on the switchgears could be adjusted in order to get better leverage when a switchgear is installed at a congested located The tension on the switch lever could not be measured at this time due to the switch being energized | Cody Magby | Kenny La Ferney | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Dale Allen | Garren Dodson |  | Gary Lassley | Network UG Supervisor to coach his Team on identifying hazards and stopping the job when necessary to assess/mitigate hazards. There is not job and no Customer so important that we would not take the time to do the job safely. This belief sometimes leads to a self imposed sense of urgency, and could lead to possible unforeseen hazards. Network UG Supervisor will also research to see if there is any available tech that could assist in performing this task. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.04 Lack of coaching | 7.11 Improper supervisory example |  | 9.09 Inadequate identification and evaluation of loss exposures |  |  |  | 13.01 Inadequate assessment of needs and risks |  |  |  | Members did not determine there was a risk of being injured while performing this task. | 19. Failure to React, Correct | 11. Overstress, Overpressure, Overexertion, Ergonomic | approved | Based on the investigation that has been provided, I have added a couple more check marks to the immediate and basic cause topic "Members did not determine there was a risk if being injured while performing this task" to better reflect the supervisors role in the incident. I changed the "immediate/Direct cause" to Failure to React, Correct. this helped to identify these causes: • 7.01 Improper performance is rewarded (tolerated) • 7.11 Improper supervisory example • 13.01 Inadequate assessment of needs and risks I do believe that these new marks are still addressed with the current corrective actions. | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2000-06-12 | 1980-03-09 |  | 2020-01-24 07:00 | 0 | 0 | received x-ray from the clinic, | FALSE |  | while closing an ATO |  | TRUE | Dale Allen |  | Recordable | Dale Allen |  |  |  |  | Sprain/Strain |  | TRUE |  | Underground Const Coord | Arm | Injury | Left | TRUE | Garren Dodson | TRUE | 2020 | 1/24/2020 7:00:00 AM | 15 years | FALSE |  |  | stress from closing an ATO | [25 empty] | 8590250
9209 | Metro Service Center | 2020-01-24 11:30 | Member was attempting to close a switch and experienced a sudden pain in his left upper arm. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Team assigned per discussion with Ops Manager | 2020-02-18 14:21 | Power Delivery | Garren Dodson |  | 2020-01-24 16:57 | 2020-01-24 16:57 | 2020-02-18 14:55 | 2020-02-07 11:30 | 2020-01-24 16:43 | 2020-02-24 08:04 | 2020-02-24 11:55 | 2020-02-20 07:46 | Nw 8th and Lincoln Blvd. , OKC, OK |  |  |  |  | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Kenny La Ferney |  | Underground network crew was working on a bad transformer in medical research park. They had isolated the transformer when the coordinator and supervisor went to pick the load back up on one building by closing a switch in the ATO gear. The elastimold switch had tripped opened and needed to be reset then closed to pick up that building. The coordinator was attempting to close the switch with a 2-piece hot stick but due to the flex in the stick and the elevation of the switchman, he could not get enough leverage to close the mechanism. He asked the supervisor if he would assist him getting it closed. While trying to close it together the coordinator felt a pain in his left arm and let go of the stick. At this time the supervisor decided to wait on another crew member to help him close the switch. They ended up using a shorter extended shotgun stick to get it closed. At the time of the incident one crew was working in another area to pick up one of the buildings, the other crew was working with crane personnel to get the crane setup. The supervisor and coordinator knew they only had to close the switch to pickup the other building and was going to do that themselves. They were trying to restore power as efficiently as possible due to the sensitive nature of work performed at the facility. After investigation is was determined the switch handle angles can be adjusted but the amount of tension required to work the mechanism cannot be adjusted At the time they had three buildings without power, and they were trying to get 2 of them back on. There was a sense of urgency to restore power to the facilities because of the sensitive work done at this location. The ATO cubicle had a berm built up around it from landscapers. This put the switchman slightly above the switch he was closing. This created an awkward angle to close the switch from. It was a pulling/leverage type movement Coordinator and supervisor had participated in the tailboard before performing any work They had all done Vimocity stretching at the jobsite Supervisor last had distribution switching class May 30, 2018 Coordinator last had distribution switching class February 26, 2018 They had the stick extended fully at 10’ to stay as far away as possible in the event of arc flash After going to GSC and looking at a new (similar) gear it was determined that the handles on the switchgears could be adjusted in order to get better leverage when a switchgear is installed at a congested located The tension on the switch lever could not be measured at this time due to the switch being energized | Cody Magby | Kenny La Ferney | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Dale Allen | Garren Dodson |  | Gary Lassley | Network UG Supervisor to coach his Team on identifying hazards and stopping the job when necessary to assess/mitigate hazards. There is not job and no Customer so important that we would not take the time to do the job safely. This belief sometimes leads to a self imposed sense of urgency, and could lead to possible unforeseen hazards. Network UG Supervisor will also research to see if there is any available tech that could assist in performing this task. | Gary Lassley | Lindle Coleman | High |  |  |  |  | 5.06 Lack of situational awareness | 6.04 Lack of coaching | 7.01 Improper performance is rewarded (tolerated) |  | 9.09 Inadequate identification and evaluation of loss exposures |  |  |  | 13.01 Inadequate assessment of needs and risks |  |  |  | Members did not determine there was a risk of being injured while performing this task. | 19. Failure to React, Correct | 11. Overstress, Overpressure, Overexertion, Ergonomic | approved | Based on the investigation that has been provided, I have added a couple more check marks to the immediate and basic cause topic "Members did not determine there was a risk if being injured while performing this task" to better reflect the supervisors role in the incident. I changed the "immediate/Direct cause" to Failure to React, Correct. this helped to identify these causes: • 7.01 Improper performance is rewarded (tolerated) • 7.11 Improper supervisory example • 13.01 Inadequate assessment of needs and risks I do believe that these new marks are still addressed with the current corrective actions. | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2000-06-12 | 1980-03-09 |  | 2020-01-24 07:00 | 0 | 0 | received x-ray from the clinic, | FALSE |  | while closing an ATO |  | TRUE | Dale Allen |  | Recordable | Dale Allen |  |  |  |  | Sprain/Strain |  | TRUE |  | Underground Const Coord | Arm | Injury | Left | TRUE | Garren Dodson | TRUE | 2020 | 1/24/2020 7:00:00 AM | 15 years | FALSE |  |  | stress from closing an ATO | [25 empty] | 8590250
9209 | Metro Service Center | 2020-01-24 11:30 | Member was attempting to close a switch and experienced a sudden pain in his left upper arm. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Team assigned per discussion with Ops Manager | 2020-02-18 14:21 | Power Delivery | Garren Dodson |  | 2020-01-24 16:57 | 2020-01-24 16:57 | 2020-02-18 14:55 | 2020-02-07 11:30 | 2020-01-24 16:43 | 2020-02-24 08:04 | 2020-02-24 11:55 | 2020-02-20 07:46 | Nw 8th and Lincoln Blvd. , OKC, OK |  |  |  |  | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Kenny La Ferney |  | Underground network crew was working on a bad transformer in medical research park. They had isolated the transformer when the coordinator and supervisor went to pick the load back up on one building by closing a switch in the ATO gear. The elastimold switch had tripped opened and needed to be reset then closed to pick up that building. The coordinator was attempting to close the switch with a 2-piece hot stick but due to the flex in the stick and the elevation of the switchman, he could not get enough leverage to close the mechanism. He asked the supervisor if he would assist him getting it closed. While trying to close it together the coordinator felt a pain in his left arm and let go of the stick. At this time the supervisor decided to wait on another crew member to help him close the switch. They ended up using a shorter extended shotgun stick to get it closed. At the time of the incident one crew was working in another area to pick up one of the buildings, the other crew was working with crane personnel to get the crane setup. The supervisor and coordinator knew they only had to close the switch to pickup the other building and was going to do that themselves. They were trying to restore power as efficiently as possible due to the sensitive nature of work performed at the facility. After investigation is was determined the switch handle angles can be adjusted but the amount of tension required to work the mechanism cannot be adjusted At the time they had three buildings without power, and they were trying to get 2 of them back on. There was a sense of urgency to restore power to the facilities because of the sensitive work done at this location. The ATO cubicle had a berm built up around it from landscapers. This put the switchman slightly above the switch he was closing. This created an awkward angle to close the switch from. It was a pulling/leverage type movement Coordinator and supervisor had participated in the tailboard before performing any work They had all done Vimocity stretching at the jobsite Supervisor last had distribution switching class May 30, 2018 Coordinator last had distribution switching class February 26, 2018 They had the stick extended fully at 10’ to stay as far away as possible in the event of arc flash After going to GSC and looking at a new (similar) gear it was determined that the handles on the switchgears could be adjusted in order to get better leverage when a switchgear is installed at a congested located The tension on the switch lever could not be measured at this time due to the switch being energized | Cody Magby | Kenny La Ferney | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Dale Allen | Garren Dodson |  | Gary Lassley | Network UG Supervisor to coach his Team on identifying hazards and stopping the job when necessary to assess/mitigate hazards. There is not job and no Customer so important that we would not take the time to do the job safely. This belief sometimes leads to a self imposed sense of urgency, and could lead to possible unforeseen hazards. Network UG Supervisor will also research to see if there is any available tech that could assist in performing this task. | Gary Lassley | Lindle Coleman | High | [9 empty] | 10.01 Inadequate assessment of loss exposures |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | The terrain surrounding the switch was elevated and created an awkward angle for the switch to be operated when using the 10 ft. extendable switching stick. | 24. Congestion or Restricted Action | 11. Overstress, Overpressure, Overexertion, Ergonomic | approved | Based on the investigation that has been provided, I have added a couple more check marks to the immediate and basic cause topic "Members did not determine there was a risk if being injured while performing this task" to better reflect the supervisors role in the incident. I changed the "immediate/Direct cause" to Failure to React, Correct. this helped to identify these causes: • 7.01 Improper performance is rewarded (tolerated) • 7.11 Improper supervisory example • 13.01 Inadequate assessment of needs and risks I do believe that these new marks are still addressed with the current corrective actions. | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2000-06-12 | 1980-03-09 |  | 2020-01-24 07:00 | 0 | 0 | received x-ray from the clinic, | FALSE |  | while closing an ATO |  | TRUE | Dale Allen |  | Recordable | Dale Allen |  |  |  |  | Sprain/Strain |  | TRUE |  | Underground Const Coord | Arm | Injury | Left | TRUE | Garren Dodson | TRUE | 2020 | 1/24/2020 7:00:00 AM | 15 years | FALSE |  |  | stress from closing an ATO | [25 empty] | 8590250
9209 | Metro Service Center | 2020-01-24 11:30 | Member was attempting to close a switch and experienced a sudden pain in his left upper arm. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Team assigned per discussion with Ops Manager | 2020-02-18 14:21 | Power Delivery | Garren Dodson |  | 2020-01-24 16:57 | 2020-01-24 16:57 | 2020-02-18 14:55 | 2020-02-07 11:30 | 2020-01-24 16:43 | 2020-02-24 08:04 | 2020-02-24 11:55 | 2020-02-20 07:46 | Nw 8th and Lincoln Blvd. , OKC, OK |  |  |  |  | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Kenny La Ferney |  | Underground network crew was working on a bad transformer in medical research park. They had isolated the transformer when the coordinator and supervisor went to pick the load back up on one building by closing a switch in the ATO gear. The elastimold switch had tripped opened and needed to be reset then closed to pick up that building. The coordinator was attempting to close the switch with a 2-piece hot stick but due to the flex in the stick and the elevation of the switchman, he could not get enough leverage to close the mechanism. He asked the supervisor if he would assist him getting it closed. While trying to close it together the coordinator felt a pain in his left arm and let go of the stick. At this time the supervisor decided to wait on another crew member to help him close the switch. They ended up using a shorter extended shotgun stick to get it closed. At the time of the incident one crew was working in another area to pick up one of the buildings, the other crew was working with crane personnel to get the crane setup. The supervisor and coordinator knew they only had to close the switch to pickup the other building and was going to do that themselves. They were trying to restore power as efficiently as possible due to the sensitive nature of work performed at the facility. After investigation is was determined the switch handle angles can be adjusted but the amount of tension required to work the mechanism cannot be adjusted At the time they had three buildings without power, and they were trying to get 2 of them back on. There was a sense of urgency to restore power to the facilities because of the sensitive work done at this location. The ATO cubicle had a berm built up around it from landscapers. This put the switchman slightly above the switch he was closing. This created an awkward angle to close the switch from. It was a pulling/leverage type movement Coordinator and supervisor had participated in the tailboard before performing any work They had all done Vimocity stretching at the jobsite Supervisor last had distribution switching class May 30, 2018 Coordinator last had distribution switching class February 26, 2018 They had the stick extended fully at 10’ to stay as far away as possible in the event of arc flash After going to GSC and looking at a new (similar) gear it was determined that the handles on the switchgears could be adjusted in order to get better leverage when a switchgear is installed at a congested located The tension on the switch lever could not be measured at this time due to the switch being energized | Cody Magby | Kenny La Ferney | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Dale Allen | Garren Dodson |  | Gary Lassley | Network UG Supervisor to coach his Team on identifying hazards and stopping the job when necessary to assess/mitigate hazards. There is not job and no Customer so important that we would not take the time to do the job safely. This belief sometimes leads to a self imposed sense of urgency, and could lead to possible unforeseen hazards. Network UG Supervisor will also research to see if there is any available tech that could assist in performing this task. | Gary Lassley | Lindle Coleman | High | [9 empty] | 10.01 Inadequate assessment of loss exposures |  |  |  | 14.01.2 Inadequate development of standards: coordination with process design |  |  | The terrain surrounding the switch was elevated and created an awkward angle for the switch to be operated when using the 10 ft. extendable switching stick. | 24. Congestion or Restricted Action | 11. Overstress, Overpressure, Overexertion, Ergonomic | approved | Based on the investigation that has been provided, I have added a couple more check marks to the immediate and basic cause topic "Members did not determine there was a risk if being injured while performing this task" to better reflect the supervisors role in the incident. I changed the "immediate/Direct cause" to Failure to React, Correct. this helped to identify these causes: • 7.01 Improper performance is rewarded (tolerated) • 7.11 Improper supervisory example • 13.01 Inadequate assessment of needs and risks I do believe that these new marks are still addressed with the current corrective actions. | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2000-06-12 | 1980-03-09 |  | 2020-01-24 07:00 | 0 | 0 | received x-ray from the clinic, | FALSE |  | while closing an ATO |  | TRUE | Dale Allen |  | Recordable | Dale Allen |  |  |  |  | Sprain/Strain |  | TRUE |  | Underground Const Coord | Arm | Injury | Left | TRUE | Garren Dodson | TRUE | 2020 | 1/24/2020 7:00:00 AM | 15 years | FALSE |  |  | stress from closing an ATO | [25 empty] | 8590250
9209 | Metro Service Center | 2020-01-24 11:30 | Member was attempting to close a switch and experienced a sudden pain in his left upper arm. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Team assigned per discussion with Ops Manager | 2020-02-18 14:21 | Power Delivery | Garren Dodson |  | 2020-01-24 16:57 | 2020-01-24 16:57 | 2020-02-18 14:55 | 2020-02-07 11:30 | 2020-01-24 16:43 | 2020-02-24 08:04 | 2020-02-24 11:55 | 2020-02-20 07:46 | Nw 8th and Lincoln Blvd. , OKC, OK |  |  |  |  | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Kenny La Ferney |  | Underground network crew was working on a bad transformer in medical research park. They had isolated the transformer when the coordinator and supervisor went to pick the load back up on one building by closing a switch in the ATO gear. The elastimold switch had tripped opened and needed to be reset then closed to pick up that building. The coordinator was attempting to close the switch with a 2-piece hot stick but due to the flex in the stick and the elevation of the switchman, he could not get enough leverage to close the mechanism. He asked the supervisor if he would assist him getting it closed. While trying to close it together the coordinator felt a pain in his left arm and let go of the stick. At this time the supervisor decided to wait on another crew member to help him close the switch. They ended up using a shorter extended shotgun stick to get it closed. At the time of the incident one crew was working in another area to pick up one of the buildings, the other crew was working with crane personnel to get the crane setup. The supervisor and coordinator knew they only had to close the switch to pickup the other building and was going to do that themselves. They were trying to restore power as efficiently as possible due to the sensitive nature of work performed at the facility. After investigation is was determined the switch handle angles can be adjusted but the amount of tension required to work the mechanism cannot be adjusted At the time they had three buildings without power, and they were trying to get 2 of them back on. There was a sense of urgency to restore power to the facilities because of the sensitive work done at this location. The ATO cubicle had a berm built up around it from landscapers. This put the switchman slightly above the switch he was closing. This created an awkward angle to close the switch from. It was a pulling/leverage type movement Coordinator and supervisor had participated in the tailboard before performing any work They had all done Vimocity stretching at the jobsite Supervisor last had distribution switching class May 30, 2018 Coordinator last had distribution switching class February 26, 2018 They had the stick extended fully at 10’ to stay as far away as possible in the event of arc flash After going to GSC and looking at a new (similar) gear it was determined that the handles on the switchgears could be adjusted in order to get better leverage when a switchgear is installed at a congested located The tension on the switch lever could not be measured at this time due to the switch being energized | Cody Magby | Kenny La Ferney | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Dale Allen | Garren Dodson |  | Gary Lassley | Network UG Supervisor to coach his Team on identifying hazards and stopping the job when necessary to assess/mitigate hazards. There is not job and no Customer so important that we would not take the time to do the job safely. This belief sometimes leads to a self imposed sense of urgency, and could lead to possible unforeseen hazards. Network UG Supervisor will also research to see if there is any available tech that could assist in performing this task. | Gary Lassley | Lindle Coleman | High | [9 empty] | 10.02 Inadequate consideration of human factors/ergonomics |  |  |  | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | The terrain surrounding the switch was elevated and created an awkward angle for the switch to be operated when using the 10 ft. extendable switching stick. | 24. Congestion or Restricted Action | 11. Overstress, Overpressure, Overexertion, Ergonomic | approved | Based on the investigation that has been provided, I have added a couple more check marks to the immediate and basic cause topic "Members did not determine there was a risk if being injured while performing this task" to better reflect the supervisors role in the incident. I changed the "immediate/Direct cause" to Failure to React, Correct. this helped to identify these causes: • 7.01 Improper performance is rewarded (tolerated) • 7.11 Improper supervisory example • 13.01 Inadequate assessment of needs and risks I do believe that these new marks are still addressed with the current corrective actions. | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2000-06-12 | 1980-03-09 |  | 2020-01-24 07:00 | 0 | 0 | received x-ray from the clinic, | FALSE |  | while closing an ATO |  | TRUE | Dale Allen |  | Recordable | Dale Allen |  |  |  |  | Sprain/Strain |  | TRUE |  | Underground Const Coord | Arm | Injury | Left | TRUE | Garren Dodson | TRUE | 2020 | 1/24/2020 7:00:00 AM | 15 years | FALSE |  |  | stress from closing an ATO | [25 empty] | 8590250
9209 | Metro Service Center | 2020-01-24 11:30 | Member was attempting to close a switch and experienced a sudden pain in his left upper arm. | Level 3 |  | FALSE | Member Injury | Andrea Dennis | Lindle Coleman | Team assigned per discussion with Ops Manager | 2020-02-18 14:21 | Power Delivery | Garren Dodson |  | 2020-01-24 16:57 | 2020-01-24 16:57 | 2020-02-18 14:55 | 2020-02-07 11:30 | 2020-01-24 16:43 | 2020-02-24 08:04 | 2020-02-24 11:55 | 2020-02-20 07:46 | Nw 8th and Lincoln Blvd. , OKC, OK |  |  |  |  | T&D Ops |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Kenny La Ferney |  | Underground network crew was working on a bad transformer in medical research park. They had isolated the transformer when the coordinator and supervisor went to pick the load back up on one building by closing a switch in the ATO gear. The elastimold switch had tripped opened and needed to be reset then closed to pick up that building. The coordinator was attempting to close the switch with a 2-piece hot stick but due to the flex in the stick and the elevation of the switchman, he could not get enough leverage to close the mechanism. He asked the supervisor if he would assist him getting it closed. While trying to close it together the coordinator felt a pain in his left arm and let go of the stick. At this time the supervisor decided to wait on another crew member to help him close the switch. They ended up using a shorter extended shotgun stick to get it closed. At the time of the incident one crew was working in another area to pick up one of the buildings, the other crew was working with crane personnel to get the crane setup. The supervisor and coordinator knew they only had to close the switch to pickup the other building and was going to do that themselves. They were trying to restore power as efficiently as possible due to the sensitive nature of work performed at the facility. After investigation is was determined the switch handle angles can be adjusted but the amount of tension required to work the mechanism cannot be adjusted At the time they had three buildings without power, and they were trying to get 2 of them back on. There was a sense of urgency to restore power to the facilities because of the sensitive work done at this location. The ATO cubicle had a berm built up around it from landscapers. This put the switchman slightly above the switch he was closing. This created an awkward angle to close the switch from. It was a pulling/leverage type movement Coordinator and supervisor had participated in the tailboard before performing any work They had all done Vimocity stretching at the jobsite Supervisor last had distribution switching class May 30, 2018 Coordinator last had distribution switching class February 26, 2018 They had the stick extended fully at 10’ to stay as far away as possible in the event of arc flash After going to GSC and looking at a new (similar) gear it was determined that the handles on the switchgears could be adjusted in order to get better leverage when a switchgear is installed at a congested located The tension on the switch lever could not be measured at this time due to the switch being energized | Cody Magby | Kenny La Ferney | FALSE | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Dale Allen | Garren Dodson |  | Gary Lassley | Network UG Supervisor to coach his Team on identifying hazards and stopping the job when necessary to assess/mitigate hazards. There is not job and no Customer so important that we would not take the time to do the job safely. This belief sometimes leads to a self imposed sense of urgency, and could lead to possible unforeseen hazards. Network UG Supervisor will also research to see if there is any available tech that could assist in performing this task. | Gary Lassley | Lindle Coleman | High | [9 empty] | 10.02 Inadequate consideration of human factors/ergonomics |  |  |  | 14.01.2 Inadequate development of standards: coordination with process design |  |  | The terrain surrounding the switch was elevated and created an awkward angle for the switch to be operated when using the 10 ft. extendable switching stick. | 24. Congestion or Restricted Action | 11. Overstress, Overpressure, Overexertion, Ergonomic | approved | Based on the investigation that has been provided, I have added a couple more check marks to the immediate and basic cause topic "Members did not determine there was a risk if being injured while performing this task" to better reflect the supervisors role in the incident. I changed the "immediate/Direct cause" to Failure to React, Correct. this helped to identify these causes: • 7.01 Improper performance is rewarded (tolerated) • 7.11 Improper supervisory example • 13.01 Inadequate assessment of needs and risks I do believe that these new marks are still addressed with the current corrective actions. | [24 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2000-06-12 | 1980-03-09 |  | 2020-01-24 07:00 | 0 | 0 | received x-ray from the clinic, | FALSE |  | while closing an ATO |  | TRUE | Dale Allen |  | Recordable | Dale Allen |  |  |  |  | Sprain/Strain |  | TRUE |  | Underground Const Coord | Arm | Injury | Left | TRUE | Garren Dodson | TRUE | 2020 | 1/24/2020 7:00:00 AM | 15 years | FALSE |  |  | stress from closing an ATO | [25 empty] | 8590250
9210 | Sooner Power Plant | 2020-01-23 17:00 | LOTO was hung on piece of equipment that was not requested. Operating authority picked the wrong template for the request. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Jimmie Allen | 2020-02-19 09:59 | 2020-01-25 16:15 | 2020-01-25 16:15 | 2020-02-08 14:32 | 2020-02-06 17:00 | 2020-01-25 16:05 | 2020-02-10 14:16 |  |  | Sooner Power Plant Unit 2 |  |  | Brady Sowell | JD, I am returning incident 9210 for the following changes. - In the incident description, it sounds as if several of the statements are assumptions and not statements from the members involved. Please clarify that the members were interviewed and that they attributed the errors to what the incident investigation says is the root cause. I have highlighted a few of the statements I am referring to below. - Clarify if the tagging and verification were done independently. see email for highlighted text | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Jimmie Allen |  | January 23, 2020 The original LOTO for 2A Precip ash blower was prepared for maintenance (WCD 8146800). After further discussing the scope of work (replacing belts and sheaves) with the PAE, the day Shift Coordinator (SC) realized a full LOTO would be safer. Both OA and PAE agreed that the new boundaries would be better suited for the job since the original LOTO got the local disconnect and the fuses and started on a new LOTO that cleared the whole blower and discharge line out. A second approval was not utilized for this, which is not required on green light templates. Although at Sooner it is a best practice that is utilized by taking the LOTO to the control room operator for the second approval. Preparing the new LOTO(WCD 8146803), the SC typed the name of equipment to be LOTOd out and as he was picking the template out in SAP, another Maintenance member walked in and asked if the LOTO for Unit 2-C system blowers (completely different system) was ready. The investigation revealed that the SC was thinking about the other maintenance members question and picked the template for 2C instead of 2A precip ash blower. Although the header on the LOTO had been filled out to say 2A precip ash blower, the actual equipment and content was for 2C blower. He then printed the LOTO out for the operators to hang. Also the LOTO for 2-C system was needed hung for maintenance to work on hoppers. Further investigation with the two operators that hung and verified the LOTO, they reported that they had taken both LOTOs with them to hang and verify but they did so independently. One operator hung the precip ash blower LOTO and the other operator hung the 2-C system LOTO. They then verified each other’s LOTO. Both operators focused on the tagging list overlooking the first page of the LOTO to be hung. Clearly both the tagger and the verifier didn’t pay close attention to the header stating 2A Precip Ash Blower. On that day, unit 2 was on Reserve Shutdown both units were manned by one Control Room Operator. Unit 1 on was online and the Tagger himself verified the equipment was red tagged (locked out) on the screen. A job briefing was conducted by the 2 operators hanging and verifying the LOTO. While verifying the boundaries, the PAE realized the boundaries were hung on the wrong precip ash blower. The PAE immediately returned to the Operating Authority and discussed the issue. A new LOTO was made for the correct precip ash blower (2A) and hung.(WCD 8146704) Another lesson learned: It has been a good practice at Sooner when Maintenance sends the 682 requests electronically ahead of time (24-hour notice) so the night crew would have the opportunity to vet the LOTO boundaries and prepare it and hang it if possible. By sending the 682s electronically, the functional location for the needed equipment is automatically populated and this will minimize additional chances for mistakes. In this incident, the 682 couldn’t be sent electronically since a Pick-Ticket has already been issued through it. Also, the investigation revealed that the 682 requests/details need to be more thorough by writing down the order number, date requested, and time. Also the Operating Authority should enforce such details and reject the request if not properly filled out. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Operations |  | Jimmie Allen | Jimmie Allen |  | Alexander Taybah | I approve. I will discuss this incident on the next MPO/MPM call Tuesday, February 11, 2020. | Alexander Taybah |  | Low | [6 empty] | 7.06 Improper attempt to save time or effort | [9 empty] | Tagger and verifier failed to compare the header information with the actual equipment being LOTO'd | 16. Failure to Follow Procedure, Policy, Practice | 5. Caught In (Pinch and Nip Points) | [92 empty] | 325384
9210 | Sooner Power Plant | 2020-01-23 17:00 | LOTO was hung on piece of equipment that was not requested. Operating authority picked the wrong template for the request. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Jimmie Allen | 2020-02-19 09:59 | 2020-01-25 16:15 | 2020-01-25 16:15 | 2020-02-08 14:32 | 2020-02-06 17:00 | 2020-01-25 16:05 | 2020-02-10 14:16 |  |  | Sooner Power Plant Unit 2 |  |  | Brady Sowell | JD, I am returning incident 9210 for the following changes. - In the incident description, it sounds as if several of the statements are assumptions and not statements from the members involved. Please clarify that the members were interviewed and that they attributed the errors to what the incident investigation says is the root cause. I have highlighted a few of the statements I am referring to below. - Clarify if the tagging and verification were done independently. see email for highlighted text | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Jimmie Allen |  | January 23, 2020 The original LOTO for 2A Precip ash blower was prepared for maintenance (WCD 8146800). After further discussing the scope of work (replacing belts and sheaves) with the PAE, the day Shift Coordinator (SC) realized a full LOTO would be safer. Both OA and PAE agreed that the new boundaries would be better suited for the job since the original LOTO got the local disconnect and the fuses and started on a new LOTO that cleared the whole blower and discharge line out. A second approval was not utilized for this, which is not required on green light templates. Although at Sooner it is a best practice that is utilized by taking the LOTO to the control room operator for the second approval. Preparing the new LOTO(WCD 8146803), the SC typed the name of equipment to be LOTOd out and as he was picking the template out in SAP, another Maintenance member walked in and asked if the LOTO for Unit 2-C system blowers (completely different system) was ready. The investigation revealed that the SC was thinking about the other maintenance members question and picked the template for 2C instead of 2A precip ash blower. Although the header on the LOTO had been filled out to say 2A precip ash blower, the actual equipment and content was for 2C blower. He then printed the LOTO out for the operators to hang. Also the LOTO for 2-C system was needed hung for maintenance to work on hoppers. Further investigation with the two operators that hung and verified the LOTO, they reported that they had taken both LOTOs with them to hang and verify but they did so independently. One operator hung the precip ash blower LOTO and the other operator hung the 2-C system LOTO. They then verified each other’s LOTO. Both operators focused on the tagging list overlooking the first page of the LOTO to be hung. Clearly both the tagger and the verifier didn’t pay close attention to the header stating 2A Precip Ash Blower. On that day, unit 2 was on Reserve Shutdown both units were manned by one Control Room Operator. Unit 1 on was online and the Tagger himself verified the equipment was red tagged (locked out) on the screen. A job briefing was conducted by the 2 operators hanging and verifying the LOTO. While verifying the boundaries, the PAE realized the boundaries were hung on the wrong precip ash blower. The PAE immediately returned to the Operating Authority and discussed the issue. A new LOTO was made for the correct precip ash blower (2A) and hung.(WCD 8146704) Another lesson learned: It has been a good practice at Sooner when Maintenance sends the 682 requests electronically ahead of time (24-hour notice) so the night crew would have the opportunity to vet the LOTO boundaries and prepare it and hang it if possible. By sending the 682s electronically, the functional location for the needed equipment is automatically populated and this will minimize additional chances for mistakes. In this incident, the 682 couldn’t be sent electronically since a Pick-Ticket has already been issued through it. Also, the investigation revealed that the 682 requests/details need to be more thorough by writing down the order number, date requested, and time. Also the Operating Authority should enforce such details and reject the request if not properly filled out. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Operations |  | Jimmie Allen | Jimmie Allen |  | Alexander Taybah | I approve. I will discuss this incident on the next MPO/MPM call Tuesday, February 11, 2020. | Alexander Taybah |  | Low |  |  |  | 4.02 Fatigue due to mental task load or speed | [12 empty] | While he was preparing the new LOTO and at the LOTO template page, another member had come into the SS office and asked if there was a LOTO for 2-C ash system ready. | 17. Failure to Identify Hazard, Risk | 5. Caught In (Pinch and Nip Points) | [92 empty] | 325384
9211 | Metro Service Center | 2020-01-27 16:00 | Vehicle F03-1234 was parked in front of sub on North side of Driveway. Contractor was spreading gravel on south side of driveway to clean up as they de-mob. Spotter ran into office trailer to retrieve something and skid steer mis-judged distance and struck vehicle on passenger rear quarter panel. | Level 1 |  | FALSE | Property Damage |  |  |  |  | OG&E Corp Services | Steven Blansett | 2020-02-12 15:57 | 2020-01-28 07:29 | 2020-01-28 07:29 | 2020-01-29 13:26 | 2020-02-10 16:00 | 2020-01-28 07:23 | 2020-01-30 14:54 |  |  | TAFB TAC Sub |  |  | Marcus Huddleston | No additional comments. MLH 2-12-20 | UTS |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Steven Blansett |  | Operator was spreading gravel outside of the GM sub, repairing ground damaged from the rain and traffic. The spotter walked away from the skid-steer taking his attention away from the equipment. The operator started to back up and the Skid-Steer made contact with the OG&E truck #FO3-1234 causing damage to the bed. |  |  |  | Metro Service Center | FALSE |  | FALSE | UTS - Project Mgmt |  | Steven Blansett | Steven Blansett |  | Christopher Lelak | No comments - CBL 01/30/2020 | Christopher Lelak |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [10 empty] | 16.01 Inadequate horizontal communication between peers | No communication between spotter and operator. | 02. Failure to Warn | 2. Struck By (Hit By Moving Object) | [68 empty] | Passenger Rear Quarter Panel has a crease in it from skid steer. | 500 |  | Vehicle (not related to operation of vehicle) |  | F03-1234
9212 | Sooner Power Plant | 2020-01-27 11:30 | A 4x12 sheet of fiberglass transite was found laying on the coal pile, the piece had blown off the roof of the stacker tower and landed north of the tower on the pile. | Level 3 |  | TRUE | Member Injury | Donnie Jones | Jesse Murray | Assign per Matt and Kent | 2020-01-29 11:08 | Power Supply | Kevin Ferguson |  | 2020-01-28 09:06 | 2020-01-28 09:06 | 2020-02-07 11:28 | 2020-02-10 11:30 | 2020-01-27 11:30 | 2020-02-12 09:11 |  | 2020-02-11 07:53 | Sooner stacker tower/coal yard |  |  |  |  | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Glen Hughes |  | On January 27, 2020 two Fuel Supply members were on the stacker tower to lubricate the turn table chain for #3 belt/boom. While performing this function they noticed a piece of roofing material laying on the ground on the Northeast side of the Stacker (see pic "Section of Stacker Roofing material on Northeast side of Stacker"). At this point the members began trying to determine where it came from, it was then they discovered that a piece of roof paneling was missing from the Southwest side of stacker tower roof (see pic "Missing Piece of Stacker Roof Southwest Corner"). The removal of this section was do to strong Southwest winds causing the material to break free from the screws and blow over the stacker tower to the Northeast side of the stacker Tower (see. pic "Path of Panel From Roof"). As a result of this incident there are corrective actions to be performed to prevent further occasions of roofing falling to the ground. It should be noted that during this investigation that this section of roofing was seen flapping approx. 2-3 months ago during strong Southerly winds by Fuel Supply members. There was a communication break down among members as to who was going to write a notification for repair, thus resulting in no one writing the hazard up for repair or providing a barricade for preventing members from being struck by the panel falling to the ground while working in the area. | Brady Sowell | Glen Hughes |  | Sooner Power Plant | FALSE |  | TRUE | Fuel Supply |  | Mark Burgess | Kevin Ferguson |  | Kent Wilson | Approved | Kent Wilson |  | High | [14 empty] | 15.03 Inadequate inspection and/or monitoring |  | Failure to perform a visual inspection of roofing material to identify missing screws or raised screws used to secure the roofing material. | 18. Failure to Check, Monitor | 12. Equipment Failure
9212 | Sooner Power Plant | 2020-01-27 11:30 | A 4x12 sheet of fiberglass transite was found laying on the coal pile, the piece had blown off the roof of the stacker tower and landed north of the tower on the pile. | Level 3 |  | TRUE | Member Injury | Donnie Jones | Jesse Murray | Assign per Matt and Kent | 2020-01-29 11:08 | Power Supply | Kevin Ferguson |  | 2020-01-28 09:06 | 2020-01-28 09:06 | 2020-02-07 11:28 | 2020-02-10 11:30 | 2020-01-27 11:30 | 2020-02-12 09:11 |  | 2020-02-11 07:53 | Sooner stacker tower/coal yard |  |  |  |  | Power Supply |  | Level 3 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Glen Hughes |  | On January 27, 2020 two Fuel Supply members were on the stacker tower to lubricate the turn table chain for #3 belt/boom. While performing this function they noticed a piece of roofing material laying on the ground on the Northeast side of the Stacker (see pic "Section of Stacker Roofing material on Northeast side of Stacker"). At this point the members began trying to determine where it came from, it was then they discovered that a piece of roof paneling was missing from the Southwest side of stacker tower roof (see pic "Missing Piece of Stacker Roof Southwest Corner"). The removal of this section was do to strong Southwest winds causing the material to break free from the screws and blow over the stacker tower to the Northeast side of the stacker Tower (see. pic "Path of Panel From Roof"). As a result of this incident there are corrective actions to be performed to prevent further occasions of roofing falling to the ground. It should be noted that during this investigation that this section of roofing was seen flapping approx. 2-3 months ago during strong Southerly winds by Fuel Supply members. There was a communication break down among members as to who was going to write a notification for repair, thus resulting in no one writing the hazard up for repair or providing a barricade for preventing members from being struck by the panel falling to the ground while working in the area. | Kevin Ferguson | Glen Hughes |  | Sooner Power Plant | FALSE |  | TRUE | Fuel Supply |  | Mark Burgess | Kevin Ferguson |  | Kent Wilson | Approved | Kent Wilson |  | High | [14 empty] | 15.03 Inadequate inspection and/or monitoring |  | Failure to perform a visual inspection of roofing material to identify missing screws or raised screws used to secure the roofing material. | 18. Failure to Check, Monitor | 12. Equipment Failure
9213 | Shawnee Service Center | 2020-01-27 10:30 | Fecon forestry mower, mowing heavy brush and trees, damaged customers gas line feeding house. | Level 1 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Wesley Lanier | 2020-02-13 14:15 | 2020-01-28 12:39 | 2020-01-28 12:39 | 2020-02-13 10:30 | 2020-02-10 10:30 | 2020-01-27 17:00 | 2020-02-13 12:56 |  |  | E of the intersection of CR 910 & CR 3500 South of Davenport. |  |  | Jerrie Looney | Did Floyd have a corrective action for damaged gas line? J. Looney, 1/20/20 Approved 1/12/20, J. Looney | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Wesley Lanier |  | see attached doc |  |  |  | Shawnee Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Wesley Lanier | Wesley Lanier |  | Michael Fox | Thanks Wes. I approve | Michael Fox |  | Low |  |  |  |  | 5.06 Lack of situational awareness |  |  |  | 9.06 Inadequate work planning or programming | [7 empty] | forestry mower damaged private gas line | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) | [5 empty] | Property Damage |  | Wesley Lanier | damage to private gas line by mower head |  |  |  |  | 2. Struck By (Hit By Moving Object) | Wesley Lanier | Asplundh Tree Expert Co. | Asplundh Tree Expert Co. |  | 3rd Party Property/Equipment |  | Wesley Lanier |  |  |  |  | FALSE | [42 empty] | while clearing right of way mower cause hole in private gas line | 200 | Steve Harris | 3rd Party Property/Equipment |  | 102-7025
9214 | Horseshoe Lake Power Plant | 2020-01-28 09:30 | Scaffold builders erecting structure around 6A boiler air preheater. Contract member thought he saw sparks from open electrical junction box and reported to contract foreman who stopped work and cleared the area. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Robert Brown |  | 2020-01-29 08:40 | 2020-01-29 08:40 | 2020-02-17 10:31 | 2020-02-11 09:30 | 2020-01-29 07:46 |  |  |  | 6A air preheater on turbine deck level. |  |  |  |  | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Robert Brown |  | Per EAI Report: EAI scaffold crew were working at the preheater in unit 6 building a scaffold for Robert Brown’s project. When one EAI employee, Javier Caraballo, saw a spark come out of a junction box that was located on an I-beam 10’ away from him and about 8’ off the ground. Javier C. notified his foreman Davit Brito. David Contacted Julian Gonzalez about the incident. Julian told them to stop working and evacuate the area until OGE gives the all clear to go back to work. Julian notified Robert Brown and Wade Gabbert. Once Robert Brown arrived and viewed the issue, he then proceeded to contact Tommy Herron in order to get him to look at the issue. After careful inspection and no issues with the wiring found, Tommy Herron closed the access door to junction box that had come loose and opened. Tommy Herron then gave the green light to go back to work. Julian Gonzalez visited with the scaffold and asbestos to ensure that any hazards or potential hazards are added to their JSA’s. Per conversation with Tommy Herron, it did not appear that there were any sparks coming out of the junction box at any time. There were not any apparent burns from contact and the wires were taped up and protected to prevent that occurrence. The screw had come loose and allowed the access panel to open; it was closed up and screws fastened tight. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Maintenance |  | Robert Brown | Robert Brown |  |  |  | Robert Doupe |  | Low | [11 empty] | 12.01.3 Inadequate preventative adjustment/assembly |  |  |  |  | Scaffold builders erecting structure around 6A boiler air preheater. Contract member thought he saw sparks from open electrical junction box and reported to contract foreman who stopped work and cleared the area. | 21. Inadequate Guards or Barriers | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Property Damage |  | Robert Brown | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Robert Brown | EAI | Julian Gonzalez |  |  |  | Robert Brown | [71 empty] | 9592477
9215 | Metro Service Center | 2020-01-27 16:30 | Member noticed damage to the passenger side rear fender of OGE truck during his 360 walk around. Damage to rear passenger bedside behind the back tire. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Kenny La Ferney | 2020-02-10 07:52 | 2020-01-29 09:22 | 2020-01-29 09:22 | 2020-01-29 09:52 | 2020-02-10 16:30 | 2020-01-28 08:30 | 2020-01-31 13:26 |  |  | Unknown- noticed at metro parking lot |  |  | Terry Hackett | Reviewed | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | TRUE |  | FALSE | TRUE | Kenny La Ferney |  | Member had been to multiple locations throughout the day and performed his 360 each time before leaving. He was parked in metro parking lot and was leaving for the day when he did his 360 and saw the damage. The damage is high up on the rear bedside. It is undetermined what hit the truck but had to be a large vehicle, possibly a delivery vehicle with a high tailgate, considering where the damage is on OGE truck. |  |  |  | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Roy Hoffman | Kenny La Ferney |  | Gary Lassley | Review driving policies and safe parking/backing practices in next meeting | Gary Lassley |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Unknown what exactly caused the incident. Suspect someone backed into the vehicle | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) | [68 empty] | Rear quarter panel damaged | 2500 | Roy Hoffman | Vehicle (not related to operation of vehicle) |  |  | FALSE |  | Oklahoma city | Other | Unknown | 1992-02-23 18:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Rain
9215 | Metro Service Center | 2020-01-27 16:30 | Member noticed damage to the passenger side rear fender of OGE truck during his 360 walk around. Damage to rear passenger bedside behind the back tire. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Delivery | Kenny La Ferney | 2020-02-10 07:52 | 2020-01-29 09:22 | 2020-01-29 09:22 | 2020-01-29 09:52 | 2020-02-10 16:30 | 2020-01-28 08:30 | 2020-01-31 13:26 |  |  | Unknown- noticed at metro parking lot |  |  | Terry Hackett | Reviewed | T&D Ops |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | TRUE | Kenny La Ferney |  | Member had been to multiple locations throughout the day and performed his 360 each time before leaving. He was parked in metro parking lot and was leaving for the day when he did his 360 and saw the damage. The damage is high up on the rear bedside. It is undetermined what hit the truck but had to be a large vehicle, possibly a delivery vehicle with a high tailgate, considering where the damage is on OGE truck. |  |  |  | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Roy Hoffman | Kenny La Ferney |  | Gary Lassley | Review driving policies and safe parking/backing practices in next meeting | Gary Lassley |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Unknown what exactly caused the incident. Suspect someone backed into the vehicle | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) | [68 empty] | Rear quarter panel damaged | 2500 | Roy Hoffman | Vehicle (not related to operation of vehicle) |  |  | FALSE |  | Oklahoma city | Other | Unknown | 1992-02-23 18:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Rain
9216 | Ft Smith Service Center | 2020-01-27 19:30 | IUS crew was given the job to change out the lighting arrestors on a pole, with out truck access in a deep rivine, so they planned to use a back yard machine ton complete this task. | Level 3 |  | FALSE | Contractor | Andrea Dennis | William Young | Investigate, establish causal factors and CA's. | 2020-02-20 10:57 | Power Delivery | Jeremy Renfro |  | 2020-01-29 13:01 | 2020-01-29 13:01 |  | 2020-02-10 19:30 | 2020-01-29 12:41 |  |  |  | 5011 Old Greenwood RD Ft. Smith, AR. 72903 Lat/Long 35336804, -94.388129 |  |  |  |  | T&D Ops |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Jeremy Renfro |  | Imperium Utility Service crew was working behind a Goodyear business off Old Greenwood Rd and I-540. Pole was off in a deep ravine. When it was determined it was not going to work due to not being able to reach the top of the pole, they decided to drive it back out. About half the way out the powerdolly got stuck. They decided to chain it up and pull it with a small bucket. While pulling it up a slope with a small bucket truck and chain, the power dolly became top heavy and turned over on its side. | Jeremy Renfro | Marcus Huddleston |  | Ft Smith Service Center | FALSE |  | FALSE | Resource Planning & Coord |  | Jeremy Renfro | John Legg |  |  |  | Michael Fox |  | High | [9 empty] | 10.05 Inadequate assessment of operational readiness | [6 empty] | While pulling it up a slope with a small bucket truck and chain, the power dolly became top heavy and turned over on its side | 11. Improper Position for Task | 9. Abnormal Operation |  | This incident needs to be updated to High. Also, we need an investigation team to review the incident. Please contact me if you have any questions. MLH 2-12-20 |  |  |  | Property Damage |  | Jeremy Renfro | Overturned Easement Machine |  |  |  |  | 4. Fall on Same Level (Slip and Fall, Trip Over) | Jeremy Renfro | Imperuim Utility Services | David Mcmurtry |  | Vehicle (not related to vehicle's operation) |  | Michael Fox |  |  |  |  | FALSE | [66 empty] | 7963007
9217 | Muskogee Power Plant | 2020-01-28 17:00 | Member was backing their personal vehicle into a parking spot and contacted the galvanized guardrail with their back bumper. | Level 1 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Scott Stidham |  | 2020-01-29 19:12 | 2020-01-29 19:12 | 2020-02-24 23:24 | 2020-02-11 17:00 | 2020-01-29 18:56 | 2020-02-26 07:22 |  |  | employee parking lot |  |  |  | Hold for call | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Scott Stidham |  | Member bumped a guard rail while backing into his parking space. The guardrail is low to the ground and very close to the curb making it hard to see from a pickup or larger vehicle. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Operations |  | Scott Stidham | Scott Stidham |  | Darcey Hayes | I'm good with the finds. The SLT team is working on redoing our plant parking lots so we will add this to the list of work to be done. | Darcey Hayes |  | Low | [9 empty] | 10.03 Inadequate standards, specifications and/or design criteria | [6 empty] | The barricade is very close to the curb and is no longer needed since we installed the concrete wall. Originally these spaces were made to be pulled forward into and not backed when we changed our parking policy we did not adapt all parking spaces. | 21. Inadequate Guards or Barriers | 1. Struck Against (Running or Bumping Into)
9218 | Ardmore Service Center | 2020-01-30 09:30 | Member was pulling through parking lot in a line truck hauling a 40' c3 wooden pole, Top of pole struck private light pole. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Terry Looney |  | 2020-01-30 12:24 | 2020-01-30 12:24 | 2020-02-11 10:06 | 2020-02-13 09:30 | 2020-01-30 09:30 | 2020-02-25 15:49 |  |  | 825 S 1st Madill, Oklahoma 73446 |  |  |  |  | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Carl Williams |  | On January 30, 2020 member was working around Madill, OK and pulled into a parking lot driving a line truck with a 40 class 3 pole on the truck. While making a turn in the parking lot the top of the pole struck a private light pole. There was damage to the light pole and OGE will be responsible for the repairs, no cost has been determined yet. There was a larger more open parking lot that the member could have parked in but due to inattention and lack of experience he just decided to park in the normal parking lot. Member should have parked in the larger lot or been more attentive to the pole overhang and drove further past the pole to avoid contact. Member had another vehicle related incident less than a year ago. |  |  |  | Ardmore Service Center | FALSE |  | FALSE | Construction Services |  | Jimmy Rowe | Terry Looney |  | Kenneth McKinzie | Approved | Kenneth McKinzie |  | Low |  |  |  |  | 5.01 Lack of experience | [11 empty] | Member failed to meet commercial vehicle driving expectations | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) | [74 empty] | TRUE |  | Madill | Struck Fixed Object | Drove Forward Into Object | 2019-05-19 19:00 |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Clear
9218 | Ardmore Service Center | 2020-01-30 09:30 | Member was pulling through parking lot in a line truck hauling a 40' c3 wooden pole, Top of pole struck private light pole. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Terry Looney |  | 2020-01-30 12:24 | 2020-01-30 12:24 | 2020-02-11 10:06 | 2020-02-13 09:30 | 2020-01-30 09:30 | 2020-02-25 15:49 |  |  | 825 S 1st Madill, Oklahoma 73446 |  |  |  |  | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Carl Williams |  | On January 30, 2020 member was working around Madill, OK and pulled into a parking lot driving a line truck with a 40 class 3 pole on the truck. While making a turn in the parking lot the top of the pole struck a private light pole. There was damage to the light pole and OGE will be responsible for the repairs, no cost has been determined yet. There was a larger more open parking lot that the member could have parked in but due to inattention and lack of experience he just decided to park in the normal parking lot. Member should have parked in the larger lot or been more attentive to the pole overhang and drove further past the pole to avoid contact. Member had another vehicle related incident less than a year ago. |  |  |  | Ardmore Service Center | FALSE |  | FALSE | Construction Services |  | Jimmy Rowe | Terry Looney |  | Kenneth McKinzie | Approved | Kenneth McKinzie |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Member failed to meet commercial vehicle driving expectations | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) | [74 empty] | TRUE |  | Madill | Struck Fixed Object | Drove Forward Into Object | 2019-05-19 19:00 |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Clear
9219 | Seminole PP; EGX Gath/Trans | 2020-01-29 15:00 | Member tripped over unmarked step near FGR seal air fan valve. | Level 1 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Scott Lee |  | 2020-01-30 12:36 | 2020-01-30 12:36 | 2020-02-13 14:23 | 2020-02-12 15:00 | 2020-01-30 12:24 | 2020-02-28 13:27 |  |  | Seminole Unit 2 Boiler on level 3 near FGR seal air fan valve. |  |  |  |  | Power Supply |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Scott Lee |  | Member tripped over unmarked step near unit 2 FGR seal air fan valve on level 3 of the boiler. Member was focused on Flue gas Recirculation Duct work as they proceeded to the ladder to north of the duct. While walking toward ladder to access Flue Gas Recirculation seal air fan valve member was focused on the duct work when members foot struck the toe board on the level transition. It was determined that the level transition did not have visual markings to identify transition hazard. It was determined to temporarily install yellow duct tape to mark the level transition until the permanent corrective action of installing yellow and black tape to mark the level transition. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | TRUE | Other |  | Scott Lee | Scott Lee |  | Matthew Schuermann | Approved | Matthew Schuermann |  | Low |  |  | 3.09 Constrained movement | [13 empty] | Failure to identify level transition due to members focus on low hanging Flue Gas Recirculation duct. | 17. Failure to Identify Hazard, Risk | 4. Fall on Same Level (Slip and Fall, Trip Over)
9220 | North Service Center | 2020-01-31 10:00 | An Asplundh Foreman removed a tree branch and as he roped it down the rope caught on the bucket. The shock caused the rope to rip out of the groundsman's hand and the branch fell on a gas meter causing it to break the meter. The fire department was dispatched and ONG had to replace the meter. | Level 1 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Christopher Martin | 2020-02-25 13:38 | 2020-01-31 13:42 | 2020-01-31 13:42 | 2020-02-06 15:05 | 2020-02-14 10:00 | 2020-01-31 13:29 | 2020-02-17 07:20 |  |  | 1008 N Nail Parkway, Moore OK |  |  | Jerrie Looney | Approved, J. Looney, 2.25.20 | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Christopher Martin |  | The Crew Foreman was pruning a hackberry tree with two main leaders. A fence and gas meter were in the drop zone area underneath the limb being pruned. The foreman placed a pull rope in the crotch of one leader and attached the pull rope to the other. His ground person pulled the rope while he cut the log using his hydraulic pole saw from the bucket. The log was approximately 17” in diameter and 40” long. As the foreman completed the cut the log dropped free, missing the fence but striking the gas meter at the base of the tree. The foreman had not accounted for the distance between the two leaders of the tree and the height of the crotch from the ground where the pull rope was placed. |  |  |  | North Service Center | FALSE |  | FALSE | PD - Resource Planning & Coord |  | Christopher Martin | Michael Fox |  | Michael Fox | Approved | Michael Fox |  | Low |  |  |  |  | 5.04 Inadequate update training | 6.02 Inadequate practice |  |  | 9.06 Inadequate work planning or programming | [7 empty] | The work was not planned correctly and the foreman has not had any updated training recently. | 36. Inadequate Preparation, Planning | 9. Abnormal Operation | [5 empty] | Property Damage |  | Christopher Martin | Broken Gas Meter |  |  |  |  | 2. Struck By (Hit By Moving Object) | Christopher Martin | Asplundh | Cody Stone |  | Fixed Equipment |  | Christopher Martin |  |  |  |  | FALSE
9221 | Metro Service Center | 2020-01-31 11:30 | Public vehicle struck Company vehicle making a turn out of the wrong lane. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Garren Dodson | 2020-01-31 14:28 | 2020-01-31 14:17 | 2020-01-31 14:17 | 2020-01-31 14:24 | 2020-02-14 11:30 | 2020-01-31 14:06 |  |  |  | I-240 westbound service road and Walker Ave |  |  | Brent Perdue | approved | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | [6 empty] | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Eduardo Rivera | Garren Dodson |  |  |  | Gary Lassley |  | Low | [93 empty] | FALSE |  | oklahoma City | Public Vehicle Struck OGE | Both Vehicles Moving | 2018-06-03 19:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
9222 | Metro Service Center | 2020-01-31 10:30 | public vehicle ran a stop light and hit the passenger side of bucket truck. | Level 1 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Carl Kemp | 2020-01-31 15:16 | 2020-01-31 15:02 | 2020-01-31 15:02 | 2020-01-31 15:09 | 2020-02-14 10:30 | 2020-01-31 14:57 |  |  |  | SE 44th and Sunnylane. OKC |  |  | Brent Perdue | This incident has been discussed with the T&D Safety Manager and the responsible supervisor. The risk ranking has been agreed as acceptable due to the nature of the incident. If repair cost go up, this incident could be ranked higher. | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | [6 empty] | Metro Service Center | FALSE |  | FALSE | Construction Services |  | Denny Morgan | Carl Kemp |  |  |  | Terry Garrett |  | Low | [93 empty] | FALSE |  | OKC | Public Vehicle Struck OGE | Both Vehicles Moving | 2003-12-16 18:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
9223 | North Service Center | 2020-02-03 11:00 | Member parked in a parking space. When he opened the door to get out, wind caught the door causing it to swing open before member could grab it. The door on the company truck struck the car next it causing a dent in the public vehicle door. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Delivery | Jeffrey Warner | 2020-02-21 10:40 | 2020-02-03 14:10 | 2020-02-03 14:10 | 2020-02-18 11:12 | 2020-02-17 11:00 | 2020-02-03 14:00 | 2020-02-19 09:16 |  |  | In the parking lot of the base exchange on Tinker Air Force Base. |  |  | Luke Kennedy | approved 2/21/2020 | T&D Ops |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Jeffrey Warner |  | Member arrived at tinker air force base on February 3rd at approximately 11 A.M. Member stated that he was in somewhat of a hurry. When he opened the door to get out, wind caught the door causing it to swing open before member could grab it. The door on the company truck struck the car next it causing a dent in the public vehicle door. Weather reports for the day did indicate wind speeds of around 15mph on and off throughout the day. Once the member realized the damage to the vehicle he waited for the public person but eventually left his information for the public driver. |  |  |  | North Service Center | FALSE |  | FALSE | Construction Services |  | Raymond Sarcoxie | Jeffrey Warner |  | Terry Garrett | I agree with the corrective action...TG | Terry Garrett |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | the wind caused the door to swing open faster than expected contacting the public vehicle next to the member | 40. Weather Conditions | 1. Struck Against (Running or Bumping Into) | [68 empty] | dent to passenger side door | 400 | Raymond Sarcoxie | Vehicle (not related to operation of vehicle) |  |  | FALSE |  | Del City |  |  |  |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Cloudy
9224 | Seminole PP; EGX Gath/Trans | 2020-02-03 12:30 | Contractor was arc gouging boiler skin. Rod made contact with instrument air line behind worker. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Supply | Justin Stahl |  | 2020-02-03 14:12 | 2020-02-03 14:12 | 2020-02-24 10:43 | 2020-02-17 12:30 | 2020-02-03 13:52 | 2020-02-28 10:20 |  |  | Seminole PP Unit 1 Level 5, NW Corner |  |  |  |  | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Justin Stahl |  | A Zachry member was working on the 5th level of unit 1 boiler. The member was using an arc gouger to remove the boiler skin from the area. While performing this task, the back end of the gouging rod made contact with an instrument air line. The contractor immediately contacted their plant contact and a temporary repair was made. |  |  |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | Maintenance |  | David Norman | Justin Stahl |  | Scott Lee | Please add corrective actions for this incident as well as determine if the cause analysis section needs to be filled out for this type of incident. | Scott Lee |  | Low | [9 empty] | 10.02 Inadequate consideration of human factors/ergonomics | [6 empty] | A Zachry member was working on the 5th level of unit 1 boiler. The member was using an arc gouger to remove the boiler skin from the area. While performing this task, the back end of the gouging rod made contact with an instrument air line. The contractor immediately contacted their plant contact and a temporary repair was made. | 24. Congestion or Restricted Action | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | Justin Stahl | Hole in Instrument Air Piping |  |  |  |  | 1. Struck Against (Running or Bumping Into) | David Norman | Zachry | Zachry Moore |  | Process Interruption |  | Justin Stahl |  |  |  |  | FALSE | [66 empty] | 9594612
9225 | Northeast District Service Cen | 2020-01-30 12:00 | Line crew had finished a job and was leaving the site and backed into fence post marking the driveway edge due to truck slipping in mud | Level 2 |  | FALSE | Vehicle | Andrea Dennis |  |  |  | Power Delivery | Donald Melson | 2020-02-11 10:11 | 2020-02-04 09:20 | 2020-02-04 09:20 | 2020-02-06 14:17 | 2020-02-13 12:00 | 2020-01-30 12:30 | 2020-02-11 09:58 |  | 2020-02-06 15:38 | County road Southeast of Bristow (7014 Goldoak Rd, Bristow, OK) |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Donald Melson |  | The line crew had completed a new business job were they had hung a transformer and set service pole for UG service to a mobile home. The road coming to the job was muddy and hard maneuver due to rain the day before. The crew had two bucket trucks, a digger truck with a mat trailer, also it was a 5 man crew. The foreman was going to leave early for a funeral taking the digger after setting the pole. F10-246 had pulled in the driveway at the job site to be out of the way for the other trucks to get in position approximately 75' to the East of the driveway is were the crew was going to start work. After the job was complete F10-319 drove off headed back to the office while F10-246 started backing out to the road. As his backer was spotting him the driver looked away to t he driver mirror to check his side and then back to see his backer. At that time the backer was trying to stop him but had already made contact with the T-posts due to the truck sliding on the mud. He was able to pull back up, they pulled the posts and backed out to the road. Before leaving the site they set the post back in position to mark the driveway edge. |  |  |  | Northeast District Service Cen | FALSE |  | FALSE | Construction Services |  | Cody McKim | Donald Melson |  | Chad Inman | Thank you for the through investigation. I approve of the corrective actions. | Chad Inman |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | As member was backing he seen his backer in passenger side mirror, he turned to check his driver mirror when he turned checking his backer they had struck the T-posts. The backer was trying to stop him during his check of the driver side mirror. | 11. Improper Position for Task | 1. Struck Against (Running or Bumping Into) |  | Good reminder to avoid backing whenever possible and if you are forced to back never take your eyes off your backer. Thank you for reporting. | [72 empty] | TRUE |  | Bristow | Struck Fixed Object | Backing Related | 2017-09-10 19:00 |  | FALSE |  |  | Day Light |  |  | Mud |  | Cloudy
9226 | Sooner Power Plant | 2020-02-03 15:30 | Members were moving a conex container with the overhead hoist past another conex container. Rigging bumped the lock on the door of the stationary conex container causing slight damage to the lock. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Trent Novotny | 2020-02-27 08:04 | 2020-02-04 11:44 | 2020-02-04 11:44 | 2020-02-21 10:55 | 2020-02-17 15:30 | 2020-02-03 16:00 | 2020-02-21 16:00 |  |  | Sooner PP Unit 2 Turbine Floor |  |  | Brady Sowell | approved | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Trent Novotny |  | Two members were tasked to move a 40 foot conex box (white one see Pic 3) from the TG basement to the turbine floor for outage. Members hooked up appropriate rigging and proceeded with the lift. Once the conex box was on the turbine floor members moved it to the west end. As they were moving the conex box past another conex box (green one see Pic 3) that they had previously located on the turbine floor, the rigging lug bumped into the lock on the stationary conex box and damaged it. (Pic 1) The rigging that is used has certain lugs that fit into the lifting eyes located on the corners of the conex boxes and protrudes from the sides around 3". (Pic 2) The member that was operating the hoist was located in the front of the conex box and the other member was located on the back corner of the conex box to keep it from bumping the interceptor valve of the turbine. (Pic 3) Members had a good SWP filled out (see SWP pic) and discussed the plan to move the conex boxes from the crane bay to the other end of the turbine floor. They had also discussed where each of them would be positioned for the lift. They had evaluated the path to be used and it was determined that the path they chose was the less congested of two possible paths. During the lift, the members were more concerned with the interceptor valves on the turbine side of the conex box and not the other side. They stated they had a foot of clearance between the conex box and the line on the interceptor valve but with a load that long that foot closed quicker than they expected. The operator also stated that the new controls are very sensitive to the buttons. The variable speed on the controls of the hoist is controlled on how much pressure the operator puts on the button, which makes it hard to be smooth with the load. The member operating the hoist is certified to operate this hoist. Upon investigation of the incident a few things could have been done different to prevent this incident. The first thing would be to have the layout of the conex boxes before the boxes arrive onsite. The members did not receive the layout from the contractor until after the first box was already placed which then made the gap between the conex box and the turbine tight. The second thing we could have done different would have been to use a different means of rigging. The rigging was appropriate but it did not allow very much head room. If we would have had more head room, we could have lifted the conex box over the first box and therefore avoiding the tight gap between the conex box and the turbine. The reason members used the rigging they did was to keep the angle of the chokers at an appropriate position. Shorter chokers would have made the angle less than 30 degrees. Longer chokers would have lessened the head room of the pick and would not have worked at all. The use of a spanner bar may need to be looked into to allow adjustable lifting points to allow a straight pull on the lifting lugs. The third, and probably the easiest would have been to use more than 1 spotter and 1 operator. If we would have had a spotter on both sides and the operator, we could have avoided the other conex box. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Maintenance |  | Scott Buchanan | Trent Novotny |  | Frank Brixey | Please help me understand what was on the members SWP? What was discussed before making the lift? Why did they not take a step back and accept the risk? Was there an additional path they could have used? Approved | Frank Brixey |  | Low | [12 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | Members were moving connex box and bumped another connex box. | 11. Improper Position for Task | 1. Struck Against (Running or Bumping Into) | [68 empty] | Lock got bumped by conex container. Lock still works. | 100 | Scott Buchanan | 3rd Party Property/Equipment | [20 empty] | 9594309
9227 | West Service Center | 2020-02-05 07:00 | Member arrived on a 350 trouble call. Member had just come to a complete stop when a public driver slid into the back of the company vehicle. No injuries resulted from the collision. | Level 2 |  | FALSE | Vehicle |  |  |  |  | Power Delivery | Coulter Swart | 2020-02-24 12:54 | 2020-02-05 09:12 | 2020-02-05 09:11 | 2020-02-18 10:00 | 2020-02-19 07:00 | 2020-02-05 08:59 | 2020-02-24 07:01 |  | 2020-02-21 10:38 | Intersection of 33rd and NW council |  |  | Lindle Coleman | approved | T&D Ops |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Coulter Swart |  | On Wednesday February 5th at 7:00 A.M Member arrived on a 350 trouble call. Member had just come to a complete stop when a public driver slid into the back of the company vehicle. The member didn't sustain any injuries. At this time the member exited his vehicle and checked on the status of the public driver. The public driver was also uninjured. The member then proceeded to alert his supervisors and contact Bethany PD to right up an incident report. The Case# is 20-900. Bethany PD has yet to provide a full police report. |  |  |  | West Service Center | FALSE |  | FALSE | Construction Services |  | Joshua Black | Coulter Swart |  | Steve Watkins | I approve. | Steve Watkins |  | Medium |  |  |  |  | 5.01 Lack of experience | [11 empty] | public driver going to fast on icy roads | 39. Road Conditions | 2. Struck By (Hit By Moving Object) |  | Approved 2/21/2020 | [72 empty] | FALSE |  | Bethany | Public Vehicle Struck OGE | OGE Vehicle Stopped/Parked | 2001-03-25 18:00 |  | FALSE |  |  | Dawn |  |  | Asphalt |  | Snow
9228 | South District Service Center | 2020-02-05 12:00 | Fleet Mechanic was operating F13-249 (bucket truck) in front of the east wash bay door at South District Garage. The member was cycling the lower boom , from the lower controls, up and down checking for a hydraulic leak at the lower boom cylinder. The member had the upper boom raised 3-4 feet out of the rest to allow for clearance while operating the lower boom. The member lowered the lower boom and put it in the rest. Member opened the wash bay overhead door and made contact with the upper boom and the garage building. It was discovered that the upper boom was still raised. | Level 2 |  | FALSE | Vehicle |  |  |  |  | OG&E Corp Services | Nathan Gooch |  | 2020-02-06 09:26 | 2020-02-06 09:26 | 2020-02-11 16:20 | 2020-02-19 12:00 | 2020-02-06 08:59 | 2020-02-12 07:47 |  | 2020-02-12 07:33 | In front of east wash bay door at the South District Garage. |  |  |  |  | UTS |  | Level 2 | Vehicle |  | FALSE | FALSE | TRUE |  | FALSE | TRUE | Nathan Gooch |  | Fleet Mechanic was operating F13-249 (bucket truck) in front of the east wash bay door at South District Garage. The member was cycling the lower boom , from the lower controls, up and down checking for a hydraulic leak at the lower boom cylinder. The member had the upper boom raised 3-4 feet out of the rest to allow for clearance while operating the lower boom. The member lowered the lower boom and put it in the rest. Member raised the outriggers. Member did not perform a walk around. Member opened the wash bay overhead door and made contact with the upper boom and the garage building. It was discovered that the upper boom was still raised. Member was not interrupted during this operation and was working by his self. Upper boom does not have an out of stow indicator. The out of stow indicator is tied to the lower boom. (Light and Buzzer in Cab on this unit). There was no indicator in the cab to warn the member that the upper boom was in the raised position. The environmental conditions: snowing, cold, daylight. Member was wearing winter gear with his hood up. Damage was confined to the sheet metal on the building and there was no damage to the structure. There was no damage to the boom and all functionality was checked out. |  |  |  | South District Service Center | FALSE |  | FALSE | UTS - Asset & LC Mgmt |  | Randolph Phillips | Nathan Gooch |  | Paul Jefferson | I approve corrective actions. | Paul Jefferson |  | Medium |  |  | 3.06 Exposure to temperature extremes |  |  |  | 7.06 Improper attempt to save time or effort | [9 empty] | Member did not lower upper boom into stowed position before moving truck. | 15. Using Equipment Improperly | 1. Struck Against (Running or Bumping Into) |  | Approved, Cody Vinyard | [66 empty] | Sheet metal damage to South District garage above the east wash bay door. Metal is rubbing the door. | 1500 | Randolph Phillips | Structural |  |  | TRUE |  | Norman | Struck Fixed Object | Drove Forward Into Object | 1995-04-09 19:00 |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Snow
9228 | South District Service Center | 2020-02-05 12:00 | Fleet Mechanic was operating F13-249 (bucket truck) in front of the east wash bay door at South District Garage. The member was cycling the lower boom , from the lower controls, up and down checking for a hydraulic leak at the lower boom cylinder. The member had the upper boom raised 3-4 feet out of the rest to allow for clearance while operating the lower boom. The member lowered the lower boom and put it in the rest. Member opened the wash bay overhead door and made contact with the upper boom and the garage building. It was discovered that the upper boom was still raised. | Level 2 |  | FALSE | Property Damage |  |  |  |  | OG&E Corp Services | Nathan Gooch |  | 2020-02-06 09:26 | 2020-02-06 09:26 | 2020-02-11 16:20 | 2020-02-19 12:00 | 2020-02-06 08:59 | 2020-02-12 07:47 |  | 2020-02-12 07:33 | In front of east wash bay door at the South District Garage. |  |  |  |  | UTS |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | TRUE | Nathan Gooch |  | Fleet Mechanic was operating F13-249 (bucket truck) in front of the east wash bay door at South District Garage. The member was cycling the lower boom , from the lower controls, up and down checking for a hydraulic leak at the lower boom cylinder. The member had the upper boom raised 3-4 feet out of the rest to allow for clearance while operating the lower boom. The member lowered the lower boom and put it in the rest. Member raised the outriggers. Member did not perform a walk around. Member opened the wash bay overhead door and made contact with the upper boom and the garage building. It was discovered that the upper boom was still raised. Member was not interrupted during this operation and was working by his self. Upper boom does not have an out of stow indicator. The out of stow indicator is tied to the lower boom. (Light and Buzzer in Cab on this unit). There was no indicator in the cab to warn the member that the upper boom was in the raised position. The environmental conditions: snowing, cold, daylight. Member was wearing winter gear with his hood up. Damage was confined to the sheet metal on the building and there was no damage to the structure. There was no damage to the boom and all functionality was checked out. |  |  |  | South District Service Center | FALSE |  | FALSE | UTS - Asset & LC Mgmt |  | Randolph Phillips | Nathan Gooch |  | Paul Jefferson | I approve corrective actions. | Paul Jefferson |  | Medium |  |  | 3.06 Exposure to temperature extremes |  |  |  | 7.06 Improper attempt to save time or effort | [9 empty] | Member did not lower upper boom into stowed position before moving truck. | 15. Using Equipment Improperly | 1. Struck Against (Running or Bumping Into) |  | Approved, Cody Vinyard | [66 empty] | Sheet metal damage to South District garage above the east wash bay door. Metal is rubbing the door. | 1500 | Randolph Phillips | Structural |  |  | TRUE |  | Norman | Struck Fixed Object | Drove Forward Into Object | 1995-04-09 19:00 |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Snow
9229 | Sooner Power Plant | 2020-02-04 15:00 | Contractor (WPE) was driving West by bent 2 and backed up onto concrete fuel vault. No injuries. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Ashley Harris | 2020-02-25 11:11 | 2020-02-06 09:40 | 2020-02-06 09:40 | 2020-02-19 13:20 | 2020-02-18 15:00 | 2020-02-04 15:30 | 2020-02-21 10:40 |  | 2020-02-19 13:40 | Sooner Power Plant- East of Bent 2 on Conveyor 10 & 11 |  |  | William Young | Reviewed and approved. WCY 2/25/2020 | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Ashley Harris |  | Contractor from WPE, Bill Moskoff was driving West on road between stacks and AQCS buildings. He stopped to observe work going on. He decided he wanted to get out and look. He backed up to clear an obstacle so he could park in the gravel. There was another obstacle that was not in his sight. This is when he drove upon the concrete fuel vault. The obstacle is low and in a depressed area and was not visible to the driver in the mirror. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | UTS - Capital Projects |  | Ashley Harris | Ashley Harris |  | Robert Weaver | Agree with the above assessment. | Robert Weaver |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Contractor was driving West on road between stacks and AQCS buildings. He stopped to observe work going on. He decided he wanted to get out and look. He backed up to clear an obstacle so he could park in the gravel. There was another obstacle that was not in his sight. This is when he drove upon the concrete fuel vault. The obstacle is low and in a depressed area and was not visible to the driver in the mirror. | 11. Improper Position for Task | 1. Struck Against (Running or Bumping Into) |  | Add additional basic causes. MLH 2/19/2020 No additional comments. MLH 2/19/2020 |  |  | Sooner 10 & 11 Conveyor | Vehicle |  | Ashley Harris | [5 empty] | 1. Struck Against (Running or Bumping Into) | Ashley Harris | Wolf Point Engineers | Bill Moskoff |  |  |  | Ashley Harris |  |  |  |  | FALSE
9230 | Corporate Headquarters Bldg | 2020-01-29 15:30 | OGE vehicle F03-1443 was traveling north on I-35 in the left lane near I-44. a private vehicle was also traveling north on I-35 near I-44 in the right lane. The private vehicle then changed lanes and struck OGE vehicle in the right front corner of unit with the left rear tire of the private vehicle. The private vehicle continued on after striking the OGE vehicle and was later stopped by OHP. The driver of the private vehicle stated he was unaware he had struck the OGE vehicle. | Level 1 |  | FALSE | Vehicle |  |  |  |  | OG&E Corp Services | Paul George |  | 2020-02-06 09:57 | 2020-02-06 09:57 |  | 2020-02-12 15:30 | 2020-02-06 09:42 |  |  |  | I-35 and I-44 |  |  |  |  | Enterprise Services |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | [6 empty] | Corporate Headquarters Bldg | FALSE |  | FALSE | Corp. Services |  | Randy Keese | Paul George |  |  |  | James Finch |  | Low | [93 empty] | FALSE |  | Oklahoma City | Public Vehicle Struck OGE | Both Vehicles Moving | 2006-10-15 19:00 |  | FALSE |  |  | Day Light |  |  | Asphalt |  | Clear
9231 | Sooner Power Plant | 2020-02-06 08:30 | WPE Sub-contractor (GBI) was helping truck driver unload. The chain binder popped up and hit contractor on lower left portion of face. Contractor was driven to urgent care. | Level 2 |  | FALSE | Contractor |  |  |  |  | OG&E Corp Services | Ashley Harris |  | 2020-02-06 10:01 | 2020-02-06 10:01 | 2020-02-21 13:16 | 2020-02-20 08:30 | 2020-02-06 09:45 | 2020-02-26 11:10 |  | 2020-02-24 10:10 | Sooner Power Plant- East side of PP by GBI satellite trailer. |  |  |  |  | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Ashley Harris |  | 2/6/2020- 11:45am- GBI had a safety stand down up by trailers. JP from GBI talked about the incident that occurred. JP has talked to the trucking companies and requested for all drivers to wear FR that come on site so they may exit the cab of the trucks. He also requested that the driver remove any additional tie downs before entering the fence of the facility that do not provide direct support to the integrity of the load. Safety first, nothing is more important than safety, all incidents and injuries are preventable, stop work authority, be your brothers keeper, proper training, don't be afraid to ask questions on new tasks, and JSA's were covered during stand down. Having disposable FR suits for drivers on site was discussed. Steven Debose (GBI Rigger) was on top of the trailer unstrapping counterweights on truck. He was using a chain lever binder/ boomer to unsecure the load. When we was doing this it popped up and hit him on the left side of his face. Jesse Littlepage (GBI Forman) was headed out of the tool room at the GBI satellite tool trailer on the East side of the plant. He saw Steven staggering and the truck driver yelled "he's hurt". Jesse started to run towards Steven and Steven collapsed to the ground. Doug Young (GBI Supervisor) saw Steven staggering down the road without his hardhat on. He collapsed to the ground lying on his back screaming he was hurt. Doug ran down to Steven rolling him on to his side to keep him from choking on his blood. Doug noticed a gash on his lip and blood on his face. Doug called Ted Pulis the GBI General Forman and reported the that Steven was hurt. All GBI upper management came down to the site. 2/17/2020- During the Monday morning Safety meeting I asked Wayman from GBI to talk on the subject of safety surrounding chain lever binders. I sent him an OGE Safety Bulletin on this topic so he could pull useful information from it and add to this information as well. This meeting is hosted by WPE, but all contractors on this project attend the meeting. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | UTS - Capital Projects |  | Ashley Harris | Ashley Harris |  | Robert Weaver | No additional comments. | Robert Weaver |  | Medium |  | 2.06 Poor coordination |  |  | 5.03 Inadequate initial training |  | 7.06 Improper attempt to save time or effort |  | 9.07 Inadequate instructions, orientation and/or training |  |  |  | 13.02 Inadequate human factors/ergonomics considerations | 14.02.2 Inadequate communication of standards: distribution |  | 16.03. Inadequate communication between different organizations | WPE Sub-contractor (GBI) was helping truck driver unload. The chain binder popped up and hit contractor on lower left portion of face. Contractor was driven to urgent care. | 11. Improper Position for Task | 2. Struck By (Hit By Moving Object) |  | No additional comments. MLH 2/24/2020 |  |  |  | Injury / Illness |  | Ashley Harris |  | laceration to left lower portion of face | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Ashley Harris | Wolf Point Engineers | Steven Dubose | Laceration |  | Chin | Ashley Harris | Left | TRUE | Company Vehicle
9232 | West Service Center | 2020-02-06 09:00 | A Wright Tree Service foreman was spotted by an OG&E foreman operating his bucket in between the three-phase primary and the neutral wire to get better access to the tree he was trimming. | Level 3 |  | TRUE | Contractor | Jean Leger | William Young | Assign team. Investigate, establish causal factors and CA's. WCY 2/7/2020. | 2020-02-07 07:43 | Power Delivery | Christopher Martin |  | 2020-02-06 11:44 | 2020-02-06 11:44 |  | 2020-02-20 09:00 | 2020-02-06 11:06 |  |  |  | 8935 NW 10th st near the Mustang Power Plant |  |  |  |  | T&D Ops |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | Wright employees observed by OGE members operating their bucket truck between phases in violation of MAD's. | Jerrie Looney | William Young |  | West Service Center | FALSE |  | TRUE | Resource Planning & Coord |  | Christopher Martin | Michael Fox |  |  |  | Michael Fox |  | High | [24 empty] | Clearance / LOTO |  | Christopher Martin | [5 empty] | 9. Abnormal Operation | Christopher Martin | Wright Tree Service | Jose Salazar |  |  |  | Christopher Martin
9232 | West Service Center | 2020-02-06 09:00 | A Wright Tree Service foreman was spotted by an OG&E foreman operating his bucket in between the three-phase primary and the neutral wire to get better access to the tree he was trimming. | Level 3 |  | TRUE | Contractor | Jean Leger | William Young | Assign team. Investigate, establish causal factors and CA's. WCY 2/7/2020. | 2020-02-07 07:43 | Power Delivery | Christopher Martin |  | 2020-02-06 11:44 | 2020-02-06 11:44 |  | 2020-02-20 09:00 | 2020-02-06 11:06 |  |  |  | 8935 NW 10th st near the Mustang Power Plant |  |  |  |  | T&D Ops |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | Wright employees observed by OGE members operating their bucket truck between phases in violation of MAD's. | Christopher Martin | William Young |  | West Service Center | FALSE |  | TRUE | Resource Planning & Coord |  | Christopher Martin | Michael Fox |  |  |  | Michael Fox |  | High | [24 empty] | Clearance / LOTO |  | Christopher Martin | [5 empty] | 9. Abnormal Operation | Christopher Martin | Wright Tree Service | Jose Salazar |  |  |  | Christopher Martin
9233 | Metro Service Center | 2020-02-06 07:30 | Aerotek Employee fell on cross walk on black ice. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Retail Energy | Scott Helgoe |  | 2020-02-07 09:33 | 2020-02-07 09:33 | 2020-02-10 15:03 | 2020-02-20 07:30 | 2020-02-07 09:25 | 2020-02-10 17:06 |  | 2020-02-10 15:26 | On the east side of parking lot in walkway. |  |  |  |  | Retail Energy |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Scott Helgoe |  | member fell on black ice in the parking lot walkway |  |  | FALSE | Metro Service Center | FALSE |  | FALSE | Customer Operations |  | Scott Helgoe | Scott Helgoe |  | Mark Charlson | Scott made me aware our Aerotek employee had fallen. We immediately reached out to Aerotek to advise. We ensured that the Aerotek employee was ok, and informed her of a medical facility Aerotek advised she could use. The employee declined to be seen by medical personnel. We sent a request for winter traction for all OGE members within the Call Center and have distributed them. | Mark Charlson |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | member fell on black ice, in the parking lot... | 31. Inadequate or Excess Illumination | 4. Fall on Same Level (Slip and Fall, Trip Over) |  | Spoke with Mayte, Aerotek, about incident and Scott reviewed site of fall with her. She was wearing Ugg boots - photo attached. Area had been cleared and ice pellets applied. She was in the pedestrian walkway and said the ice was not visible. Approved. J. Looney, 2.10.20 |  |  |  | Injury / Illness |  | Scott Helgoe |  | Fall to pavement non injury | FALSE |  |  | 4. Fall on Same Level (Slip and Fall, Trip Over) | Scott Helgoe | Aerotek | Mayte Lopez | Contusion |  | Knee | Scott Helgoe | Top | FALSE |  |  |  | FALSE |  |  | 2019-11-07 | 1999-04-03 |  | 2020-02-06 08:00 | 0 | 0 |  | FALSE |  | she slipped on black ice |  |  | Mayte Lopez |  | Non-Recordable | Mayte Lopez |  |  |  |  | Contusion |  | FALSE |  |  | Knee |  | Left | FALSE | Scott Helgoe | FALSE |  | 2/6/2020 8:00:00 AM | 4 months | FALSE |  |  | hitting the pavement | walking into the office
9234 | Enid Service Center | 2020-02-05 10:00 | While travelling southbound on 54th member noticed that there was a popping noise coming from the back in end of the vehicle. Member returned to the service center to assess the issue. At this time he found that there were some broken studs and loose lug nuts. At this time member reported the issue to fleet services. | Level 1 |  | TRUE | Vehicle |  |  |  |  | Power Delivery | Darrin Nickel | 2020-02-26 08:13 | 2020-02-10 12:53 | 2020-02-10 12:53 | 2020-02-19 13:35 | 2020-02-19 10:00 | 2020-02-10 12:45 | 2020-02-21 11:42 |  |  | 54th st & 412 hwy |  |  | Luke Kennedy | I agree with the corrective actions and believe they will prevent similar incidents going forward. | T&D Ops |  | Level 1 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | Darrin Nickel |  | While travelling southbound on 54th member noticed that there was a popping noise coming from the back in end of the vehicle. Member returned to the service center to assess the issue. At this time he found that there were some broken studs and loose lug nuts. The member then reported the issue to fleet services. -The vehicle was initially turned in to have the rear brakes fixed at Northcutts Chevy. Upon further investigation in addition to the lug nuts not being properly torqued, the wheels were also clocked wrong so that the inside tire valve stem was not accessible. -The following day the vehicle was hauled back to Northcutts Chevy to address the issue. They did replace the broken studs and repaired it at no cost to the company. -When the vehicle was returned for the second time it was noted that the rear wheels were still clocked wrong. -At this time member returned the truck back to Northcutts for the third time and instructed them on how to correctly install the rear wheels so that access to inside wheel valve stem can be accessed. Fleets response to issue was that they do not have the manpower to inspect all repairs made by contractors. |  |  |  | Enid Service Center | FALSE |  | TRUE | PD Operations Services |  | Mathew Weingartner | Darrin Nickel |  | James Hutchison | I have reviewed this report and concur with it's findings as well as the corrective actions to be taken. | James Hutchison |  | Low | [6 empty] | 7.09 Inadequate discipline |  |  |  |  | 12.02.3 Inadequate reparative examination of units |  |  |  |  | Contractor failed to properly torque lug nuts to manufacturer specifications | 37. Inadequate Support, Assistance | 9. Abnormal Operation
9235 | River Valley | 2020-02-08 12:00 | The inspection riser had a leak and was being repaired with fiberglass patch. The pumps were LOTO'd, but Unit 1 water boxes were not drained. Saturday, the water boxes drains were opened and water was able to flow to the work area of the patch. | Level 1 |  | FALSE | System Operational Incident |  |  |  |  | Power Supply | Melton Morris |  | 2020-02-11 09:34 |  |  | 2020-03-21 12:00 | 2020-02-08 12:00 |  |  |  | River Valley PP cooling tower inspection riser |  |  |  |  | Power Supply |  | Level 1 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE | [6 empty] | River Valley | FALSE |  | FALSE | Operations |  | John Scott | Melton Morris |  |  |  | Timothy Chancellor |  | Low
9236 | Horseshoe Lake Power Plant | 2020-02-11 11:30 | SCAFFOLD MATERIAL UNDER THE THROTTLE VALVE CAUGHT FIRE DUE TO STRESS RELIEVE LEADS MAKING CONTACT WITH THE BOARDS. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Wade Gabbert |  | 2020-02-11 11:45 | 2020-02-11 11:45 | 2020-02-28 15:28 | 2020-02-25 11:30 | 2020-02-11 11:29 |  |  |  | HORSESHOE LAKE POWER PLANT UNIT #8 RIGHT HAND THROTTLE VALVE. |  |  |  |  | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Wade Gabbert |  | On 02/11/2020, at approximately 1100, an incident concerning a small incipient stage fire was reported. Power Plant Services had been repairing the right-hand throttle valve on unit 8. The work involved a procedure to weld and machine the stud bores in the valve chest. The weld procedure also required pre heat and post weld heat treat be applied. The process uses heating elements installed on the valve to maintain pre heat temperatures and to bring the valve to its post weld temperature of 1350 F. This work was being performed by contract company, PPRS. Scaffolding and wood platform with a fire blanket was installed under the valve prior to work starting in order to prevent dropped objects to the area below. The fire occurred during the post weld heat treating stage. Fire was noticed on the lower right portion of the valve where the booster element leads were located. The fire and heat from the equipment damaged the booster leads exposing the copper and creating a secondary hazard. At this time the stress technician was not onsite, and the welder was monitoring the equipment from a safe distance. While the welder monitored the area, immediate action that could be taken on the damaged booster were discussed. Welder made contact with the company office that suggested we wait on the tech to arrive before any changes were made to the process. When the stress tech arrived they pulled the fire blanket from under the valve and elevated the leads and it appeared that the process could continue. For two hours there were no issues and then the area under the valve re-ignited. The tech having confirmed the damaged booster section was the problem began to lower the temperature so the power to that section could be disconnected. After disconnecting power to the booster section, we removed the smoldering boards and the process continued to completion with no further incident. Contractor Report: • Post weld heat treat with heating pads and KOA wool insulation installed. • Fire was approximately one foot in diameter. • Distance from the heating pad to the plywood deck was approximately 14-18 inches. • Powder fire extinguisher was used and continued to smolder because of the heat being generated. • The post weld heat treat tech was not on-site and was contacted. • Fire ignited again at about 1400 and was extinguished a with a dry chemical extinguisher. • It was noticed that some of the insulation on one of the cables was melting. • The post weld heat treat tech was reached and on-site at this time and determined that the lead could be shut down but not disconnected from the unit due to post weld heat treatment still going on and temperatures were at approximately 1350 F. • JHA for this event was not found and reported to have been discarded in the trash. Findings: • Oil on the blanket from the machining process is believed to be the ignition source transferring rapidly to the board underneath. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Maintenance |  | Terry Creed | Wade Gabbert |  |  |  | Daniel Perry |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [8 empty] | 14.01.1 Inadequate development of standards: inventory and evaluation of exposures and needs |  |  | SCAFFOLD MATERIAL UNDER THE THROTTLE VALVE CAUGHT FIRE DUE TO STRESS RELIEVE LEADS MAKING CONTACT WITH THE BOARDS | 17. Failure to Identify Hazard, Risk | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [5 empty] | Property Damage |  | Wade Gabbert | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Terry Creed | POWER PLANT SERVICES | Andy Herndon |  |  |  | Wade Gabbert | [71 empty] | 9596464
9237 | Muskogee Power Plant | 2020-02-10 17:30 | Contractor backed into member personal vehicle. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Peter Soules |  | 2020-02-11 15:34 | 2020-02-11 15:34 | 2020-02-25 14:54 | 2020-02-24 17:30 | 2020-02-11 15:25 |  |  | 2020-02-26 14:23 | MK6 parking lot |  |  |  |  | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Peter Soules |  | On Monday 2-10-2020 at 5:30pm contractor was leaving work for the day. As he was backing up and bump into member's car in his blind spot. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | Engineering & Planning |  | Jonathan Capps | Peter Soules |  |  | Reviewed. Incident report added since last review. | Carol Rollins |  | Medium | [5 empty] | 6.02 Inadequate practice | [10 empty] | On Monday 2-10-2020 at 5:30pm contractor was leaving work for the day. As he was backing up and bump into member's car in his blind spot. | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) |  | Reviewed Bob Wright |  |  |  | Vehicle |  | Peter Soules | [5 empty] | 1. Struck Against (Running or Bumping Into) | Jonathan Capps | Zachry | William Ramsey |  |  |  | Peter Soules |  |  |  |  | FALSE
9238 | Sooner Power Plant | 2020-02-10 16:00 | Contractor employee, Upon arrival they were instructed to troubleshoot and then call the plant contact and request a LOTO before performing any work. They began troubleshooting and decided to pull the fuses and unbolt the spool piece from the gearbox without obtaining a LOTO. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Jerry Bocox |  | 2020-02-11 15:56 | 2020-02-11 15:56 | 2020-02-24 09:32 | 2020-02-24 16:00 | 2020-02-11 15:45 |  |  | 2020-02-27 08:16 | Sooner Power Plant Turbine Floor |  |  |  |  | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Jerry Bocox |  | Kone was in a monthly safety meeting on the morning of Monday February 10th , they were already scheduled to be onsite at Sooner for repairs that day and were going to head this way after their meeting. About mid morning I was notified that our turbine floor crane was making a terrible noise and we needed Kone asap to troubleshoot and repair, because GE was onsite the following Monday and needed it. I called Kone and they told me Jules was already on his way, and that they were sending two others from OKC branch to assist. Jules arrived and I met with him in my office and we talked about what we were going to skip that was scheduled for the day and work on the emergency job first. We then discussed what the issue was with the Turbine floor crane and that he could troubleshoot but before he took anything apart he would need to call plant contact, and request a LOTO. The OKC guys showed up and Jules left to meet up with them and sign into the control room. They worked until that evening and left for the day and returned the next morning. When I met with Jules the next morning he stated that he had removed the drive shaft the day before and was sure the coupling was the problem. I asked him if he remembered our conversation about having to get a LOTO before they performed any work and he stated he did not remember that and that he had a lot on his mind while we were talking. Another planner had overheard the discussion and reinforced that he did hear the directions given by the planner to obtain LOTO before any work was to be done by contractor. Jules stated that they discussed amongst themselves if a LOTO was required and the decision was made to pull the fuses and proceed with work. We called plant contact and asked him to have the LOTO hung so they could remove the couplings. The LOTO was hung on Tuesday morning the work was performed and the repair was made with no further issues. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Jeffery Beck | Jerry Bocox |  |  |  | Donald Wyckoff |  | Medium |  |  |  |  | 5.05 Misunderstood directions |  |  |  | 9.02 Unclear or conflicting assignment of responsibility | [7 empty] | Contractor proceeded to work on overhead crane on Turbine floor without proper LOTO in place. | 16. Failure to Follow Procedure, Policy, Practice | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) |  | Approved by Brady Sowell |  |  |  | Clearance / LOTO |  | Jerry Bocox | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Jeffery Beck | Kone Cranes | Jules McMurtry |  |  |  | Jerry Bocox | [71 empty] | 9597230
9239 | Sooner Power Plant | 2020-02-12 11:00 | Contractor found live wire while checking for dead before starting work. No injuries. | Level 3 |  | TRUE | Contractor | Robert Burch | William Young | Investigate, establish causal factors and CA's. | 2020-02-20 11:00 | OG&E Corp Services | Ashley Harris |  | 2020-02-12 17:21 | 2020-02-12 17:21 |  | 2020-02-26 11:00 | 2020-02-12 16:55 |  |  |  | Sooner Power Plant- Dumper Barrell Drive Motor |  |  |  |  | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | 2/13/20 @ 11:45AM- Safety Stand Down on the Dumper Project. We held a safety stand down at Richmond Engineers trailer to discuss the LOTO process to all contractors on this project. It was felt there was a disconnect and the process was not clear to all contractors. Wade Alley spoke on the LOTO process. | Brady Sowell | Marcus Huddleston |  | Sooner Power Plant | FALSE |  | TRUE | UTS - Capital Projects |  | Pete Hamby | Ashley Harris |  |  |  | Robert Weaver |  | High | [24 empty] | Injury / Illness |  | Ashley Harris | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Pete Hamby | Richmond | Eagle Electricians |  |  |  | Ashley Harris
9239 | Sooner Power Plant | 2020-02-12 11:00 | Contractor found live wire while checking for dead before starting work. No injuries. | Level 3 |  | TRUE | Contractor | Robert Burch | William Young | Investigate, establish causal factors and CA's. | 2020-02-20 11:00 | OG&E Corp Services | Ashley Harris |  | 2020-02-12 17:21 | 2020-02-12 17:21 |  | 2020-02-26 11:00 | 2020-02-12 16:55 |  |  |  | Sooner Power Plant- Dumper Barrell Drive Motor |  |  |  |  | UTS |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | 2/13/20 @ 11:45AM- Safety Stand Down on the Dumper Project. We held a safety stand down at Richmond Engineers trailer to discuss the LOTO process to all contractors on this project. It was felt there was a disconnect and the process was not clear to all contractors. Wade Alley spoke on the LOTO process. | Ashley Harris | Marcus Huddleston |  | Sooner Power Plant | FALSE |  | TRUE | UTS - Capital Projects |  | Pete Hamby | Ashley Harris |  |  |  | Robert Weaver |  | High | [24 empty] | Injury / Illness |  | Ashley Harris | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Pete Hamby | Richmond | Eagle Electricians |  |  |  | Ashley Harris
9240 | Horseshoe Lake Power Plant | 2020-02-12 14:30 | While preparing header pipe to paint one end feel from jack stand. No injury or property damage | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Matthew Cox |  | 2020-02-12 17:57 | 2020-02-12 17:57 |  | 2020-02-26 14:30 | 2020-02-12 17:48 |  |  | 2020-02-21 13:53 | Horseshoe Lake welding shop |  |  |  |  | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Matthew Cox |  | On 2/12/2020 at approximately 2:30 pm, another member and myself were in the process of preparing a new header pipe for Horseshoe Lake #6 generator hydrogen cooling water system for paint. While building the new header, we had been using a roller pipe stand that has 5 legs, but once flanges were added to the stub outs, it was discovered that the flanges would not clear the legs to be rolled into the position needed. We then changed out the pipe stand with another rolling pipe stand that has a thinner top and only 3 legs so we could roll to position. While rolling to the last side that needed cleaned, the new stand we put in place tipped over causing one end of the header to fall to the ground. No one was under the pipe when it fell and no property damage occurred. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Matthew Cox | Kelly Casey |  | Kelly Casey |  | Kelly Casey |  | Medium | [12 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | Pipe stand tipped over causing 8" pipe header to fall to the ground | 08. Improper Loading | 2. Struck By (Hit By Moving Object) |  | See workflow comments for reason being returned. UPDATE: Reviewed and approved. | [90 empty] | 9595508
9240 | Horseshoe Lake Power Plant | 2020-02-12 14:30 | While preparing header pipe to paint one end feel from jack stand. No injury or property damage | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Matthew Cox |  | 2020-02-12 17:57 | 2020-02-12 17:57 |  | 2020-02-26 14:30 | 2020-02-12 17:48 |  |  | 2020-02-21 13:53 | Horseshoe Lake welding shop |  |  |  |  | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Matthew Cox |  | On 2/12/2020 at approximately 2:30 pm, another member and myself were in the process of preparing a new header pipe for Horseshoe Lake #6 generator hydrogen cooling water system for paint. While building the new header, we had been using a roller pipe stand that has 5 legs, but once flanges were added to the stub outs, it was discovered that the flanges would not clear the legs to be rolled into the position needed. We then changed out the pipe stand with another rolling pipe stand that has a thinner top and only 3 legs so we could roll to position. While rolling to the last side that needed cleaned, the new stand we put in place tipped over causing one end of the header to fall to the ground. No one was under the pipe when it fell and no property damage occurred. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Matthew Cox | Kelly Casey |  | Kelly Casey |  | Kelly Casey |  | Medium | [12 empty] | 13.04 Inadequate availability |  |  |  | Pipe stand tipped over causing 8" pipe header to fall to the ground | 08. Improper Loading | 2. Struck By (Hit By Moving Object) |  | See workflow comments for reason being returned. UPDATE: Reviewed and approved. | [90 empty] | 9595508
9240 | Horseshoe Lake Power Plant | 2020-02-12 14:30 | While preparing header pipe to paint one end feel from jack stand. No injury or property damage | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Matthew Cox |  | 2020-02-12 17:57 | 2020-02-12 17:57 |  | 2020-02-26 14:30 | 2020-02-12 17:48 |  |  | 2020-02-21 13:53 | Horseshoe Lake welding shop |  |  |  |  | Power Supply |  | Level 2 | Property Damage |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Matthew Cox |  | On 2/12/2020 at approximately 2:30 pm, another member and myself were in the process of preparing a new header pipe for Horseshoe Lake #6 generator hydrogen cooling water system for paint. While building the new header, we had been using a roller pipe stand that has 5 legs, but once flanges were added to the stub outs, it was discovered that the flanges would not clear the legs to be rolled into the position needed. We then changed out the pipe stand with another rolling pipe stand that has a thinner top and only 3 legs so we could roll to position. While rolling to the last side that needed cleaned, the new stand we put in place tipped over causing one end of the header to fall to the ground. No one was under the pipe when it fell and no property damage occurred. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Matthew Cox | Kelly Casey |  | Kelly Casey |  | Kelly Casey |  | Medium | [12 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | Pipe stand tipped over causing 8" pipe header to fall to the ground | 08. Improper Loading | 2. Struck By (Hit By Moving Object) |  | See workflow comments for reason being returned. UPDATE: Reviewed and approved. | [90 empty] | 9595508
9240 | Horseshoe Lake Power Plant | 2020-02-12 14:30 | While preparing header pipe to paint one end feel from jack stand. No injury or property damage | Level 2 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Matthew Cox |  | 2020-02-12 17:57 | 2020-02-12 17:57 |  | 2020-02-26 14:30 | 2020-02-12 17:48 |  |  | 2020-02-21 13:53 | Horseshoe Lake welding shop |  |  |  |  | Power Supply |  | Level 2 | Property Damage |  | FALSE | TRUE | TRUE |  | FALSE | FALSE | Matthew Cox |  | On 2/12/2020 at approximately 2:30 pm, another member and myself were in the process of preparing a new header pipe for Horseshoe Lake #6 generator hydrogen cooling water system for paint. While building the new header, we had been using a roller pipe stand that has 5 legs, but once flanges were added to the stub outs, it was discovered that the flanges would not clear the legs to be rolled into the position needed. We then changed out the pipe stand with another rolling pipe stand that has a thinner top and only 3 legs so we could roll to position. While rolling to the last side that needed cleaned, the new stand we put in place tipped over causing one end of the header to fall to the ground. No one was under the pipe when it fell and no property damage occurred. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Special Services |  | Matthew Cox | Kelly Casey |  | Kelly Casey |  | Kelly Casey |  | Medium | [12 empty] | 13.04 Inadequate availability |  |  |  | Pipe stand tipped over causing 8" pipe header to fall to the ground | 08. Improper Loading | 2. Struck By (Hit By Moving Object) |  | See workflow comments for reason being returned. UPDATE: Reviewed and approved. | [90 empty] | 9595508
9241 | North Service Center | 2020-02-12 | Member was stripping wire when he felt discomfort in his right elbow. No medical attention required. Member was able to return to work. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Eric Engles | 2020-02-28 11:05 | 2020-02-13 11:35 | 2020-02-13 11:35 | 2020-02-26 09:33 | 2020-02-26 | 2020-02-13 11:21 | 2020-02-26 13:44 |  | 2020-02-26 12:42 | 8309 Greystone Ave Okc Ok |  |  | Lindle Coleman | Approve | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Eric Engles |  | On February 12th at approximately 12:00 A.M member arrived at 8309 Greystone avenue OKC, OK to build a riser. As he was stripping 3 conductor 350 the pocket knife he was using slipped as he was stripping the wire jarring his right elbow. The conductor was cold which makes it harder to strip. Member stated that he knew of the stripping devices offered by the company but didn't have one on his truck. After he felt the pain in his elbow he texted his supervisor that he needed a 4way stripper and returned to work. He didn't feel that he required any medical attention at that time. When he brought up the discomfort to his supervisor the next day his supervisor then urged him to fill out a first aid. Peter has been with the company since 2018 and has been with the North Service dept. since October 21, 2019. |  |  | FALSE | North Service Center | FALSE |  | FALSE | Construction Services |  | Peter Bilicki III | Eric Engles |  | Steve Watkins | I approve | Steve Watkins |  | Medium | [5 empty] | 6.02 Inadequate practice | [10 empty] | Member was using wrong tool for the job. | 16. Failure to Follow Procedure, Policy, Practice | 11. Overstress, Overpressure, Overexertion, Ergonomic |  | I have reviewed the investigation and concur with the corrective actions | [24 empty] | FALSE |  |  | 2019-04-08 | 1974-03-25 |  | 2020-02-12 08:00 | 0 | 0 |  | FALSE |  | member was stripping wire away from himself, knife slipped, hyperextending elbow. |  |  | Peter Bilicki III |  | First Aid | Peter Bilicki III |  |  |  |  | Sprain/Strain |  | FALSE |  | Service Technician | Elbow |  |  |  | Eric Engles |  |  | 2/12/2020 8:00:00 AM |  | FALSE |  |  | Force of pushing
9242 | Sooner Power Plant | 2020-02-16 17:30 | As contractor was performing de-slagging procedures for upcoming outage they shot through a closed small inspection door that had no refractory. Rounds from the shotgun shell struck a beam and economizer hopper 35 feet from the door. All current boiler de-slagging procedures were followed. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Trent Novotny |  | 2020-02-17 09:56 | 2020-02-17 09:56 | 2020-02-24 17:00 | 2020-03-01 17:30 | 2020-02-17 09:15 |  |  | 2020-02-27 17:21 | Sooner PP Unit 1 Level 7 North side of Boiler |  |  |  |  | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Trent Novotny |  | De-slagging is necessary to clean the furnace area of the boiler from hardened ash that has accumulated over time. De-slagging process requires the use of explosives and the use of a shotgun. According to SOP 323.048 section 5 & 6 members are not allowed on the boiler structure unless they are granted permission from the plant director and restricted to work at least 2 levels above or below where the explosive experts are working. (See pic SOP) This means no one can work on the level immediately above or below where the explosive experts are working. On February 16th at around 1700 Expro discovered that a small porthole on level 7 North side of the boiler had been shot through and immediately called their plant contact. The OGE member was shown the door and he immediately shut down the use of the shotgun and notified his supervisor. The incident was promptly reported the next morning. Upon investigation we seen 3 marks on a beam that was directly behind the door and 1 hole on the economizer hopper that is 35 feet behind the door. (See pic Beam and Hopper) The inspection door did not have any refractory in it nor was there much left of the metal skin that holds the refractory. (See pic Inside) The outer part of the door is cast iron which would become brittle over time when exposed to high temps of the boiler due to not having refractory protecting it.(See pic Outside) It appears to have been a direct shot on the door due to angle of the pellet marks on the beam and hopper. When questioning the Expro supervisor he stated they used high brass 00 buck shot in their 12 gauge shotguns. When asked about the barricading of the boiler during de-slagging he stated they would put up “red” barricades on the level above and below where they were working but when they started their inspection process with shotguns they did not put up barricades. This procedure was followed. They are also required to give an all call prior to using explosives and they are also required to notify their plant contact and the SS when they start shot gunning. This procedure was also followed. (See pic Procedure) He did state that when they start shot gunning that they would go to an inspection door and shoot all the ash they could see from that porthole and then move on to the next inspection door. This could not ensure that members would be safe 2 levels below the level they are working on since there are no marks on the inside of the boiler. He added he has been doing this for 15 years and this is the first time this has happened. Expro has done their own investigation and there were no discrepancies found with their report. (See pic Expro Report) Expro has already changed their procedure as far as shot gunning is concerned. The changes are represented by the red lettering in their procedure. (See pic Procedure) The current SOP states that a “Boiler Structure Caution Tagging List” will be made by the OA at each plant and a Work Clearance Document will be developed and housed in SAP. This was also followed per the procedure. The Structure Caution Tagging List has been interpreted to use “Caution” tags with “Caution” tape. This is the current practice at Sooner. (See Pic Barricade) The “Caution” tags offer no description of the hazards present, does not state anything about “de-slagging” being done, or the necessity to obtain the Plant Director’s permission to cross the boundary. (See Pic Tag) With this current practice anyone can cross that boundary with no idea of the hazards. When the tags are printed through SAP the program only allows 40 characters for the description of where to hang the clearance, which hinders the OA from entering anything about the hazards or requirements. The condition of the door was very poor. (See pic Good Door) A thermography survey should be performed every year and 6 weeks before a major outage. When speaking with Sooner’s reliability technician he stated he has never seen an order for that survey. We could not find an order within SAP as well. Our reliability technician contacted the technician he replaced and he stated that he would just go and perform the survey once a year and just knew it had to be done. The survey was last done in 2016. There were no broken procedures or negligence on anyone’s part during this incident. There are some gaps and inconsistencies within the fleet that need to be closed to ensure the safety of everyone during de-slagging. 1. Replace the door and perform a visual inspection during this outage for any more doors that need to be repaired or replaced. 2. Set up a meeting to discuss the changes that need to be made with the other plants that perform de-slagging. 3. Change the current procedure. 4. Communicate the changes with the fleet. 5. Create a PM Order to perform Thermography Survey. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Houston Mendenhall | Trent Novotny |  |  |  | Frank Brixey |  | Medium | [13 empty] | 14.01.4 Inadequate development of standards: procedures/practices/rules |  |  | Procedures have gaps to ensure safety. | 16. Failure to Follow Procedure, Policy, Practice | 2. Struck By (Hit By Moving Object) |  | Trent, Excellent investigation. You have been very thorough and worked hard to make sure this doesn't happen again at OGE or any other site where expro is employed. Great Job. | [90 empty] | 9595791
9242 | Sooner Power Plant | 2020-02-16 17:30 | As contractor was performing de-slagging procedures for upcoming outage they shot through a closed small inspection door that had no refractory. Rounds from the shotgun shell struck a beam and economizer hopper 35 feet from the door. All current boiler de-slagging procedures were followed. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Trent Novotny |  | 2020-02-17 09:56 | 2020-02-17 09:56 | 2020-02-24 17:00 | 2020-03-01 17:30 | 2020-02-17 09:15 |  |  | 2020-02-27 17:21 | Sooner PP Unit 1 Level 7 North side of Boiler |  |  |  |  | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Trent Novotny |  | De-slagging is necessary to clean the furnace area of the boiler from hardened ash that has accumulated over time. De-slagging process requires the use of explosives and the use of a shotgun. According to SOP 323.048 section 5 & 6 members are not allowed on the boiler structure unless they are granted permission from the plant director and restricted to work at least 2 levels above or below where the explosive experts are working. (See pic SOP) This means no one can work on the level immediately above or below where the explosive experts are working. On February 16th at around 1700 Expro discovered that a small porthole on level 7 North side of the boiler had been shot through and immediately called their plant contact. The OGE member was shown the door and he immediately shut down the use of the shotgun and notified his supervisor. The incident was promptly reported the next morning. Upon investigation we seen 3 marks on a beam that was directly behind the door and 1 hole on the economizer hopper that is 35 feet behind the door. (See pic Beam and Hopper) The inspection door did not have any refractory in it nor was there much left of the metal skin that holds the refractory. (See pic Inside) The outer part of the door is cast iron which would become brittle over time when exposed to high temps of the boiler due to not having refractory protecting it.(See pic Outside) It appears to have been a direct shot on the door due to angle of the pellet marks on the beam and hopper. When questioning the Expro supervisor he stated they used high brass 00 buck shot in their 12 gauge shotguns. When asked about the barricading of the boiler during de-slagging he stated they would put up “red” barricades on the level above and below where they were working but when they started their inspection process with shotguns they did not put up barricades. This procedure was followed. They are also required to give an all call prior to using explosives and they are also required to notify their plant contact and the SS when they start shot gunning. This procedure was also followed. (See pic Procedure) He did state that when they start shot gunning that they would go to an inspection door and shoot all the ash they could see from that porthole and then move on to the next inspection door. This could not ensure that members would be safe 2 levels below the level they are working on since there are no marks on the inside of the boiler. He added he has been doing this for 15 years and this is the first time this has happened. Expro has done their own investigation and there were no discrepancies found with their report. (See pic Expro Report) Expro has already changed their procedure as far as shot gunning is concerned. The changes are represented by the red lettering in their procedure. (See pic Procedure) The current SOP states that a “Boiler Structure Caution Tagging List” will be made by the OA at each plant and a Work Clearance Document will be developed and housed in SAP. This was also followed per the procedure. The Structure Caution Tagging List has been interpreted to use “Caution” tags with “Caution” tape. This is the current practice at Sooner. (See Pic Barricade) The “Caution” tags offer no description of the hazards present, does not state anything about “de-slagging” being done, or the necessity to obtain the Plant Director’s permission to cross the boundary. (See Pic Tag) With this current practice anyone can cross that boundary with no idea of the hazards. When the tags are printed through SAP the program only allows 40 characters for the description of where to hang the clearance, which hinders the OA from entering anything about the hazards or requirements. The condition of the door was very poor. (See pic Good Door) A thermography survey should be performed every year and 6 weeks before a major outage. When speaking with Sooner’s reliability technician he stated he has never seen an order for that survey. We could not find an order within SAP as well. Our reliability technician contacted the technician he replaced and he stated that he would just go and perform the survey once a year and just knew it had to be done. The survey was last done in 2016. There were no broken procedures or negligence on anyone’s part during this incident. There are some gaps and inconsistencies within the fleet that need to be closed to ensure the safety of everyone during de-slagging. 1. Replace the door and perform a visual inspection during this outage for any more doors that need to be repaired or replaced. 2. Set up a meeting to discuss the changes that need to be made with the other plants that perform de-slagging. 3. Change the current procedure. 4. Communicate the changes with the fleet. 5. Create a PM Order to perform Thermography Survey. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Houston Mendenhall | Trent Novotny |  |  |  | Frank Brixey |  | Medium | [11 empty] | 12.02.3 Inadequate reparative examination of units |  |  |  |  | Door in poor condition. | 18. Failure to Check, Monitor | 2. Struck By (Hit By Moving Object) |  | Trent, Excellent investigation. You have been very thorough and worked hard to make sure this doesn't happen again at OGE or any other site where expro is employed. Great Job. | [90 empty] | 9595791
9242 | Sooner Power Plant | 2020-02-16 17:30 | As contractor was performing de-slagging procedures for upcoming outage they shot through a closed small inspection door that had no refractory. Rounds from the shotgun shell struck a beam and economizer hopper 35 feet from the door. All current boiler de-slagging procedures were followed. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Trent Novotny |  | 2020-02-17 09:56 | 2020-02-17 09:56 | 2020-02-24 17:00 | 2020-03-01 17:30 | 2020-02-17 09:15 |  |  | 2020-02-27 17:21 | Sooner PP Unit 1 Level 7 North side of Boiler |  |  |  |  | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | Trent Novotny |  | De-slagging is necessary to clean the furnace area of the boiler from hardened ash that has accumulated over time. De-slagging process requires the use of explosives and the use of a shotgun. According to SOP 323.048 section 5 & 6 members are not allowed on the boiler structure unless they are granted permission from the plant director and restricted to work at least 2 levels above or below where the explosive experts are working. (See pic SOP) This means no one can work on the level immediately above or below where the explosive experts are working. On February 16th at around 1700 Expro discovered that a small porthole on level 7 North side of the boiler had been shot through and immediately called their plant contact. The OGE member was shown the door and he immediately shut down the use of the shotgun and notified his supervisor. The incident was promptly reported the next morning. Upon investigation we seen 3 marks on a beam that was directly behind the door and 1 hole on the economizer hopper that is 35 feet behind the door. (See pic Beam and Hopper) The inspection door did not have any refractory in it nor was there much left of the metal skin that holds the refractory. (See pic Inside) The outer part of the door is cast iron which would become brittle over time when exposed to high temps of the boiler due to not having refractory protecting it.(See pic Outside) It appears to have been a direct shot on the door due to angle of the pellet marks on the beam and hopper. When questioning the Expro supervisor he stated they used high brass 00 buck shot in their 12 gauge shotguns. When asked about the barricading of the boiler during de-slagging he stated they would put up “red” barricades on the level above and below where they were working but when they started their inspection process with shotguns they did not put up barricades. This procedure was followed. They are also required to give an all call prior to using explosives and they are also required to notify their plant contact and the SS when they start shot gunning. This procedure was also followed. (See pic Procedure) He did state that when they start shot gunning that they would go to an inspection door and shoot all the ash they could see from that porthole and then move on to the next inspection door. This could not ensure that members would be safe 2 levels below the level they are working on since there are no marks on the inside of the boiler. He added he has been doing this for 15 years and this is the first time this has happened. Expro has done their own investigation and there were no discrepancies found with their report. (See pic Expro Report) Expro has already changed their procedure as far as shot gunning is concerned. The changes are represented by the red lettering in their procedure. (See pic Procedure) The current SOP states that a “Boiler Structure Caution Tagging List” will be made by the OA at each plant and a Work Clearance Document will be developed and housed in SAP. This was also followed per the procedure. The Structure Caution Tagging List has been interpreted to use “Caution” tags with “Caution” tape. This is the current practice at Sooner. (See Pic Barricade) The “Caution” tags offer no description of the hazards present, does not state anything about “de-slagging” being done, or the necessity to obtain the Plant Director’s permission to cross the boundary. (See Pic Tag) With this current practice anyone can cross that boundary with no idea of the hazards. When the tags are printed through SAP the program only allows 40 characters for the description of where to hang the clearance, which hinders the OA from entering anything about the hazards or requirements. The condition of the door was very poor. (See pic Good Door) A thermography survey should be performed every year and 6 weeks before a major outage. When speaking with Sooner’s reliability technician he stated he has never seen an order for that survey. We could not find an order within SAP as well. Our reliability technician contacted the technician he replaced and he stated that he would just go and perform the survey once a year and just knew it had to be done. The survey was last done in 2016. There were no broken procedures or negligence on anyone’s part during this incident. There are some gaps and inconsistencies within the fleet that need to be closed to ensure the safety of everyone during de-slagging. 1. Replace the door and perform a visual inspection during this outage for any more doors that need to be repaired or replaced. 2. Set up a meeting to discuss the changes that need to be made with the other plants that perform de-slagging. 3. Change the current procedure. 4. Communicate the changes with the fleet. 5. Create a PM Order to perform Thermography Survey. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | Houston Mendenhall | Trent Novotny |  |  |  | Frank Brixey |  | Medium | [11 empty] | 12.02.2 Inadequate reparative scheduling of work |  |  |  |  | No PM for thermography survey. | 18. Failure to Check, Monitor | 2. Struck By (Hit By Moving Object) |  | Trent, Excellent investigation. You have been very thorough and worked hard to make sure this doesn't happen again at OGE or any other site where expro is employed. Great Job. | [90 empty] | 9595791
9243 | Sooner Power Plant | 2020-02-18 10:00 | EAI Employee was moving SkyJack SJ45T Manlift towards the west when the basket came in contact with OGE owned Bobcat Skid-steer. The OGE Skid-steer was not in operation at the time of contact. OGE safety witnessed the near miss. There was no damage to either piece of equipment. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | David Willis |  | 2020-02-18 14:21 | 2020-02-18 14:21 | 2020-02-24 09:21 | 2020-03-03 10:00 | 2020-02-18 14:13 | 2020-02-27 11:40 |  |  | Coal Yard |  |  |  |  | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | David Willis |  | EAI employee was moving a aerial lift in the coal yard where it had been parked the previous day to the west at which point it contacted another stationary vehicle a Bobcat Skid-steer which was not in operation at the time. No damage was visible to either piece of equipment. Aerial lift operator was not using a spotter at the time. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Engineering & Planning |  | Brady Sowell | David Willis |  | Donald Wyckoff | I have reviewed the contractor investigation report and supporting documents. I have also had follow up conversations with the contract company safety professional to clarify some details. The contract worker was certified in aerial lift operation with many years experience, the worker was not required to be retrained for this event, contractor has added spotter and 360 to JSA forms, and are looking to develop specific JSA items for when mobile equipment is used. DEW 2/25/2020. | Donald Wyckoff |  | Low |  |  |  | 4.09 Preoccupation with problems | [12 empty] | Contractor was moving Aerial Lift without the use of a spotter. | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | David Willis | [5 empty] | 1. Struck Against (Running or Bumping Into) | Brady Sowell | Zachry | Fidencio Avila |  |  |  | David Willis | [71 empty] | 9590552
9243 | Sooner Power Plant | 2020-02-18 10:00 | EAI Employee was moving SkyJack SJ45T Manlift towards the west when the basket came in contact with OGE owned Bobcat Skid-steer. The OGE Skid-steer was not in operation at the time of contact. OGE safety witnessed the near miss. There was no damage to either piece of equipment. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | David Willis |  | 2020-02-18 14:21 | 2020-02-18 14:21 | 2020-02-24 09:21 | 2020-03-03 10:00 | 2020-02-18 14:13 | 2020-02-27 11:40 |  |  | Coal Yard |  |  |  |  | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | David Willis |  | EAI employee was moving a aerial lift in the coal yard where it had been parked the previous day to the west at which point it contacted another stationary vehicle a Bobcat Skid-steer which was not in operation at the time. No damage was visible to either piece of equipment. Aerial lift operator was not using a spotter at the time. |  |  |  | Sooner Power Plant | FALSE |  | TRUE | Engineering & Planning |  | Brady Sowell | David Willis |  | Donald Wyckoff | I have reviewed the contractor investigation report and supporting documents. I have also had follow up conversations with the contract company safety professional to clarify some details. The contract worker was certified in aerial lift operation with many years experience, the worker was not required to be retrained for this event, contractor has added spotter and 360 to JSA forms, and are looking to develop specific JSA items for when mobile equipment is used. DEW 2/25/2020. | Donald Wyckoff |  | Low |  |  |  | 4.04 Routine, monotony, demand for uneventful vigilance | [12 empty] | Contractor was moving Aerial Lift without the use of a spotter. | 16. Failure to Follow Procedure, Policy, Practice | 1. Struck Against (Running or Bumping Into) | [5 empty] | Property Damage |  | David Willis | [5 empty] | 1. Struck Against (Running or Bumping Into) | Brady Sowell | Zachry | Fidencio Avila |  |  |  | David Willis | [71 empty] | 9590552
9244 | Horseshoe Lake Power Plant | 2020-02-18 09:00 | Contractors inside the storage tank witnessed steam coming from the suction piping. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Wade Gabbert |  | 2020-02-18 14:47 | 2020-02-18 14:47 |  | 2020-03-03 09:00 | 2020-02-18 09:00 |  |  |  | Horseshoe Lake Power Plant Unit 6 Deaerator storage tank. |  |  |  |  | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | [6 empty] | Horseshoe Lake Power Plant | FALSE |  | TRUE | Maintenance |  | Billy Gladden | Wade Gabbert |  |  |  | Daniel Perry |  | Low | [24 empty] | Clearance / LOTO |  | Wade Gabbert | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Billy Gladden | Thielsch | Alex Fink |  |  |  | Tiana Cradduck
9245 | Muskogee Power Plant | 2020-02-18 15:00 | While traveling back from holding ponds the window on the sky track came open causing the window to shatter. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Jerry Knight |  | 2020-02-18 15:35 | 2020-02-18 15:34 | 2020-02-18 16:30 | 2020-03-03 15:00 | 2020-02-18 15:10 |  |  |  | Muskogee power plant Traveling north on the south side of plant coming back from holding ponds |  |  |  |  | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Jerry Knight |  | Driving back to the plant from holding pond the wind was blowing along with a poor designed window latch the window came open and allowed the window to hit the side of skytrack causing window to shatter. saying bad design this is the third window replaced on this piece of equipment. |  |  |  | Muskogee Power Plant | FALSE |  | FALSE | Maintenance |  | James Greathouse | Jerry Knight |  |  |  | Andy Hedge |  | Low | [9 empty] | 10.03 Inadequate standards, specifications and/or design criteria | [6 empty] | The latch on the window failed to hold the window in place. | 23. Defective Tools, Equipment or Materials | 1. Struck Against (Running or Bumping Into) | [68 empty] | window was shattered | 500 | James Greathouse | Industrial/Heavy Equipment |  | F34-787
9247 | Metro Service Center | 2020-02-17 06:30 | Failure to secure load before mobilizing. Crew leaving yard looses load causing following truck to crush OGE material component resulting in a property damage. | Level 3 |  | FALSE | Contractor | Andrea Dennis | William Young | Investigate, establish causal factors and CA's. | 2020-02-20 11:05 | Power Delivery | Jeremy Renfro |  | 2020-02-19 13:21 | 2020-02-19 13:21 |  | 2020-03-02 06:30 | 2020-02-19 13:11 |  |  |  | Imperium Utility Services show up yard located in Alma AR. |  |  |  |  | T&D Ops |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  |  | Jeremy Renfro | Marcus Huddleston |  | Metro Service Center | FALSE |  | FALSE | Resource Planning & Coord |  | Jeremy Renfro | Jeremy Renfro |  |  |  | John Legg |  | High | [24 empty] | Property Damage |  | Jeremy Renfro | Trip Saver crushed |  |  |  |  | 2. Struck By (Hit By Moving Object) | Jeremy Renfro | Imperium Utility Services | Tim Martinez |  | Portable Tool |  | Jeremy Renfro |  |  |  |  | FALSE
9248 | Horseshoe Lake Power Plant | 2020-02-19 11:00 | An oil cooler LOTO was returned on 8B Main Turbine Oil Cooler. The cooler was placed in service to inspect the cooler head for leaks. A plug was left out of the side of the oil cooler causing oil to spray out after the oil pump was started. No member injuries occurred as a result of this incident. | Level 2 |  | TRUE | Member Injury |  |  |  |  | Power Supply | Jon Harriet |  | 2020-02-19 15:18 | 2020-02-19 15:18 |  | 2020-03-04 11:00 | 2020-02-19 14:55 |  |  |  | Horseshoe Lake Unit 8 Main Turbine Oil Reservoir |  |  |  |  | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE |  |  | A LOTO was being hung on 8B Main Lube Oil Cooler to repair a leaking head. This required all the oil to be pumped out of the cooler. Operations were in the process of hanging the LOTO and the mechanic that was going to take the LOTO wanted to verify that the cooler was completely drained. He had an experience in the past where not verifying this was a mistake. He discussed with operations about taking the plug out so he could verify the oil was completely pumped out and also felt that pulling the plug would allow the pumping out process to be more efficient, since most valves were LOTO'd out already, it would work well as a vent. He went to the shop to get a wrench and proceeded to pull the plug. He laid his wrench and plug on the roll around work table at the job site. At some point this mechanic was pulled off the job and given another job to work on and two new mechanics completed the repair. The LOTO was signed off for operations to put back in service to verify the head of the cooler was no longer leaking. The operations crew that had hung the LOTO was off so a new crew had come on shift that would remove the LOTO and place the system in service. 2 AO's were at the cooler for start up. When the oil system was started is when it was discovered that the plug was not put back in. The oil system was immediately shut down. The foreman stopped the job, made notifications and began investigating why the plug was out.The plug is located on the side of the top cooler approximately 8' high. The job had begun on January 27, 2020 and the head had been removed for more than two weeks before it was repaired. Prior to the head removal, the plug to the oil side of the cooler was removed to vent the cooler while it was draining and to visually ensure that oil was completely drained. The members whom had originally removed the head were involved with other projects when it came time for it to be returned and put back in service. The re-installation of equipment was performed by members different than that of whom performed the head removal. Upon completing the head installation, the members signed off the LOTO and notified the PAE that they had finished the job. The LOTO was then signed off by all other members that were involved in this project including the PAE. On February 19, 2020 8B Main Turbine Oil Cooler LOTO 8146732 was returned. The cooler was then placed in service in order to check the cooler head for leaks. The oil pump was started and oil began to spray out of the side of the cooler. It was discovered that a plug on the upper South West side of the cooler had been left out. The oil pump was immediately removed from service and the oil flow was swapped back to 8A oil cooler. Additional steps were taken to prevent the oil from entering the floor drain sump. It is estimate that approximately fifty gallons of oil was spilled on the floor. The PAE stated that he had removed the plug from the side of the heater while operators were pumping the oil out to make sure it drained completely. PAE stated that he had left the plug and the wrench on the roll around work platform beside the cooler. PAE said they removed the head of the cooler and didn’t know why he hadn’t put the plug back in. He said he thought he would have remembered if he had re-installed the head. Findings: • We did not have a greenlighted template for this equipment LOTO. One was made, verified and approved for this project. • The members performing repairs/maintenance at the beginning (removing heads) were not the same employees reinstalling head. • There was minimal communication from one member to the other regarding project status/briefing when job was handed off from one member to another. • There was not a checklist or JHA available for this job. • Oil spill was cleaned contained immediately and cleaned up as soon as safely possible. |  |  |  | Horseshoe Lake Power Plant | FALSE |  | TRUE | Operations |  | Jon Harriet | Jon Harriet |  |  |  | Michael Kennedy |  | Medium | [15 empty] | 16.09 Inadequate communication due to job turnover | The PAE stated that he had removed the plug from the side of the cooler while operators were pumping the oil out to make sure it drained completely. He said that he had left the plug and the wrench on the roll around work platform beside the cooler. He said they removed the head of the cooler and didn’t know why he hadn’t put the plug back in. He said he thought he would have remembered if he had re-installed the head. | 16. Failure to Follow Procedure, Policy, Practice | 2. Struck By (Hit By Moving Object) | [92 empty] | 9595520
9249 | Seminole PP; EGX Gath/Trans | 2020-02-14 14:00 | Operating Authority did not call TCC system operator for direction to operate switch 343. All switching steps were performed in order. No injuries or property damage occurred. | Level 3 |  | FALSE | System Operational Incident | Donnie Jones | Jesse Murray | .Jesse, I would like for Paul Schoelen to lead the investigation with Drew Walker from TCC and Chrysty Dorsey from Safety as team members. Thank you, Scott Lee | 2020-02-24 19:48 | Power Supply | Paul Schoelen |  | 2020-02-19 16:31 |  |  | 2020-03-27 14:00 | 2020-02-14 16:00 |  |  |  | SMPP |  |  |  |  | Power Supply |  | Level 3 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE |  |  |  | Chrysty Dorsey | Paul Schoelen |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | Operations |  | Brandon Wood | Paul Schoelen |  |  |  | Scott Lee |  | High
9249 | Seminole PP; EGX Gath/Trans | 2020-02-14 14:00 | Operating Authority did not call TCC system operator for direction to operate switch 343. All switching steps were performed in order. No injuries or property damage occurred. | Level 3 |  | FALSE | System Operational Incident | Donnie Jones | Jesse Murray | .Jesse, I would like for Paul Schoelen to lead the investigation with Drew Walker from TCC and Chrysty Dorsey from Safety as team members. Thank you, Scott Lee | 2020-02-24 19:48 | Power Supply | Paul Schoelen |  | 2020-02-19 16:31 |  |  | 2020-03-27 14:00 | 2020-02-14 16:00 |  |  |  | SMPP |  |  |  |  | Power Supply |  | Level 3 | System Operational Incident |  | FALSE | FALSE | FALSE |  | TRUE | FALSE |  |  |  | Drew Walker | Paul Schoelen |  | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | Operations |  | Brandon Wood | Paul Schoelen |  |  |  | Scott Lee |  | High
9250 | West Service Center | 2020-02-19 10:00 | While member was descending pole he felt discomfort in his left bicep. | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Joshua Robertson | 2020-02-27 07:52 | 2020-02-20 06:53 | 2020-02-20 06:53 | 2020-02-26 13:29 | 2020-03-04 10:00 | 2020-02-20 06:44 |  |  |  | 5928 N Prospect, Oklahoma City Oklhoma |  |  | Luke Kennedy | Check workflow comment for additional specifics of incident. Approved 2/27/20 | T&D Ops |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | [5 empty] | FALSE | West Service Center | FALSE |  | FALSE | Construction Services |  | Sean Bowen | Joshua Robertson |  |  |  | Terry Garrett |  | Low | [45 empty] | FALSE |  |  | 2008-01-07 | 1976-12-24 |  | 2020-02-19 07:00 | 0 | 0 |  | FALSE |  | Member felt discomfort in left arm when descending pole. |  |  | Sean Bowen |  | First Aid | Sean Bowen |  |  |  |  | Sprain/Strain |  | FALSE |  | Foreman Construction | Arm |  |  |  | Joshua Robertson |  |  | 2/19/2020 7:00:00 AM |  | FALSE |  |  | strain while climbing
9251 | Shawnee Service Center | 2020-02-20 10:30 | Fence was found damaged from vehicle backing into it. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Delivery | Mark Martin |  | 2020-02-20 14:41 | 2020-02-20 14:41 |  | 2020-03-05 10:30 | 2020-02-20 14:39 |  |  |  | West End of Pole Yard |  |  |  |  | T&D Ops |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | [6 empty] | Shawnee Service Center | FALSE |  | FALSE | Construction Services |  | Berry Davis | Mark Martin |  |  |  | Terry Garrett |  | Low | [87 empty] | top rail and vertical post damaged | 1000 |  | Vehicle (not related to operation of vehicle)
9252 | Sooner Power Plant | 2020-02-19 15:00 | While performing NDE on lifting eyes prior to rigging. Contractor was observed wearing fall protection but not tied off while on top of cross-over piping. | Level 3 |  | TRUE | Contractor | Donnie Jones |  |  |  | Power Supply | Kelly Casey |  | 2020-02-20 15:41 | 2020-02-20 15:41 |  | 2020-03-04 15:00 | 2020-02-20 09:30 |  |  |  | Sooner Power Plant Unit 2 Turbine Cross Over |  |  |  |  | Power Supply |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | [6 empty] | Sooner Power Plant | FALSE |  | TRUE | Power Supply Services |  | Brady Sowell | Kelly Casey |  |  |  | Brian Huckabay |  | High | [24 empty] | Injury / Illness |  | Kelly Casey | [5 empty] | 3. Fall from Elevation to Lower Level | Brady Sowell | Tulsa Gamma Ray | Darren Sloan |  |  |  | Justin Buchanan
9253 | Sooner Power Plant | 2020-02-20 19:30 | Smoke reported in Dumper control Room. Embers falling from drop ceiling and embers in wall near receptacle. Fire department called. | Level 3 |  | FALSE | Property Damage | Donnie Jones | Jesse Murray | We propose Glen Hughes to lead, Pate Hamby to represent the project and Ashley Harris as the safety professional. Kent Wilson | 2020-02-24 19:55 | Power Supply | Daniel Dickinson |  | 2020-02-20 19:58 | 2020-02-20 19:58 |  | 2020-03-05 19:30 | 2020-02-20 19:52 |  |  |  | Sooner PP, Dumper control room |  |  |  |  | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE |  |  |  | Pete Hamby | Glen Hughes |  | Sooner Power Plant | FALSE |  | FALSE | Fuel Supply |  | Daniel Dickinson | Daniel Dickinson |  |  |  | Glen Hughes |  | High | [87 empty] | Drop Ceiling, walls, and equipment damaged initially from smoldering coal on drop ceiling and walls. Fire Department arrived and put the smoldering coal out using F500 and water. Most of the damage was created from the water being used to stop the smoldering coal. | 300000 | Daniel Dickinson | Fire
9253 | Sooner Power Plant | 2020-02-20 19:30 | Smoke reported in Dumper control Room. Embers falling from drop ceiling and embers in wall near receptacle. Fire department called. | Level 3 |  | FALSE | Property Damage | Donnie Jones | Jesse Murray | We propose Glen Hughes to lead, Pate Hamby to represent the project and Ashley Harris as the safety professional. Kent Wilson | 2020-02-24 19:55 | Power Supply | Daniel Dickinson |  | 2020-02-20 19:58 | 2020-02-20 19:58 |  | 2020-03-05 19:30 | 2020-02-20 19:52 |  |  |  | Sooner PP, Dumper control room |  |  |  |  | Power Supply |  | Level 3 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE |  |  |  | Ashley Harris | Glen Hughes |  | Sooner Power Plant | FALSE |  | FALSE | Fuel Supply |  | Daniel Dickinson | Daniel Dickinson |  |  |  | Glen Hughes |  | High | [87 empty] | Drop Ceiling, walls, and equipment damaged initially from smoldering coal on drop ceiling and walls. Fire Department arrived and put the smoldering coal out using F500 and water. Most of the damage was created from the water being used to stop the smoldering coal. | 300000 | Daniel Dickinson | Fire
9254 | Horseshoe Lake Power Plant | 2020-02-19 12:00 | WHILE REMOVING FLANGE BOLTS WITH A MATBO GRINDER THE MEMBER NICKED THE GASKET WICH WAS ACM. NO INJURY OR EXPOSURE | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Wade Gabbert |  | 2020-02-21 12:58 | 2020-02-21 12:58 |  | 2020-03-04 11:00 | 2020-02-19 12:00 |  |  |  | HLS UNIT 6 DEAERATOR |  |  |  |  | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | [6 empty] | Horseshoe Lake Power Plant | TRUE |  | TRUE | Power Supply Services |  | Billy Gladden | Wade Gabbert |  |  |  | Daniel Perry |  | Medium | [24 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Wade Gabbert | [5 empty] | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | Billy Gladden | ZACHRY | TBD |  |  |  | Tiana Cradduck
9255 | River Valley | 2020-02-20 00:30 | During unit operation, the unit was fed some wet coal that plugged the coal chute to the combustor. This coal started to combust in the coal chute. The coal combustion was confined to the coal chute. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Timothy Chancellor |  | 2020-02-21 16:02 | 2020-02-21 16:02 |  | 2020-03-05 00:30 | 2020-02-20 07:30 |  |  |  | River Valley PP Unit 2 Coal Chutes |  |  |  |  | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | [6 empty] | River Valley | FALSE |  | FALSE | Operations |  | Raymond Bowen | George Haney |  |  |  | George Haney |  | Low | [87 empty] | Coal chute gaskets were damaged by the heat and must be replaced. Coal chute must also be cleaned. | 3000 | Raymond Bowen | Fire
9256 | Sooner Power Plant | 2020-02-21 13:30 | Member was sticking head into manway to verify position of SOFA damper. As he was crossing the plain his hardhat knocked a piece of rust off into his left eye. Member was treated and released to full duty. | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Supply | William Cash |  | 2020-02-21 16:22 | 2020-02-21 16:22 |  | 2020-03-06 13:30 | 2020-02-21 16:10 |  |  |  | Sooner Unit 2 Boiler level 7.5 |  |  |  |  | Power Supply |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | [5 empty] | FALSE | Sooner Power Plant | FALSE |  | FALSE | Maintenance |  | Ty Goodno | William Cash |  |  |  | Frank Brixey |  | Medium |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Members failed to recognize the hazard of the rust on the sealing surface of the manway cover. | 17. Failure to Identify Hazard, Risk | 2. Struck By (Hit By Moving Object) | [26 empty] | FALSE |  | Other Recordable Cases (J) No days away from work, job transfer or restriction | 2018-11-05 | 1990-12-21 |  | 2020-02-21 07:00 | 0 | 0 | Member flushed eye in eyewash station. | FALSE |  | Member was crossing the plain of a manway to verify sofa duct position and his hard hat dislodged a piece of rust that fell into his eye. |  | TRUE | Ty Goodno |  | Recordable | Ty Goodno | TRUE |  |  |  | Foreign Body |  | TRUE |  | I&C Technician I | Eye | Injury | Left | TRUE | William Cash | TRUE | 2020 | 2/21/2020 7:00:00 AM |  | TRUE | FALSE | FALSE | Piece of rust.
9257 | Sooner Power Plant | 2020-02-22 11:30 | Contractor (West Virginia Electric) removed a 2 foot corner section of mid rail and top rail on scaffold. No injuries and no property damage. | Level 2 |  | TRUE | Contractor |  |  |  |  | OG&E Corp Services | Ashley Harris |  | 2020-02-22 14:43 | 2020-02-22 14:43 |  | 2020-03-07 11:30 | 2020-02-22 13:47 |  |  |  | Sooner Power Plant- Unit 2 old ID fan pedestal. |  |  |  |  | UTS |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  | Safety Stand Down- 2.22.2020 1:30PM |  |  |  | Sooner Power Plant | FALSE |  | TRUE | UTS - Capital Projects |  | Ashley Harris | Ashley Harris |  |  |  | Robert Weaver |  | Medium | [24 empty] | Injury / Illness |  | Ashley Harris | [5 empty] | 9. Abnormal Operation | Ashley Harris | Wolf Point Engineers | WVE |  |  |  | Ashley Harris
9258 | General Service Center | 2020-02-24 09:00 | Member exited I-35 Northbound on to service road at 29th street. As he pulled up to light there were two cars in front of him. He waited at light to turn for two different light changes before realizing the front car was stalled. He then attempted to move over to middle lane to go around the stalled vehicle. As he was doing so a public vehicle pulled up in right lane to crosswalk. Member swung to far to the right making contact with public vehicle on driver side rear quarter. | Level 2 |  | FALSE | Vehicle |  |  |  |  | OGE Energy Corp | Charles Shetley |  | 2020-02-24 10:23 | 2020-02-24 10:23 |  | 2020-03-09 09:00 | 2020-02-24 09:46 |  |  |  | Intersection of I-35 service Rd and 29th street. |  |  |  |  | Enterprise Services |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | [6 empty] | General Service Center | FALSE |  | FALSE | Supply Chain |  | Christian Britton | Charles Shetley |  |  |  | Dustin Nimmo |  | Medium | [93 empty] | TRUE |  | Oklahoma City | OGE Vehicle Struck Other Vehicle | Both Vehicles Moving | 2018-11-04 18:00 |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Rain
9258 | General Service Center | 2020-02-24 09:00 | Member exited I-35 Northbound on to service road at 29th street. As he pulled up to light there were two cars in front of him. He waited at light to turn for two different light changes before realizing the front car was stalled. He then attempted to move over to middle lane to go around the stalled vehicle. As he was doing so a public vehicle pulled up in right lane to crosswalk. Member swung to far to the right making contact with public vehicle on driver side rear quarter. | Level 2 |  | FALSE | Vehicle |  |  |  |  | OGE Energy Corp | Charles Shetley |  | 2020-02-24 10:23 | 2020-02-24 10:23 |  | 2020-03-09 09:00 | 2020-02-24 09:46 |  |  |  | Intersection of I-35 service Rd and 29th street. |  |  |  |  | Enterprise Services |  | Level 2 | Vehicle |  | FALSE | FALSE | FALSE |  | FALSE | TRUE | [6 empty] | General Service Center | FALSE |  | FALSE | Supply Chain |  | Christian Britton | Charles Shetley |  |  |  | Dustin Nimmo |  | Medium | [93 empty] | TRUE |  | Oklahoma City | OGE Vehicle Struck Other Vehicle | Both Vehicles Moving |  |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Rain
9259 | Durant Service Center | 2020-02-22 23:30 | Member had pulled some 4/0 underground wire out of backyard by hand and began experiencing pain in lower abdomen the following morning. The work was performed from 11 pm to approximately 3 am. | Level 1 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Jeremy Mullens |  | 2020-02-24 15:05 | 2020-02-24 15:05 | 2020-02-24 15:12 | 2020-03-07 23:30 | 2020-02-24 14:53 |  |  |  | 1723 Maple St. Durant Ok, |  |  |  |  | T&D Ops |  | Level 1 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE | [5 empty] | FALSE | Durant Service Center | FALSE |  | FALSE | Construction Services |  | Shad Barnett | Jeremy Mullens |  |  |  | Kenneth McKinzie |  | Low | [45 empty] | FALSE |  |  | 2005-06-13 | 1978-08-08 |  | 2020-02-22 23:00 | 0 | 0 |  | FALSE |  | Pulling 4/0 underground wire |  | FALSE | Shad Barnett |  | First Aid | Shad Barnett |  |  |  |  | Unknown |  | FALSE |  | Lineman | Abdomen |  |  |  | Lyle Just |  |  | 2/22/2020 11:00:00 PM | 15 years | FALSE |  |  | na
9260 | Central District Office | 2020-02-24 15:00 | This is a first aid. Member was using pocket knife to trim excess plastic from electrical cord plug-in, when the knife slipped and cut the pad of his right thumb | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Gerald Smith |  | 2020-02-25 07:50 | 2020-02-25 07:50 |  | 2020-03-09 15:00 | 2020-02-25 07:42 |  |  |  | Tulsa Substation |  |  |  |  | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE |  |  | Member was working on an LTC to remove water from the unit. The last task of the day was to install a heater inside of the LTC to help dry the moisture. This particular LTC was elevated about 15' above ground level. The member, an apprentice, and a journeyman were in a man lift while installing the heater. Member was trying to feed the cord through a hole in the LTC, but the plugin was too large. The member chose to try trimming the access plastic around the plug in to reduce the size. When trimming the plastic, the knife slipped and cut the members thumb. |  |  | FALSE | Central District Office | FALSE |  | FALSE | PD Operations Services |  | Taylor Barnett | Gerald Smith |  |  |  | James Hutchison |  | Medium | [12 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | member chose the wrong tool for the job | 19. Failure to React, Correct | 8. Contact With (Electricity, Heat, Cold, Radiation, Caustics, Toxics, Biological, Noise) | [26 empty] | FALSE |  |  | 2018-03-12 | 1995-08-03 |  | 2020-02-24 07:00 | 0 | 0 |  | FALSE |  | when trimming excess plastic of the plug-in on an electric cord, the knife slipped and cut the pad on the members right thumb |  |  | Taylor Barnett |  | First Aid | Taylor Barnett | TRUE |  | Mcbride | Estep | Laceration |  | FALSE |  | Substation Maint Tech Appr | Thumb (1) |  | Right | FALSE | William Fisher | FALSE |  | 2/24/2020 7:00:00 AM | .5 | TRUE | FALSE | FALSE | personal pocket knife | placing a heater inside a LTC to eliminate moisture inside the equipment, and running the cord outside the cabinet
9260 | Central District Office | 2020-02-24 15:00 | This is a first aid. Member was using pocket knife to trim excess plastic from electrical cord plug-in, when the knife slipped and cut the pad of his right thumb | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Gerald Smith |  | 2020-02-25 07:50 | 2020-02-25 07:50 |  | 2020-03-09 15:00 | 2020-02-25 07:42 |  |  |  | Tulsa Substation |  |  |  |  | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE |  |  | Member was working on an LTC to remove water from the unit. The last task of the day was to install a heater inside of the LTC to help dry the moisture. This particular LTC was elevated about 15' above ground level. The member, an apprentice, and a journeyman were in a man lift while installing the heater. Member was trying to feed the cord through a hole in the LTC, but the plugin was too large. The member chose to try trimming the access plastic around the plug in to reduce the size. When trimming the plastic, the knife slipped and cut the members thumb. |  |  | FALSE | Central District Office | FALSE |  | FALSE | PD Operations Services |  | Taylor Barnett | Gerald Smith |  |  |  | James Hutchison |  | Medium |  |  |  |  | 5.01 Lack of experience |  | 7.06 Improper attempt to save time or effort | [9 empty] | using a knife without proper PPE | 16. Failure to Follow Procedure, Policy, Practice | 2. Struck By (Hit By Moving Object) | [26 empty] | FALSE |  |  | 2018-03-12 | 1995-08-03 |  | 2020-02-24 07:00 | 0 | 0 |  | FALSE |  | when trimming excess plastic of the plug-in on an electric cord, the knife slipped and cut the pad on the members right thumb |  |  | Taylor Barnett |  | First Aid | Taylor Barnett | TRUE |  | Mcbride | Estep | Laceration |  | FALSE |  | Substation Maint Tech Appr | Thumb (1) |  | Right | FALSE | William Fisher | FALSE |  | 2/24/2020 7:00:00 AM | .5 | TRUE | FALSE | FALSE | personal pocket knife | placing a heater inside a LTC to eliminate moisture inside the equipment, and running the cord outside the cabinet
9260 | Central District Office | 2020-02-24 15:00 | This is a first aid. Member was using pocket knife to trim excess plastic from electrical cord plug-in, when the knife slipped and cut the pad of his right thumb | Level 2 |  | FALSE | Member Injury |  |  |  |  | Power Delivery | Gerald Smith |  | 2020-02-25 07:50 | 2020-02-25 07:50 |  | 2020-03-09 15:00 | 2020-02-25 07:42 |  |  |  | Tulsa Substation |  |  |  |  | T&D Ops |  | Level 2 | Member Injury |  | FALSE | TRUE | FALSE |  | FALSE | FALSE |  |  | Member was working on an LTC to remove water from the unit. The last task of the day was to install a heater inside of the LTC to help dry the moisture. This particular LTC was elevated about 15' above ground level. The member, an apprentice, and a journeyman were in a man lift while installing the heater. Member was trying to feed the cord through a hole in the LTC, but the plugin was too large. The member chose to try trimming the access plastic around the plug in to reduce the size. When trimming the plastic, the knife slipped and cut the members thumb. |  |  | FALSE | Central District Office | FALSE |  | FALSE | PD Operations Services |  | Taylor Barnett | Gerald Smith |  |  |  | James Hutchison |  | Medium |  |  |  |  | 5.06 Lack of situational awareness |  | 7.06 Improper attempt to save time or effort | [9 empty] | using a knife without proper PPE | 16. Failure to Follow Procedure, Policy, Practice | 2. Struck By (Hit By Moving Object) | [26 empty] | FALSE |  |  | 2018-03-12 | 1995-08-03 |  | 2020-02-24 07:00 | 0 | 0 |  | FALSE |  | when trimming excess plastic of the plug-in on an electric cord, the knife slipped and cut the pad on the members right thumb |  |  | Taylor Barnett |  | First Aid | Taylor Barnett | TRUE |  | Mcbride | Estep | Laceration |  | FALSE |  | Substation Maint Tech Appr | Thumb (1) |  | Right | FALSE | William Fisher | FALSE |  | 2/24/2020 7:00:00 AM | .5 | TRUE | FALSE | FALSE | personal pocket knife | placing a heater inside a LTC to eliminate moisture inside the equipment, and running the cord outside the cabinet
9261 | Sooner Power Plant | 2020-02-24 10:00 | Four contract members were picking air volume tank up to upper level of surge bin tower. Two members were from Zachry and two members were from ECA. The ECA members were making the lift because they were the only ones trained to operate the tugger. OGE member noticed from the ground level that member leaning out of doorway was not wearing any fall protection and immediately went up to stop the job. | Level 3 |  | TRUE | Contractor | Donnie Jones | Jesse Murray | Chance Wade, Robert Sharp, Marwah Alfulfulee per Kelly Casey | 2020-02-25 12:10 | Power Supply | Kelly Casey |  | 2020-02-25 08:16 | 2020-02-25 08:16 |  | 2020-03-09 10:00 | 2020-02-25 07:54 |  |  |  | Sooner plant surge bin top elevation crane access doorway |  |  |  |  | Power Supply |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  |  | Marwah Alfulfulee | Chance Wade |  | Sooner Power Plant | FALSE |  | TRUE | Power Supply Services |  | Chance Wade | Kelly Casey |  |  |  | Brian Huckabay |  | High | [24 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 3. Fall from Elevation to Lower Level | Chance Wade | Zachry / EAI | Zachry / EAI |  |  |  | Paul Johnson
9261 | Sooner Power Plant | 2020-02-24 10:00 | Four contract members were picking air volume tank up to upper level of surge bin tower. Two members were from Zachry and two members were from ECA. The ECA members were making the lift because they were the only ones trained to operate the tugger. OGE member noticed from the ground level that member leaning out of doorway was not wearing any fall protection and immediately went up to stop the job. | Level 3 |  | TRUE | Contractor | Donnie Jones | Jesse Murray | Chance Wade, Robert Sharp, Marwah Alfulfulee per Kelly Casey | 2020-02-25 12:10 | Power Supply | Kelly Casey |  | 2020-02-25 08:16 | 2020-02-25 08:16 |  | 2020-03-09 10:00 | 2020-02-25 07:54 |  |  |  | Sooner plant surge bin top elevation crane access doorway |  |  |  |  | Power Supply |  | Level 3 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE |  |  |  | Robert Sharp | Chance Wade |  | Sooner Power Plant | FALSE |  | TRUE | Power Supply Services |  | Chance Wade | Kelly Casey |  |  |  | Brian Huckabay |  | High | [24 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 3. Fall from Elevation to Lower Level | Chance Wade | Zachry / EAI | Zachry / EAI |  |  |  | Paul Johnson
9262 | Shawnee Service Center | 2020-02-24 14:30 | Fleet mechanic was backing up F10-176 (bucket truck) to the north east overhead door at Shawnee garage. The door was shut. The mechanic was going to stop and then open the door and back the truck into the bay. The mechanic herd a noise. He stopped and upon investigation found the bucket trucks jib had made contact with the closed overhead door. The door was damaged, There was no damage to the truck. | Level 2 |  | FALSE | Vehicle |  |  |  |  | OG&E Corp Services | Nathan Gooch |  | 2020-02-25 09:09 | 2020-02-25 09:09 |  | 2020-03-09 14:30 | 2020-02-25 08:56 |  |  |  | The north east overhead door at Shawnee Garage. |  |  |  |  | UTS |  | Level 2 | Vehicle |  | FALSE | FALSE | TRUE |  | FALSE | TRUE | [6 empty] | Shawnee Service Center | FALSE |  | FALSE | UTS - Asset & LC Mgmt |  | Ryan Stafford | Nathan Gooch |  |  |  | Paul Jefferson |  | Medium | [87 empty] | North east overhead door is bent about 3/4 of the way to the top and the door is not operational | 3000 | Ryan Stafford | Structural |  | F10-176 | TRUE |  | Shawnee | Struck Fixed Object | Backing Related | 2018-09-09 19:00 |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Rain
9262 | Shawnee Service Center | 2020-02-24 14:30 | Fleet mechanic was backing up F10-176 (bucket truck) to the north east overhead door at Shawnee garage. The door was shut. The mechanic was going to stop and then open the door and back the truck into the bay. The mechanic herd a noise. He stopped and upon investigation found the bucket trucks jib had made contact with the closed overhead door. The door was damaged, There was no damage to the truck. | Level 2 |  | FALSE | Property Damage |  |  |  |  | OG&E Corp Services | Nathan Gooch |  | 2020-02-25 09:09 | 2020-02-25 09:09 |  | 2020-03-09 14:30 | 2020-02-25 08:56 |  |  |  | The north east overhead door at Shawnee Garage. |  |  |  |  | UTS |  | Level 2 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | TRUE | [6 empty] | Shawnee Service Center | FALSE |  | FALSE | UTS - Asset & LC Mgmt |  | Ryan Stafford | Nathan Gooch |  |  |  | Paul Jefferson |  | Medium | [87 empty] | North east overhead door is bent about 3/4 of the way to the top and the door is not operational | 3000 | Ryan Stafford | Structural |  | F10-176 | TRUE |  | Shawnee | Struck Fixed Object | Backing Related | 2018-09-09 19:00 |  | FALSE |  |  | Day Light |  |  | Concrete/Pavement |  | Rain
9263 | Muskogee Power Plant | 2020-02-25 13:00 | While lowering his tool bag by a rope. His knot gave way dropping his tool bag approximately 7' and hit the floor spilling his tools out. A spotter was at the scene ensuring no foot traffic in the area was in the line of fire while member lowered his tool bag. | Level 1 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Daniel Moffett |  | 2020-02-25 15:25 | 2020-02-25 15:25 | 2020-02-25 15:43 | 2020-03-10 13:00 | 2020-02-25 14:55 |  |  |  | U6 Air receivers |  |  |  |  | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Daniel Moffett |  | JC Trent and Keith Bloomer were working on a elevated house heater by U6 Compressed air receivers off of a previously built scaffolding. When the job was complete JC had Keith climb down and watch for foot traffic while he lowered his tool bag down to the floor ( He chose to do this because a pipe interfered wit his decent with his bag donned on his shoulder). With Keith in place JC tied a quick overhand knot on a piece of rope and started to lower his bag. When the bag passed the decking the knot slipped and his bag and contents fell to the floor. JC then called me to the scene. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Maintenance |  | James Trent | Daniel Moffett |  |  |  | Andy Hedge |  | Low | [12 empty] | 13.01 Inadequate assessment of needs and risks |  |  |  | A improperly tied knot failed | 03. Failure to Secure | 3. Fall from Elevation to Lower Level
9263 | Muskogee Power Plant | 2020-02-25 13:00 | While lowering his tool bag by a rope. His knot gave way dropping his tool bag approximately 7' and hit the floor spilling his tools out. A spotter was at the scene ensuring no foot traffic in the area was in the line of fire while member lowered his tool bag. | Level 1 |  | TRUE | Property Damage |  |  |  |  | Power Supply | Daniel Moffett |  | 2020-02-25 15:25 | 2020-02-25 15:25 | 2020-02-25 15:43 | 2020-03-10 13:00 | 2020-02-25 14:55 |  |  |  | U6 Air receivers |  |  |  |  | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | Daniel Moffett |  | JC Trent and Keith Bloomer were working on a elevated house heater by U6 Compressed air receivers off of a previously built scaffolding. When the job was complete JC had Keith climb down and watch for foot traffic while he lowered his tool bag down to the floor ( He chose to do this because a pipe interfered wit his decent with his bag donned on his shoulder). With Keith in place JC tied a quick overhand knot on a piece of rope and started to lower his bag. When the bag passed the decking the knot slipped and his bag and contents fell to the floor. JC then called me to the scene. |  |  |  | Muskogee Power Plant | FALSE |  | TRUE | Maintenance |  | James Trent | Daniel Moffett |  |  |  | Andy Hedge |  | Low | [12 empty] | 13.02 Inadequate human factors/ergonomics considerations |  |  |  | A improperly tied knot failed | 03. Failure to Secure | 3. Fall from Elevation to Lower Level
9264 | Sooner Power Plant | 2020-02-24 16:10 | On 02/24/2020 Zachry team removed insulation from this piping and found broken heat tracing wires that were found to be hot. They stopped work at that time. James Brasuell, Zachry foreman, called me to report this. I then called Justin Nealis asking for help to identify the heat trace power source and disable same. On 02/25/2020 Trent Long noticed one of these wire ends was arcing to a nearby pipe. Long and Nealis then found the heat trace LOTO point and removed the power. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Curtis Vickery |  | 2020-02-25 16:04 | 2020-02-25 16:04 |  | 2020-03-09 16:10 | 2020-02-25 15:50 |  |  |  | OGE-Sooner U2 Intermittent Blowdown Tank (IBDT) 6" blowdown piping |  |  |  |  | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | [6 empty] | Sooner Power Plant | FALSE |  | FALSE | Engineering & Planning |  | Curtis Vickery | Donald Wyckoff |  |  |  | Donald Wyckoff |  | Medium
9265 | Sooner Power Plant | 2020-02-26 06:00 | When removing U2 exciter house sole plate for the exciter slid off the deck to the level below. Area below was barricaded off with danger barricade. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Kelly Casey |  | 2020-02-26 09:06 | 2020-02-26 09:06 |  | 2020-03-11 06:00 | 2020-02-26 06:30 |  |  |  | Sooner U2 turbine deck exciter house. |  |  |  |  | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | [6 empty] | Sooner Power Plant | FALSE |  | TRUE | Power Supply Services |  | Randy Ellis | Kelly Casey |  |  |  | Brian Huckabay |  | Low | [24 empty] | Exposure (Hazardous Substance, radiation, etc. Do not use in place of Injury, such as Heat.) |  | Kelly Casey | [5 empty] | 3. Fall from Elevation to Lower Level | Randy Ellis | Feild Core | Sebastian Martino |  |  |  | Randy Ellis
9266 | Sooner Power Plant | 2020-02-26 09:00 | EAI member walked through a Zachary red barricade during a journal removal. Zachary member immediately stopped work and notified supervisor. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Trent Novotny |  | 2020-02-26 15:45 | 2020-02-26 15:45 |  | 2020-03-11 09:00 | 2020-02-26 10:30 |  |  |  | Sooner PP Unit 2A Mill |  |  |  |  | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | [6 empty] | Sooner Power Plant | FALSE |  | TRUE | Maintenance |  | James Brasuell | Trent Novotny |  |  |  | Frank Brixey |  | Medium | [24 empty] | Injury / Illness |  | Trent Novotny | [5 empty] | 2. Struck By (Hit By Moving Object) | James Brasuell | EAI | Benancio Olvera |  |  |  | Lance Lantz
9267 | Seminole PP; EGX Gath/Trans | 2020-02-25 17:30 | Road side grass fire on OG&E property | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Paul Schoelen |  | 2020-02-26 15:56 | 2020-02-26 15:56 |  | 2020-03-10 17:30 | 2020-02-25 18:00 |  |  |  | SE side of lake on county road 3540 |  |  |  |  | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE | [6 empty] | Seminole PP; EGX Gath/Trans | FALSE |  | FALSE | Other |  | Timothy Coffey | Paul Schoelen |  |  |  | Scott Lee |  | Low | [87 empty] | Small grass fire | 0 |  | Fire
9268 | Metro Service Center | 2020-02-21 10:00 | Public vehicle came into BHI contractor lane an hit their bucket truck. see attached document. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Delivery | Lewis Wilson |  | 2020-02-27 15:40 | 2020-02-27 15:40 | 2020-02-28 14:16 | 2020-03-06 10:00 | 2020-02-27 15:09 |  |  |  | Traveling south 24th St. Muskogee, ok |  |  |  |  | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | Lewis Wilson |  | Employees were traveling South on 24th street to the OG&E yard and noticed a white truck traveling North bound in their lane of traffic. The BHI driver immediately began slowing down and pull to the edge of the road, then as he saw the white truck was not correcting its lane BHI driver then steered off of the road to avoid contact with the vehicle. (pictures taken of tire tracks made by BHI vehicle) The white truck did not alter its destination and collided with the BHI Company vehicle behind the driver’s side door into the work bed causing damage from immediately behind the cab to the rear tire. Our employees state after the truck came to a complete stop, they exited the vehicle and assessed the situation to their own wellbeing and then went to the driver of the white truck to check on his wellbeing. The driver told them "He was fine”. Employees also both reported smelling alcohol on the driver of the white truck. After they determined all parties were not injured both employees retrieved their phones and called all predetermined authorities that they had previously been trained to following BHI procedure. Stated by employees: 911, Mike Lewis, and Robert Sullivan were contacted within 5 minutes of the accident occurring. Officer Solis Badge# 559 of the Muskogee Police Department then arrived and investigated the accident site. He stated to our employees the Company could obtain a copy of his report at 112 South Third Street Muskogee OK, 74401 Case#2020-6266 Muskogee Police Department /Office phone 918-683-8000. The Company Vehicle was towed to OKC by Morgan Towing 918-683-3776. Employees did state the driver of the white truck was hand cuffed and arrested by Officer Solis for drinking and driving under the influence. After completion of safety investigation at the accident site, both employees were transported to the BHI yard in Oklahoma City by safety representative. Both employees appeared to be in good health and spirits, and we exchanged phone numbers as to contact me if anything in their condition Investigation/Discussion: Upon initial investigation completed by safety this has been determined to be a not at fault (NAF) MVA. The driver of BHI bucket truck performed movement of the truck to try and avoid the collision by the public driver. The event will be shared with BHI employees as Leeson learn to our drivers using defensive driving techniques to minimize the effects of the collision. Throughout the weekend Safety Representative contact BHI employees to ensure that their condition was still good and no medical services were needed. Notifications: BHI Energy T&D Supervision and the safety department were notified by foreman. In addition to the water company and OGE representative. CC: Ken Loynes, Bob Beckman, Max Wolford, Kerney Pipkin, Robert Kevin Sullivan, and Cheyenne Allen Thank you, Tammy Carter T&D Safety Director See attached photos: |  |  |  | Metro Service Center | FALSE |  | FALSE | Resource Planning & Coord |  | Lewis Wilson | John Legg |  |  |  | John Legg |  | Low |  |  |  |  | 5.06 Lack of situational awareness | [11 empty] | Employees were traveling South on 24th street to the OG&E yard and noticed a white truck traveling North bound in their lane of traffic. The BHI driver immediately began slowing down and pull to the edge of the road, then as he saw the white truck was not correcting its lane BHI driver then steered off of the road to avoid contact with the vehicle. (pictures taken of tire tracks made by BHI vehicle) The white truck did not alter its destination and collided with the BHI Company vehicle behind the driver’s side door into the work bed causing damage from immediately behind the cab to the rear tire. Our employees state after the truck came to a complete stop, they exited the vehicle and assessed the situation to their own wellbeing and then went to the driver of the white truck to check on his wellbeing. The driver told them "He was fine”. Employees also both reported smelling alcohol on the driver of the white truck. After they determined all parties were not injured both employees retrieved their phones and called all predetermined authorities that they had previously been trained to following BHI procedure. Stated by employees: 911, Mike Lewis, and Robert Sullivan were contacted within 5 minutes of the accident occurring. Officer Solis Badge# 559 of the Muskogee Police Department then arrived and investigated the accident site. He stated to our employees the Company could obtain a copy of his report at 112 South Third Street Muskogee OK, 74401 Case#2020-6266 Muskogee Police Department /Office phone 918-683-8000. The Company Vehicle was towed to OKC by Morgan Towing 918-683-3776. Employees did state the driver of the white truck was hand cuffed and arrested by Officer Solis for drinking and driving under the influence. After completion of safety investigation at the accident site, both employees were transported to the BHI yard in Oklahoma City by safety representative. Both employees appeared to be in good health and spirits, and we exchanged phone numbers as to contact me if anything in their condition Investigation/Discussion: Upon initial investigation completed by safety this has been determined to be a not at fault (NAF) MVA. The driver of BHI bucket truck performed movement of the truck to try and avoid the collision by the public driver. The event will be shared with BHI employees as Leeson learn to our drivers using defensive driving techniques to minimize the effects of the collision. Throughout the weekend Safety Representative contact BHI employees to ensure that their condition was still good and no medical services were needed. Notifications: BHI Energy T&D Supervision and the safety department were notified by foreman. In addition to the water company and OGE representative. CC: Ken Loynes, Bob Beckman, Max Wolford, Kerney Pipkin, Robert Kevin Sullivan, and Cheyenne Allen Thank you, Tammy Carter T&D Safety Director | 39. Road Conditions | 2. Struck By (Hit By Moving Object) | [5 empty] | Vehicle |  | Lewis Wilson | [5 empty] | 2. Struck By (Hit By Moving Object) | Lewis Wilson | BHI | Cody Bruce |  |  |  | John Legg |  |  |  |  | FALSE
9269 | Mustang Power Plant | 2020-02-27 15:30 | Contractor was working on red tagged scaffold. There were no injuries. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Timothy Ramey |  | 2020-02-27 17:00 | 2020-02-27 17:00 |  | 2020-03-12 15:30 | 2020-02-27 16:30 |  |  |  | Unit 11 GT enclosure exhaust fans |  |  |  |  | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | [6 empty] | Mustang Power Plant | FALSE |  | TRUE | Other |  | Tanner Brady | Timothy Ramey |  |  |  | William Sanders |  | Medium |  |  | 3.05 Exposure to health hazards |  |  | 6.05 Inadequate review instruction | 7.06 Improper attempt to save time or effort | [9 empty] | Siemen's Contractors climbed on EAI Scaffolding while they were still erecting. The scaffold was red tagged. | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level | [5 empty] | Injury / Illness |  | Timothy Ramey | [5 empty] | 3. Fall from Elevation to Lower Level | Tanner Brady | Seimens | Jess Kelso and Bob Reese |  |  |  | Kristopher Gasaway
9269 | Mustang Power Plant | 2020-02-27 15:30 | Contractor was working on red tagged scaffold. There were no injuries. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Timothy Ramey |  | 2020-02-27 17:00 | 2020-02-27 17:00 |  | 2020-03-12 15:30 | 2020-02-27 16:30 |  |  |  | Unit 11 GT enclosure exhaust fans |  |  |  |  | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | [6 empty] | Mustang Power Plant | FALSE |  | TRUE | Other |  | Tanner Brady | Timothy Ramey |  |  |  | William Sanders |  | Medium |  |  | 3.05 Exposure to health hazards |  |  | 6.02 Inadequate practice | 7.06 Improper attempt to save time or effort | [9 empty] | Siemen's Contractors climbed on EAI Scaffolding while they were still erecting. The scaffold was red tagged. | 17. Failure to Identify Hazard, Risk | 3. Fall from Elevation to Lower Level | [5 empty] | Injury / Illness |  | Timothy Ramey | [5 empty] | 3. Fall from Elevation to Lower Level | Tanner Brady | Seimens | Jess Kelso and Bob Reese |  |  |  | Kristopher Gasaway
9269 | Mustang Power Plant | 2020-02-27 15:30 | Contractor was working on red tagged scaffold. There were no injuries. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Timothy Ramey |  | 2020-02-27 17:00 | 2020-02-27 17:00 |  | 2020-03-12 15:30 | 2020-02-27 16:30 |  |  |  | Unit 11 GT enclosure exhaust fans |  |  |  |  | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | [6 empty] | Mustang Power Plant | FALSE |  | TRUE | Other |  | Tanner Brady | Timothy Ramey |  |  |  | William Sanders |  | Medium | [8 empty] | 9.06 Inadequate work planning or programming | 10.04 Inadequate monitoring of construction | 11.06 Inadequate communication of safety and health data | [5 empty] | Contractor did not wait for scaffold to be complete. | 21. Inadequate Guards or Barriers | 3. Fall from Elevation to Lower Level | [5 empty] | Injury / Illness |  | Timothy Ramey | [5 empty] | 3. Fall from Elevation to Lower Level | Tanner Brady | Seimens | Jess Kelso and Bob Reese |  |  |  | Kristopher Gasaway
9269 | Mustang Power Plant | 2020-02-27 15:30 | Contractor was working on red tagged scaffold. There were no injuries. | Level 2 |  | TRUE | Contractor |  |  |  |  | Power Supply | Timothy Ramey |  | 2020-02-27 17:00 | 2020-02-27 17:00 |  | 2020-03-12 15:30 | 2020-02-27 16:30 |  |  |  | Unit 11 GT enclosure exhaust fans |  |  |  |  | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | [6 empty] | Mustang Power Plant | FALSE |  | TRUE | Other |  | Tanner Brady | Timothy Ramey |  |  |  | William Sanders |  | Medium | [8 empty] | 9.06 Inadequate work planning or programming | 10.05 Inadequate assessment of operational readiness | 11.06 Inadequate communication of safety and health data | [5 empty] | Contractor did not wait for scaffold to be complete. | 21. Inadequate Guards or Barriers | 3. Fall from Elevation to Lower Level | [5 empty] | Injury / Illness |  | Timothy Ramey | [5 empty] | 3. Fall from Elevation to Lower Level | Tanner Brady | Seimens | Jess Kelso and Bob Reese |  |  |  | Kristopher Gasaway
9270 | Sooner Power Plant | 2020-02-27 11:30 | Contract Field Service Engineer for Arvos was exiting the T/G building when he felt a stinging sensation on his neck as he walked through the doorway. No insects were identified after looking, but a sting/bite mark was visible. No first aid applied. | Level 1 |  | TRUE | Contractor |  |  |  |  | Power Supply | Donald Wyckoff |  | 2020-02-28 16:14 | 2020-02-28 16:14 |  | 2020-03-12 11:30 | 2020-02-28 15:59 |  |  |  | Unit 2 Turbine Generator building at South West access doorway. |  |  |  |  | Power Supply |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | [6 empty] | Sooner Power Plant | FALSE |  | TRUE | Engineering & Planning |  | Keith Massar | Donald Wyckoff |  |  |  | Kent Wilson |  | Low
9271 | General Service Center | 2020-02-27 10:00 | Contractor, West Tree Service, rec'd shallow hand cut while pushing limb from vines. First aid. | Level 1 |  | FALSE | Contractor |  |  |  |  | Power Delivery | Elizabeth Mason-Reynolds |  | 2020-02-28 17:26 | 2020-02-28 17:26 |  | 2020-03-12 10:00 | 2020-02-28 17:09 |  |  |  | 7215 Cameron Park Drive, Ft. Smith Arkansas |  |  |  |  | T&D Ops |  | Level 1 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | [6 empty] | General Service Center | FALSE |  | FALSE | Resource Planning & Coord |  | Elizabeth Mason-Reynolds | Elizabeth Mason-Reynolds |  |  |  | Danny Coffey |  | Low | [24 empty] | Injury / Illness |  | Elizabeth Mason-Reynolds |  | one inch shallow cut | FALSE |  |  | 6. Caught On (Snagged, Hung) | Elizabeth Mason-Reynolds | West Tree Service | Walker English | Laceration |  | Hand | Elizabeth Mason-Reynolds | Left | FALSE
9272 | Sooner Power Plant | 2020-02-29 10:30 | Contract member grinding with emery flapper wheel prepping tubes for wall blowers and felt particle enter left eye. | Level 2 |  | FALSE | Contractor |  |  |  |  | Power Supply | Robert Sharp |  | 2020-02-29 13:36 | 2020-02-29 13:36 |  | 2020-03-14 10:30 | 2020-02-29 13:18 |  |  |  | SO 1 Boiler Basement |  |  |  |  | Power Supply |  | Level 2 | Contractor |  | TRUE | FALSE | FALSE |  | FALSE | FALSE | [6 empty] | Sooner Power Plant | FALSE |  | FALSE | Engineering & Planning |  | Robert Sharp | Donald Wyckoff |  |  |  | Donald Wyckoff |  | Medium | [24 empty] | Injury / Illness |  | Robert Sharp |  | Grinding particle in eye | FALSE |  |  | 2. Struck By (Hit By Moving Object) | Robert Sharp | DZ | James Burrow | Foreign Body |  | Eye | Robert Sharp | Left | FALSE
9273 | Sooner Power Plant | 2020-02-29 17:00 | Member was fueling 900 scraper with the quick fill connection. Member did not disconnect the fuel hose before departing and pulled the fuel hose off. | Level 1 |  | FALSE | Property Damage |  |  |  |  | Power Supply | Jeffrey Smith |  | 2020-02-29 17:28 | 2020-02-29 17:28 |  | 2020-03-14 17:00 | 2020-02-29 17:13 |  |  |  | Sooner Coal Yard Equipment fueling station |  |  |  |  | Power Supply |  | Level 1 | Property Damage |  | FALSE | FALSE | TRUE |  | FALSE | FALSE |  |  | Member pulled the scraper up to the east side of the fueling station and hooked up the quick fill fueling hose. After the member did this, he made his was over to the west side on the fueling station to assist another member fueling on that side. Once the other scraper was fueled the member stood on the catwalk of the fueling station and guided him back to make sure he was clear of the fueling station. After the scraper was cleared, member shut off the fuel pump and walked around the west side of the fueling station to the front of 900 scraper. If the member would have walked around the east side of the fuel station, he would have seen that the quick fill connection was still attached to 900 scraper. |  |  |  | Sooner Power Plant | FALSE |  | FALSE | Fuel Supply |  | Tom Sayre | Jeffrey Smith |  |  |  | Glen Hughes |  | Low | [87 empty] | The quick fill mounting bracket from the pump was broken. The fueling hose seems to still be operational. | 200 | Tom Sayre | Fixed Equipment |  | 900
Location: OGE
Sunday, March 01, 2020 2:02:57 AM (UTC-06:00) Central Time (US & Canada) by B J Thompson